## Instructions
AES Indiana Business Rebates & Incentives Program
Chiller Calculators
Welcome. This document has been prepared by CLEAResult.
The purpose of this workbook is to determine the savings from implementing various chiller plant optimization measure. This tool
specifically focuses on chiller system applications for space temperature conditioning. Process chillers cannot be run through this calculator.
The first optimization strategy is a chilled water and/or condenser water reset to a water cooled chilled system with a cooling tower.
The second optimization strategy is installing a waterside economizer to take advantage of free cooling.
Enter all initial parameters on the "Reset Calculator" tab. The necessary items are highlighted in Green.
All required fields must be filled in for savings to be properly displayed.
For technical support on this tool contact custom@aesindianarebates.com.
Chiller Definition Input Fields
Building ID: Enter the Building Identification name or number.
Area Description: Describe the area effected by the chiller resets.
Calculation Year: Enter the year during which the project will be complete.
Weather Station: Choose from the list the closest applicable weather station.
Electricity Rate ($/kWh): Enter the blended average cost of electricity.
Primary Schedule: Enter the daily operating hours of the building for Monday - Sunday
Mechanical Cooling Lockout Temperature: This is the lowest outdoor temperature that the chiller will operate.
Number of Chillers: Choose from the list the number of chiller in the plant (1-2)
Chiller #1 Type: Choose from the list the type of characteristics of chiller 1.
Chiller #2 Type: Choose from the list the type of characteristics of chiller 2.
Chiller Definitions
11 a. Chiller #1: Enter the Rated Tons, kW, and Minimum Part Load Percentage of Chiller #1
11 b. Chiller #2: Enter the Rated Tons, kW, and Minimum Part Load Percentage of Chiller #2
11 c. Maximum Plant Capacity: These values are calculated automatically. No need for user defined values.
11 d. Part Load of CH-1 Capacity When CH-2 Activates: This is the percentage part load of chiller #1 that sequences Chiller #2 to come online.
11 e. Max. Pct. Operating Load: Chillers often do not run a their peak capacity. This is the percentage of total plant load that is used during design conditions.
Primary Chiller Pump Size: Enter the nameplate motor horsepower of the primary chiller pump (pump that circulate water through the chiller). If lead/lag pumps exist only use horsepower from one pump.
Primary Chiller Pump Efficiency: Enter the nameplate efficiency of the condenser pump.
Primary Chiller Pump Power Factor: Enter the nameplate power factor of the condenser pump. If unknown use 0.85.
Condenser Water Pump Size: Enter the nameplate motor horsepower of the condenser water pump. If lead/lag pumps exist only use horsepower from one pump.
Condenser Water Pump Efficiency: Enter the nameplate efficiency of the primary chiller pump.
Condenser Water Pump Power Factor: Enter the nameplate power factor of the condenser pump. If unknown use 0.85.
Condenser Water Pump Type: : Choose from the drop down list the condenser water pump type.
Minimum VFD Operating Pct. or Pct. Of Max Capacity Available at Low Fan Speed: If the condenser water pump is a two-speed pump, enter the percentage the pump operates at low speed. If the condenser water pump is a variable speed pump, enter the minimum operating percentage of the VFD at low loads. Skip this field if the condenser water pump is constant speed.
Cooling Tower Approach to Wet Bulb Temperature: The cooling tower approach is the temperature difference between the condenser water and the outdoor air wet bulb temperature. Typical values are between 7°F and 10°F.
Cooling Tower Fan Type: Choose from the drop down list the cooling tower fan type
Pct. Max Capacity Available at Low Fan Speed: If the cooling tower fan is a two-speed fan, enter the percentage the fan operates at low speed. Skip this field if the cooling tower fan is not a two-speed fan.
Minimum Avg. Pct. of Each Hours Fan(s) Operates: If the cooling tower fan is a two-speed fan or a constant volume fan it may cycle at low loads. If so, enter the percentage of time the fan cycles at the system's lowest operating load. Skip this field if the cooling tower fan is a variable speed fan.
Minimum VFD Operating Pct.: If the cooling tower fan is a variable speed fan, enter the minimum operating percentage of the VFD at low loads. Skip this field if the cooling tower fan is not a variable speed fan.
Cooling Tower Design Load (kW): Enter the combine total rated kW of all cooling tower fans.
Reset Calculator Input Fields
Chilled Water Supply Temperature Setpoint: Enter the system's existing chilled water setpoint temperature.
Condenser Water Supply Setpoint Temperature: Enter the system's existing condenser water setpoint temperature.
Does the CHW Supply Temperature Currently Reset?: Indicate (Yes/No) if there is an existing Chilled Water Reset.
29 a. Chilled Water Supply Temperature StPt - Min.: If there is an existing CHW Reset, indicate the minimum chilled water temperature that the chiller(s) supply.
29 b. Chilled Water Supply Temperature StPt - Max.: If there is an existing CHW Reset, indicate the maximum chilled water temperature that the chiller(s) supply.
30. Does the Condenser Water Supply Temperature Currently Reset?: Indicate (Yes/No) if there is an existing Condenser Water Reset.
31 a. New Condenser Water Supply Temperature StPt - Min.: Indicate the new minimum condenser water temperature supplied to the chiller.
31 b. New Condenser Water Supply Temperature StPt - Max.: Indicate the new maximum condenser water temperature supplied to the chiller.
32 a. Condenser Water Supply Temperature StPt - Min.: If there is an existing CW Reset, indicate the minimum condenser water temperature supplied to the chiller.
32 b. Condenser Water Supply Temperature StPt - Max.: If there is an existing CW Reset, indicate the maximum condenser water temperature supplied to the chiller.
33 a. New Chilled Water Supply Temperature StPt - Min.: Indicate the new minimum chilled water temperature that the chiller(s) supply.
33 b. New Chilled Water Supply Temperature StPt - Max.: Indicate the new maximum chilled water temperature that the chiller(s) supply.
Estimated Cost to Implement this Measure: Enter this estimated implementation cost.
Other Estimated Cost Savings for this Measure ($/Yr.): Enter any additional cost savings that can be justified from the implementation of these resets.
Waterside Economizer Input Fields
Cooling Tower Size: Enter the rated tonnage of the cooling tower.
Wet Bulb High Limit: Enter the wet bulb temperature above which mechanical cooling will be required. Below this wet bulb temperature free cooling can be utilized.
Please Note: This calculator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this calculator is deemed acceptable for the AES Indiana Custom Incentive program. However, the assumptions used by the applicant to calculate the annual savings will be reviewed by the AES Indiana Custom Incentive program, which is solely responsible for the final determination of the annual energy savings to be used in calculating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities.
Incentive amount is calculated based on first year energy savings. The incentives are earned at $0.08 kWh saved. Incentives are limited to a maximum cap of $1,000,000 per project at a service ID and/or building behind a master meter. Total combined custom and prescriptive incentives are capped at $1,000,000 per customer per calendar year.

## Methodology
AES Indiana Business Rebates & Incentives Program
AES Indiana Business Rebates & Incentives Program
Chiller Reset Saving Calculator Methodology | [6 empty] | Waterside Economizer Saving Calculator Methodology
This calculator follows a bin methodology utilizing TMYs Weather Data. The weather file is divided into 2 degree rages and the total hours and each range is calculated. A user defined schedule adjusts the bin hours to only include times when the facility is occupied. The equations displayed below occur at each bin. Each equations occurs for both baseline and proposed conditions. The methodology in each case is the same. | [6 empty] | This calculator estimates the savings potential from installing a waterside economizer on an existing chiller system. The inputs from the Reset Calculator are used to define the chiller systems annual operation and consumption. From this baseline the hour which savings can occur is based on the wetbulb temperature. This calculator follows a bin methodology utilizing TMYs Weather Data. The weather file is divided into 2 degree rages and the total hours and each range is calculated. A user defined schedule adjusts the bin hours to only include times when the facility is occupied. The equations displayed below occur at each bin. Each equations occurs for both baseline and proposed conditions. The methodology in each case is the same. For bins where the outdoor wet bulb temperature is less than the entered wet bulb high limit and the system tonnage is less than the total cooling tower tonnage, savings can be claimed as shown below.
Motor Eff
Where:
Total EnergykWh is the summation of energy consumed by the chiller(s) and the cooling tower
Chiller#1kW is the energy demand of chiller #1 at each bin hour
Chiller#2kW is the energy demand of chiller #2 at each bin hour
CT Fan EnergykW is the energy demand of the cooling tower at each bin hour
Bin Hrs are the amount of hours that occur throughout the year at a given temperature range
Chiller Cycle is the percentage of time the chiller runs at a given bin hours. This is to account for low load conditions were the system load drops below the chiller's min part load. Cycle is determined based off a default balance point temperatures of 60°F which equates to 100% and the mechanical lockout temperature (°F) set by the user equating to 0%. Then the outdoor air temperature is between these two values, the chiller cycles linearly.
Perf Correction (PLR)% is a correction factor taken from DOE-2 chiller energy modeling methodology. The coefficient for the equation vary based on the type of chiller and can be viewed below.
Rated PowerkW is the name plate kW rating of the chiller
DT is temperature difference between condensers water temperature and chilled water temperature at a given bin.
PLR is the part load of the chiller at a given bin.
Corrected Chiller Load is the chiller output in tons multiplied by the Capacity Correction % factor
Chiller Capacity is rated tonnage of the chiller.
Chiller Output is chiller output that directly matches system loading. The system loading is determined based on a linear equation. Peak chiller system load is entered by the user as a percentage of total plant capacity and occurs at the design temperature which is also entered by the user. Minimum chiller operations, a user defined input, occurs at the default balance point temperatures of 60°F. When the outdoor air is in-between the design temperature and the balance point, load ramps linearly.
Capacity Correction % is a correction factor taken from DOE-2 chiller energy modeling methodology. The coefficient for the equation vary based on the type of chiller and can be viewed below.
CWT is the condenser water temperature. This value is constant when no reset exists and ramps linearly between the user defined reset values when reset occurs. During times of reset the highest condenser water temperature will occur at peak outdoor air temperatures and the minimum condenser water temperature will occur as outdoor air temperature approaches the mechanical lockout temperature.
CHWT is the chilled water temperature. This value is constant when no reset exists and ramps linearly between the user defined reset values when reset occurs. During times of reset the minimum chilled water temperature will occur at peak outdoor air temperatures and the maximum chilled water temperature will occur as outdoor air temperature approaches the mechanical lockout temperature.
CT Fans Max Load is cooling tower demand that occurs at each bin.
% Power is a function of the fan curve equation referenced from ASHRAE Standard 90.1 1989 and referenced below.
% Speed is percentage of speed the fan operates at. Constant volume fans operate at 100%, two-speed fans operate at 100% and the low speed percentage defined by the user, and variable speed fans operate between 100% and the user defined minimum percentage varying linearly with system load.
CW Pump HP is the rated nameplate horsepower of the condenser water pump.
Motor Eff is the rated nameplate efficiency of the condenser water/chilled water pump
Power factor is the rated nameplate power factor of the condenser water/chilled water pump
Chiller Pump HP is the rated nameplate horsepower of the chilled water pump.
DOE-2 Chller Performance Curves
Water-cooled
Description | DOE-2 label
Electrical centrifugal | CentH2O
Electrical centrifugal VSD | CentH2OVSD
Electrical reciprocating | RecipH2O (2Comp/Ckt for PLR)
Electric screw | ScrewH2O (2Comp/Ckt for PLR)
Water Cooled Coefficients - from DOE-2
Capacity correction | Capacity Correction (%) = a + b*CHWT + c*CHWT2 + d*CWT + e*CWT2 + f*CHWT*CWT
| Constant | CHWT | CHWT^2 | CWT | CWT^2 | CHWT*CWT
| a | b | c | d | e | f
Electrical centrifugal | -0.49737 | -0.0095607 | -0.00059561 | 0.043521 | -0.00058394 | 0.00096007
Electrical centrifugal VSD | -0.38925 | -0.21951 | -0.00027343 | 0.049748 | -0.00053441 | 0.00067295
Electric reciprocating | 0.64718 | 0.015888 | 0.00010313 | -0.0041667 | 6.69e-06 | -6.418e-05
Electric screw | 0.89823 | 0.0004535 | 0.0002369 | -0.0010475 | -2.93e-05 | -2.035e-05
EIR correction - temp | Performance Correction (%) = a + b*CHWT + c*CHWT2 + d*CWT + e*CWT2 + f*CHWT*CWT
| Constant | CHWT | CHWT^2 | CWT | CWT^2 | CHWT*CWT
| a | b | c | d | e | f
Electrical centrifugal | 1.1536 | -0.030679 | 0.00030591 | 0.0067087 | 5.28e-05 | -9.297e-05
Electrical centrifugal VSD | 1.4287 | -0.082278 | 0.00030243 | 0.036222 | -0.00029211 | 0.00043788
Electric reciprocating | 0.56406 | -0.011463 | 0.00011174 | 0.0080905 | 7.043e-05 | -0.00012635
Electric screw | 0.62494 | -0.00099309 | 0.00017366 | -0.00086447 | 0.00019627 | -0.0003377
EIR correction - PLR | Part Load (PLR) Performance Correction (%) = a + b*PLR + c*PLR2 + d*DT + e*DT2 + f*PLR*DT
(DT between CHWT and CWT)
| Constant | PLR | PLR^2 | DT | DT^2 | PLR*DT
| a | b | c | d | e | f
Electrical centrifugal | 0.2797 | 0.57376 | 0.2569 | -0.0058072 | 0.00014649 | -0.0035301
Electrical centrifugal VSD | 0.14703 | -0.0034967 | 1.0116 | -0.003597 | 0.00027167 | -0.011645
Electric reciprocating | 0.023918 | 0.88947 | 0.077931 | -0.00026357 | 7.2e-06 | 0.00017998
Electric screw | -0.27111 | 1.4901 | -0.33198 | 0.0097534 | -5.891e-05 | -0.0045818
Fan Curve Constants - ASHRAE Standard 90.1-1989 User's Manual
| A | B | C | Min turndown
Constant volume | 1 | 0 | 0 | 100%
Inlet guide vanes | 0.58435 | -0.57917 | 0.97024 | 30%
Riding curve | 0.22714 | 1.1789 | -0.41071 | 45%
Vane axial variable pitch blades | 0.21205 | -0.56929 | 1.3452 | 40%
Variable speed drive | 0.21976 | -0.87478 | 1.6526 | 26%
Note on J60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ben, these charts are images and therefore I can't reformat them. Can you either update the original and replace or send me the file so that I can make the formatting changes?
〖𝐶ℎ𝑖𝑙𝑙𝑒𝑟 #1〗_𝑘𝑊=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑖𝑜𝑛 (%)∗𝑃𝑒𝑟𝑓 𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑖𝑜𝑛 (𝑃𝐿𝑅)%∗𝑃𝑒𝑟𝑓𝑜𝑟𝑚𝑎𝑛𝑐𝑒 𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑖𝑜𝑛 %∗〖𝑅𝑎𝑡𝑒𝑑 𝑃𝑜𝑤𝑒𝑟〗_𝑘𝑊
〖𝑇𝑜𝑡𝑎𝑙 𝐸𝑛𝑒𝑟𝑔𝑦〗_𝑘𝑊ℎ=〖(𝐶ℎ𝑖𝑙𝑙𝑒𝑟#1〗_𝑘𝑊+〖𝐶ℎ𝑖𝑙𝑙𝑒𝑟#2〗_𝑘𝑊+〖𝐶𝑇 𝐹𝑎𝑛 𝐸𝑛𝑒𝑟𝑔𝑦〗_𝑘𝑊)∗Bin Hrs∗Chiller Cycling
𝑃𝑒𝑟𝑓 𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑖𝑜𝑛 (𝑃𝐿𝑅)%= 𝑎 + 𝑏∗𝑃𝐿𝑅 + 𝑐∗𝑃𝐿𝑅2 + 𝑑∗𝐷𝑇 + 𝑒∗𝐷𝑇2 + 𝑓∗𝑃𝐿𝑅∗𝐷𝑇
𝐷𝑇=𝐶𝑊𝑇 −𝐶𝐻𝑊𝑇
𝑃𝐿𝑅=(〖𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑒𝑑 𝐶ℎ𝑖𝑙𝑙𝑒𝑟 𝐿𝑜𝑎𝑑〗_𝑇𝑜𝑛)/(〖𝐶ℎ𝑖𝑙𝑙𝑒𝑟 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦〗_𝑇𝑜𝑛)
𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑒𝑑 𝐶ℎ𝑖𝑙𝑙𝑒𝑟 𝐿𝑜𝑎𝑑=〖𝐶ℎ𝑖𝑙𝑙𝑒𝑟 𝑂𝑢𝑡𝑝𝑢𝑡〗_𝑇𝑜𝑛∗𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑖𝑜𝑛 %
𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑖𝑜𝑛 (%) = 𝑎 + 𝑏∗𝐶𝐻𝑊𝑇 + 𝑐∗𝐶𝐻𝑊𝑇2 + 𝑑∗𝐶𝑊𝑇 + 𝑒∗𝐶𝑊𝑇2 + 𝑓∗𝐶𝐻𝑊𝑇∗𝐶𝑊𝑇
〖𝐶𝑇 𝐹𝑎𝑛 𝐸𝑛𝑒𝑟𝑔𝑦〗_𝑘𝑊=CT Fans Max Load∗% Power
𝑃𝑒𝑟𝑓𝑜𝑟𝑚𝑎𝑛𝑐𝑒 𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑖𝑜𝑛 %= 𝑎 + 𝑏∗𝐶𝐻𝑊𝑇 + 𝑐∗𝐶𝐻𝑊𝑇2 + 𝑑∗𝐶𝑊𝑇 + 𝑒∗𝐶𝑊𝑇2 + 𝑓∗𝐶𝐻𝑊𝑇∗𝐶𝑊𝑇
〖𝐸𝑛𝑒𝑟𝑔𝑦 𝑆𝑎𝑣𝑖𝑛𝑔𝑠〗_𝑘𝑊ℎ=〖𝐶ℎ𝑖𝑙𝑙𝑒𝑟 𝐸𝑛𝑒𝑟𝑔𝑦 𝐴𝑓𝑡𝑒𝑟 𝑅𝑒𝑠𝑒𝑡𝑠〗_𝑘𝑊ℎ−(〖𝐶𝑇 𝐹𝑎𝑛 𝐷𝑒𝑚𝑎𝑛𝑑〗_𝑘𝑊−〖𝐶𝑊 𝑃𝑢𝑚𝑝 𝐷𝑒𝑚𝑎𝑛𝑑〗_( 𝑘𝑊)−〖𝐶ℎ𝑖𝑙𝑙𝑒𝑑 𝑊𝑎𝑡𝑒𝑟 𝑃𝑢𝑚𝑝 𝐷𝑒𝑚𝑎𝑛𝑑〗_𝑘𝑊)∗𝐻𝑜𝑢𝑟𝑠
〖𝐶𝑊 𝑃𝑢𝑚𝑝 𝐸𝑛𝑒𝑟𝑔𝑦〗_𝑘𝑊=%𝑃𝑜𝑤𝑒𝑟∗(𝐶𝑊 𝑃𝑢𝑚𝑝 𝐻𝑃∗0.746)/(𝑀𝑜𝑡𝑜𝑟 𝐸𝑓𝑓 ∗𝑃𝑜𝑤𝑒𝑟 𝐹𝑎𝑐𝑡𝑜𝑟)
〖𝐶ℎ𝑖𝑙𝑙𝑒𝑟 𝑃𝑢𝑚𝑝 𝐸𝑛𝑒𝑟𝑔𝑦〗_𝑘𝑊=(𝐶ℎ𝑖𝑙𝑙𝑒𝑟 𝑃𝑢𝑚𝑝 𝐻𝑃∗0.746)/(𝑀𝑜𝑡𝑜𝑟 𝐸𝑓𝑓 ∗𝑃𝑜𝑤𝑒𝑟 𝐹𝑎𝑐𝑡𝑜𝑟)
% 𝑃𝑜𝑤𝑒𝑟 = 𝐴 + 𝐵 ∗ %𝑆𝑝𝑒𝑒𝑑 + 𝐶 ∗ %𝑆𝑝𝑒𝑒𝑑^2 (% 𝑓𝑙𝑜𝑤 = 𝑡𝑜 % 𝑠𝑝𝑒𝑒𝑑 𝑓𝑜𝑟 𝑉𝑎𝑟𝑖𝑎𝑏𝑙𝑒 𝑆𝑝𝑒𝑒𝑑)

## Chiller Definitions
AES Indiana Custom Incentives Program
Chiller Optimization - Definitions
Input:
Results:
Site Information
1. Building ID:
2. Area Description
3. Calculation Year
4. Weather Station | Indianapolis Intl AP
5. Electricity Rate ($/kWh)
Operating Hours
6. Primary Schedule: | From |  | To
Monday
Tuesday
Wednesday
Thursday
Friday
Saturday
Sunday
Chillers
7. Mechanical Cooling Lockout Temperature (°F)
8. Number of Chillers in Plant
9. Chiller #1 Type
10. Chiller #2 Type
11. Chiller Definitions | Chiller Capacity (tons) | Rated Power at Maximum Capacity (kW) | Minimum Part Load (%Cap) | Rated Efficiency (kW/ton)
a. Chiller #1 | 500 | 450 | 0.1 | 0.9
b. Chiller #2 | 250 | 240 | 0.2 | 0.96
c. Maximum Plant Capacity: | 750 | 690 | 0.1 | 0.92
d. Part Load of CH-1 Capacity When CH-2 Activates: | 0.9
e. Max. Pct. Operating Load | 100%
Pumps
12. Primary Chiller Pump Size (HP)
13. Primary Chiller Pump Efficiency
14. Primary Chiller Pump Power Factor
15. Condenser Water Pump Size (HP)
16. Condenser Water Pump Efficiency
17. Condenser Water Pump Power Factor
18. Condenser Water Pump Type
Cooling Tower
20. Cooling Tower Approach to Wet Bulb Temperature (°F)
21. Cooling Tower Fan Type
22. Pct. of Max Capacity Available at Low Fan Speed
23. Minimum Avg. Pct. of Each Hour Fan(s) Operates
24. Minimum VFD Operating Pct.
25. Cooling Tower Fan Design Load (kW)

## Reset Calculator
AES Indiana Business Rebates & Incentives Program
Chiller Reset Savings Calculator
Color Legend Highlighting
Input:
Results:
Baseline Reset Conditions
26. Chilled Water Supply Temperature Setpoint (°F)
27. Cond. Water Supply Temperature Setpoint (°F)
28. Does the Chilled Water Supply Temperature Currently Reset?
29(a). Chilled Water Supply Temperature StPt - Min. (°F)
29(b). Chilled Water Supply Temperature StPt - Max. (°F)
30. Does the Cond. Water Supply Temp Currently Reset?
31(a). Cond. Water Supply Temperature StPt - Min. (°F)
31(b). Cond. Water Supply Temperature StPt - Max. (°F)
Proposed Reset Conditions
32(a). New Chilled Water Supply Temperature StPt - Min. (°F)
32(b). New Chilled Water Supply Temperature StPt - Max. (°F)
33(a). New Condenser Water Supply Temperature StPt - Min. (°F)
33(b). New Condenser Water Supply Temperature StPt - Max. (°F)
34. Estimated Cost to Implement this Measure
35. Other Estimated Cost Savings for this Measure ($/Yr.)
Energy Consumption Summary
Baseline Energy Consumption (kWh/Yr.) |  | #DIV/0! | Weighted Degrees of Reset
Proposed Energy Consumption (kWh/Yr.) |  | #VALUE! | <---Pct Savings per Setback Degree
Energy Savings (kWh/Yr.) |  | #N/A | EFLH
Energy Cost Savings ($/Yr.)
Eligible Custom Incentive
Incentive is based on:
Simple Payback Period without Incentive (Yrs.)
Simple Payback Period with Incentive (Yrs.)

## Waterside Economizer
AES Indiana Business Rebates & Incentives Program
Waterside Economizer Savings Calculator
Color Legend Highlighting
Input:
Results:
Inputs
37. Cooling Tower Size: |  | Ton
38. Wet Bulb High Limit: |  | F
Calculations & Savings
Total Existing Chiller Run Time | 0 | Hrs.
Potential Recovery Time | 0 | Hrs.
Chiller Plant Existing Annual Consumption |  | kWh
Chiller Plant w/ Economizer Annual Consumption |  | kWh
Cooling Tower Fan Consumption during Economizer Function | 0 | kWh
Cooling Tower Pump Consumption during Economizer Function | 0 | kWh
Est. Waterside Economizer Savings Potential | 0 | kWh

## Bin Calculations (hidden)
[11 empty] | Baseline | [19 empty] | Proposed | [27 empty] | Waterside Economizer Savings | [5 empty] | Energy Savings Totals - All Bins
Bin Temps and System | [10 empty] | Performance Factors |  |  |  |  | Chiller #1 |  |  |  |  | Chiller #2 |  |  |  |  | CT Fan Energy |  |  |  | Total | Performance Factors |  |  |  |  | Chiller #1 |  |  |  |  | Chiller #2 |  |  |  |  | CT Fan Energy |  |  |  |  | Total | Pumps |  |  | Baseline |  | Proposed | [8 empty] | Baseline | Proposed
Dry Bulb Bin | Approx Wet Bulb Temp | Min. CW Supply Temp | Sytem Load Output | Sytem Load % of Max Capacity | Chiller Cycling | Chiller #1 Output | Chiller #2 Output | Bin Hours | Ton-Hr | EFLH | Chilled Water Supply Temp | Condenser Water Supply Temp | DT | Capacity Correction % | Performance Correction % | Corrected Chiller Capacity | Corrected Part Load | Perf. Correction (PLR) % | Chiller Eff | Chiller Power (kW) | Corrected Chiller Capacity | Corrected Part Load | Perf. Correction (PLR) % | Chiller Eff | Chiller Power (kW)) | CT Fan Speed | CT Fan Demand | Time Operating Each Hour | Avg Fan Power Over the Hour | Electric Demand | Chilled Water Supply Temp | Condenser Water Supply Temp | DT | Capacity Correction % | Performance Correction % | Corrected Chiller Capacity | Corrected Part Load | Perf. Correction (PLR) % | Chiller Eff | Chiller Power (kW)) | Corrected Chiller Capacity | Corrected Part Load | Perf. Correction (PLR) % | Chiller Eff | Chiller Power (kW)) | CT Fan Speed | CT Fan Speed Correction | CT Fan Demand | Time Operating Each Hour | Avg Fan Power Over the Hour | Electric Demand | CW Pump Speed | CW Pump Demand | Chiller Pump Demand | Total Elec Energy | Elec Demand | Total Elec Energy | Elec Demand | CT Fan Speed | CT Fan Speed Correction | CT Fan Demand | Cooling Tower Fan | CW Pump | Total Economizer Savings | Hrs | kWh/yr | kWh/yr
(F) | (F) | (F) | tons | (%) | (%) | tons | tons | (hrs.) |  |  | (F) | (F) | (degF) | (%) | (%) | (tons) | (%) | (%) | (kW/ton) | (kW) | (tons) | (%) | (%) | (kW/ton) | (kW) | (%) | (kW) | (%) | (kW) | (kW) | (F) | (F) | (degF) | (%) | (%) | (tons) | (%) | (%) | (kW/ton) | (kW) | (tons) | (%) | (%) | (kW/ton) | (kW) | (%) |  | (kW) | (%) | (kW) | (kW) | (%) | (kW) | (kW) | (kWh) | (kW) | (kWh) | (kW) | (%) |  | (kW) | (kWh) | (kWh) | (kWh) | 0 | #N/A | #N/A
-13 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 |  | Difference: | #N/A
-11 | -9.82 | -9.82 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 |  |  | #N/A
-9 | -8.26 | -8.26 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 |  | #N/A | #N/A
-7 | -6.11 | -6.11 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
-5 | -4.925 | -4.925 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
-3 | -3.4141 | -3.4141 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
-1 | -1.5733 | -1.5733 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
1 | 0.5325 | 0.5325 | 50 | 6.667% | 1.818% | 50 | 0 | 0 | 0 | 0 | 0 | 0.5325 | 0.5325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 0.5325 | 0.5325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
3 | 2.3867 | 2.3867 | 50 | 6.667% | 5.455% | 50 | 0 | 0 | 0 | 0 | 0 | 2.3867 | 2.3867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 2.3867 | 2.3867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
5 | 4.9873 | 4.9873 | 50 | 6.667% | 9.091% | 50 | 0 | 0 | 0 | 0 | 0 | 4.9873 | 4.9873 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 4.9873 | 4.9873 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
7 | 7.2881 | 7.2881 | 50 | 6.667% | 12.73% | 50 | 0 | 0 | 0 | 0 | 0 | 7.2881 | 7.2881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 7.2881 | 7.2881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
9 | 8.8986 | 8.8986 | 50 | 6.667% | 16.36% | 50 | 0 | 0 | 0 | 0 | 0 | 8.8986 | 8.8986 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 8.8986 | 8.8986 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
11 | 10.8862 | 10.8862 | 50 | 6.667% | 20% | 50 | 0 | 0 | 0 | 0 | 0 | 10.8862 | 10.8862 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 10.8862 | 10.8862 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
13 | 12.1167 | 12.1167 | 50 | 6.667% | 23.64% | 50 | 0 | 0 | 0 | 0 | 0 | 12.1167 | 12.1167 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 12.1167 | 12.1167 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
15 | 13.8494 | 13.8494 | 50 | 6.667% | 27.27% | 50 | 0 | 0 | 0 | 0 | 0 | 13.8494 | 13.8494 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 13.8494 | 13.8494 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
17 | 15.7249 | 15.7249 | 50 | 6.667% | 30.91% | 50 | 0 | 0 | 0 | 0 | 0 | 15.7249 | 15.7249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 15.7249 | 15.7249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
19 | 17.4336 | 17.4336 | 50 | 6.667% | 34.55% | 50 | 0 | 0 | 0 | 0 | 0 | 17.4336 | 17.4336 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 17.4336 | 17.4336 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
21 | 19.4477 | 19.4477 | 50 | 6.667% | 38.18% | 50 | 0 | 0 | 0 | 0 | 0 | 19.4477 | 19.4477 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 19.4477 | 19.4477 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
23 | 21.9351 | 21.9351 | 50 | 6.667% | 41.82% | 50 | 0 | 0 | 0 | 0 | 0 | 21.9351 | 21.9351 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 21.9351 | 21.9351 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
25 | 24.3156 | 24.3156 | 50 | 6.667% | 45.45% | 50 | 0 | 0 | 0 | 0 | 0 | 24.3156 | 24.3156 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 24.3156 | 24.3156 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
27 | 26.1737 | 26.1737 | 50 | 6.667% | 49.09% | 50 | 0 | 0 | 0 | 0 | 0 | 26.1737 | 26.1737 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 26.1737 | 26.1737 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
29 | 28.1495 | 28.1495 | 50 | 6.667% | 52.73% | 50 | 0 | 0 | 0 | 0 | 0 | 28.1495 | 28.1495 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 28.1495 | 28.1495 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
31 | 29.923 | 29.923 | 50 | 6.667% | 56.36% | 50 | 0 | 0 | 0 | 0 | 0 | 29.923 | 29.923 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 29.923 | 29.923 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
33 | 31.3769 | 31.3769 | 50 | 6.667% | 60% | 50 | 0 | 0 | 0 | 0 | 0 | 31.3769 | 31.3769 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 31.3769 | 31.3769 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
35 | 32.6309 | 32.6309 | 50 | 6.667% | 63.64% | 50 | 0 | 0 | 0 | 0 | 0 | 32.6309 | 32.6309 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 32.6309 | 32.6309 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
37 | 34.1249 | 34.1249 | 50 | 6.667% | 67.27% | 50 | 0 | 0 | 0 | 0 | 0 | 34.1249 | 34.1249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 34.1249 | 34.1249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
39 | 36.2443 | 36.2443 | 50 | 6.667% | 70.91% | 50 | 0 | 0 | 0 | 0 | 0 | 36.2443 | 36.2443 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 36.2443 | 36.2443 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
41 | 38.3259 | 38.3259 | 50 | 6.667% | 74.55% | 50 | 0 | 0 | 0 | 0 | 0 | 38.3259 | 38.3259 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 38.3259 | 38.3259 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
43 | 40.5339 | 40.5339 | 50 | 6.667% | 78.18% | 50 | 0 | 0 | 0 | 0 | 0 | 40.5339 | 40.5339 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 40.5339 | 40.5339 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
45 | 42.4181 | 42.4181 | 50 | 6.667% | 81.82% | 50 | 0 | 0 | 0 | 0 | 0 | 42.4181 | 42.4181 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 42.4181 | 42.4181 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
47 | 44.3567 | 44.3567 | 50 | 6.667% | 85.45% | 50 | 0 | 0 | 0 | 0 | 0 | 44.3567 | 44.3567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 44.3567 | 44.3567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
49 | 45.7706 | 45.7706 | 50 | 6.667% | 89.09% | 50 | 0 | 0 | 0 | 0 | 0 | 45.7706 | 45.7706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 45.7706 | 45.7706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
51 | 46.8472 | 46.8472 | 50 | 6.667% | 92.73% | 50 | 0 | 0 | 0 | 0 | 0 | 46.8472 | 46.8472 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 46.8472 | 46.8472 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
53 | 48.2498 | 48.2498 | 50 | 6.667% | 96.36% | 50 | 0 | 0 | 0 | 0 | 0 | 48.2498 | 48.2498 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 48.2498 | 48.2498 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
55 | 49.881 | 49.881 | 50 | 6.667% | 100% | 50 | 0 | 0 | 0 | 0 | 0 | 49.881 | 49.881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | 0 | 100% | 0 | #N/A | 0 | 49.881 | 49.881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 6.667% | -93.33% | 0 | 100% | 0 | #N/A | 6.667% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 26.67% | -73.33% | 0 | 0 | 0 | 0
57 | 51.3736 | 51.3736 | 83.3492 | 11.11% | 100% | 83.3492 | 0 | 0 | 0 | 0 | 0 | 51.3736 | 51.3736 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 11.11% | 0 | 100% | 0 | #N/A | 0 | 51.3736 | 51.3736 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 11.11% | -88.89% | 0 | 100% | 0 | #N/A | 11.11% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 31.11% | -68.89% | 0 | 0 | 0 | 0
59 | 54.0588 | 54.0588 | 116.6984 | 15.56% | 100% | 116.6984 | 0 | 0 | 0 | 0 | 0 | 54.0588 | 54.0588 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 15.56% | 0 | 100% | 0 | #N/A | 0 | 54.0588 | 54.0588 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 15.56% | -84.44% | 0 | 100% | 0 | #N/A | 15.56% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 35.56% | -64.44% | 0 | 0 | 0 | 0
61 | 55.9655 | 55.9655 | 150.0476 | 20.01% | 100% | 150.0476 | 0 | 0 | 0 | 0 | 0 | 55.9655 | 55.9655 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 20.01% | 0 | 100% | 0 | #N/A | 0 | 55.9655 | 55.9655 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 20.01% | -79.99% | 0 | 100% | 0 | #N/A | 20.01% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 40.01% | -59.99% | 0 | 0 | 0 | 0
63 | 57.8575 | 57.8575 | 183.3969 | 24.45% | 100% | 183.3969 | 0 | 0 | 0 | 0 | 0 | 57.8575 | 57.8575 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 24.45% | 0 | 100% | 0 | #N/A | 0 | 57.8575 | 57.8575 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 24.45% | -75.55% | 0 | 100% | 0 | #N/A | 24.45% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 44.45% | -55.55% | 0 | 0 | 0 | 0
65 | 59.7528 | 59.7528 | 216.7461 | 28.9% | 100% | 216.7461 | 0 | 0 | 0 | 0 | 0 | 59.7528 | 59.7528 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 28.9% | 0 | 100% | 0 | #N/A | 0 | 59.7528 | 59.7528 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 28.9% | -71.1% | 0 | 100% | 0 | #N/A | 28.9% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 48.9% | -51.1% | 0 | 0 | 0 | 0
67 | 61.6238 | 61.6238 | 250.0953 | 33.35% | 100% | 250.0953 | 0 | 0 | 0 | 0 | 0 | 61.6238 | 61.6238 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 33.35% | 0 | 100% | 0 | #N/A | 0 | 61.6238 | 61.6238 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 33.35% | -66.65% | 0 | 100% | 0 | #N/A | 33.35% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 53.35% | -46.65% | 0 | 0 | 0 | 0
69 | 63.2131 | 63.2131 | 283.4445 | 37.79% | 100% | 283.4445 | 0 | 0 | 0 | 0 | 0 | 63.2131 | 63.2131 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 37.79% | 0 | 100% | 0 | #N/A | 0 | 63.2131 | 63.2131 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 37.79% | -62.21% | 0 | 100% | 0 | #N/A | 37.79% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 57.79% | -42.21% | 0 | 0 | 0 | 0
71 | 65.6742 | 65.6742 | 316.7937 | 42.24% | 100% | 316.7937 | 0 | 0 | 0 | 0 | 0 | 65.6742 | 65.6742 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 42.24% | 0 | 100% | 0 | #N/A | 0 | 65.6742 | 65.6742 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 42.24% | -57.76% | 0 | 100% | 0 | #N/A | 42.24% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 62.24% | -37.76% | 0 | 0 | 0 | 0
73 | 66.2022 | 66.2022 | 350.1429 | 46.69% | 100% | 350.1429 | 0 | 0 | 0 | 0 | 0 | 66.2022 | 66.2022 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 46.69% | 0 | 100% | 0 | #N/A | 0 | 66.2022 | 66.2022 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 46.69% | -53.31% | 0 | 100% | 0 | #N/A | 46.69% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 66.69% | -33.31% | 0 | 0 | 0 | 0
75 | 67.2869 | 67.2869 | 383.4921 | 51.13% | 100% | 383.4921 | 0 | 0 | 0 | 0 | 0 | 67.2869 | 67.2869 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 51.13% | 0 | 100% | 0 | #N/A | 0 | 67.2869 | 67.2869 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 51.13% | -48.87% | 0 | 100% | 0 | #N/A | 51.13% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 71.13% | -28.87% | 0 | 0 | 0 | 0
77 | 68.2655 | 68.2655 | 416.8414 | 55.58% | 100% | 416.8414 | 0 | 0 | 0 | 0 | 0 | 68.2655 | 68.2655 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 55.58% | 0 | 100% | 0 | #N/A | 0 | 68.2655 | 68.2655 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0% | 0 | #N/A | 55.58% | -44.42% | 0 | 100% | 0 | #N/A | 55.58% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 75.58% | -24.42% | 0 | 0 | 0 | 0
79 | 69.8367 | 69.8367 | 450.1906 | 60.03% | 100% | 225.0953 | 225.0953 | 0 | 0 | 0 | 0 | 69.8367 | 69.8367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60.03% | 0 | 100% | 0 | #N/A | 0 | 69.8367 | 69.8367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60.03% | -39.97% | 0 | 100% | 0 | #N/A | 60.03% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 80.03% | -19.97% | 0 | 0 | 0 | 0
81 | 70.0674 | 70.0674 | 483.5398 | 64.47% | 100% | 241.7699 | 241.7699 | 0 | 0 | 0 | 0 | 70.0674 | 70.0674 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 64.47% | 0 | 100% | 0 | #N/A | 0 | 70.0674 | 70.0674 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 64.47% | -35.53% | 0 | 100% | 0 | #N/A | 64.47% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 84.47% | -15.53% | 0 | 0 | 0 | 0
83 | 70.9078 | 70.9078 | 516.889 | 68.92% | 100% | 258.4445 | 258.4445 | 0 | 0 | 0 | 0 | 70.9078 | 70.9078 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 68.92% | 0 | 100% | 0 | #N/A | 0 | 70.9078 | 70.9078 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 68.92% | -31.08% | 0 | 100% | 0 | #N/A | 68.92% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 88.92% | -11.08% | 0 | 0 | 0 | 0
85 | 72.8685 | 72.8685 | 550.2382 | 73.37% | 100% | 275.1191 | 275.1191 | 0 | 0 | 0 | 0 | 72.8685 | 72.8685 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 73.37% | 0 | 100% | 0 | #N/A | 0 | 72.8685 | 72.8685 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 73.37% | -26.63% | 0 | 100% | 0 | #N/A | 73.37% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 93.37% | -6.635% | 0 | 0 | 0 | 0
87 | 73.5143 | 73.5143 | 583.5874 | 77.81% | 100% | 291.7937 | 291.7937 | 0 | 0 | 0 | 0 | 73.5143 | 73.5143 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 77.81% | 0 | 100% | 0 | #N/A | 0 | 73.5143 | 73.5143 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 77.81% | -22.19% | 0 | 100% | 0 | #N/A | 77.81% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 97.81% | -2.188% | 0 | 0 | 0 | 0
89 | 75.3149 | 75.3149 | 616.9366 | 82.26% | 100% | 308.4683 | 308.4683 | 0 | 0 | 0 | 0 | 75.3149 | 75.3149 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 82.26% | 0 | 100% | 0 | #N/A | 0 | 75.3149 | 75.3149 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 82.26% | -17.74% | 0 | 100% | 0 | #N/A | 82.26% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 100% | 0% | 0 | 0 | 0 | 0
91 | 75.8825 | 75.8825 | 650.2859 | 86.7% | 100% | 325.1429 | 325.1429 | 0 | 0 | 0 | 0 | 75.8825 | 75.8825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 86.7% | 0 | 100% | 0 | #N/A | 0 | 75.8825 | 75.8825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 86.7% | -13.3% | 0 | 100% | 0 | #N/A | 86.7% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 100% | 0% | 0 | 0 | 0 | 0
93 | 79.2867 | 79.2867 | 683.6351 | 91.15% | 100% | 341.8175 | 341.8175 | 0 | 0 | 0 | 0 | 79.2867 | 79.2867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 91.15% | 0 | 100% | 0 | #N/A | 0 | 79.2867 | 79.2867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 91.15% | -8.849% | 0 | 100% | 0 | #N/A | 91.15% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 100% | 0% | 0 | 0 | 0 | 0
95 | 80.68 | 80.68 | 716.9843 | 95.6% | 100% | 358.4921 | 358.4921 | 0 | 0 | 0 | 0 | 80.68 | 80.68 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 95.6% | 0 | 100% | 0 | #N/A | 0 | 80.68 | 80.68 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 95.6% | -4.402% | 0 | 100% | 0 | #N/A | 95.6% | 0 | #DIV/0! | #N/A | 0 | #N/A | 0 | 100% | 0% | 0 | 0 | 0 | 0
97 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
99 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
101 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
103 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
105 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
107 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
109 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
111 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
113 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
Note on C4: The wet bulb temp is determined by the mean coincident wet bulb at each dry bulb bin for the specific schedule selected. It is generated with a macro and pasted here.
Note on AF4: The kW used for demand will be different than the kW used for energy if the CT fans are constant speed. If the fans are constant speed, the demand is likely set at the rated fan power and a change in demand is unlikely. If the fans are variable speed or 2-speed, there is more likely to be a change in demand.
Note on BA4: The kW used for demand will be different than the kW used for energy if the CT fans are constant speed. If the fans are constant speed, the demand is likely set at the rated fan power and a change in demand is unlikely. If the fans are variable speed or 2-speed, there is more likely to be a change in demand.

## Resets (hidden)
Chiller Load |  |  |  | Baseline CHWST Reset Slope |  |  |  | Proposed CHWST Reset Slope
% of MaxCapacity: | 100% |  |  | OA (F) | CHWST |  |  | OA (F) | CHWST
OA (F) | Total System Load (tons) |  |  | 96.98 | 0 | 0 | Slope | 96.98 | 0 | 0 | Slope
96.98 | 750 | 16.6746 | Slope | 0 | 0 | 0 | Intercept | 0 | 0 | 0 | Intercept
55 | 50 | -867.1034 | Intercept
|  |  |  | Baseline CWST Reset Slope |  |  |  | Proposed CWST Reset Slope
Chiller Cycling |  |  |  | OA (F) | CWST |  |  | OA (F) | CWST
55 | 100% | 0.018182 | Slope | 96.98 | 0 | 0 | Slope | 96.98 | 0 | 0 | Slope
0 | 0% | 0 | Intercept | 0 | 0 | 0 | Intercept | 0 | 0 | 0 | Intercept
Assumed CW approach to Wb:
0 | deg F
Baseline CT Fan Energy Operating Fraction
*For 2-speed and constant speed only
Variable speed CT fans are assumed to operate all hour
OA (F) | % of Hour
96.98 | 100% | 0.010311 | Slope
0 | 0% | 5.5511e-17 | Intercept

## Fan and Pump Curves (hidden)
Fan Power Coefficients
Power Constants for Control Type Selected:
| Type | A | B | C | Min % Turndown
| Variable Speed Drive | 0.21976 | -0.87478 | 1.6526 | 26%
% Power = A + B * %Speed + C * %Speed^2 (% flow = to % speed)
Fan Curve Constants - ASHRAE Standard 90.1-1989 User's Manual
| A | B | C | Min Turndown
Constant Volume | 1 | 0 | 0 | 100%
Inlet Guide Vanes | 0.58435 | -0.57917 | 0.97024 | 30%
Riding Curve | 0.22714 | 1.1789 | -0.41071 | 45%
Vane Axial Variable Pitch Blades | 0.21205 | -0.56929 | 1.3452 | 40%
Variable Speed Drive | 0.21976 | -0.87478 | 1.6526 | 26%
% Fan Power = A + B * %CFM + C * %CFM^2
(LOOKUP_CFMControl_ShortList)
Inlet Guide Vanes
Vane Axial Variable Pitch Blades
Variable Speed Drive
% Fan Power = A + B * %CFM + C * %CFM^2
Note on B10: Behzad Aghababazadeh: Update this table
Note on B13: These constants are for airfoil and backward incline fans. These values are more conservative (higher energy use) than forward curve constants.
Note on B14: These constants are for airfoil and backward incline fans. These values are more conservative (higher energy use) than forward curve constants.
Note on B21: These constants are for airfoil and backward incline fans. These values are more conservative (higher energy use) than forward curve constants.

## Chiller 1 Performance Curves (hidden)
Chiller Type Selected: | 0
Performance Curves Used
|  | Constant | CHWT | CHWT^2 | CWT or db | CWT or db^2 | CHWT*CWT or db
|  | 1 | 44 | 1936 | 85 | 7225 | 3740
|  | a | b | c | d | e | f
| Column Index | 2 | 3 | 4 | 5 | 6 | 7
Capacity Correction % |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Perf. Correction % |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PLR - % of total load |  | Constant | PLR | PLR^2 | DT | DT^2 | PLR*DT
DT - between CHWT and CWT or OSA |  | 1 | 1 | 1 | 41 | 1681 | 41
Perf. Correction (PLR) % |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | 7: Total Check: | #N/A
DOE-2 Chiller Performance Curves
Water-Cooled
Description | DOE-2 Label
Electric Centrifugal | CentH2O
Electric Centrifugal VSD | CentH2OVSD
Electric Reciprocating | RecipH2O (2Comp/Ckt for PLR)
Electric Screw | ScrewH2O (2Comp/Ckt for PLR)
Water Cooled Coefficients - From DOE-2
Capacity Correction | Capacity Correction (%) = a + b*CHWT + c*CHWT2 + d*CWT + e*CWT2 + f*CHWT*CWT
| Constant | CHWT | CHWT^2 | CWT | CWT^2 | CHWT*CWT
| a | b | c | d | e | f
Electric Centrifugal | -0.49737 | -0.0095607 | -0.00059561 | 0.043521 | -0.00058394 | 0.00096007
Electric Centrifugal VSD | -0.38925 | -0.021951 | -0.00027343 | 0.049748 | -0.00053441 | 0.00067295
Electric Reciprocating | 0.64718 | 0.015888 | 0.00010313 | -0.0041667 | 6.69e-06 | -6.418e-05
Electric Screw | 0.89823 | 0.0004535 | 0.0002369 | -0.0010475 | -2.93e-05 | -2.035e-05
EIR Correction - Temp | Performance Correction (%) = a + b*CHWT + c*CHWT2 + d*CWT + e*CWT2 + f*CHWT*CWT
| Constant | CHWT | CHWT^2 | CWT | CWT^2 | CHWT*CWT
| a | b | c | d | e | f
Electric Centrifugal | 1.1536 | -0.030679 | 0.00030591 | 0.0067087 | 5.28e-05 | -9.297e-05
Electric Centrifugal VSD | 1.4287 | -0.082278 | 0.00030243 | 0.036222 | -0.00029211 | 0.00043788
Electric Reciprocating | 0.56406 | -0.011463 | 0.00011174 | 0.0080905 | 7.043e-05 | -0.00012635
Electric Screw | 0.62494 | -0.00099309 | 0.00017366 | -0.00086447 | 0.00019627 | -0.0003377
EIR Correction - PLR | Part Load (PLR) Performance Correction (%) = a + b*PLR + c*PLR2 + d*DT + e*DT2 + f*PLR*DT
(DT between CHWT and CWT) | Constant | PLR | PLR^2 | DT | DT^2 | PLR*DT
| a | b | c | d | e | f
Electric Centrifugal | 0.2797 | 0.57376 | 0.2569 | -0.0058072 | 0.00014649 | -0.0035301
Electric Centrifugal VSD | 0.14703 | -0.0034967 | 1.0116 | -0.003597 | 0.00027167 | -0.011645
Electric Reciprocating | 0.023918 | 0.88947 | 0.077931 | -0.00026357 | 7.2e-06 | 0.00017998
Electric Screw | -0.27111 | 1.4901 | -0.33198 | 0.0097534 | -5.891e-05 | -0.0045818

## Chiller 2 Performance Curves (hidden)
Chiller Type Selected: | 0
Performance Curves Used
|  | Constant | CHWT | CHWT^2 | CWT or db | CWT or db^2 | CHWT*CWT or db
|  | 1 | 44 | 1936 | 85 | 7225 | 3740
|  | a | b | c | d | e | f
| Column Index | 2 | 3 | 4 | 5 | 6 | 7
Capacity Correction |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Perf. Correction (Temp) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PLR - % of total load |  | Constant | PLR | PLR^2 | DT | DT^2 | PLR*DT
DT - between CHWT and CWT or OSA |  | 1 | 1 | 1 | 41 | 1681 | 41
Perf. Correction (PLR) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | 7: Total Check: | #N/A
DOE-2 Chiller Performance Curves
Water-Cooled
Description | DOE-2 Label
Electric Centrifugal | CentH2O
Electric Centrifugal VSD | CentH2OVSD
Electric Reciprocating | RecipH2O (2Comp/Ckt for PLR)
Electric Screw | ScrewH2O (2Comp/Ckt for PLR)
Water Cooled Coefficients - From DOE-2
Capacity Correction | Capacity Correction (%) = a + b*CHWT + c*CHWT2 + d*CWT + e*CWT2 + f*CHWT*CWT
| Constant | CHWT | CHWT^2 | CWT | CWT^2 | CHWT*CWT
| a | b | c | d | e | f
Electric Centrifugal | -0.49737 | -0.0095607 | -0.00059561 | 0.043521 | -0.00058394 | 0.00096007
Electric Centrifugal VSD | -0.38925 | -0.021951 | -0.00027343 | 0.049748 | -0.00053441 | 0.00067295
Electric Reciprocating | 0.64718 | 0.015888 | 0.00010313 | -0.0041667 | 6.69e-06 | -6.418e-05
Electric Screw | 0.89823 | 0.0004535 | 0.0002369 | -0.0010475 | -2.93e-05 | -2.035e-05
EIR Correction - Temp | Performance Correction (%) = a + b*CHWT + c*CHWT2 + d*CWT + e*CWT2 + f*CHWT*CWT
| Constant | CHWT | CHWT^2 | CWT | CWT^2 | CHWT*CWT
| a | b | c | d | e | f
Electric Centrifugal | 1.1536 | -0.030679 | 0.00030591 | 0.0067087 | 5.28e-05 | -9.297e-05
Electric Centrifugal VSD | 1.4287 | -0.082278 | 0.00030243 | 0.036222 | -0.00029211 | 0.00043788
Electric Reciprocating | 0.56406 | -0.011463 | 0.00011174 | 0.0080905 | 7.043e-05 | -0.00012635
Electric Screw | 0.62494 | -0.00099309 | 0.00017366 | -0.00086447 | 0.00019627 | -0.0003377
EIR Correction - PLR | Part Load (PLR) Performance Correction (%) = a + b*PLR + c*PLR2 + d*DT + e*DT2 + f*PLR*DT
(DT between CHWT and CWT) | Constant | PLR | PLR^2 | DT | DT^2 | PLR*DT
| a | b | c | d | e | f
Electric Centrifugal | 0.2797 | 0.57376 | 0.2569 | -0.0058072 | 0.00014649 | -0.0035301
Electric Centrifugal VSD | 0.14703 | -0.0034967 | 1.0116 | -0.003597 | 0.00027167 | -0.011645
Electric Reciprocating | 0.023918 | 0.88947 | 0.077931 | -0.00026357 | 7.2e-06 | 0.00017998
Electric Screw | -0.27111 | 1.4901 | -0.33198 | 0.0097534 | -5.891e-05 | -0.0045818

## Weekly Schedule Creator (hidden)
YearRound (1 = Yes, 2 = No) | Primary Schedule | [7 empty] | Secondery Schedule
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 2 | 3 | 4 | 5 | 6 | 7 | 1
| Hour | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Hour | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE!

## Bin Hours (hidden)
| Total Hours: | 0
Bin Temp | Wet Bulb Temp (F) | Hours
-13 | 0 | 0
-11 | -9.82 | 0
-9 | -8.26 | 0
-7 | -6.11 | 0
-5 | -4.925 | 0
-3 | -3.4141 | 0
-1 | -1.5733 | 0
1 | 0.5325 | 0
3 | 2.3867 | 0
5 | 4.9873 | 0
7 | 7.2881 | 0
9 | 8.8986 | 0
11 | 10.8862 | 0
13 | 12.1167 | 0
15 | 13.8494 | 0
17 | 15.7249 | 0
19 | 17.4336 | 0
21 | 19.4477 | 0
23 | 21.9351 | 0
25 | 24.3156 | 0
27 | 26.1737 | 0
29 | 28.1495 | 0
31 | 29.923 | 0
33 | 31.3769 | 0
35 | 32.6309 | 0
37 | 34.1249 | 0
39 | 36.2443 | 0
41 | 38.3259 | 0
43 | 40.5339 | 0
45 | 42.4181 | 0
47 | 44.3567 | 0
49 | 45.7706 | 0
51 | 46.8472 | 0
53 | 48.2498 | 0
55 | 49.881 | 0
57 | 51.3736 | 0
59 | 54.0588 | 0
61 | 55.9655 | 0
63 | 57.8575 | 0
65 | 59.7528 | 0
67 | 61.6238 | 0
69 | 63.2131 | 0
71 | 65.6742 | 0
73 | 66.2022 | 0
75 | 67.2869 | 0
77 | 68.2655 | 0
79 | 69.8367 | 0
81 | 70.0674 | 0
83 | 70.9078 | 0
85 | 72.8685 | 0
87 | 73.5143 | 0
89 | 75.3149 | 0
91 | 75.8825 | 0
93 | 79.2867 | 0
95 | 80.68 | 0
97 | 0 | 0
99 | 0 | 0
101 | 0 | 0
103 | 0 | 0
105 | 0 | 0
107 | 0 | 0
109 | 0 | 0
111 | 0 | 0
113 | 0 | 0

## Dropdowns (hidden)
Dropdowns
Year
2014
2015
2016
2017
2018
2019
2020
Yes/No
Yes
No
| From/To | Design Temp |  | Water Cooled Chiller Type
| 0:00 | Winter | Summer | Electric Centrifugal
| 1:00 | 10 | 96 | Electric Centrifugal VSD
| 2:00 | 9 | 95 | Electric Reciprocating
| 3:00 | 8 | 94 | Electric Screw
| 4:00 | 7
| 5:00 | 6 |  |  | Number of Chillers
| 6:00 | 5 |  |  | 1
| 7:00 | 4 |  |  | 2
| 8:00 | 3
| 9:00 | 2
| 10:00 | 1
| 11:00 | 0
| 12:00 | -1
| 13:00 | -2
| 14:00 | -3
| 15:00 | -4
| 16:00 | -5
| 17:00 | -6
| 18:00 | -7
| 19:00 | -8
| 20:00 | -9
| 21:00 | -10
22:00
23:00
Closed
300000
Weather Stations
Indianapolis Intl AP
Cooling Tower Fan Type
2-Speed
Constant Speed
Variable Speed
DB/WB
Dry Bulb
Wet Bulb

## Updates (hidden)
Date | Version | Engineer | QC Engineer | Description | Future Consideration
10.28.2014 | 1.1 | Behzad Aghababazadeh | Mary Clayton | 1st Draft Submitted | 1. Adding secondary schedule 2. Adding weather station 3. Adding a separate chiller type cell for Chiller #2
2017-01-13 | 1.2 | Ben Reinhart | Will Nichols | Updated Incentive Caps to match IPL 2017 Program Year | Review for 2018 program changes
2018-01-08 | 1.3 | Ben Reinhart | Will Nichols | Updated incentive for 2018 to be based on $0.08 per annual kWh saved (instead of $0.07) | Review for 2019 program changes

## Kansas City, MO (hidden)
724460 |  | KANSAS CITY INT'L ARPT |  | MO | -6 | 39.3 | -94.717 | 298
Date (MM/DD/YYYY) | 2014 Date | Time (HH:MM) | Hour | ETR (W/m^2) | ETRN (W/m^2) | GHI (W/m^2) | GHI source | GHI uncert (%) | DNI (W/m^2) | DNI source | DNI uncert (%) | DHI (W/m^2) | DHI source | DHI uncert (%) | GH illum (lx) | GH illum source | Global illum uncert (%) | DN illum (lx) | DN illum source | DN illum uncert (%) | DH illum (lx) | DH illum source | DH illum uncert (%) | Zenith lum (cd/m^2) | Zenith lum source | Zenith lum uncert (%) | TotCld (tenths) | TotCld source | TotCld uncert (code) | OpqCld (tenths) | OpqCld source | OpqCld uncert (code) | Dry-bulb (C) | Dry-bulb (F) | Dry-bulb source | Dry-bulb uncert (code) | Dew-point (C) | Dew-point (F) | Dew-point source | Dew-point uncert (code) | RHum (%) | RHum source | RHum uncert (code) | Pressure (mbar) | Pressure source | Pressure uncert (code) | Wdir (degrees) | Wdir source | Wdir uncert (code) | Wspd (m/s) | Wspd source | Wspd uncert (code) | Hvis (m) | Hvis source | Hvis uncert (code) | CeilHgt (m) | CeilHgt source | CeilHgt uncert (code) | Pwat (cm) | Pwat source | Pwat uncert (code) | AOD (unitless) | AOD source | AOD uncert (code) | Alb (unitless) | Alb source | Alb uncert (code) | Lprecip depth (mm) | Lprecip quantity (hr) | Lprecip source | Lprecip uncert (code) | Wet Bulb (F) | Day of Week | Primary Schedule
1988-01-01 | 1899-12-31 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.88 | A | 7 | 995 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.36 | 1 | 0 | Max | 98.96
1988-01-01 | 1899-12-31 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.84 | A | 7 | 996 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.26 | 1 | 0 | Min | -0.04
1988-01-01 | 1899-12-31 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -13.9 | 6.98 | A | 7 | 0.88 | A | 7 | 996 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.38 | 1 | 0
1988-01-01 | 1899-12-31 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -13.9 | 6.98 | A | 7 | 0.84 | A | 7 | 996 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.18 | 1 | 0
1988-01-01 | 1899-12-31 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -15 | 5 | A | 7 | 0.84 | A | 7 | 996 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.3 | 1 | 0
1988-01-01 | 1899-12-31 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -15 | 5 | A | 7 | 0.8 | A | 7 | 997 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.1 | 1 | 0
1988-01-01 | 1899-12-31 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 997 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 1 | 0
1988-01-01 | 1899-12-31 | 8:00 | 8 | 12 | 460 | 15 | 1 | 13 | 106 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -15 | 5 | A | 7 | 0.84 | A | 7 | 998 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.3 | 1 | 0
1988-01-01 | 1899-12-31 | 9:00 | 9 | 184 | 1415 | 92 | 1 | 13 | 518 | 1 | 9 | 24 | 1 | 13 | 9696 | 1 | 13 | 37276 | 1 | 9 | 4813 | 1 | 13 | 510 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -11.1 | 12.02 | A | 7 | -14.4 | 6.08 | A | 7 | 0.77 | A | 7 | 999 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.98 | 1 | 0
1988-01-01 | 1899-12-31 | 10:00 | 10 | 385 | 1415 | 209 | 1 | 13 | 418 | 1 | 13 | 94 | 1 | 13 | 21647 | 1 | 13 | 35691 | 1 | 13 | 11885 | 1 | 13 | 1753 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | -10 | 14 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 1000 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.6 | 1 | 0
1988-01-01 | 1899-12-31 | 11:00 | 11 | 537 | 1415 | 384 | 1 | 9 | 859 | 1 | 9 | 56 | 1 | 13 | 40269 | 1 | 9 | 80691 | 1 | 9 | 9499 | 1 | 13 | 1217 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -7.8 | 17.96 | A | 7 | -15 | 5 | A | 7 | 0.57 | A | 7 | 1000 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.1 | 1 | 0
1988-01-01 | 1899-12-31 | 12:00 | 12 | 629 | 1415 | 462 | 1 | 9 | 935 | 1 | 9 | 44 | 1 | 13 | 48897 | 1 | 9 | 90102 | 1 | 9 | 8661 | 1 | 13 | 1192 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -15 | 5 | A | 7 | 0.5 | A | 7 | 1000 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.8 | 1 | 0
1988-01-01 | 1899-12-31 | 13:00 | 13 | 654 | 1415 | 471 | 1 | 9 | 919 | 1 | 9 | 45 | 1 | 13 | 49991 | 1 | 9 | 88994 | 1 | 9 | 8643 | 1 | 13 | 1226 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -15 | 5 | A | 7 | 0.46 | A | 7 | 999 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.7 | 1 | 0
1988-01-01 | 1899-12-31 | 14:00 | 14 | 612 | 1415 | 448 | 1 | 9 | 935 | 1 | 9 | 43 | 1 | 13 | 47592 | 1 | 9 | 89778 | 1 | 9 | 8604 | 1 | 13 | 1165 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -15 | 5 | A | 7 | 0.41 | A | 7 | 998 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.5 | 1 | 0
1988-01-01 | 1899-12-31 | 15:00 | 15 | 504 | 1415 | 349 | 1 | 9 | 876 | 1 | 9 | 37 | 1 | 13 | 37198 | 1 | 9 | 81641 | 1 | 9 | 8002 | 1 | 13 | 1003 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -15 | 5 | A | 7 | 0.39 | A | 7 | 998 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.4 | 1 | 0
1988-01-01 | 1899-12-31 | 16:00 | 16 | 338 | 1415 | 213 | 1 | 13 | 775 | 1 | 9 | 28 | 1 | 13 | 22766 | 1 | 13 | 66318 | 1 | 9 | 6848 | 1 | 13 | 752 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -14.4 | 6.08 | A | 7 | 0.41 | A | 7 | 998 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.38 | 1 | 0
1988-01-01 | 1899-12-31 | 17:00 | 17 | 128 | 1415 | 60 | 1 | 13 | 493 | 1 | 9 | 16 | 1 | 13 | 6431 | 1 | 13 | 31879 | 1 | 9 | 3542 | 1 | 13 | 376 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.5 | A | 7 | 998 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.66 | 1 | 0
1988-01-01 | 1899-12-31 | 18:00 | 18 | 1 | 106 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -13.9 | 6.98 | A | 7 | 0.57 | A | 7 | 998 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.98 | 1 | 0
1988-01-01 | 1899-12-31 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 998 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.54 | 1 | 0
1988-01-01 | 1899-12-31 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -13.3 | 8.06 | A | 7 | 0.62 | A | 7 | 998 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.16 | 1 | 0
1988-01-01 | 1899-12-31 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -13.3 | 8.06 | A | 7 | 0.65 | A | 7 | 998 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.36 | 1 | 0
1988-01-01 | 1899-12-31 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -13.3 | 8.06 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.46 | 1 | 0
1988-01-01 | 1899-12-31 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.77 | A | 7 | 998 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 1 | 0
1988-01-01 | 1899-12-31 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.77 | A | 7 | 999 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 1 | 0
1988-01-02 | 1900-01-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -12.8 | 8.96 | A | 7 | 0.8 | A | 7 | 998 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.96 | 2 | 0
1988-01-02 | 1900-01-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -13.3 | 8.06 | A | 7 | 0.8 | A | 7 | 998 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.06 | 2 | 0
1988-01-02 | 1900-01-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.88 | A | 7 | 997 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.36 | 2 | 0
1988-01-02 | 1900-01-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.88 | A | 7 | 997 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.46 | 2 | 0
1988-01-02 | 1900-01-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.84 | A | 7 | 996 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.16 | 2 | 0
1988-01-02 | 1900-01-01 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.92 | A | 7 | 996 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.54 | 2 | 0
1988-01-02 | 1900-01-01 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.92 | A | 7 | 995 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.44 | 2 | 0
1988-01-02 | 1900-01-01 | 8:00 | 8 | 12 | 460 | 10 | 1 | 13 | 50 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.88 | A | 7 | 995 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.32 | 2 | 0
1988-01-02 | 1900-01-01 | 9:00 | 9 | 184 | 1415 | 91 | 1 | 13 | 478 | 1 | 9 | 28 | 1 | 13 | 91 | 1 | 13 | 326 | 1 | 9 | 49 | 1 | 13 | 53 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.84 | A | 7 | 995 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 2 | 0
1988-01-02 | 1900-01-01 | 10:00 | 10 | 385 | 1415 | 241 | 1 | 9 | 722 | 1 | 9 | 43 | 1 | 13 | 252 | 1 | 9 | 634 | 1 | 9 | 79 | 1 | 13 | 90 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -7.8 | 17.96 | A | 7 | 0.75 | A | 7 | 995 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.16 | 2 | 0
1988-01-02 | 1900-01-01 | 11:00 | 11 | 538 | 1415 | 370 | 1 | 9 | 827 | 1 | 9 | 53 | 1 | 13 | 388 | 1 | 9 | 777 | 1 | 9 | 91 | 1 | 13 | 120 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.61 | A | 7 | 995 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.26 | 2 | 0
1988-01-02 | 1900-01-01 | 12:00 | 12 | 630 | 1415 | 450 | 1 | 9 | 872 | 1 | 9 | 60 | 1 | 13 | 473 | 1 | 9 | 839 | 1 | 9 | 97 | 1 | 13 | 137 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.5 | A | 7 | 994 | A | 7 | 210 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.66 | 2 | 0
1988-01-02 | 1900-01-01 | 13:00 | 13 | 656 | 1415 | 473 | 1 | 9 | 884 | 1 | 9 | 62 | 1 | 13 | 497 | 1 | 9 | 854 | 1 | 9 | 99 | 1 | 13 | 142 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.44 | A | 7 | 992 | A | 7 | 210 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.26 | 2 | 0
1988-01-02 | 1900-01-01 | 14:00 | 14 | 614 | 1415 | 435 | 1 | 9 | 866 | 1 | 9 | 59 | 1 | 13 | 458 | 1 | 9 | 830 | 1 | 9 | 96 | 1 | 13 | 134 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -7.2 | 19.04 | A | 7 | 0.46 | A | 7 | 991 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.04 | 2 | 0
1988-01-02 | 1900-01-01 | 15:00 | 15 | 506 | 1415 | 341 | 1 | 9 | 808 | 1 | 9 | 51 | 1 | 13 | 359 | 1 | 9 | 752 | 1 | 9 | 89 | 1 | 13 | 115 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.41 | A | 7 | 990 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.76 | 2 | 0
1988-01-02 | 1900-01-01 | 16:00 | 16 | 341 | 1415 | 203 | 1 | 13 | 679 | 1 | 9 | 39 | 1 | 13 | 212 | 1 | 13 | 576 | 1 | 9 | 73 | 1 | 13 | 81 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.43 | A | 7 | 990 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.96 | 2 | 0
1988-01-02 | 1900-01-01 | 17:00 | 17 | 131 | 1415 | 55 | 1 | 13 | 363 | 1 | 9 | 22 | 1 | 13 | 56 | 1 | 13 | 217 | 1 | 9 | 36 | 1 | 13 | 40 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.54 | A | 7 | 989 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.44 | 2 | 0
1988-01-02 | 1900-01-01 | 18:00 | 18 | 1 | 130 | 3 | 1 | 13 | 3 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -6.7 | 19.94 | A | 7 | 0.61 | A | 7 | 989 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.04 | 2 | 0
1988-01-02 | 1900-01-01 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 988 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.24 | 2 | 0
1988-01-02 | 1900-01-01 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.61 | A | 7 | 988 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.24 | 2 | 0
1988-01-02 | 1900-01-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -7.2 | 19.04 | A | 7 | 0.64 | A | 7 | 988 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.44 | 2 | 0
1988-01-02 | 1900-01-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -7.2 | 19.04 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.74 | 2 | 0
1988-01-02 | 1900-01-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -1.7 | 28.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.46 | 2 | 0
1988-01-02 | 1900-01-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -1.7 | 28.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.46 | 2 | 0
1988-01-03 | 1900-01-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | -1.1 | 30.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.61 | A | 7 | 986 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 2290 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.26 | 3 | 0
1988-01-03 | 1900-01-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | -1.7 | 28.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.64 | A | 7 | 986 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.46 | 3 | 0
1988-01-03 | 1900-01-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -2.2 | 28.04 | A | 7 | -7.8 | 17.96 | A | 7 | 0.66 | A | 7 | 986 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.56 | 3 | 0
1988-01-03 | 1900-01-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -1.7 | 28.94 | A | 7 | -7.2 | 19.04 | A | 7 | 0.66 | A | 7 | 985 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 2290 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.54 | 3 | 0
1988-01-03 | 1900-01-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | -0.6 | 30.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.61 | A | 7 | 985 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 1830 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.24 | 3 | 0
1988-01-03 | 1900-01-02 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | -0.6 | 30.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.59 | A | 7 | 985 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 3 | 0
1988-01-03 | 1900-01-02 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -1.1 | 30.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.61 | A | 7 | 985 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.26 | 3 | 0
1988-01-03 | 1900-01-02 | 8:00 | 8 | 11 | 460 | 8 | 1 | 13 | 8 | 1 | 13 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -2.2 | 28.04 | A | 7 | -7.8 | 17.96 | A | 7 | 0.66 | A | 7 | 986 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 0.7 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.56 | 3 | 0
1988-01-03 | 1900-01-02 | 9:00 | 9 | 184 | 1415 | 60 | 1 | 13 | 53 | 1 | 13 | 53 | 1 | 13 | 65 | 1 | 13 | 34 | 1 | 13 | 60 | 1 | 13 | 112 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 986 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 0.7 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 3 | 0
1988-01-03 | 1900-01-02 | 10:00 | 10 | 386 | 1415 | 136 | 1 | 9 | 23 | 1 | 9 | 130 | 1 | 13 | 149 | 1 | 9 | 15 | 1 | 9 | 145 | 1 | 13 | 415 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.67 | A | 7 | 987 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 0.8 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.42 | 3 | 0
1988-01-03 | 1900-01-02 | 11:00 | 11 | 539 | 1415 | 232 | 1 | 9 | 154 | 1 | 9 | 173 | 1 | 13 | 251 | 1 | 9 | 150 | 1 | 9 | 194 | 1 | 13 | 402 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 0.8 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.42 | 3 | 0
1988-01-03 | 1900-01-02 | 12:00 | 12 | 632 | 1415 | 340 | 1 | 13 | 428 | 1 | 13 | 148 | 1 | 13 | 359 | 1 | 13 | 421 | 1 | 13 | 170 | 1 | 13 | 299 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 3 | 0
1988-01-03 | 1900-01-02 | 13:00 | 13 | 658 | 1415 | 367 | 1 | 13 | 543 | 1 | 13 | 114 | 1 | 13 | 384 | 1 | 13 | 529 | 1 | 13 | 137 | 1 | 13 | 234 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | -0.6 | 30.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.59 | A | 7 | 986 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 3 | 0
1988-01-03 | 1900-01-02 | 14:00 | 14 | 617 | 1415 | 442 | 1 | 9 | 897 | 1 | 9 | 50 | 1 | 13 | 467 | 1 | 9 | 861 | 1 | 9 | 90 | 1 | 13 | 126 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.5 | A | 7 | 986 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.46 | 3 | 0
1988-01-03 | 1900-01-02 | 15:00 | 15 | 509 | 1415 | 347 | 1 | 9 | 843 | 1 | 9 | 44 | 1 | 13 | 369 | 1 | 9 | 786 | 1 | 9 | 84 | 1 | 13 | 110 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.46 | A | 7 | 986 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.38 | 3 | 0
1988-01-03 | 1900-01-02 | 16:00 | 16 | 344 | 1415 | 211 | 1 | 13 | 731 | 1 | 9 | 34 | 1 | 13 | 225 | 1 | 13 | 627 | 1 | 9 | 72 | 1 | 13 | 82 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.46 | A | 7 | 987 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.38 | 3 | 0
1988-01-03 | 1900-01-02 | 17:00 | 17 | 134 | 1415 | 60 | 1 | 13 | 435 | 1 | 9 | 20 | 1 | 13 | 62 | 1 | 13 | 266 | 1 | 9 | 37 | 1 | 13 | 39 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -8.9 | 15.98 | A | 7 | 0.52 | A | 7 | 987 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.78 | 3 | 0
1988-01-03 | 1900-01-02 | 18:00 | 18 | 1 | 153 | 4 | 1 | 13 | 9 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.58 | A | 7 | 987 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.38 | 3 | 0
1988-01-03 | 1900-01-02 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -2.8 | 26.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.61 | A | 7 | 988 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.58 | 3 | 0
1988-01-03 | 1900-01-02 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -3.9 | 24.98 | A | 7 | -8.9 | 15.98 | A | 7 | 0.69 | A | 7 | 989 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.98 | 3 | 0
1988-01-03 | 1900-01-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -3.9 | 24.98 | A | 7 | -10 | 14 | A | 7 | 0.63 | A | 7 | 990 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.7 | 3 | 0
1988-01-03 | 1900-01-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -5 | 23 | A | 7 | -12.2 | 10.04 | A | 7 | 0.57 | A | 7 | 990 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.74 | 3 | 0
1988-01-03 | 1900-01-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -5.6 | 21.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.6 | A | 7 | 991 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.94 | 3 | 0
1988-01-03 | 1900-01-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -7.8 | 17.96 | A | 7 | -12.8 | 8.96 | A | 7 | 0.68 | A | 7 | 991 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.36 | 3 | 0
1988-01-04 | 1900-01-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 991 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 4 | 0
1988-01-04 | 1900-01-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.74 | A | 7 | 992 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.66 | 4 | 0
1988-01-04 | 1900-01-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -9.4 | 15.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.77 | A | 7 | 992 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.76 | 4 | 0
1988-01-04 | 1900-01-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -8.9 | 15.98 | A | 7 | -13.9 | 6.98 | A | 7 | 0.68 | A | 7 | 993 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.48 | 4 | 0
1988-01-04 | 1900-01-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 993 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 4 | 0
1988-01-04 | 1900-01-03 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 993 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 4 | 0
1988-01-04 | 1900-01-03 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -15 | 5 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.7 | 4 | 0
1988-01-04 | 1900-01-03 | 8:00 | 8 | 11 | 460 | 9 | 1 | 13 | 26 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -15 | 5 | A | 7 | 0.62 | A | 7 | 995 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.4 | 4 | 0
1988-01-04 | 1900-01-03 | 9:00 | 9 | 184 | 1415 | 86 | 1 | 13 | 395 | 1 | 9 | 34 | 1 | 13 | 88 | 1 | 13 | 251 | 1 | 9 | 55 | 1 | 13 | 61 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -13.3 | 8.06 | A | 7 | 0.65 | A | 7 | 996 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.36 | 4 | 0
1988-01-04 | 1900-01-03 | 10:00 | 10 | 386 | 1415 | 235 | 1 | 9 | 665 | 1 | 9 | 52 | 1 | 13 | 241 | 1 | 9 | 579 | 1 | 9 | 82 | 1 | 13 | 101 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -17.2 | 1.04 | A | 7 | 0.51 | A | 7 | 997 | A | 7 | 300 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.76 | 4 | 0
1988-01-04 | 1900-01-03 | 11:00 | 11 | 540 | 1415 | 367 | 1 | 9 | 785 | 1 | 9 | 66 | 1 | 13 | 382 | 1 | 9 | 740 | 1 | 9 | 99 | 1 | 13 | 135 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -20.6 | -5.08 | A | 7 | 0.42 | A | 7 | 999 | A | 7 | 320 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.68 | 4 | 0
1988-01-04 | 1900-01-03 | 12:00 | 12 | 634 | 1415 | 450 | 1 | 9 | 836 | 1 | 9 | 74 | 1 | 13 | 472 | 1 | 9 | 810 | 1 | 9 | 108 | 1 | 13 | 157 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -21.7 | -7.06 | A | 7 | 0.38 | A | 7 | 999 | A | 7 | 300 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.66 | 4 | 0
1988-01-04 | 1900-01-03 | 13:00 | 13 | 661 | 1415 | 473 | 1 | 9 | 849 | 1 | 9 | 76 | 1 | 13 | 499 | 1 | 9 | 828 | 1 | 9 | 111 | 1 | 13 | 164 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -21.7 | -7.06 | A | 7 | 0.38 | A | 7 | 998 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.66 | 4 | 0
1988-01-04 | 1900-01-03 | 14:00 | 14 | 619 | 1415 | 435 | 1 | 9 | 828 | 1 | 9 | 73 | 1 | 13 | 458 | 1 | 9 | 799 | 1 | 9 | 107 | 1 | 13 | 154 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -20.6 | -5.08 | A | 7 | 0.4 | A | 7 | 998 | A | 7 | 290 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.78 | 4 | 0
1988-01-04 | 1900-01-03 | 15:00 | 15 | 513 | 1415 | 340 | 1 | 9 | 765 | 1 | 9 | 63 | 1 | 13 | 355 | 1 | 9 | 714 | 1 | 9 | 95 | 1 | 13 | 128 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -21.7 | -7.06 | A | 7 | 0.37 | A | 7 | 998 | A | 7 | 270 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.66 | 4 | 0
1988-01-04 | 1900-01-03 | 16:00 | 16 | 348 | 1415 | 203 | 1 | 13 | 632 | 1 | 9 | 49 | 1 | 13 | 209 | 1 | 13 | 533 | 1 | 9 | 77 | 1 | 13 | 93 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -22.8 | -9.04 | A | 7 | 0.35 | A | 7 | 999 | A | 7 | 290 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.54 | 4 | 0
1988-01-04 | 1900-01-03 | 17:00 | 17 | 138 | 1415 | 55 | 1 | 13 | 297 | 1 | 9 | 27 | 1 | 13 | 57 | 1 | 13 | 164 | 1 | 9 | 41 | 1 | 13 | 48 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -23.3 | -9.94 | A | 7 | 0.36 | A | 7 | 999 | A | 7 | 300 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -11.34 | 4 | 0
1988-01-04 | 1900-01-03 | 18:00 | 18 | 1 | 153 | 2 | 1 | 13 | 4 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -22.2 | -7.96 | A | 7 | 0.44 | A | 7 | 1000 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -9.36 | 4 | 0
1988-01-04 | 1900-01-03 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -21.7 | -7.06 | A | 7 | 0.48 | A | 7 | 1000 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.36 | 4 | 0
1988-01-04 | 1900-01-03 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -21.7 | -7.06 | A | 7 | 0.5 | A | 7 | 1000 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.36 | 4 | 0
1988-01-04 | 1900-01-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -21.7 | -7.06 | A | 7 | 0.52 | A | 7 | 1000 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.26 | 4 | 0
1988-01-04 | 1900-01-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -21.1 | -5.98 | A | 7 | 0.6 | A | 7 | 1000 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -7.08 | 4 | 0
1988-01-04 | 1900-01-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -20.6 | -5.08 | A | 7 | 0.66 | A | 7 | 1001 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.08 | 4 | 0
1988-01-04 | 1900-01-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -20 | -4 | A | 7 | 0.72 | A | 7 | 1001 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.8 | 4 | 0
1988-01-05 | 1900-01-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -21.1 | -5.98 | A | 7 | 0.63 | A | 7 | 1001 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.98 | 5 | 0
1988-01-05 | 1900-01-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -20.6 | -5.08 | A | 7 | 0.66 | A | 7 | 1001 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.08 | 5 | 0
1988-01-05 | 1900-01-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 1 | A | 7 | -15.6 | 3.92 | A | 7 | -20 | -4 | A | 7 | 0.69 | A | 7 | 1001 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.9 | 5 | 0
1988-01-05 | 1900-01-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -15.6 | 3.92 | A | 7 | -21.1 | -5.98 | A | 7 | 0.63 | A | 7 | 1001 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.98 | 5 | 0
1988-01-05 | 1900-01-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 3 | A | 7 | -15 | 5 | A | 7 | -21.7 | -7.06 | A | 7 | 0.57 | A | 7 | 1002 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.16 | 5 | 0
1988-01-05 | 1900-01-04 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 4 | A | 7 | -15 | 5 | A | 7 | -21.7 | -7.06 | A | 7 | 0.57 | A | 7 | 1002 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.16 | 5 | 0
1988-01-05 | 1900-01-04 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 4 | A | 7 | -15 | 5 | A | 7 | -21.1 | -5.98 | A | 7 | 0.6 | A | 7 | 1003 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -7.08 | 5 | 0
1988-01-05 | 1900-01-04 | 8:00 | 8 | 11 | 460 | 12 | 1 | 13 | 8 | 1 | 13 | 11 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | -15 | 5 | A | 7 | -21.7 | -7.06 | A | 7 | 0.57 | A | 7 | 1003 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.16 | 5 | 0
1988-01-05 | 1900-01-04 | 9:00 | 9 | 184 | 1415 | 62 | 1 | 13 | 31 | 1 | 9 | 58 | 1 | 13 | 68 | 1 | 13 | 22 | 1 | 9 | 65 | 1 | 13 | 132 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -14.4 | 6.08 | A | 7 | -21.7 | -7.06 | A | 7 | 0.55 | A | 7 | 1004 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.26 | 5 | 0
1988-01-05 | 1900-01-04 | 10:00 | 10 | 387 | 1415 | 149 | 1 | 9 | 71 | 1 | 9 | 129 | 1 | 13 | 162 | 1 | 9 | 64 | 1 | 9 | 145 | 1 | 13 | 318 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -13.3 | 8.06 | A | 7 | -21.1 | -5.98 | A | 7 | 0.52 | A | 7 | 1004 | A | 7 | 80 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -7.28 | 5 | 0
1988-01-05 | 1900-01-04 | 11:00 | 11 | 541 | 1415 | 145 | 1 | 9 | 1 | 1 | 9 | 145 | 1 | 13 | 164 | 1 | 9 | 1 | 1 | 9 | 164 | 1 | 13 | 547 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -12.8 | 8.96 | A | 7 | -20.6 | -5.08 | A | 7 | 0.53 | A | 7 | 1004 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.38 | 5 | 0
1988-01-05 | 1900-01-04 | 12:00 | 12 | 635 | 1415 | 200 | 1 | 9 | 72 | 1 | 9 | 167 | 1 | 13 | 219 | 1 | 9 | 70 | 1 | 9 | 187 | 1 | 13 | 495 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -12.2 | 10.04 | A | 7 | -21.7 | -7.06 | A | 7 | 0.46 | A | 7 | 1003 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.46 | 5 | 0
1988-01-05 | 1900-01-04 | 13:00 | 13 | 663 | 1415 | 265 | 1 | 9 | 171 | 1 | 9 | 184 | 1 | 13 | 290 | 1 | 9 | 174 | 1 | 9 | 208 | 1 | 13 | 449 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | -10.6 | 12.92 | A | 7 | -20.6 | -5.08 | A | 7 | 0.44 | A | 7 | 1002 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.68 | 5 | 0
1988-01-05 | 1900-01-04 | 14:00 | 14 | 622 | 1415 | 405 | 1 | 9 | 554 | 1 | 9 | 161 | 1 | 13 | 423 | 1 | 9 | 542 | 1 | 9 | 184 | 1 | 13 | 327 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | -10 | 14 | A | 7 | -20.6 | -5.08 | A | 7 | 0.42 | A | 7 | 1001 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.68 | 5 | 0
1988-01-05 | 1900-01-04 | 15:00 | 15 | 516 | 1415 | 238 | 1 | 13 | 279 | 1 | 13 | 137 | 1 | 13 | 255 | 1 | 13 | 269 | 1 | 13 | 156 | 1 | 13 | 280 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | -9.4 | 15.08 | A | 7 | -20.6 | -5.08 | A | 7 | 0.4 | A | 7 | 1001 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.78 | 5 | 0
1988-01-05 | 1900-01-04 | 16:00 | 16 | 351 | 1415 | 162 | 1 | 13 | 138 | 1 | 13 | 128 | 1 | 13 | 173 | 1 | 13 | 117 | 1 | 13 | 144 | 1 | 13 | 281 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | -9.4 | 15.08 | A | 7 | -20 | -4 | A | 7 | 0.42 | A | 7 | 1001 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.7 | 5 | 0
1988-01-05 | 1900-01-04 | 17:00 | 17 | 141 | 1415 | 46 | 1 | 13 | 71 | 1 | 9 | 39 | 1 | 13 | 50 | 1 | 13 | 39 | 1 | 9 | 46 | 1 | 13 | 81 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -10.6 | 12.92 | A | 7 | -20.6 | -5.08 | A | 7 | 0.44 | A | 7 | 1000 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.68 | 5 | 0
1988-01-05 | 1900-01-04 | 18:00 | 18 | 2 | 177 | 4 | 1 | 13 | 1 | 1 | 13 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | -11.1 | 12.02 | A | 7 | -19.4 | -2.92 | A | 7 | 0.51 | A | 7 | 1000 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.42 | 5 | 0
1988-01-05 | 1900-01-04 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -11.7 | 10.94 | A | 7 | -20 | -4 | A | 7 | 0.5 | A | 7 | 1000 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.5 | 5 | 0
1988-01-05 | 1900-01-04 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -12.2 | 10.04 | A | 7 | -19.4 | -2.92 | A | 7 | 0.55 | A | 7 | 1000 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.32 | 5 | 0
1988-01-05 | 1900-01-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -12.2 | 10.04 | A | 7 | -18.9 | -2.02 | A | 7 | 0.58 | A | 7 | 1001 | A | 7 | 350 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.32 | 5 | 0
1988-01-05 | 1900-01-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -12.2 | 10.04 | A | 7 | -18.9 | -2.02 | A | 7 | 0.58 | A | 7 | 1001 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.32 | 5 | 0
1988-01-05 | 1900-01-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 7 | A | 7 | -12.8 | 8.96 | A | 7 | -18.3 | -0.94 | A | 7 | 0.64 | A | 7 | 1001 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.14 | 5 | 0
1988-01-05 | 1900-01-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -12.8 | 8.96 | A | 7 | -18.3 | -0.94 | A | 7 | 0.64 | A | 7 | 1001 | A | 7 | 30 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.14 | 5 | 0
1988-01-06 | 1900-01-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 3 | A | 7 | -13.3 | 8.06 | A | 7 | -18.9 | -2.02 | A | 7 | 0.63 | A | 7 | 1001 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.22 | 6 | 0
1988-01-06 | 1900-01-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 1 | A | 7 | -13.9 | 6.98 | A | 7 | -19.4 | -2.92 | A | 7 | 0.63 | A | 7 | 1001 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.02 | 6 | 0
1988-01-06 | 1900-01-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 1 | A | 7 | -13.9 | 6.98 | A | 7 | -18.9 | -2.02 | A | 7 | 0.66 | A | 7 | 1001 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.12 | 6 | 0
1988-01-06 | 1900-01-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -18.9 | -2.02 | A | 7 | 0.76 | A | 7 | 1001 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.82 | 6 | 0
1988-01-06 | 1900-01-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | -16.1 | 3.02 | A | 7 | -18.9 | -2.02 | A | 7 | 0.79 | A | 7 | 1001 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.72 | 6 | 0
1988-01-06 | 1900-01-05 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 6 | A | 7 | -15.6 | 3.92 | A | 7 | -19.4 | -2.92 | A | 7 | 0.72 | A | 7 | 1001 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.82 | 6 | 0
1988-01-06 | 1900-01-05 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -15.6 | 3.92 | A | 7 | -20 | -4 | A | 7 | 0.69 | A | 7 | 1000 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.9 | 6 | 0
1988-01-06 | 1900-01-05 | 8:00 | 8 | 11 | 460 | 7 | 1 | 13 | 0 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -15.6 | 3.92 | A | 7 | -20 | -4 | A | 7 | 0.69 | A | 7 | 1000 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.9 | 6 | 0
1988-01-06 | 1900-01-05 | 9:00 | 9 | 185 | 1415 | 50 | 1 | 13 | 49 | 1 | 9 | 44 | 1 | 13 | 55 | 1 | 13 | 31 | 1 | 9 | 51 | 1 | 13 | 93 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -15.6 | 3.92 | A | 7 | -20 | -4 | A | 7 | 0.69 | A | 7 | 1000 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.9 | 6 | 0
1988-01-06 | 1900-01-05 | 10:00 | 10 | 388 | 1415 | 160 | 1 | 9 | 199 | 1 | 9 | 105 | 1 | 13 | 169 | 1 | 9 | 173 | 1 | 9 | 121 | 1 | 13 | 207 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -13.9 | 6.98 | A | 7 | -18.9 | -2.02 | A | 7 | 0.66 | A | 7 | 1000 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.12 | 6 | 0
1988-01-06 | 1900-01-05 | 11:00 | 11 | 543 | 1415 | 107 | 1 | 9 | 4 | 1 | 9 | 105 | 1 | 13 | 123 | 1 | 9 | 3 | 1 | 9 | 122 | 1 | 13 | 433 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -13.3 | 8.06 | A | 7 | -20 | -4 | A | 7 | 0.58 | A | 7 | 1000 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.2 | 6 | 0
1988-01-06 | 1900-01-05 | 12:00 | 12 | 637 | 1415 | 206 | 1 | 9 | 9 | 1 | 9 | 202 | 1 | 13 | 231 | 1 | 9 | 8 | 1 | 9 | 228 | 1 | 13 | 748 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -20.6 | -5.08 | A | 7 | 0.5 | A | 7 | 1000 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.48 | 6 | 0
1988-01-06 | 1900-01-05 | 13:00 | 13 | 666 | 1415 | 200 | 1 | 9 | 5 | 1 | 9 | 197 | 1 | 13 | 225 | 1 | 9 | 4 | 1 | 9 | 223 | 1 | 13 | 758 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -20 | -4 | A | 7 | 0.5 | A | 7 | 998 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.5 | 6 | 0
1988-01-06 | 1900-01-05 | 14:00 | 14 | 625 | 1415 | 165 | 1 | 9 | 8 | 1 | 9 | 162 | 1 | 13 | 189 | 1 | 9 | 6 | 1 | 9 | 186 | 1 | 13 | 640 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -21.1 | -5.98 | A | 7 | 0.44 | A | 7 | 997 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -7.48 | 6 | 0
1988-01-06 | 1900-01-05 | 15:00 | 15 | 519 | 1415 | 150 | 1 | 9 | 4 | 1 | 9 | 149 | 1 | 13 | 169 | 1 | 9 | 3 | 1 | 9 | 168 | 1 | 13 | 544 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -21.1 | -5.98 | A | 7 | 0.44 | A | 7 | 997 | A | 7 | 60 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -7.48 | 6 | 0
1988-01-06 | 1900-01-05 | 16:00 | 16 | 355 | 1415 | 92 | 1 | 13 | 5 | 1 | 9 | 91 | 1 | 13 | 103 | 1 | 13 | 2 | 1 | 9 | 103 | 1 | 13 | 320 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -21.7 | -7.06 | A | 7 | 0.42 | A | 7 | 996 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.56 | 6 | 0
1988-01-06 | 1900-01-05 | 17:00 | 17 | 145 | 1415 | 60 | 1 | 13 | 54 | 1 | 13 | 54 | 1 | 13 | 63 | 1 | 13 | 30 | 1 | 13 | 60 | 1 | 13 | 113 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | -11.7 | 10.94 | A | 7 | -20.6 | -5.08 | A | 7 | 0.48 | A | 7 | 996 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.48 | 6 | 0
1988-01-06 | 1900-01-05 | 18:00 | 18 | 2 | 200 | 1 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -20 | -4 | A | 7 | 0.5 | A | 7 | 996 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.5 | 6 | 0
1988-01-06 | 1900-01-05 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -20.6 | -5.08 | A | 7 | 0.5 | A | 7 | 996 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.48 | 6 | 0
1988-01-06 | 1900-01-05 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -20.6 | -5.08 | A | 7 | 0.5 | A | 7 | 996 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.48 | 6 | 0
1988-01-06 | 1900-01-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -20.6 | -5.08 | A | 7 | 0.5 | A | 7 | 996 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.48 | 6 | 0
1988-01-06 | 1900-01-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -20 | -4 | A | 7 | 0.55 | A | 7 | 996 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.3 | 6 | 0
1988-01-06 | 1900-01-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -19.4 | -2.92 | A | 7 | 0.58 | A | 7 | 997 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1460 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.22 | 6 | 0
1988-01-06 | 1900-01-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -19.4 | -2.92 | A | 7 | 0.55 | A | 7 | 996 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.32 | 6 | 0
1988-01-07 | 1900-01-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -18.9 | -2.02 | A | 7 | 0.61 | A | 7 | 996 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.32 | 7 | 0
1988-01-07 | 1900-01-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -13.3 | 8.06 | A | 7 | -15.6 | 3.92 | A | 7 | 0.84 | A | 7 | 995 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 1220 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.22 | 7 | 0
1988-01-07 | 1900-01-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -13.3 | 8.06 | A | 7 | -15.6 | 3.92 | A | 7 | 0.84 | A | 7 | 995 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 4800 | A | 7 | 1070 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.22 | 7 | 0
1988-01-07 | 1900-01-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 994 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 1520 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 7 | 0
1988-01-07 | 1900-01-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 994 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 1070 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 7 | 0
1988-01-07 | 1900-01-06 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 7 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 994 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 9700 | A | 7 | 980 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 7 | 0
1988-01-07 | 1900-01-06 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 7 | A | 7 | -13.9 | 6.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.87 | A | 7 | 994 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 2130 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.32 | 7 | 0
1988-01-07 | 1900-01-06 | 8:00 | 8 | 11 | 460 | 12 | 1 | 13 | 39 | 1 | 13 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | -14.4 | 6.08 | A | 7 | -15.6 | 3.92 | A | 7 | 0.91 | A | 7 | 994 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.52 | 7 | 0
1988-01-07 | 1900-01-06 | 9:00 | 9 | 185 | 1415 | 74 | 1 | 13 | 273 | 1 | 13 | 38 | 1 | 13 | 78 | 1 | 13 | 165 | 1 | 13 | 56 | 1 | 13 | 68 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | -12.8 | 8.96 | A | 7 | -15 | 5 | A | 7 | 0.84 | A | 7 | 994 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.3 | 7 | 0
1988-01-07 | 1900-01-06 | 10:00 | 10 | 389 | 1415 | 224 | 1 | 9 | 617 | 1 | 9 | 53 | 1 | 13 | 229 | 1 | 9 | 538 | 1 | 9 | 80 | 1 | 13 | 102 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | -11.7 | 10.94 | A | 7 | -15 | 5 | A | 7 | 0.77 | A | 7 | 994 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4 | 7 | 0
1988-01-07 | 1900-01-06 | 11:00 | 11 | 544 | 1415 | 332 | 1 | 9 | 666 | 1 | 9 | 74 | 1 | 13 | 350 | 1 | 9 | 633 | 1 | 9 | 106 | 1 | 13 | 149 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 993 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 7 | 0
1988-01-07 | 1900-01-06 | 12:00 | 12 | 640 | 1415 | 454 | 1 | 9 | 865 | 1 | 9 | 62 | 1 | 13 | 477 | 1 | 9 | 833 | 1 | 9 | 99 | 1 | 13 | 140 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | -9.4 | 15.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.74 | A | 7 | 993 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 7 | 0
1988-01-07 | 1900-01-06 | 13:00 | 13 | 668 | 1415 | 459 | 1 | 9 | 878 | 1 | 9 | 43 | 1 | 13 | 487 | 1 | 9 | 853 | 1 | 9 | 83 | 1 | 13 | 120 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | -7.8 | 17.96 | A | 7 | -13.3 | 8.06 | A | 7 | 0.65 | A | 7 | 992 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.36 | 7 | 0
1988-01-07 | 1900-01-06 | 14:00 | 14 | 628 | 1415 | 462 | 1 | 9 | 902 | 1 | 9 | 61 | 1 | 13 | 486 | 1 | 9 | 867 | 1 | 9 | 99 | 1 | 13 | 137 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 990 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 7 | 0
1988-01-07 | 1900-01-06 | 15:00 | 15 | 523 | 1415 | 317 | 1 | 9 | 606 | 1 | 9 | 94 | 1 | 13 | 330 | 1 | 9 | 563 | 1 | 9 | 121 | 1 | 13 | 180 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 990 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.14 | 7 | 0
1988-01-07 | 1900-01-06 | 16:00 | 16 | 358 | 1415 | 204 | 1 | 13 | 582 | 1 | 13 | 57 | 1 | 13 | 213 | 1 | 13 | 489 | 1 | 13 | 88 | 1 | 13 | 107 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 990 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.54 | 7 | 0
1988-01-07 | 1900-01-06 | 17:00 | 17 | 149 | 1415 | 65 | 1 | 13 | 318 | 1 | 9 | 32 | 1 | 13 | 66 | 1 | 13 | 181 | 1 | 9 | 47 | 1 | 13 | 55 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.77 | A | 7 | 990 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.64 | 7 | 0
1988-01-07 | 1900-01-06 | 18:00 | 18 | 3 | 224 | 9 | 1 | 13 | 36 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.77 | A | 7 | 990 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.76 | 7 | 0
1988-01-07 | 1900-01-06 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -12.8 | 8.96 | A | 7 | 0.8 | A | 7 | 990 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.96 | 7 | 0
1988-01-07 | 1900-01-06 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.84 | A | 7 | 990 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.16 | 7 | 0
1988-01-07 | 1900-01-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -13.3 | 8.06 | A | 7 | 0.92 | A | 7 | 989 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.66 | 7 | 0
1988-01-07 | 1900-01-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -13.9 | 6.98 | A | 7 | 0.92 | A | 7 | 989 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.58 | 7 | 0
1988-01-07 | 1900-01-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.92 | A | 7 | 989 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.56 | 7 | 0
1988-01-07 | 1900-01-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -13.3 | 8.06 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.86 | 7 | 0
1988-01-08 | 1900-01-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 989 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 1 | 0
1988-01-08 | 1900-01-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -15 | 5 | A | 7 | 0.91 | A | 7 | 989 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.6 | 1 | 0
1988-01-08 | 1900-01-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -16.1 | 3.02 | A | 7 | 0.91 | A | 7 | 989 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.62 | 1 | 0
1988-01-08 | 1900-01-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -15.6 | 3.92 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.72 | 1 | 0
1988-01-08 | 1900-01-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -16.1 | 3.02 | A | 7 | 0.91 | A | 7 | 988 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.62 | 1 | 0
1988-01-08 | 1900-01-07 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | -14.4 | 6.08 | A | 7 | -15.6 | 3.92 | A | 7 | 0.91 | A | 7 | 988 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.52 | 1 | 0
1988-01-08 | 1900-01-07 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | -15 | 5 | A | 7 | -16.1 | 3.02 | A | 7 | 0.91 | A | 7 | 988 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.62 | 1 | 0
1988-01-08 | 1900-01-07 | 8:00 | 8 | 12 | 460 | 12 | 1 | 13 | 46 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | -15 | 5 | A | 7 | -16.7 | 1.94 | A | 7 | 0.87 | A | 7 | 989 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.44 | 1 | 0
1988-01-08 | 1900-01-07 | 9:00 | 9 | 186 | 1415 | 98 | 1 | 13 | 572 | 1 | 9 | 22 | 1 | 13 | 103 | 1 | 13 | 413 | 1 | 9 | 49 | 1 | 13 | 51 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 989 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 1 | 0
1988-01-08 | 1900-01-07 | 10:00 | 10 | 390 | 1415 | 253 | 1 | 9 | 785 | 1 | 9 | 35 | 1 | 13 | 268 | 1 | 9 | 694 | 1 | 9 | 75 | 1 | 13 | 88 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -13.9 | 6.98 | A | 7 | 0.84 | A | 7 | 989 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.18 | 1 | 0
1988-01-08 | 1900-01-07 | 11:00 | 11 | 546 | 1415 | 385 | 1 | 9 | 880 | 1 | 9 | 45 | 1 | 13 | 408 | 1 | 9 | 830 | 1 | 9 | 86 | 1 | 13 | 114 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -12.8 | 8.96 | A | 7 | 0.8 | A | 7 | 990 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.96 | 1 | 0
1988-01-08 | 1900-01-07 | 12:00 | 12 | 642 | 1415 | 468 | 1 | 9 | 885 | 1 | 9 | 65 | 1 | 13 | 490 | 1 | 9 | 853 | 1 | 9 | 102 | 1 | 13 | 142 | 1 | 18 | 5 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -13.3 | 8.06 | A | 7 | 0.68 | A | 7 | 989 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.46 | 1 | 0
1988-01-08 | 1900-01-07 | 13:00 | 13 | 671 | 1415 | 490 | 1 | 9 | 890 | 1 | 9 | 68 | 1 | 13 | 515 | 1 | 9 | 862 | 1 | 9 | 104 | 1 | 13 | 148 | 1 | 18 | 5 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.8 | 8.96 | A | 7 | 0.65 | A | 7 | 988 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.16 | 1 | 0
1988-01-08 | 1900-01-07 | 14:00 | 14 | 632 | 1415 | 459 | 1 | 9 | 906 | 1 | 9 | 54 | 1 | 13 | 485 | 1 | 9 | 872 | 1 | 9 | 94 | 1 | 13 | 132 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.06 | 1 | 0
1988-01-08 | 1900-01-07 | 15:00 | 15 | 526 | 1415 | 365 | 1 | 9 | 847 | 1 | 9 | 51 | 1 | 13 | 387 | 1 | 9 | 794 | 1 | 9 | 90 | 1 | 13 | 117 | 1 | 18 | 4 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.96 | 1 | 0
1988-01-08 | 1900-01-07 | 16:00 | 16 | 362 | 1415 | 227 | 1 | 13 | 753 | 1 | 9 | 36 | 1 | 13 | 243 | 1 | 13 | 654 | 1 | 9 | 75 | 1 | 13 | 86 | 1 | 21 | 3 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.6 | A | 7 | 988 | A | 7 | 320 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.06 | 1 | 0
1988-01-08 | 1900-01-07 | 17:00 | 17 | 153 | 1415 | 72 | 1 | 13 | 489 | 1 | 9 | 20 | 1 | 13 | 77 | 1 | 13 | 333 | 1 | 9 | 41 | 1 | 13 | 44 | 1 | 21 | 3 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -13.9 | 6.98 | A | 7 | 0.62 | A | 7 | 988 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.18 | 1 | 0
1988-01-08 | 1900-01-07 | 18:00 | 18 | 3 | 248 | 4 | 1 | 13 | 14 | 1 | 13 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 988 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 1 | 0
1988-01-08 | 1900-01-07 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 990 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.68 | 1 | 0
1988-01-08 | 1900-01-07 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 990 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.68 | 1 | 0
1988-01-08 | 1900-01-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -10.6 | 12.92 | A | 7 | -15 | 5 | A | 7 | 0.7 | A | 7 | 989 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.7 | 1 | 0
1988-01-08 | 1900-01-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -15.6 | 3.92 | A | 7 | 0.7 | A | 7 | 990 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.62 | 1 | 0
1988-01-08 | 1900-01-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -11.1 | 12.02 | A | 7 | -15 | 5 | A | 7 | 0.73 | A | 7 | 991 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.8 | 1 | 0
1988-01-08 | 1900-01-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 2 | A | 7 | -10.6 | 12.92 | A | 7 | -15 | 5 | A | 7 | 0.7 | A | 7 | 990 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.7 | 1 | 0
1988-01-09 | 1900-01-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -15.6 | 3.92 | A | 7 | 0.67 | A | 7 | 991 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.52 | 2 | 0
1988-01-09 | 1900-01-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -15.6 | 3.92 | A | 7 | 0.67 | A | 7 | 991 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.52 | 2 | 0
1988-01-09 | 1900-01-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -15 | 5 | A | 7 | 0.7 | A | 7 | 991 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.7 | 2 | 0
1988-01-09 | 1900-01-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -14.4 | 6.08 | A | 7 | 0.77 | A | 7 | 991 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.98 | 2 | 0
1988-01-09 | 1900-01-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -13.9 | 6.98 | A | 7 | 0.88 | A | 7 | 991 | A | 7 | 350 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.38 | 2 | 0
1988-01-09 | 1900-01-08 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -13.9 | 6.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.87 | A | 7 | 992 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.32 | 2 | 0
1988-01-09 | 1900-01-08 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -15.6 | 3.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.91 | A | 7 | 992 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.54 | 2 | 0
1988-01-09 | 1900-01-08 | 8:00 | 8 | 12 | 460 | 9 | 1 | 13 | 13 | 1 | 13 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | -15.6 | 3.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.91 | A | 7 | 993 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.54 | 2 | 0
1988-01-09 | 1900-01-08 | 9:00 | 9 | 187 | 1415 | 82 | 1 | 13 | 323 | 1 | 9 | 39 | 1 | 13 | 83 | 1 | 13 | 205 | 1 | 9 | 56 | 1 | 13 | 68 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 993 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 2 | 0
1988-01-09 | 1900-01-08 | 10:00 | 10 | 391 | 1415 | 155 | 1 | 13 | 156 | 1 | 13 | 112 | 1 | 13 | 169 | 1 | 13 | 138 | 1 | 13 | 130 | 1 | 13 | 248 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | -11.7 | 10.94 | A | 7 | -14.4 | 6.08 | A | 7 | 0.8 | A | 7 | 993 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.18 | 2 | 0
1988-01-09 | 1900-01-08 | 11:00 | 11 | 548 | 1415 | 298 | 1 | 13 | 463 | 1 | 13 | 118 | 1 | 13 | 316 | 1 | 13 | 442 | 1 | 13 | 144 | 1 | 13 | 227 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.68 | 2 | 0
1988-01-09 | 1900-01-08 | 12:00 | 12 | 644 | 1415 | 433 | 1 | 13 | 673 | 1 | 13 | 125 | 1 | 13 | 448 | 1 | 13 | 649 | 1 | 13 | 151 | 1 | 13 | 249 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -8.9 | 15.98 | A | 7 | -14.4 | 6.08 | A | 7 | 0.65 | A | 7 | 992 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.48 | 2 | 0
1988-01-09 | 1900-01-08 | 13:00 | 13 | 674 | 1415 | 472 | 1 | 13 | 810 | 1 | 13 | 85 | 1 | 13 | 493 | 1 | 13 | 789 | 1 | 13 | 115 | 1 | 13 | 177 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -8.3 | 17.06 | A | 7 | -13.9 | 6.98 | A | 7 | 0.65 | A | 7 | 991 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.38 | 2 | 0
1988-01-09 | 1900-01-08 | 14:00 | 14 | 635 | 1415 | 433 | 1 | 13 | 702 | 1 | 13 | 118 | 1 | 13 | 451 | 1 | 13 | 677 | 1 | 13 | 145 | 1 | 13 | 236 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -8.9 | 15.98 | A | 7 | -15 | 5 | A | 7 | 0.62 | A | 7 | 991 | A | 7 | 40 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.4 | 2 | 0
1988-01-09 | 1900-01-08 | 15:00 | 15 | 530 | 1415 | 376 | 1 | 13 | 770 | 1 | 13 | 88 | 1 | 13 | 393 | 1 | 13 | 721 | 1 | 13 | 122 | 1 | 13 | 171 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -8.9 | 15.98 | A | 7 | -14.4 | 6.08 | A | 7 | 0.65 | A | 7 | 990 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.48 | 2 | 0
1988-01-09 | 1900-01-08 | 16:00 | 16 | 366 | 1415 | 218 | 1 | 13 | 621 | 1 | 9 | 58 | 1 | 13 | 228 | 1 | 13 | 526 | 1 | 9 | 91 | 1 | 13 | 109 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | -7.8 | 17.96 | A | 7 | -13.9 | 6.98 | A | 7 | 0.62 | A | 7 | 991 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.18 | 2 | 0
1988-01-09 | 1900-01-08 | 17:00 | 17 | 157 | 1415 | 67 | 1 | 13 | 375 | 1 | 9 | 27 | 1 | 13 | 71 | 1 | 13 | 223 | 1 | 9 | 46 | 1 | 13 | 49 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -8.9 | 15.98 | A | 7 | -14.4 | 6.08 | A | 7 | 0.65 | A | 7 | 991 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.48 | 2 | 0
1988-01-09 | 1900-01-08 | 18:00 | 18 | 4 | 271 | 5 | 1 | 13 | 14 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 991 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.68 | 2 | 0
1988-01-09 | 1900-01-08 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -14.4 | 6.08 | A | 7 | 0.8 | A | 7 | 992 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.18 | 2 | 0
1988-01-09 | 1900-01-08 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -15 | 5 | A | 7 | 0.8 | A | 7 | 992 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.1 | 2 | 0
1988-01-09 | 1900-01-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -15 | 5 | A | 7 | 0.8 | A | 7 | 992 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.1 | 2 | 0
1988-01-09 | 1900-01-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -12.2 | 10.04 | A | 7 | -14.4 | 6.08 | A | 7 | 0.84 | A | 7 | 992 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.38 | 2 | 0
1988-01-09 | 1900-01-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -14.4 | 6.08 | A | 7 | 0.88 | A | 7 | 992 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.48 | 2 | 0
1988-01-09 | 1900-01-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -15.6 | 3.92 | A | 7 | 0.91 | A | 7 | 992 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.52 | 2 | 0
1988-01-10 | 1900-01-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 992 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 3 | 0
1988-01-10 | 1900-01-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 992 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 3 | 0
1988-01-10 | 1900-01-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -15 | 5 | A | 7 | 0.91 | A | 7 | 992 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.6 | 3 | 0
1988-01-10 | 1900-01-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -15 | 5 | A | 7 | 0.91 | A | 7 | 992 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.6 | 3 | 0
1988-01-10 | 1900-01-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 992 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 3 | 0
1988-01-10 | 1900-01-09 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -15 | 5 | A | 7 | 0.91 | A | 7 | 992 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.6 | 3 | 0
1988-01-10 | 1900-01-09 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.87 | A | 7 | 992 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.32 | 3 | 0
1988-01-10 | 1900-01-09 | 8:00 | 8 | 12 | 460 | 7 | 1 | 13 | 13 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.87 | A | 7 | 992 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.32 | 3 | 0
1988-01-10 | 1900-01-09 | 9:00 | 9 | 188 | 1415 | 83 | 1 | 13 | 325 | 1 | 9 | 39 | 1 | 13 | 83 | 1 | 13 | 207 | 1 | 9 | 56 | 1 | 13 | 68 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.88 | A | 7 | 992 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.46 | 3 | 0
1988-01-10 | 1900-01-09 | 10:00 | 10 | 393 | 1415 | 229 | 1 | 9 | 599 | 1 | 9 | 62 | 1 | 13 | 238 | 1 | 9 | 519 | 1 | 9 | 93 | 1 | 13 | 117 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.81 | A | 7 | 992 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.04 | 3 | 0
1988-01-10 | 1900-01-09 | 11:00 | 11 | 550 | 1415 | 363 | 1 | 9 | 730 | 1 | 9 | 79 | 1 | 13 | 383 | 1 | 9 | 693 | 1 | 9 | 112 | 1 | 13 | 158 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 992 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 3 | 0
1988-01-10 | 1900-01-09 | 12:00 | 12 | 647 | 1415 | 447 | 1 | 9 | 780 | 1 | 9 | 89 | 1 | 13 | 461 | 1 | 9 | 752 | 1 | 9 | 116 | 1 | 13 | 177 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.62 | A | 7 | 991 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.06 | 3 | 0
1988-01-10 | 1900-01-09 | 13:00 | 13 | 677 | 1415 | 199 | 1 | 9 | 44 | 1 | 9 | 178 | 1 | 13 | 219 | 1 | 9 | 43 | 1 | 9 | 198 | 1 | 13 | 539 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -10 | 14 | A | 7 | 0.71 | A | 7 | 990 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 0.6 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.2 | 3 | 0
1988-01-10 | 1900-01-09 | 14:00 | 14 | 639 | 1415 | 204 | 1 | 9 | 30 | 1 | 9 | 191 | 1 | 13 | 225 | 1 | 9 | 30 | 1 | 9 | 211 | 1 | 13 | 552 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 990 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 520 | A | 7 | 0.6 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.68 | 3 | 0
1988-01-10 | 1900-01-09 | 15:00 | 15 | 534 | 1415 | 125 | 1 | 9 | 10 | 1 | 9 | 121 | 1 | 13 | 143 | 1 | 9 | 7 | 1 | 9 | 140 | 1 | 13 | 479 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 988 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 0.7 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.06 | 3 | 0
1988-01-10 | 1900-01-09 | 16:00 | 16 | 370 | 1415 | 91 | 1 | 9 | 8 | 1 | 9 | 88 | 1 | 13 | 102 | 1 | 9 | 4 | 1 | 9 | 100 | 1 | 13 | 319 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.85 | A | 7 | 988 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 0.7 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.06 | 3 | 0
1988-01-10 | 1900-01-09 | 17:00 | 17 | 161 | 1415 | 26 | 1 | 13 | 2 | 1 | 9 | 25 | 1 | 13 | 29 | 1 | 13 | 0 | 1 | 9 | 29 | 1 | 13 | 92 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 370 | A | 7 | 0.7 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.06 | 3 | 0
1988-01-10 | 1900-01-09 | 18:00 | 18 | 5 | 295 | 1 | 1 | 13 | 0 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.85 | A | 7 | 988 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 370 | A | 7 | 0.7 | E | 8 | 0.111 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.86 | 3 | 0
1988-01-10 | 1900-01-09 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 11300 | A | 7 | 370 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.06 | 3 | 0
1988-01-10 | 1900-01-09 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 986 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 340 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.06 | 3 | 0
1988-01-10 | 1900-01-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.2 | 19.04 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 200 | A | 7 | 11.8 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.44 | 3 | 0
1988-01-10 | 1900-01-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 985 | A | 7 | 200 | A | 7 | 12.4 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.06 | 3 | 0
1988-01-10 | 1900-01-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 985 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.06 | 3 | 0
1988-01-10 | 1900-01-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.34 | 3 | 0
1988-01-11 | 1900-01-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 983 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.04 | 4 | 0
1988-01-11 | 1900-01-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 983 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 340 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.04 | 4 | 0
1988-01-11 | 1900-01-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -5.6 | 21.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.92 | A | 7 | 982 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 340 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.34 | 4 | 0
1988-01-11 | 1900-01-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -5 | 23 | A | 7 | -6.1 | 21.02 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.32 | 4 | 0
1988-01-11 | 1900-01-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -5 | 23 | A | 7 | -6.1 | 21.02 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.32 | 4 | 0
1988-01-11 | 1900-01-10 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -5 | 23 | A | 7 | -6.1 | 21.02 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.32 | 4 | 0
1988-01-11 | 1900-01-10 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.22 | 4 | 0
1988-01-11 | 1900-01-10 | 8:00 | 8 | 12 | 483 | 6 | 1 | 13 | 0 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 12900 | A | 7 | 210 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 4 | 0
1988-01-11 | 1900-01-10 | 9:00 | 9 | 189 | 1414 | 48 | 1 | 13 | 2 | 1 | 9 | 48 | 1 | 13 | 54 | 1 | 13 | 0 | 1 | 9 | 54 | 1 | 13 | 157 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 9700 | A | 7 | 270 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.26 | 4 | 0
1988-01-11 | 1900-01-10 | 10:00 | 10 | 395 | 1414 | 187 | 1 | 9 | 405 | 1 | 9 | 73 | 1 | 13 | 200 | 1 | 9 | 350 | 1 | 9 | 101 | 1 | 13 | 132 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 190 | A | 7 | 10.8 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 4 | 0
1988-01-11 | 1900-01-10 | 11:00 | 11 | 552 | 1414 | 352 | 1 | 9 | 677 | 1 | 9 | 87 | 1 | 13 | 369 | 1 | 9 | 641 | 1 | 9 | 117 | 1 | 13 | 172 | 1 | 18 | 6 | A | 7 | 1 | A | 7 | 0.6 | 33.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.48 | 4 | 0
1988-01-11 | 1900-01-10 | 12:00 | 12 | 650 | 1414 | 368 | 1 | 9 | 514 | 1 | 9 | 131 | 1 | 13 | 395 | 1 | 9 | 509 | 1 | 9 | 160 | 1 | 13 | 263 | 1 | 18 | 9 | A | 7 | 2 | A | 7 | 2.2 | 35.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 978 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.78 | 4 | 0
1988-01-11 | 1900-01-10 | 13:00 | 13 | 680 | 1414 | 360 | 1 | 13 | 362 | 1 | 13 | 186 | 1 | 13 | 387 | 1 | 13 | 373 | 1 | 13 | 207 | 1 | 13 | 410 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 4 | 0
1988-01-11 | 1900-01-10 | 14:00 | 14 | 642 | 1414 | 341 | 1 | 9 | 298 | 1 | 9 | 206 | 1 | 13 | 362 | 1 | 9 | 303 | 1 | 9 | 223 | 1 | 13 | 461 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 975 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 4 | 0
1988-01-11 | 1900-01-10 | 15:00 | 15 | 538 | 1414 | 202 | 1 | 13 | 93 | 1 | 13 | 167 | 1 | 13 | 222 | 1 | 13 | 89 | 1 | 13 | 188 | 1 | 13 | 454 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 4 | 0
1988-01-11 | 1900-01-10 | 16:00 | 16 | 375 | 1414 | 85 | 1 | 9 | 57 | 1 | 9 | 70 | 1 | 13 | 95 | 1 | 9 | 50 | 1 | 9 | 82 | 1 | 13 | 154 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 4 | 0
1988-01-11 | 1900-01-10 | 17:00 | 17 | 165 | 1414 | 66 | 1 | 13 | 40 | 1 | 13 | 61 | 1 | 13 | 72 | 1 | 13 | 28 | 1 | 13 | 68 | 1 | 13 | 131 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 2.2 | 35.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.62 | A | 7 | 972 | A | 7 | 180 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.78 | 4 | 0
1988-01-11 | 1900-01-10 | 18:00 | 18 | 6 | 318 | 1 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 2.2 | 35.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.62 | A | 7 | 970 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.78 | 4 | 0
1988-01-11 | 1900-01-10 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 2.8 | 37.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.59 | A | 7 | 969 | A | 7 | 170 | A | 7 | 11.8 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.58 | 4 | 0
1988-01-11 | 1900-01-10 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 968 | A | 7 | 180 | A | 7 | 11.8 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 4 | 0
1988-01-11 | 1900-01-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 967 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 4 | 0
1988-01-11 | 1900-01-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.55 | A | 7 | 966 | A | 7 | 190 | A | 7 | 15.4 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.18 | 4 | 0
1988-01-11 | 1900-01-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.57 | A | 7 | 966 | A | 7 | 190 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.18 | 4 | 0
1988-01-11 | 1900-01-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 966 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 4 | 0
1988-01-12 | 1900-01-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 965 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 5 | 0
1988-01-12 | 1900-01-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 966 | A | 7 | 200 | A | 7 | 13.4 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 5 | 0
1988-01-12 | 1900-01-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 4 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 965 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 5 | 0
1988-01-12 | 1900-01-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 966 | A | 7 | 200 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 5 | 0
1988-01-12 | 1900-01-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 1.7 | 35.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.82 | A | 7 | 966 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.22 | 5 | 0
1988-01-12 | 1900-01-11 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 1.7 | 35.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.82 | A | 7 | 968 | A | 7 | 230 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.22 | 5 | 0
1988-01-12 | 1900-01-11 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 1.1 | 33.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.82 | A | 7 | 969 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.14 | 5 | 0
1988-01-12 | 1900-01-11 | 8:00 | 8 | 13 | 483 | 10 | 1 | 13 | 35 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 0.6 | 33.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.73 | A | 7 | 971 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.58 | 5 | 0
1988-01-12 | 1900-01-11 | 9:00 | 9 | 190 | 1414 | 71 | 1 | 13 | 164 | 1 | 13 | 49 | 1 | 13 | 75 | 1 | 13 | 97 | 1 | 13 | 62 | 1 | 13 | 92 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 1.7 | 35.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.76 | A | 7 | 972 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.74 | 5 | 0
1988-01-12 | 1900-01-11 | 10:00 | 10 | 396 | 1414 | 246 | 1 | 9 | 725 | 1 | 9 | 42 | 1 | 13 | 260 | 1 | 9 | 643 | 1 | 9 | 78 | 1 | 13 | 94 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 280 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 5 | 0
1988-01-12 | 1900-01-11 | 11:00 | 11 | 554 | 1414 | 206 | 1 | 9 | 104 | 1 | 9 | 165 | 1 | 13 | 224 | 1 | 9 | 102 | 1 | 9 | 184 | 1 | 13 | 385 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 1.1 | 33.98 | A | 7 | -5 | 23 | A | 7 | 0.64 | A | 7 | 976 | A | 7 | 300 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20 | 5 | 0
1988-01-12 | 1900-01-11 | 12:00 | 12 | 652 | 1414 | 473 | 1 | 9 | 895 | 1 | 9 | 59 | 1 | 13 | 498 | 1 | 9 | 865 | 1 | 9 | 97 | 1 | 13 | 139 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -11.1 | 12.02 | A | 7 | 0.45 | A | 7 | 978 | A | 7 | 290 | A | 7 | 13.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.92 | 5 | 0
1988-01-12 | 1900-01-11 | 13:00 | 13 | 684 | 1414 | 504 | 1 | 9 | 914 | 1 | 9 | 61 | 1 | 13 | 530 | 1 | 9 | 888 | 1 | 9 | 99 | 1 | 13 | 145 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -15 | 5 | A | 7 | 0.42 | A | 7 | 979 | A | 7 | 270 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.5 | 5 | 0
1988-01-12 | 1900-01-11 | 14:00 | 14 | 646 | 1414 | 466 | 1 | 9 | 893 | 1 | 9 | 58 | 1 | 13 | 492 | 1 | 9 | 862 | 1 | 9 | 96 | 1 | 13 | 138 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.4 | A | 7 | 980 | A | 7 | 310 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.42 | 5 | 0
1988-01-12 | 1900-01-11 | 15:00 | 15 | 542 | 1414 | 377 | 1 | 9 | 851 | 1 | 9 | 51 | 1 | 13 | 399 | 1 | 9 | 801 | 1 | 9 | 90 | 1 | 13 | 119 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -16.7 | 1.94 | A | 7 | 0.4 | A | 7 | 982 | A | 7 | 300 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.36 | 5 | 0
1988-01-12 | 1900-01-11 | 16:00 | 16 | 379 | 1414 | 234 | 1 | 9 | 729 | 1 | 9 | 40 | 1 | 13 | 249 | 1 | 9 | 640 | 1 | 9 | 77 | 1 | 13 | 91 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -16.1 | 3.02 | A | 7 | 0.46 | A | 7 | 984 | A | 7 | 300 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.92 | 5 | 0
1988-01-12 | 1900-01-11 | 17:00 | 17 | 169 | 1414 | 79 | 1 | 13 | 462 | 1 | 9 | 25 | 1 | 13 | 82 | 1 | 13 | 306 | 1 | 9 | 45 | 1 | 13 | 48 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -16.1 | 3.02 | A | 7 | 0.52 | A | 7 | 985 | A | 7 | 300 | A | 7 | 13.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.12 | 5 | 0
1988-01-12 | 1900-01-11 | 18:00 | 18 | 6 | 342 | 7 | 1 | 13 | 32 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -15.6 | 3.92 | A | 7 | 0.56 | A | 7 | 987 | A | 7 | 320 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.12 | 5 | 0
1988-01-12 | 1900-01-11 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -15 | 5 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.4 | 5 | 0
1988-01-12 | 1900-01-11 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 991 | A | 7 | 310 | A | 7 | 9.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 5 | 0
1988-01-12 | 1900-01-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 992 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 5 | 0
1988-01-12 | 1900-01-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 993 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 5 | 0
1988-01-12 | 1900-01-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 994 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.6 | 5 | 0
1988-01-12 | 1900-01-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -15.6 | 3.92 | A | 7 | 0.7 | A | 7 | 995 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.62 | 5 | 0
1988-01-13 | 1900-01-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -20 | -4 | A | 7 | 0.55 | A | 7 | 995 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.3 | 6 | 0
1988-01-13 | 1900-01-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -18.3 | -0.94 | A | 7 | 0.66 | A | 7 | 996 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.14 | 6 | 0
1988-01-13 | 1900-01-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -18.3 | -0.94 | A | 7 | 0.69 | A | 7 | 996 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.04 | 6 | 0
1988-01-13 | 1900-01-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -19.4 | -2.92 | A | 7 | 0.69 | A | 7 | 997 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.92 | 6 | 0
1988-01-13 | 1900-01-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -18.9 | -2.02 | A | 7 | 0.73 | A | 7 | 997 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.92 | 6 | 0
1988-01-13 | 1900-01-12 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -18.9 | -2.02 | A | 7 | 0.76 | A | 7 | 997 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.82 | 6 | 0
1988-01-13 | 1900-01-12 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -18.9 | -2.02 | A | 7 | 0.76 | A | 7 | 997 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.82 | 6 | 0
1988-01-13 | 1900-01-12 | 8:00 | 8 | 13 | 483 | 12 | 1 | 13 | 52 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -18.3 | -0.94 | A | 7 | 0.8 | A | 7 | 997 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.64 | 6 | 0
1988-01-13 | 1900-01-12 | 9:00 | 9 | 192 | 1414 | 97 | 1 | 13 | 487 | 1 | 9 | 30 | 1 | 13 | 97 | 1 | 13 | 336 | 1 | 9 | 51 | 1 | 13 | 55 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -17.2 | 1.04 | A | 7 | 0.7 | A | 7 | 997 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.06 | 6 | 0
1988-01-13 | 1900-01-12 | 10:00 | 10 | 398 | 1414 | 255 | 1 | 9 | 740 | 1 | 9 | 45 | 1 | 13 | 266 | 1 | 9 | 655 | 1 | 9 | 81 | 1 | 13 | 94 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -16.7 | 1.94 | A | 7 | 0.59 | A | 7 | 998 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.34 | 6 | 0
1988-01-13 | 1900-01-12 | 11:00 | 11 | 557 | 1414 | 390 | 1 | 9 | 844 | 1 | 9 | 56 | 1 | 13 | 410 | 1 | 9 | 798 | 1 | 9 | 94 | 1 | 13 | 125 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -17.2 | 1.04 | A | 7 | 0.43 | A | 7 | 998 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.06 | 6 | 0
1988-01-13 | 1900-01-12 | 12:00 | 12 | 656 | 1414 | 477 | 1 | 9 | 890 | 1 | 9 | 63 | 1 | 13 | 501 | 1 | 9 | 860 | 1 | 9 | 100 | 1 | 13 | 143 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -17.2 | 1.04 | A | 7 | 0.35 | A | 7 | 997 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.36 | 6 | 0
1988-01-13 | 1900-01-12 | 13:00 | 13 | 687 | 1414 | 502 | 1 | 9 | 897 | 1 | 9 | 66 | 1 | 13 | 528 | 1 | 9 | 871 | 1 | 9 | 103 | 1 | 13 | 149 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -15 | 5 | A | 7 | 0.34 | A | 7 | 995 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.2 | 6 | 0
1988-01-13 | 1900-01-12 | 14:00 | 14 | 650 | 1414 | 468 | 1 | 9 | 882 | 1 | 9 | 63 | 1 | 13 | 493 | 1 | 9 | 851 | 1 | 9 | 100 | 1 | 13 | 142 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.35 | A | 7 | 995 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.86 | 6 | 0
1988-01-13 | 1900-01-12 | 15:00 | 15 | 546 | 1414 | 375 | 1 | 9 | 831 | 1 | 9 | 55 | 1 | 13 | 397 | 1 | 9 | 783 | 1 | 9 | 93 | 1 | 13 | 123 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.35 | A | 7 | 994 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.66 | 6 | 0
1988-01-13 | 1900-01-12 | 16:00 | 16 | 383 | 1414 | 235 | 1 | 9 | 712 | 1 | 9 | 43 | 1 | 13 | 248 | 1 | 9 | 624 | 1 | 9 | 78 | 1 | 13 | 90 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.37 | A | 7 | 994 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.54 | 6 | 0
1988-01-13 | 1900-01-12 | 17:00 | 17 | 173 | 1414 | 80 | 1 | 13 | 436 | 1 | 9 | 27 | 1 | 13 | 81 | 1 | 13 | 291 | 1 | 9 | 46 | 1 | 13 | 50 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -11.1 | 12.02 | A | 7 | 0.43 | A | 7 | 994 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.82 | 6 | 0
1988-01-13 | 1900-01-12 | 18:00 | 18 | 7 | 365 | 8 | 1 | 13 | 29 | 1 | 9 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.53 | A | 7 | 994 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.32 | 6 | 0
1988-01-13 | 1900-01-12 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -11.1 | 12.02 | A | 7 | 0.65 | A | 7 | 994 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.02 | 6 | 0
1988-01-13 | 1900-01-12 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -9.4 | 15.08 | A | 7 | 0.71 | A | 7 | 994 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.18 | 6 | 0
1988-01-13 | 1900-01-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -10 | 14 | A | 7 | 0.78 | A | 7 | 994 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.6 | 6 | 0
1988-01-13 | 1900-01-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.81 | A | 7 | 994 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.88 | 6 | 0
1988-01-13 | 1900-01-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.78 | A | 7 | 994 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 6 | 0
1988-01-13 | 1900-01-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | -4.4 | 24.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.75 | A | 7 | 995 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.36 | 6 | 0
1988-01-14 | 1900-01-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -5.6 | 21.92 | A | 7 | -9.4 | 15.08 | A | 7 | 0.74 | A | 7 | 994 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.38 | 7 | 0
1988-01-14 | 1900-01-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -10 | 14 | A | 7 | 0.78 | A | 7 | 994 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.6 | 7 | 0
1988-01-14 | 1900-01-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -6.7 | 19.94 | A | 7 | -10 | 14 | A | 7 | 0.78 | A | 7 | 993 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.6 | 7 | 0
1988-01-14 | 1900-01-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -6.7 | 19.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.84 | A | 7 | 993 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 7 | 0
1988-01-14 | 1900-01-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.78 | A | 7 | 992 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.48 | 7 | 0
1988-01-14 | 1900-01-13 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -9.4 | 15.08 | A | 7 | 0.74 | A | 7 | 992 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.38 | 7 | 0
1988-01-14 | 1900-01-13 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -10 | 14 | A | 7 | 0.66 | A | 7 | 991 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.9 | 7 | 0
1988-01-14 | 1900-01-13 | 8:00 | 8 | 13 | 483 | 9 | 1 | 13 | 9 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -5 | 23 | A | 7 | -10 | 14 | A | 7 | 0.68 | A | 7 | 991 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12 | 7 | 0
1988-01-14 | 1900-01-13 | 9:00 | 9 | 193 | 1414 | 70 | 1 | 13 | 50 | 1 | 13 | 63 | 1 | 13 | 76 | 1 | 13 | 37 | 1 | 13 | 71 | 1 | 13 | 142 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | -3.9 | 24.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.58 | A | 7 | 990 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.62 | 7 | 0
1988-01-14 | 1900-01-13 | 10:00 | 10 | 400 | 1414 | 181 | 1 | 13 | 152 | 1 | 13 | 138 | 1 | 13 | 194 | 1 | 13 | 135 | 1 | 13 | 156 | 1 | 13 | 307 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | -1.7 | 28.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.47 | A | 7 | 991 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.04 | 7 | 0
1988-01-14 | 1900-01-13 | 11:00 | 11 | 560 | 1414 | 268 | 1 | 13 | 291 | 1 | 13 | 153 | 1 | 13 | 286 | 1 | 13 | 287 | 1 | 13 | 172 | 1 | 13 | 320 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 0.6 | 33.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.44 | A | 7 | 990 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.62 | 7 | 0
1988-01-14 | 1900-01-13 | 12:00 | 12 | 659 | 1414 | 188 | 1 | 9 | 9 | 1 | 9 | 184 | 1 | 13 | 214 | 1 | 9 | 7 | 1 | 9 | 210 | 1 | 13 | 720 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.36 | A | 7 | 990 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 0.6 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.42 | 7 | 0
1988-01-14 | 1900-01-13 | 13:00 | 13 | 691 | 1414 | 415 | 1 | 13 | 619 | 1 | 13 | 111 | 1 | 13 | 436 | 1 | 13 | 609 | 1 | 13 | 137 | 1 | 13 | 235 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 5 | 41 | A | 7 | -11.1 | 12.02 | A | 7 | 0.3 | A | 7 | 987 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.02 | 7 | 0
1988-01-14 | 1900-01-13 | 14:00 | 14 | 654 | 1414 | 363 | 1 | 13 | 549 | 1 | 13 | 109 | 1 | 13 | 381 | 1 | 13 | 535 | 1 | 13 | 132 | 1 | 13 | 224 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 5 | 41 | A | 7 | -10.6 | 12.92 | A | 7 | 0.32 | A | 7 | 985 | A | 7 | 190 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.92 | 7 | 0
1988-01-14 | 1900-01-13 | 15:00 | 15 | 551 | 1414 | 380 | 1 | 9 | 856 | 1 | 9 | 47 | 1 | 13 | 403 | 1 | 9 | 809 | 1 | 9 | 87 | 1 | 13 | 117 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -9.4 | 15.08 | A | 7 | 0.35 | A | 7 | 985 | A | 7 | 190 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.98 | 7 | 0
1988-01-14 | 1900-01-13 | 16:00 | 16 | 388 | 1414 | 234 | 1 | 9 | 729 | 1 | 9 | 35 | 1 | 13 | 250 | 1 | 9 | 644 | 1 | 9 | 72 | 1 | 13 | 88 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.41 | A | 7 | 985 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.06 | 7 | 0
1988-01-14 | 1900-01-13 | 17:00 | 17 | 178 | 1414 | 85 | 1 | 13 | 486 | 1 | 9 | 25 | 1 | 13 | 88 | 1 | 13 | 329 | 1 | 9 | 46 | 1 | 13 | 49 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -7.8 | 17.96 | A | 7 | 0.48 | A | 7 | 984 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.26 | 7 | 0
1988-01-14 | 1900-01-13 | 18:00 | 18 | 9 | 389 | 11 | 1 | 13 | 50 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -7.8 | 17.96 | A | 7 | 0.56 | A | 7 | 984 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.86 | 7 | 0
1988-01-14 | 1900-01-13 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 984 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 7 | 0
1988-01-14 | 1900-01-13 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.75 | A | 7 | 984 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 7 | 0
1988-01-14 | 1900-01-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 984 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 7 | 0
1988-01-14 | 1900-01-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 983 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 7 | 0
1988-01-14 | 1900-01-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -5 | 23 | A | 7 | 0.85 | A | 7 | 983 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.7 | 7 | 0
1988-01-14 | 1900-01-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -5 | 23 | A | 7 | 0.88 | A | 7 | 983 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22 | 7 | 0
1988-01-15 | 1900-01-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.92 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.22 | 1 | 0
1988-01-15 | 1900-01-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.92 | A | 7 | 982 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.22 | 1 | 0
1988-01-15 | 1900-01-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.22 | 1 | 0
1988-01-15 | 1900-01-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -6.1 | 21.02 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.32 | 1 | 0
1988-01-15 | 1900-01-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.22 | 1 | 0
1988-01-15 | 1900-01-14 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -5 | 23 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.3 | 1 | 0
1988-01-15 | 1900-01-14 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -5 | 23 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.3 | 1 | 0
1988-01-15 | 1900-01-14 | 8:00 | 8 | 14 | 507 | 14 | 1 | 13 | 56 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 4 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -5 | 23 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22 | 1 | 0
1988-01-15 | 1900-01-14 | 9:00 | 9 | 195 | 1414 | 83 | 1 | 13 | 304 | 1 | 9 | 41 | 1 | 13 | 84 | 1 | 13 | 197 | 1 | 9 | 57 | 1 | 13 | 71 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.38 | 1 | 0
1988-01-15 | 1900-01-14 | 10:00 | 10 | 403 | 1414 | 253 | 1 | 9 | 725 | 1 | 9 | 45 | 1 | 13 | 265 | 1 | 9 | 644 | 1 | 9 | 80 | 1 | 13 | 94 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.06 | 1 | 0
1988-01-15 | 1900-01-14 | 11:00 | 11 | 562 | 1414 | 388 | 1 | 9 | 819 | 1 | 9 | 61 | 1 | 13 | 410 | 1 | 9 | 781 | 1 | 9 | 98 | 1 | 13 | 131 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.51 | A | 7 | 979 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.58 | 1 | 0
1988-01-15 | 1900-01-14 | 12:00 | 12 | 662 | 1414 | 474 | 1 | 9 | 864 | 1 | 9 | 69 | 1 | 13 | 497 | 1 | 9 | 835 | 1 | 9 | 104 | 1 | 13 | 147 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.42 | A | 7 | 978 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.78 | 1 | 0
1988-01-15 | 1900-01-14 | 13:00 | 13 | 695 | 1414 | 500 | 1 | 9 | 849 | 1 | 9 | 83 | 1 | 13 | 527 | 1 | 9 | 832 | 1 | 9 | 116 | 1 | 13 | 179 | 1 | 18 | 5 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.35 | A | 7 | 977 | A | 7 | 210 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.38 | 1 | 0
1988-01-15 | 1900-01-14 | 14:00 | 14 | 658 | 1414 | 469 | 1 | 9 | 827 | 1 | 9 | 85 | 1 | 13 | 490 | 1 | 9 | 802 | 1 | 9 | 115 | 1 | 13 | 175 | 1 | 18 | 6 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.32 | A | 7 | 976 | A | 7 | 200 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.18 | 1 | 0
1988-01-15 | 1900-01-14 | 15:00 | 15 | 555 | 1414 | 377 | 1 | 9 | 775 | 1 | 9 | 73 | 1 | 13 | 391 | 1 | 9 | 731 | 1 | 9 | 103 | 1 | 13 | 145 | 1 | 18 | 6 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.32 | A | 7 | 975 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.18 | 1 | 0
1988-01-15 | 1900-01-14 | 16:00 | 16 | 392 | 1414 | 218 | 1 | 9 | 603 | 1 | 9 | 52 | 1 | 13 | 226 | 1 | 9 | 527 | 1 | 9 | 79 | 1 | 13 | 102 | 1 | 18 | 7 | A | 7 | 1 | A | 7 | 11.1 | 51.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.34 | A | 7 | 974 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.28 | 1 | 0
1988-01-15 | 1900-01-14 | 17:00 | 17 | 182 | 1414 | 82 | 1 | 13 | 347 | 1 | 9 | 38 | 1 | 13 | 84 | 1 | 13 | 218 | 1 | 9 | 56 | 1 | 13 | 66 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | 9.4 | 48.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.35 | A | 7 | 974 | A | 7 | 210 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.62 | 1 | 0
1988-01-15 | 1900-01-14 | 18:00 | 18 | 10 | 412 | 10 | 1 | 13 | 27 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | 6.7 | 44.06 | A | 7 | -5 | 23 | A | 7 | 0.44 | A | 7 | 973 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.3 | 1 | 0
1988-01-15 | 1900-01-14 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 6.1 | 42.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.49 | A | 7 | 973 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.48 | 1 | 0
1988-01-15 | 1900-01-14 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | -2.8 | 26.96 | A | 7 | 0.58 | A | 7 | 972 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.96 | 1 | 0
1988-01-15 | 1900-01-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.53 | A | 7 | 972 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.56 | 1 | 0
1988-01-15 | 1900-01-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.51 | A | 7 | 971 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 1 | 0
1988-01-15 | 1900-01-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.52 | A | 7 | 970 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.34 | 1 | 0
1988-01-15 | 1900-01-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.56 | A | 7 | 969 | A | 7 | 190 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.54 | 1 | 0
1988-01-16 | 1900-01-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.63 | A | 7 | 969 | A | 7 | 180 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.88 | 2 | 0
1988-01-16 | 1900-01-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.66 | A | 7 | 968 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.98 | 2 | 0
1988-01-16 | 1900-01-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.68 | A | 7 | 967 | A | 7 | 190 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.16 | 2 | 0
1988-01-16 | 1900-01-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.74 | A | 7 | 966 | A | 7 | 180 | A | 7 | 14.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.84 | 2 | 0
1988-01-16 | 1900-01-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 3.9 | 39.02 | A | 7 | 0.8 | A | 7 | 966 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.52 | 2 | 0
1988-01-16 | 1900-01-15 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 4.4 | 39.92 | A | 7 | 0.8 | A | 7 | 967 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.32 | 2 | 0
1988-01-16 | 1900-01-15 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 7.8 | 46.04 | A | 7 | 5 | 41 | A | 7 | 0.83 | A | 7 | 967 | A | 7 | 200 | A | 7 | 13.4 | A | 7 | 32200 | A | 7 | 550 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.7 | 2 | 0
1988-01-16 | 1900-01-15 | 8:00 | 8 | 14 | 507 | 7 | 1 | 13 | 0 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 968 | A | 7 | 210 | A | 7 | 13.4 | A | 7 | 32200 | A | 7 | 520 | A | 7 | 1.5 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.78 | 2 | 0
1988-01-16 | 1900-01-15 | 9:00 | 9 | 197 | 1414 | 75 | 1 | 13 | 103 | 1 | 13 | 61 | 1 | 13 | 81 | 1 | 13 | 68 | 1 | 13 | 72 | 1 | 13 | 129 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 969 | A | 7 | 210 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 550 | A | 7 | 1.5 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.78 | 2 | 0
1988-01-16 | 1900-01-15 | 10:00 | 10 | 405 | 1414 | 193 | 1 | 13 | 371 | 1 | 13 | 87 | 1 | 13 | 204 | 1 | 13 | 323 | 1 | 13 | 111 | 1 | 13 | 161 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 9.4 | 48.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.77 | A | 7 | 969 | A | 7 | 220 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.98 | 2 | 0
1988-01-16 | 1900-01-15 | 11:00 | 11 | 565 | 1414 | 336 | 1 | 13 | 551 | 1 | 13 | 115 | 1 | 13 | 345 | 1 | 13 | 517 | 1 | 13 | 138 | 1 | 13 | 219 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 11.1 | 51.98 | A | 7 | 5 | 41 | A | 7 | 0.66 | A | 7 | 970 | A | 7 | 220 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.4 | 2 | 0
1988-01-16 | 1900-01-15 | 12:00 | 12 | 665 | 1414 | 407 | 1 | 13 | 567 | 1 | 13 | 140 | 1 | 13 | 436 | 1 | 13 | 563 | 1 | 13 | 170 | 1 | 13 | 285 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 11.1 | 51.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.61 | A | 7 | 970 | A | 7 | 230 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.02 | 2 | 0
1988-01-16 | 1900-01-15 | 13:00 | 13 | 699 | 1414 | 449 | 1 | 9 | 701 | 1 | 9 | 102 | 1 | 13 | 476 | 1 | 9 | 694 | 1 | 9 | 132 | 1 | 13 | 220 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 12.2 | 53.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.53 | A | 7 | 970 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.94 | 2 | 0
1988-01-16 | 1900-01-15 | 14:00 | 14 | 662 | 1414 | 394 | 1 | 13 | 529 | 1 | 13 | 147 | 1 | 13 | 421 | 1 | 13 | 525 | 1 | 13 | 174 | 1 | 13 | 300 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 12.2 | 53.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.53 | A | 7 | 970 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.94 | 2 | 0
1988-01-16 | 1900-01-15 | 15:00 | 15 | 559 | 1414 | 161 | 1 | 13 | 134 | 1 | 13 | 108 | 1 | 13 | 180 | 1 | 13 | 133 | 1 | 13 | 127 | 1 | 13 | 252 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 12.8 | 55.04 | A | 7 | 2.8 | 37.04 | A | 7 | 0.51 | A | 7 | 970 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.74 | 2 | 0
1988-01-16 | 1900-01-15 | 16:00 | 16 | 397 | 1414 | 154 | 1 | 13 | 68 | 1 | 13 | 135 | 1 | 13 | 169 | 1 | 13 | 62 | 1 | 13 | 151 | 1 | 13 | 333 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 11.1 | 51.98 | A | 7 | 2.2 | 35.96 | A | 7 | 0.55 | A | 7 | 971 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.36 | 2 | 0
1988-01-16 | 1900-01-15 | 17:00 | 17 | 187 | 1414 | 43 | 1 | 13 | 29 | 1 | 9 | 39 | 1 | 13 | 47 | 1 | 13 | 21 | 1 | 9 | 44 | 1 | 13 | 97 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 10 | 50 | A | 7 | 2.2 | 35.96 | A | 7 | 0.59 | A | 7 | 972 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.86 | 2 | 0
1988-01-16 | 1900-01-15 | 18:00 | 18 | 11 | 436 | 5 | 1 | 13 | 2 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 7.8 | 46.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.63 | A | 7 | 972 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.68 | 2 | 0
1988-01-16 | 1900-01-15 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 7.2 | 44.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.66 | A | 7 | 972 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.98 | 2 | 0
1988-01-16 | 1900-01-15 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.74 | A | 7 | 973 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.06 | 2 | 0
1988-01-16 | 1900-01-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.76 | A | 7 | 974 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.26 | 2 | 0
1988-01-16 | 1900-01-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 1.1 | 33.98 | A | 7 | 0.76 | A | 7 | 974 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.18 | 2 | 0
1988-01-16 | 1900-01-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 2 | 0
1988-01-16 | 1900-01-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 1.7 | 35.06 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.66 | 2 | 0
1988-01-17 | 1900-01-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.86 | A | 7 | 974 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.46 | 3 | 0
1988-01-17 | 1900-01-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 3 | 0
1988-01-17 | 1900-01-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.18 | 3 | 0
1988-01-17 | 1900-01-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.18 | 3 | 0
1988-01-17 | 1900-01-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.18 | 3 | 0
1988-01-17 | 1900-01-16 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.18 | 3 | 0
1988-01-17 | 1900-01-16 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 2590 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.18 | 3 | 0
1988-01-17 | 1900-01-16 | 8:00 | 8 | 15 | 507 | 6 | 1 | 13 | 1 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 2590 | A | 7 | 1.1 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.18 | 3 | 0
1988-01-17 | 1900-01-16 | 9:00 | 9 | 199 | 1414 | 48 | 1 | 13 | 15 | 1 | 9 | 46 | 1 | 13 | 53 | 1 | 13 | 11 | 1 | 9 | 51 | 1 | 13 | 113 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 3 | 0
1988-01-17 | 1900-01-16 | 10:00 | 10 | 408 | 1414 | 118 | 1 | 9 | 4 | 1 | 9 | 117 | 1 | 13 | 131 | 1 | 9 | 2 | 1 | 9 | 131 | 1 | 13 | 405 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 1680 | A | 7 | 1.2 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.76 | 3 | 0
1988-01-17 | 1900-01-16 | 11:00 | 11 | 568 | 1414 | 231 | 1 | 9 | 53 | 1 | 9 | 210 | 1 | 13 | 253 | 1 | 9 | 52 | 1 | 9 | 232 | 1 | 13 | 553 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 4.4 | 39.92 | A | 7 | 1.7 | 35.06 | A | 7 | 0.82 | A | 7 | 974 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 1680 | A | 7 | 1.2 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.96 | 3 | 0
1988-01-17 | 1900-01-16 | 12:00 | 12 | 669 | 1414 | 290 | 1 | 9 | 161 | 1 | 9 | 214 | 1 | 13 | 315 | 1 | 9 | 163 | 1 | 9 | 238 | 1 | 13 | 524 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 5.6 | 42.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.46 | 3 | 0
1988-01-17 | 1900-01-16 | 13:00 | 13 | 703 | 1414 | 496 | 1 | 13 | 711 | 1 | 13 | 142 | 1 | 13 | 513 | 1 | 13 | 693 | 1 | 13 | 167 | 1 | 13 | 291 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 8.9 | 48.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.66 | A | 7 | 973 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.94 | 3 | 0
1988-01-17 | 1900-01-16 | 14:00 | 14 | 667 | 1414 | 341 | 1 | 13 | 307 | 1 | 13 | 196 | 1 | 13 | 364 | 1 | 13 | 315 | 1 | 13 | 215 | 1 | 13 | 436 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 10 | 50 | A | 7 | 2.8 | 37.04 | A | 7 | 0.61 | A | 7 | 973 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.24 | 3 | 0
1988-01-17 | 1900-01-16 | 15:00 | 15 | 564 | 1414 | 342 | 1 | 13 | 654 | 1 | 13 | 82 | 1 | 13 | 362 | 1 | 13 | 624 | 1 | 13 | 112 | 1 | 13 | 165 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 10 | 50 | A | 7 | -0.6 | 30.92 | A | 7 | 0.48 | A | 7 | 974 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.42 | 3 | 0
1988-01-17 | 1900-01-16 | 16:00 | 16 | 402 | 1414 | 255 | 1 | 9 | 784 | 1 | 9 | 34 | 1 | 13 | 274 | 1 | 9 | 698 | 1 | 9 | 74 | 1 | 13 | 88 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | -1.7 | 28.94 | A | 7 | 0.45 | A | 7 | 974 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.44 | 3 | 0
1988-01-17 | 1900-01-16 | 17:00 | 17 | 192 | 1414 | 96 | 1 | 13 | 563 | 1 | 9 | 22 | 1 | 13 | 105 | 1 | 13 | 411 | 1 | 9 | 49 | 1 | 13 | 52 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.48 | A | 7 | 975 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.94 | 3 | 0
1988-01-17 | 1900-01-16 | 18:00 | 18 | 12 | 459 | 15 | 1 | 13 | 80 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.55 | A | 7 | 975 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.027 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.76 | 3 | 0
1988-01-17 | 1900-01-16 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 3 | 0
1988-01-17 | 1900-01-16 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 350 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.28 | 3 | 0
1988-01-17 | 1900-01-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.58 | 3 | 0
1988-01-17 | 1900-01-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 3 | 0
1988-01-17 | 1900-01-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 210 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 3 | 0
1988-01-17 | 1900-01-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 3 | 0
1988-01-18 | 1900-01-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 0 | 32 | A | 7 | -2.8 | 26.96 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.26 | 4 | 0
1988-01-18 | 1900-01-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 4 | 0
1988-01-18 | 1900-01-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -1.1 | 30.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 4 | 0
1988-01-18 | 1900-01-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -2.8 | 26.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 4 | 0
1988-01-18 | 1900-01-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 4 | 0
1988-01-18 | 1900-01-17 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 978 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 4 | 0
1988-01-18 | 1900-01-17 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.96 | A | 7 | 978 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.54 | 4 | 0
1988-01-18 | 1900-01-17 | 8:00 | 8 | 16 | 530 | 14 | 1 | 13 | 51 | 1 | 13 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 978 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 4 | 0
1988-01-18 | 1900-01-17 | 9:00 | 9 | 201 | 1413 | 80 | 1 | 13 | 62 | 1 | 13 | 71 | 1 | 13 | 87 | 1 | 13 | 46 | 1 | 13 | 81 | 1 | 13 | 157 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 978 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 9140 | A | 7 | 1.1 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.1 | 4 | 0
1988-01-18 | 1900-01-17 | 10:00 | 10 | 411 | 1413 | 205 | 1 | 9 | 444 | 1 | 9 | 75 | 1 | 13 | 211 | 1 | 9 | 387 | 1 | 9 | 98 | 1 | 13 | 138 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 3.9 | 39.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.68 | 4 | 0
1988-01-18 | 1900-01-17 | 11:00 | 11 | 572 | 1413 | 306 | 1 | 9 | 459 | 1 | 9 | 120 | 1 | 13 | 326 | 1 | 9 | 442 | 1 | 9 | 146 | 1 | 13 | 233 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 7.2 | 44.96 | A | 7 | 0 | 32 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.8 | 4 | 0
1988-01-18 | 1900-01-17 | 12:00 | 12 | 673 | 1413 | 394 | 1 | 13 | 542 | 1 | 13 | 135 | 1 | 13 | 423 | 1 | 13 | 540 | 1 | 13 | 165 | 1 | 13 | 274 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 8.3 | 46.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.56 | 4 | 0
1988-01-18 | 1900-01-17 | 13:00 | 13 | 707 | 1413 | 374 | 1 | 13 | 306 | 1 | 13 | 221 | 1 | 13 | 398 | 1 | 13 | 317 | 1 | 13 | 239 | 1 | 13 | 508 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 7.8 | 46.04 | A | 7 | 2.2 | 35.96 | A | 7 | 0.68 | A | 7 | 976 | A | 7 | 100 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 1.2 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.16 | 4 | 0
1988-01-18 | 1900-01-17 | 14:00 | 14 | 671 | 1413 | 360 | 1 | 13 | 467 | 1 | 13 | 139 | 1 | 13 | 387 | 1 | 13 | 465 | 1 | 13 | 166 | 1 | 13 | 283 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 8.9 | 48.02 | A | 7 | 3.3 | 37.94 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 100 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 1.3 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.04 | 4 | 0
1988-01-18 | 1900-01-17 | 15:00 | 15 | 569 | 1413 | 354 | 1 | 9 | 679 | 1 | 9 | 82 | 1 | 13 | 376 | 1 | 9 | 650 | 1 | 9 | 113 | 1 | 13 | 166 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 9.4 | 48.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.64 | A | 7 | 974 | A | 7 | 100 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.64 | 4 | 0
1988-01-18 | 1900-01-17 | 16:00 | 16 | 406 | 1413 | 177 | 1 | 13 | 131 | 1 | 13 | 140 | 1 | 13 | 191 | 1 | 13 | 117 | 1 | 13 | 157 | 1 | 13 | 312 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 7.8 | 46.04 | A | 7 | 2.8 | 37.04 | A | 7 | 0.71 | A | 7 | 973 | A | 7 | 80 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 1.2 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.54 | 4 | 0
1988-01-18 | 1900-01-17 | 17:00 | 17 | 196 | 1413 | 68 | 1 | 13 | 4 | 1 | 9 | 67 | 1 | 13 | 73 | 1 | 13 | 1 | 1 | 9 | 73 | 1 | 13 | 194 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 6.7 | 44.06 | A | 7 | 2.8 | 37.04 | A | 7 | 0.77 | A | 7 | 973 | A | 7 | 80 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 1.3 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.24 | 4 | 0
1988-01-18 | 1900-01-17 | 18:00 | 18 | 14 | 506 | 4 | 1 | 13 | 2 | 1 | 9 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 5 | 41 | A | 7 | 2.2 | 35.96 | A | 7 | 0.83 | A | 7 | 973 | A | 7 | 90 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 3350 | A | 7 | 1.2 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.96 | 4 | 0
1988-01-18 | 1900-01-17 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 2.2 | 35.96 | A | 7 | 0.83 | A | 7 | 974 | A | 7 | 80 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.96 | 4 | 0
1988-01-18 | 1900-01-17 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 2.8 | 37.04 | A | 7 | 0.86 | A | 7 | 973 | A | 7 | 100 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 270 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.34 | 4 | 0
1988-01-18 | 1900-01-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 2.2 | 35.96 | A | 7 | 0.89 | A | 7 | 972 | A | 7 | 90 | A | 7 | 10.3 | A | 7 | 9700 | A | 7 | 150 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.66 | 4 | 0
1988-01-18 | 1900-01-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.2 | 35.96 | A | 7 | 0.96 | A | 7 | 971 | A | 7 | 90 | A | 7 | 7.7 | A | 7 | 3200 | A | 7 | 90 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.46 | 4 | 0
1988-01-18 | 1900-01-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.96 | A | 7 | 971 | A | 7 | 80 | A | 7 | 9.3 | A | 7 | 3200 | A | 7 | 90 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 4 | 0
1988-01-18 | 1900-01-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.96 | A | 7 | 970 | A | 7 | 100 | A | 7 | 6.7 | A | 7 | 3200 | A | 7 | 90 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 4 | 0
1988-01-19 | 1900-01-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 970 | A | 7 | 110 | A | 7 | 6.7 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 5 | 0
1988-01-19 | 1900-01-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 969 | A | 7 | 80 | A | 7 | 7.2 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 5 | 0
1988-01-19 | 1900-01-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 968 | A | 7 | 80 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 150 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 5 | 0
1988-01-19 | 1900-01-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 968 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 120 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 5 | 0
1988-01-19 | 1900-01-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 964 | A | 7 | 100 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 90 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 5 | 0
1988-01-19 | 1900-01-18 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 966 | A | 7 | 110 | A | 7 | 8.2 | A | 7 | 2400 | A | 7 | 90 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 5 | 0
1988-01-19 | 1900-01-18 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.8 | 37.04 | A | 7 | 1 | A | 7 | 965 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 2400 | A | 7 | 90 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.04 | 5 | 0
1988-01-19 | 1900-01-18 | 8:00 | 8 | 16 | 530 | 4 | 1 | 13 | 14 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.8 | 37.04 | A | 7 | 1 | A | 7 | 964 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 600 | A | 7 | 60 | A | 7 | 1.2 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.04 | 5 | 0
1988-01-19 | 1900-01-18 | 9:00 | 9 | 204 | 1413 | 28 | 1 | 13 | 8 | 1 | 9 | 27 | 1 | 13 | 31 | 1 | 13 | 6 | 1 | 9 | 30 | 1 | 13 | 72 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.8 | 37.04 | A | 7 | 1 | A | 7 | 964 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 200 | A | 7 | 30 | A | 7 | 1.2 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.04 | 5 | 0
1988-01-19 | 1900-01-18 | 10:00 | 10 | 413 | 1413 | 136 | 1 | 9 | 1 | 1 | 9 | 136 | 1 | 13 | 150 | 1 | 9 | 1 | 1 | 9 | 150 | 1 | 13 | 446 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.8 | 37.04 | A | 7 | 1 | A | 7 | 964 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 100 | A | 7 | 30 | A | 7 | 1.2 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.04 | 5 | 0
1988-01-19 | 1900-01-18 | 11:00 | 11 | 575 | 1413 | 172 | 1 | 9 | 7 | 1 | 9 | 169 | 1 | 13 | 193 | 1 | 9 | 5 | 1 | 9 | 191 | 1 | 13 | 627 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 964 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 100 | A | 7 | 30 | A | 7 | 1.3 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 5 | 0
1988-01-19 | 1900-01-18 | 12:00 | 12 | 677 | 1413 | 218 | 1 | 9 | 8 | 1 | 9 | 214 | 1 | 13 | 245 | 1 | 9 | 7 | 1 | 9 | 242 | 1 | 13 | 807 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 3.9 | 39.02 | A | 7 | 1 | A | 7 | 963 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 100 | A | 7 | 0 | A | 7 | 1.3 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.92 | 5 | 0
1988-01-19 | 1900-01-18 | 13:00 | 13 | 711 | 1413 | 284 | 1 | 9 | 6 | 1 | 9 | 281 | 1 | 13 | 314 | 1 | 9 | 6 | 1 | 9 | 311 | 1 | 13 | 971 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5.6 | 42.08 | A | 7 | 1 | A | 7 | 962 | A | 7 | 0 | A | 7 | 0 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.98 | 5 | 0
1988-01-19 | 1900-01-18 | 14:00 | 14 | 676 | 1413 | 210 | 1 | 9 | 4 | 1 | 9 | 208 | 1 | 13 | 237 | 1 | 9 | 3 | 1 | 9 | 235 | 1 | 13 | 792 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5.6 | 42.08 | A | 7 | 1 | A | 7 | 962 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1.4 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.98 | 5 | 0
1988-01-19 | 1900-01-18 | 15:00 | 15 | 574 | 1413 | 205 | 1 | 9 | 4 | 1 | 9 | 204 | 1 | 13 | 227 | 1 | 9 | 3 | 1 | 9 | 226 | 1 | 13 | 698 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5.6 | 42.08 | A | 7 | 1 | A | 7 | 962 | A | 7 | 0 | A | 7 | 0 | A | 7 | 400 | A | 7 | 30 | A | 7 | 1.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.98 | 5 | 0
1988-01-19 | 1900-01-18 | 16:00 | 16 | 411 | 1413 | 131 | 1 | 9 | 1 | 1 | 9 | 130 | 1 | 13 | 144 | 1 | 9 | 1 | 1 | 9 | 144 | 1 | 13 | 433 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 6.1 | 42.98 | A | 7 | 1 | A | 7 | 962 | A | 7 | 0 | A | 7 | 0 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.88 | 5 | 0
1988-01-19 | 1900-01-18 | 17:00 | 17 | 201 | 1413 | 70 | 1 | 13 | 0 | 1 | 9 | 70 | 1 | 13 | 76 | 1 | 13 | 0 | 1 | 9 | 76 | 1 | 13 | 201 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5.6 | 42.08 | A | 7 | 1 | A | 7 | 962 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 600 | A | 7 | 30 | A | 7 | 1.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.98 | 5 | 0
1988-01-19 | 1900-01-18 | 18:00 | 18 | 15 | 530 | 11 | 1 | 13 | 0 | 1 | 9 | 11 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 4.4 | 39.92 | A | 7 | 1 | A | 7 | 962 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.4 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.92 | 5 | 0
1988-01-19 | 1900-01-18 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 3.9 | 39.02 | A | 7 | 1 | A | 7 | 963 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.92 | 5 | 0
1988-01-19 | 1900-01-18 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 964 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 100 | A | 7 | 60 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 5 | 0
1988-01-19 | 1900-01-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.8 | 37.04 | A | 7 | 1 | A | 7 | 964 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 400 | A | 7 | 30 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.04 | 5 | 0
1988-01-19 | 1900-01-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 2.2 | 35.96 | A | 7 | 1 | A | 7 | 964 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 150 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.86 | 5 | 0
1988-01-19 | 1900-01-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 1.7 | 35.06 | A | 7 | 1 | A | 7 | 965 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 210 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.96 | 5 | 0
1988-01-19 | 1900-01-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 1.1 | 33.98 | A | 7 | 1 | A | 7 | 966 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.88 | 5 | 0
1988-01-20 | 1900-01-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 967 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 120 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 6 | 0
1988-01-20 | 1900-01-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 968 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 240 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.42 | 6 | 0
1988-01-20 | 1900-01-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 968 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 210 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 6 | 0
1988-01-20 | 1900-01-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 968 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 800 | A | 7 | 180 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 6 | 0
1988-01-20 | 1900-01-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 969 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 1600 | A | 7 | 210 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 6 | 0
1988-01-20 | 1900-01-19 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.96 | A | 7 | 969 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 1600 | A | 7 | 210 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.62 | 6 | 0
1988-01-20 | 1900-01-19 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 971 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 3200 | A | 7 | 270 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 6 | 0
1988-01-20 | 1900-01-19 | 8:00 | 8 | 17 | 553 | 8 | 1 | 13 | 0 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.92 | A | 7 | 972 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 400 | A | 7 | 0.9 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 6 | 0
1988-01-20 | 1900-01-19 | 9:00 | 9 | 206 | 1413 | 61 | 1 | 13 | 1 | 1 | 9 | 61 | 1 | 13 | 67 | 1 | 13 | 0 | 1 | 9 | 67 | 1 | 13 | 189 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1988-01-20 | 1900-01-19 | 10:00 | 10 | 416 | 1413 | 120 | 1 | 9 | 0 | 1 | 9 | 120 | 1 | 13 | 134 | 1 | 9 | 0 | 1 | 9 | 134 | 1 | 13 | 417 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 490 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1988-01-20 | 1900-01-19 | 11:00 | 11 | 579 | 1413 | 179 | 1 | 9 | 1 | 1 | 9 | 179 | 1 | 13 | 201 | 1 | 9 | 1 | 1 | 9 | 200 | 1 | 13 | 652 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.85 | A | 7 | 976 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 490 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 6 | 0
1988-01-20 | 1900-01-19 | 12:00 | 12 | 681 | 1413 | 222 | 1 | 9 | 0 | 1 | 9 | 222 | 1 | 13 | 249 | 1 | 9 | 0 | 1 | 9 | 249 | 1 | 13 | 828 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 6 | 0
1988-01-20 | 1900-01-19 | 13:00 | 13 | 715 | 1413 | 237 | 1 | 9 | 0 | 1 | 9 | 237 | 1 | 13 | 266 | 1 | 9 | 0 | 1 | 9 | 266 | 1 | 13 | 891 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 6 | 0
1988-01-20 | 1900-01-19 | 14:00 | 14 | 681 | 1413 | 237 | 1 | 9 | 0 | 1 | 9 | 236 | 1 | 13 | 264 | 1 | 9 | 0 | 1 | 9 | 264 | 1 | 13 | 858 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 976 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 460 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 6 | 0
1988-01-20 | 1900-01-19 | 15:00 | 15 | 579 | 1413 | 177 | 1 | 9 | 0 | 1 | 9 | 176 | 1 | 13 | 197 | 1 | 9 | 0 | 1 | 9 | 197 | 1 | 13 | 646 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 977 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 460 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 6 | 0
1988-01-20 | 1900-01-19 | 16:00 | 16 | 416 | 1413 | 117 | 1 | 9 | 0 | 1 | 9 | 117 | 1 | 13 | 130 | 1 | 9 | 0 | 1 | 9 | 130 | 1 | 13 | 410 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 6 | 0
1988-01-20 | 1900-01-19 | 17:00 | 17 | 206 | 1413 | 57 | 1 | 13 | 0 | 1 | 9 | 57 | 1 | 13 | 63 | 1 | 13 | 0 | 1 | 9 | 63 | 1 | 13 | 182 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 6 | 0
1988-01-20 | 1900-01-19 | 18:00 | 18 | 17 | 553 | 7 | 1 | 13 | 0 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.82 | 6 | 0
1988-01-20 | 1900-01-19 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1010 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.84 | 6 | 0
1988-01-20 | 1900-01-19 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.04 | 6 | 0
1988-01-20 | 1900-01-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 430 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.06 | 6 | 0
1988-01-20 | 1900-01-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | -7.2 | 19.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 460 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 6 | 0
1988-01-20 | 1900-01-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 400 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 6 | 0
1988-01-20 | 1900-01-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -8.9 | 15.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.84 | 6 | 0
1988-01-21 | 1900-01-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -10 | 14 | A | 7 | -12.2 | 10.04 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 7 | 0
1988-01-21 | 1900-01-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.88 | A | 7 | 981 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.36 | 7 | 0
1988-01-21 | 1900-01-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -13.3 | 8.06 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.66 | 7 | 0
1988-01-21 | 1900-01-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -13.3 | 8.06 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.86 | 7 | 0
1988-01-21 | 1900-01-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -13.9 | 6.98 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.78 | 7 | 0
1988-01-21 | 1900-01-20 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -13.3 | 8.06 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.66 | 7 | 0
1988-01-21 | 1900-01-20 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -12.8 | 8.96 | A | 7 | -13.9 | 6.98 | A | 7 | 0.92 | A | 7 | 982 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.58 | 7 | 0
1988-01-21 | 1900-01-20 | 8:00 | 8 | 18 | 553 | 14 | 1 | 13 | 71 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | -13.3 | 8.06 | A | 7 | -13.9 | 6.98 | A | 7 | 0.96 | A | 7 | 982 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.78 | 7 | 0
1988-01-21 | 1900-01-20 | 9:00 | 9 | 209 | 1413 | 86 | 1 | 13 | 156 | 1 | 13 | 63 | 1 | 13 | 90 | 1 | 13 | 98 | 1 | 13 | 75 | 1 | 13 | 122 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | -11.7 | 10.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.74 | 7 | 0
1988-01-21 | 1900-01-20 | 10:00 | 10 | 420 | 1413 | 188 | 1 | 9 | 133 | 1 | 9 | 148 | 1 | 13 | 201 | 1 | 9 | 120 | 1 | 9 | 165 | 1 | 13 | 331 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -10 | 14 | A | 7 | -11.1 | 12.02 | A | 7 | 0.92 | A | 7 | 983 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 340 | A | 7 | 0.6 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.52 | 7 | 0
1988-01-21 | 1900-01-20 | 11:00 | 11 | 582 | 1413 | 136 | 1 | 9 | 78 | 1 | 9 | 104 | 1 | 13 | 153 | 1 | 9 | 78 | 1 | 9 | 121 | 1 | 13 | 245 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -10 | 14 | A | 7 | 0.88 | A | 7 | 984 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 340 | A | 7 | 0.6 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.2 | 7 | 0
1988-01-21 | 1900-01-20 | 12:00 | 12 | 685 | 1413 | 156 | 1 | 9 | 9 | 1 | 9 | 152 | 1 | 13 | 181 | 1 | 9 | 7 | 1 | 9 | 178 | 1 | 13 | 642 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.84 | A | 7 | 984 | A | 7 | 30 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 340 | A | 7 | 0.6 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 7 | 0
1988-01-21 | 1900-01-20 | 13:00 | 13 | 720 | 1413 | 182 | 1 | 9 | 11 | 1 | 9 | 176 | 1 | 13 | 209 | 1 | 9 | 9 | 1 | 9 | 205 | 1 | 13 | 735 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.84 | A | 7 | 984 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 370 | A | 7 | 0.6 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 7 | 0
1988-01-21 | 1900-01-20 | 14:00 | 14 | 685 | 1413 | 234 | 1 | 9 | 12 | 1 | 9 | 228 | 1 | 13 | 262 | 1 | 9 | 11 | 1 | 9 | 257 | 1 | 13 | 845 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.85 | A | 7 | 984 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 400 | A | 7 | 0.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.06 | 7 | 0
1988-01-21 | 1900-01-20 | 15:00 | 15 | 583 | 1413 | 181 | 1 | 9 | 5 | 1 | 9 | 179 | 1 | 13 | 203 | 1 | 9 | 4 | 1 | 9 | 201 | 1 | 13 | 656 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 0.6 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.68 | 7 | 0
1988-01-21 | 1900-01-20 | 16:00 | 16 | 421 | 1413 | 111 | 1 | 9 | 8 | 1 | 9 | 109 | 1 | 13 | 125 | 1 | 9 | 5 | 1 | 9 | 124 | 1 | 13 | 394 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 0.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.06 | 7 | 0
1988-01-21 | 1900-01-20 | 17:00 | 17 | 211 | 1413 | 61 | 1 | 13 | 1 | 1 | 9 | 61 | 1 | 13 | 67 | 1 | 13 | 0 | 1 | 9 | 67 | 1 | 13 | 192 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 430 | A | 7 | 0.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.06 | 7 | 0
1988-01-21 | 1900-01-20 | 18:00 | 18 | 19 | 577 | 8 | 1 | 13 | 0 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.84 | A | 7 | 985 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 430 | A | 7 | 0.6 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 7 | 0
1988-01-21 | 1900-01-20 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.81 | A | 7 | 986 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 430 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.88 | 7 | 0
1988-01-21 | 1900-01-20 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -7.2 | 19.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.84 | A | 7 | 986 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 430 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 7 | 0
1988-01-21 | 1900-01-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -7.2 | 19.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 430 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.18 | 7 | 0
1988-01-21 | 1900-01-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -7.2 | 19.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 270 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 400 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.18 | 7 | 0
1988-01-21 | 1900-01-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -9.4 | 15.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.92 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.42 | 7 | 0
1988-01-21 | 1900-01-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -10 | 14 | A | 7 | -10.6 | 12.92 | A | 7 | 0.96 | A | 7 | 987 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.62 | 7 | 0
1988-01-22 | 1900-01-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -11.7 | 10.94 | A | 7 | 0.96 | A | 7 | 986 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.64 | 1 | 0
1988-01-22 | 1900-01-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.96 | A | 7 | 985 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.74 | 1 | 0
1988-01-22 | 1900-01-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -11.1 | 12.02 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.52 | 1 | 0
1988-01-22 | 1900-01-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.96 | A | 7 | 984 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.74 | 1 | 0
1988-01-22 | 1900-01-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -11.1 | 12.02 | A | 7 | 0.92 | A | 7 | 983 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.52 | 1 | 0
1988-01-22 | 1900-01-21 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -10.6 | 12.92 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.62 | 1 | 0
1988-01-22 | 1900-01-21 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -7.8 | 17.96 | A | 7 | -8.9 | 15.98 | A | 7 | 0.92 | A | 7 | 983 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.38 | 1 | 0
1988-01-22 | 1900-01-21 | 8:00 | 8 | 19 | 577 | 13 | 1 | 13 | 0 | 1 | 9 | 13 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -7.8 | 17.96 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 610 | A | 7 | 0.7 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.66 | 1 | 0
1988-01-22 | 1900-01-21 | 9:00 | 9 | 212 | 1412 | 81 | 1 | 13 | 66 | 1 | 9 | 71 | 1 | 13 | 87 | 1 | 13 | 45 | 1 | 9 | 80 | 1 | 13 | 150 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -6.1 | 21.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 940 | A | 7 | 0.7 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.64 | 1 | 0
1988-01-22 | 1900-01-21 | 10:00 | 10 | 423 | 1412 | 263 | 1 | 13 | 659 | 1 | 13 | 65 | 1 | 13 | 275 | 1 | 13 | 585 | 1 | 13 | 99 | 1 | 13 | 124 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -3.9 | 24.98 | A | 7 | -5 | 23 | A | 7 | 0.92 | A | 7 | 983 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.3 | 1 | 0
1988-01-22 | 1900-01-21 | 11:00 | 11 | 586 | 1412 | 411 | 1 | 9 | 880 | 1 | 9 | 44 | 1 | 13 | 435 | 1 | 9 | 840 | 1 | 9 | 85 | 1 | 13 | 116 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.82 | A | 7 | 983 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 1 | 0
1988-01-22 | 1900-01-21 | 12:00 | 12 | 689 | 1412 | 270 | 1 | 13 | 164 | 1 | 13 | 190 | 1 | 13 | 296 | 1 | 13 | 168 | 1 | 13 | 214 | 1 | 13 | 470 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.7 | A | 7 | 982 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 0.9 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.28 | 1 | 0
1988-01-22 | 1900-01-21 | 13:00 | 13 | 724 | 1412 | 341 | 1 | 9 | 287 | 1 | 9 | 194 | 1 | 13 | 368 | 1 | 9 | 299 | 1 | 9 | 214 | 1 | 13 | 437 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 2.2 | 35.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 280 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 0.9 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.06 | 1 | 0
1988-01-22 | 1900-01-21 | 14:00 | 14 | 690 | 1412 | 314 | 1 | 9 | 203 | 1 | 9 | 214 | 1 | 13 | 341 | 1 | 9 | 207 | 1 | 9 | 240 | 1 | 13 | 529 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 1.7 | 35.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.8 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.08 | 1 | 0
1988-01-22 | 1900-01-21 | 15:00 | 15 | 589 | 1412 | 197 | 1 | 9 | 1 | 1 | 9 | 197 | 1 | 13 | 220 | 1 | 9 | 1 | 1 | 9 | 219 | 1 | 13 | 698 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.28 | 1 | 0
1988-01-22 | 1900-01-21 | 16:00 | 16 | 427 | 1412 | 96 | 1 | 9 | 39 | 1 | 9 | 84 | 1 | 13 | 105 | 1 | 9 | 35 | 1 | 9 | 95 | 1 | 13 | 236 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 0.6 | 33.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.9 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.58 | 1 | 0
1988-01-22 | 1900-01-21 | 17:00 | 17 | 216 | 1412 | 56 | 1 | 13 | 2 | 1 | 9 | 56 | 1 | 13 | 62 | 1 | 13 | 0 | 1 | 9 | 62 | 1 | 13 | 184 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.9 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.86 | 1 | 0
1988-01-22 | 1900-01-21 | 18:00 | 18 | 21 | 600 | 8 | 1 | 13 | 1 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | 0.03 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 1 | 0
1988-01-22 | 1900-01-21 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 981 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.42 | 1 | 0
1988-01-22 | 1900-01-21 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 981 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 1 | 0
1988-01-22 | 1900-01-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.72 | 1 | 0
1988-01-22 | 1900-01-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.18 | 1 | 0
1988-01-22 | 1900-01-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -5 | 23 | A | 7 | 0.75 | A | 7 | 980 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.9 | 1 | 0
1988-01-22 | 1900-01-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 1 | 0
1988-01-23 | 1900-01-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 910 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.84 | 2 | 0
1988-01-23 | 1900-01-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.81 | A | 7 | 977 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.56 | 2 | 0
1988-01-23 | 1900-01-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.88 | A | 7 | 976 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 2 | 0
1988-01-23 | 1900-01-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -6.1 | 21.02 | A | 7 | 0.92 | A | 7 | 974 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.32 | 2 | 0
1988-01-23 | 1900-01-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 972 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.04 | 2 | 0
1988-01-23 | 1900-01-22 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 972 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.04 | 2 | 0
1988-01-23 | 1900-01-22 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -3.9 | 24.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.85 | A | 7 | 971 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.82 | 2 | 0
1988-01-23 | 1900-01-22 | 8:00 | 8 | 20 | 600 | 8 | 1 | 13 | 2 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -5 | 23 | A | 7 | 0.85 | A | 7 | 970 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 0.8 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.7 | 2 | 0
1988-01-23 | 1900-01-22 | 9:00 | 9 | 215 | 1412 | 50 | 1 | 13 | 19 | 1 | 9 | 47 | 1 | 13 | 55 | 1 | 13 | 14 | 1 | 9 | 53 | 1 | 13 | 118 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -1.7 | 28.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.82 | A | 7 | 969 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1370 | A | 7 | 0.8 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 2 | 0
1988-01-23 | 1900-01-22 | 10:00 | 10 | 426 | 1412 | 140 | 1 | 9 | 4 | 1 | 9 | 138 | 1 | 13 | 154 | 1 | 9 | 3 | 1 | 9 | 153 | 1 | 13 | 459 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.79 | A | 7 | 969 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.8 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 2 | 0
1988-01-23 | 1900-01-22 | 11:00 | 11 | 590 | 1412 | 197 | 1 | 9 | 5 | 1 | 9 | 195 | 1 | 13 | 220 | 1 | 9 | 4 | 1 | 9 | 218 | 1 | 13 | 695 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.7 | A | 7 | 969 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.8 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.28 | 2 | 0
1988-01-23 | 1900-01-22 | 12:00 | 12 | 693 | 1412 | 215 | 1 | 9 | 3 | 1 | 9 | 214 | 1 | 13 | 243 | 1 | 9 | 3 | 1 | 9 | 242 | 1 | 13 | 821 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.73 | A | 7 | 967 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 0.9 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 2 | 0
1988-01-23 | 1900-01-22 | 13:00 | 13 | 729 | 1412 | 224 | 1 | 9 | 1 | 1 | 9 | 224 | 1 | 13 | 254 | 1 | 9 | 1 | 1 | 9 | 254 | 1 | 13 | 873 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 967 | A | 7 | 230 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.9 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 2 | 0
1988-01-23 | 1900-01-22 | 14:00 | 14 | 695 | 1412 | 293 | 1 | 9 | 75 | 1 | 9 | 256 | 1 | 13 | 321 | 1 | 9 | 75 | 1 | 9 | 284 | 1 | 13 | 725 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 4.4 | 39.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.68 | A | 7 | 967 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.72 | 2 | 0
1988-01-23 | 1900-01-22 | 15:00 | 15 | 594 | 1412 | 281 | 1 | 13 | 381 | 1 | 13 | 122 | 1 | 13 | 302 | 1 | 13 | 371 | 1 | 13 | 146 | 1 | 13 | 239 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 6.7 | 44.06 | A | 7 | 0 | 32 | A | 7 | 0.63 | A | 7 | 967 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28 | 2 | 0
1988-01-23 | 1900-01-22 | 16:00 | 16 | 432 | 1412 | 236 | 1 | 13 | 499 | 1 | 13 | 84 | 1 | 13 | 243 | 1 | 13 | 440 | 1 | 13 | 108 | 1 | 13 | 154 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 7.2 | 44.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.63 | A | 7 | 967 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.88 | 2 | 0
1988-01-23 | 1900-01-22 | 17:00 | 17 | 221 | 1412 | 84 | 1 | 13 | 129 | 1 | 9 | 64 | 1 | 13 | 88 | 1 | 13 | 84 | 1 | 9 | 75 | 1 | 13 | 124 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 6.7 | 44.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.65 | A | 7 | 967 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.08 | 2 | 0
1988-01-23 | 1900-01-22 | 18:00 | 18 | 23 | 624 | 14 | 1 | 13 | 21 | 1 | 13 | 12 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 5.6 | 42.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.65 | A | 7 | 968 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.22 | 2 | 0
1988-01-23 | 1900-01-22 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 5 | 41 | A | 7 | -0.6 | 30.92 | A | 7 | 0.68 | A | 7 | 969 | A | 7 | 300 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.52 | 2 | 0
1988-01-23 | 1900-01-22 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 1070 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 2 | 0
1988-01-23 | 1900-01-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -0.6 | 30.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.61 | A | 7 | 972 | A | 7 | 300 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.24 | 2 | 0
1988-01-23 | 1900-01-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | -2.8 | 26.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.72 | A | 7 | 974 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.04 | 2 | 0
1988-01-23 | 1900-01-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -4.4 | 24.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.36 | 2 | 0
1988-01-23 | 1900-01-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -6.1 | 21.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.22 | 2 | 0
1988-01-24 | 1900-01-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 977 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 3 | 0
1988-01-24 | 1900-01-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.72 | 3 | 0
1988-01-24 | 1900-01-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.72 | 3 | 0
1988-01-24 | 1900-01-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 978 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.72 | 3 | 0
1988-01-24 | 1900-01-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.12 | 3 | 0
1988-01-24 | 1900-01-23 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.84 | A | 7 | 979 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.12 | 3 | 0
1988-01-24 | 1900-01-23 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.88 | A | 7 | 979 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.22 | 3 | 0
1988-01-24 | 1900-01-23 | 8:00 | 8 | 21 | 600 | 10 | 1 | 13 | 16 | 1 | 9 | 9 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -10 | 14 | A | 7 | 0.88 | A | 7 | 979 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.2 | 3 | 0
1988-01-24 | 1900-01-23 | 9:00 | 9 | 218 | 1412 | 96 | 1 | 13 | 323 | 1 | 9 | 46 | 1 | 13 | 101 | 1 | 13 | 214 | 1 | 9 | 68 | 1 | 13 | 82 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 3 | 0
1988-01-24 | 1900-01-23 | 10:00 | 10 | 430 | 1412 | 253 | 1 | 9 | 592 | 1 | 9 | 72 | 1 | 13 | 262 | 1 | 9 | 526 | 1 | 9 | 102 | 1 | 13 | 136 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.84 | 3 | 0
1988-01-24 | 1900-01-23 | 11:00 | 11 | 594 | 1412 | 377 | 1 | 9 | 683 | 1 | 9 | 89 | 1 | 13 | 397 | 1 | 9 | 658 | 1 | 9 | 119 | 1 | 13 | 181 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 0.6 | 33.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.48 | 3 | 0
1988-01-24 | 1900-01-23 | 12:00 | 12 | 698 | 1412 | 478 | 1 | 9 | 759 | 1 | 9 | 103 | 1 | 13 | 507 | 1 | 9 | 751 | 1 | 9 | 134 | 1 | 13 | 222 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.56 | 3 | 0
1988-01-24 | 1900-01-23 | 13:00 | 13 | 734 | 1412 | 470 | 1 | 13 | 561 | 1 | 13 | 179 | 1 | 13 | 498 | 1 | 13 | 565 | 1 | 13 | 203 | 1 | 13 | 386 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 5 | 41 | A | 7 | -2.8 | 26.96 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 280 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.96 | 3 | 0
1988-01-24 | 1900-01-23 | 14:00 | 14 | 700 | 1412 | 200 | 1 | 9 | 94 | 1 | 9 | 154 | 1 | 13 | 223 | 1 | 9 | 97 | 1 | 9 | 175 | 1 | 13 | 382 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 4.4 | 39.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.6 | A | 7 | 979 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 1070 | A | 7 | 0.9 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.16 | 3 | 0
1988-01-24 | 1900-01-23 | 15:00 | 15 | 599 | 1412 | 264 | 1 | 13 | 274 | 1 | 13 | 148 | 1 | 13 | 285 | 1 | 13 | 275 | 1 | 13 | 168 | 1 | 13 | 308 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 5.6 | 42.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.9 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.94 | 3 | 0
1988-01-24 | 1900-01-23 | 16:00 | 16 | 437 | 1412 | 143 | 1 | 13 | 140 | 1 | 13 | 100 | 1 | 13 | 158 | 1 | 13 | 130 | 1 | 13 | 118 | 1 | 13 | 224 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 4.4 | 39.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 0.9 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 3 | 0
1988-01-24 | 1900-01-23 | 17:00 | 17 | 226 | 1412 | 71 | 1 | 13 | 66 | 1 | 13 | 61 | 1 | 13 | 78 | 1 | 13 | 47 | 1 | 13 | 70 | 1 | 13 | 130 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 3.3 | 37.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 1680 | A | 7 | 0.9 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.56 | 3 | 0
1988-01-24 | 1900-01-23 | 18:00 | 18 | 25 | 647 | 5 | 1 | 13 | 1 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 0.9 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.44 | 3 | 0
1988-01-24 | 1900-01-23 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 280 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1370 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.86 | 3 | 0
1988-01-24 | 1900-01-23 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.84 | 3 | 0
1988-01-24 | 1900-01-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 0.6 | 33.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1370 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.92 | 3 | 0
1988-01-24 | 1900-01-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 320 | A | 7 | 13.4 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 3 | 0
1988-01-24 | 1900-01-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | -3.9 | 24.98 | A | 7 | -9.4 | 15.08 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 310 | A | 7 | 13.4 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.88 | 3 | 0
1988-01-24 | 1900-01-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 320 | A | 7 | 11.3 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 3 | 0
1988-01-25 | 1900-01-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 987 | A | 7 | 310 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 760 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.68 | 4 | 0
1988-01-25 | 1900-01-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -11.7 | 10.94 | A | 7 | -17.2 | 1.04 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 320 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.26 | 4 | 0
1988-01-25 | 1900-01-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -17.8 | -0.04 | A | 7 | 0.67 | A | 7 | 988 | A | 7 | 320 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.24 | 4 | 0
1988-01-25 | 1900-01-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -17.8 | -0.04 | A | 7 | 0.7 | A | 7 | 988 | A | 7 | 320 | A | 7 | 9.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.14 | 4 | 0
1988-01-25 | 1900-01-24 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -13.9 | 6.98 | A | 7 | -17.8 | -0.04 | A | 7 | 0.73 | A | 7 | 988 | A | 7 | 310 | A | 7 | 9.8 | A | 7 | 32200 | A | 7 | 610 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.04 | 4 | 0
1988-01-25 | 1900-01-24 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | -13.9 | 6.98 | A | 7 | -17.2 | 1.04 | A | 7 | 0.76 | A | 7 | 988 | A | 7 | 310 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.14 | 4 | 0
1988-01-25 | 1900-01-24 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.73 | A | 7 | 988 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.84 | 4 | 0
1988-01-25 | 1900-01-24 | 8:00 | 8 | 22 | 623 | 14 | 1 | 13 | 40 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.73 | A | 7 | 989 | A | 7 | 300 | A | 7 | 9.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.84 | 4 | 0
1988-01-25 | 1900-01-24 | 9:00 | 9 | 221 | 1411 | 108 | 1 | 13 | 439 | 1 | 9 | 39 | 1 | 13 | 111 | 1 | 13 | 304 | 1 | 9 | 63 | 1 | 13 | 70 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -19.4 | -2.92 | A | 7 | 0.63 | A | 7 | 989 | A | 7 | 300 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.02 | 4 | 0
1988-01-25 | 1900-01-24 | 10:00 | 10 | 434 | 1411 | 271 | 1 | 9 | 688 | 1 | 9 | 59 | 1 | 13 | 279 | 1 | 9 | 616 | 1 | 9 | 88 | 1 | 13 | 114 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -18.9 | -2.02 | A | 7 | 0.61 | A | 7 | 989 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.32 | 4 | 0
1988-01-25 | 1900-01-24 | 11:00 | 11 | 598 | 1411 | 412 | 1 | 9 | 795 | 1 | 9 | 74 | 1 | 13 | 430 | 1 | 9 | 762 | 1 | 9 | 105 | 1 | 13 | 152 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -18.9 | -2.02 | A | 7 | 0.55 | A | 7 | 988 | A | 7 | 310 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.42 | 4 | 0
1988-01-25 | 1900-01-24 | 12:00 | 12 | 702 | 1411 | 508 | 1 | 9 | 852 | 1 | 9 | 83 | 1 | 13 | 535 | 1 | 9 | 836 | 1 | 9 | 117 | 1 | 13 | 180 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -19.4 | -2.92 | A | 7 | 0.51 | A | 7 | 988 | A | 7 | 300 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.42 | 4 | 0
1988-01-25 | 1900-01-24 | 13:00 | 13 | 739 | 1411 | 539 | 1 | 9 | 864 | 1 | 9 | 86 | 1 | 13 | 569 | 1 | 9 | 853 | 1 | 9 | 121 | 1 | 13 | 191 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -20 | -4 | A | 7 | 0.44 | A | 7 | 987 | A | 7 | 320 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.6 | 4 | 0
1988-01-25 | 1900-01-24 | 14:00 | 14 | 705 | 1411 | 507 | 1 | 9 | 849 | 1 | 9 | 83 | 1 | 13 | 535 | 1 | 9 | 834 | 1 | 9 | 117 | 1 | 13 | 181 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -18.3 | -0.94 | A | 7 | 0.45 | A | 7 | 986 | A | 7 | 290 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.74 | 4 | 0
1988-01-25 | 1900-01-24 | 15:00 | 15 | 604 | 1411 | 386 | 1 | 9 | 660 | 1 | 9 | 104 | 1 | 13 | 404 | 1 | 9 | 634 | 1 | 9 | 131 | 1 | 13 | 208 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | -8.3 | 17.06 | A | 7 | -18.9 | -2.02 | A | 7 | 0.43 | A | 7 | 985 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.82 | 4 | 0
1988-01-25 | 1900-01-24 | 16:00 | 16 | 442 | 1411 | 243 | 1 | 9 | 469 | 1 | 9 | 97 | 1 | 13 | 258 | 1 | 9 | 421 | 1 | 9 | 125 | 1 | 13 | 181 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | -8.3 | 17.06 | A | 7 | -19.4 | -2.92 | A | 7 | 0.41 | A | 7 | 985 | A | 7 | 290 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.72 | 4 | 0
1988-01-25 | 1900-01-24 | 17:00 | 17 | 231 | 1411 | 85 | 1 | 13 | 193 | 1 | 13 | 54 | 1 | 13 | 91 | 1 | 13 | 130 | 1 | 13 | 70 | 1 | 13 | 100 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | -9.4 | 15.08 | A | 7 | -19.4 | -2.92 | A | 7 | 0.44 | A | 7 | 986 | A | 7 | 290 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.62 | 4 | 0
1988-01-25 | 1900-01-24 | 18:00 | 18 | 27 | 694 | 10 | 1 | 13 | 3 | 1 | 13 | 10 | 1 | 13 | 12 | 1 | 13 | 0 | 1 | 13 | 12 | 1 | 13 | 36 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | -10 | 14 | A | 7 | -19.4 | -2.92 | A | 7 | 0.46 | A | 7 | 986 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.62 | 4 | 0
1988-01-25 | 1900-01-24 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | -10.6 | 12.92 | A | 7 | -18.9 | -2.02 | A | 7 | 0.51 | A | 7 | 986 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.62 | 4 | 0
1988-01-25 | 1900-01-24 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -11.1 | 12.02 | A | 7 | -18.9 | -2.02 | A | 7 | 0.53 | A | 7 | 986 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.52 | 4 | 0
1988-01-25 | 1900-01-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -11.7 | 10.94 | A | 7 | -18.3 | -0.94 | A | 7 | 0.58 | A | 7 | 986 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.34 | 4 | 0
1988-01-25 | 1900-01-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | -12.2 | 10.04 | A | 7 | -19.4 | -2.92 | A | 7 | 0.55 | A | 7 | 987 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.32 | 4 | 0
1988-01-25 | 1900-01-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -12.8 | 8.96 | A | 7 | -21.1 | -5.98 | A | 7 | 0.5 | A | 7 | 986 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -7.28 | 4 | 0
1988-01-25 | 1900-01-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -13.3 | 8.06 | A | 7 | -20 | -4 | A | 7 | 0.58 | A | 7 | 987 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.2 | 4 | 0
1988-01-26 | 1900-01-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -13.9 | 6.98 | A | 7 | -20 | -4 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.2 | 5 | 0
1988-01-26 | 1900-01-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -13.9 | 6.98 | A | 7 | -20 | -4 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 4270 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.2 | 5 | 0
1988-01-26 | 1900-01-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -19.4 | -2.92 | A | 7 | 0.66 | A | 7 | 988 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 4270 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.02 | 5 | 0
1988-01-26 | 1900-01-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -15 | 5 | A | 7 | -18.9 | -2.02 | A | 7 | 0.73 | A | 7 | 988 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 4270 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.92 | 5 | 0
1988-01-26 | 1900-01-25 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -15.6 | 3.92 | A | 7 | -19.4 | -2.92 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.82 | 5 | 0
1988-01-26 | 1900-01-25 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -19.4 | -2.92 | A | 7 | 0.76 | A | 7 | 989 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.72 | 5 | 0
1988-01-26 | 1900-01-25 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -20 | -4 | A | 7 | 0.76 | A | 7 | 990 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.7 | 5 | 0
1988-01-26 | 1900-01-25 | 8:00 | 8 | 24 | 647 | 23 | 1 | 13 | 141 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -19.4 | -2.92 | A | 7 | 0.79 | A | 7 | 990 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.62 | 5 | 0
1988-01-26 | 1900-01-25 | 9:00 | 9 | 225 | 1411 | 126 | 1 | 13 | 641 | 1 | 9 | 24 | 1 | 13 | 134 | 1 | 13 | 490 | 1 | 9 | 56 | 1 | 13 | 58 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -18.9 | -2.02 | A | 7 | 0.76 | A | 7 | 991 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.82 | 5 | 0
1988-01-26 | 1900-01-25 | 10:00 | 10 | 438 | 1411 | 298 | 1 | 9 | 846 | 1 | 9 | 35 | 1 | 13 | 317 | 1 | 9 | 768 | 1 | 9 | 78 | 1 | 13 | 93 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -18.9 | -2.02 | A | 7 | 0.63 | A | 7 | 992 | A | 7 | 320 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.22 | 5 | 0
1988-01-26 | 1900-01-25 | 11:00 | 11 | 603 | 1411 | 437 | 1 | 9 | 919 | 1 | 9 | 44 | 1 | 13 | 464 | 1 | 9 | 881 | 1 | 9 | 86 | 1 | 13 | 117 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -18.3 | -0.94 | A | 7 | 0.51 | A | 7 | 993 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.54 | 5 | 0
1988-01-26 | 1900-01-25 | 12:00 | 12 | 707 | 1411 | 532 | 1 | 9 | 962 | 1 | 9 | 50 | 1 | 13 | 564 | 1 | 9 | 939 | 1 | 9 | 92 | 1 | 13 | 134 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -18.9 | -2.02 | A | 7 | 0.43 | A | 7 | 992 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.82 | 5 | 0
1988-01-26 | 1900-01-25 | 13:00 | 13 | 744 | 1411 | 568 | 1 | 9 | 979 | 1 | 9 | 52 | 1 | 13 | 602 | 1 | 9 | 961 | 1 | 9 | 93 | 1 | 13 | 141 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -20 | -4 | A | 7 | 0.36 | A | 7 | 992 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.9 | 5 | 0
1988-01-26 | 1900-01-25 | 14:00 | 14 | 711 | 1411 | 536 | 1 | 9 | 968 | 1 | 9 | 50 | 1 | 13 | 570 | 1 | 9 | 946 | 1 | 9 | 92 | 1 | 13 | 135 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -18.3 | -0.94 | A | 7 | 0.36 | A | 7 | 991 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.04 | 5 | 0
1988-01-26 | 1900-01-25 | 15:00 | 15 | 610 | 1411 | 391 | 1 | 9 | 719 | 1 | 9 | 81 | 1 | 13 | 406 | 1 | 9 | 689 | 1 | 9 | 108 | 1 | 13 | 162 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -5 | 23 | A | 7 | -18.3 | -0.94 | A | 7 | 0.35 | A | 7 | 991 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.14 | 5 | 0
1988-01-26 | 1900-01-25 | 16:00 | 16 | 448 | 1411 | 201 | 1 | 13 | 249 | 1 | 13 | 122 | 1 | 13 | 213 | 1 | 13 | 229 | 1 | 13 | 140 | 1 | 13 | 245 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | -5 | 23 | A | 7 | -18.3 | -0.94 | A | 7 | 0.35 | A | 7 | 990 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.14 | 5 | 0
1988-01-26 | 1900-01-25 | 17:00 | 17 | 236 | 1411 | 59 | 1 | 13 | 7 | 1 | 9 | 58 | 1 | 13 | 66 | 1 | 13 | 2 | 1 | 9 | 66 | 1 | 13 | 196 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -4.4 | 24.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.38 | A | 7 | 990 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.4 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.36 | 5 | 0
1988-01-26 | 1900-01-25 | 18:00 | 18 | 29 | 717 | 6 | 1 | 13 | 1 | 1 | 9 | 6 | 1 | 13 | 7 | 1 | 13 | 0 | 1 | 9 | 7 | 1 | 13 | 23 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -15.6 | 3.92 | A | 7 | 0.42 | A | 7 | 990 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 0.5 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.52 | 5 | 0
1988-01-26 | 1900-01-25 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -14.4 | 6.08 | A | 7 | 0.48 | A | 7 | 990 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 1070 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.78 | 5 | 0
1988-01-26 | 1900-01-25 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.5 | A | 7 | 990 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 1070 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.66 | 5 | 0
1988-01-26 | 1900-01-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.6 | A | 7 | 990 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 1070 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.72 | 5 | 0
1988-01-26 | 1900-01-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.72 | A | 7 | 990 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 1070 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.16 | 5 | 0
1988-01-26 | 1900-01-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.72 | A | 7 | 990 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 1830 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 5 | 0
1988-01-26 | 1900-01-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 990 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 5 | 0
1988-01-27 | 1900-01-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 990 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 610 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 6 | 0
1988-01-27 | 1900-01-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.88 | A | 7 | 991 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 6 | 0
1988-01-27 | 1900-01-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.85 | A | 7 | 991 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.82 | 6 | 0
1988-01-27 | 1900-01-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.64 | 6 | 0
1988-01-27 | 1900-01-26 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -5.6 | 21.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.62 | 6 | 0
1988-01-27 | 1900-01-26 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -4.4 | 24.08 | A | 7 | -5 | 23 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.6 | 6 | 0
1988-01-27 | 1900-01-26 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -6.7 | 19.94 | A | 7 | 1 | A | 7 | 992 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.84 | 6 | 0
1988-01-27 | 1900-01-26 | 8:00 | 8 | 25 | 647 | 19 | 1 | 13 | 93 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -4.4 | 24.08 | A | 7 | -5 | 23 | A | 7 | 0.96 | A | 7 | 992 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.6 | 6 | 0
1988-01-27 | 1900-01-26 | 9:00 | 9 | 228 | 1411 | 120 | 1 | 13 | 450 | 1 | 13 | 47 | 1 | 13 | 122 | 1 | 13 | 313 | 1 | 13 | 71 | 1 | 13 | 82 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -1.7 | 28.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.92 | A | 7 | 993 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 6 | 0
1988-01-27 | 1900-01-26 | 10:00 | 10 | 442 | 1411 | 217 | 1 | 9 | 450 | 1 | 9 | 76 | 1 | 13 | 225 | 1 | 9 | 402 | 1 | 9 | 99 | 1 | 13 | 143 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 993 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 6 | 0
1988-01-27 | 1900-01-26 | 11:00 | 11 | 607 | 1411 | 285 | 1 | 13 | 341 | 1 | 13 | 138 | 1 | 13 | 302 | 1 | 13 | 333 | 1 | 13 | 158 | 1 | 13 | 274 | 1 | 23 | 7 | A | 7 | 4 | A | 7 | 1.1 | 33.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.79 | A | 7 | 993 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 4270 | A | 7 | 0.9 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.04 | 6 | 0
1988-01-27 | 1900-01-26 | 12:00 | 12 | 712 | 1411 | 385 | 1 | 13 | 426 | 1 | 13 | 170 | 1 | 13 | 408 | 1 | 13 | 427 | 1 | 13 | 191 | 1 | 13 | 360 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 3.3 | 37.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 6 | 0
1988-01-27 | 1900-01-26 | 13:00 | 13 | 749 | 1411 | 456 | 1 | 13 | 578 | 1 | 13 | 150 | 1 | 13 | 475 | 1 | 13 | 569 | 1 | 13 | 171 | 1 | 13 | 319 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 6.1 | 42.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.58 | A | 7 | 992 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.74 | 6 | 0
1988-01-27 | 1900-01-26 | 14:00 | 14 | 716 | 1411 | 510 | 1 | 9 | 883 | 1 | 9 | 63 | 1 | 13 | 538 | 1 | 9 | 862 | 1 | 9 | 99 | 1 | 13 | 151 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 7.2 | 44.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.54 | A | 7 | 992 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 6 | 0
1988-01-27 | 1900-01-26 | 15:00 | 15 | 615 | 1411 | 395 | 1 | 9 | 768 | 1 | 9 | 61 | 1 | 13 | 424 | 1 | 9 | 746 | 1 | 9 | 98 | 1 | 13 | 137 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 7.8 | 46.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.48 | A | 7 | 991 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.06 | 6 | 0
1988-01-27 | 1900-01-26 | 16:00 | 16 | 453 | 1411 | 287 | 1 | 9 | 723 | 1 | 9 | 56 | 1 | 13 | 300 | 1 | 9 | 657 | 1 | 9 | 88 | 1 | 13 | 113 | 1 | 18 | 5 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.46 | A | 7 | 990 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.86 | 6 | 0
1988-01-27 | 1900-01-26 | 17:00 | 17 | 242 | 1411 | 125 | 1 | 13 | 542 | 1 | 9 | 34 | 1 | 13 | 130 | 1 | 13 | 409 | 1 | 9 | 59 | 1 | 13 | 66 | 1 | 21 | 4 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.49 | A | 7 | 990 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 6 | 0
1988-01-27 | 1900-01-26 | 18:00 | 18 | 32 | 741 | 22 | 1 | 13 | 96 | 1 | 9 | 12 | 1 | 13 | 18 | 1 | 13 | 32 | 1 | 9 | 16 | 1 | 13 | 21 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | 4.4 | 39.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.6 | A | 7 | 990 | A | 7 | 140 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.16 | 6 | 0
1988-01-27 | 1900-01-26 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 990 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 6 | 0
1988-01-27 | 1900-01-26 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.67 | A | 7 | 990 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.86 | 6 | 0
1988-01-27 | 1900-01-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.73 | A | 7 | 990 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 6 | 0
1988-01-27 | 1900-01-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.73 | A | 7 | 990 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 6 | 0
1988-01-27 | 1900-01-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 989 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 6 | 0
1988-01-27 | 1900-01-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 989 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 6 | 0
1988-01-28 | 1900-01-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.76 | A | 7 | 988 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.74 | 7 | 0
1988-01-28 | 1900-01-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 988 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 7 | 0
1988-01-28 | 1900-01-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 7 | 0
1988-01-28 | 1900-01-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 7 | 0
1988-01-28 | 1900-01-27 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 7 | 0
1988-01-28 | 1900-01-27 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 987 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 7 | 0
1988-01-28 | 1900-01-27 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 987 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 7 | 0
1988-01-28 | 1900-01-27 | 8:00 | 8 | 26 | 670 | 23 | 1 | 13 | 114 | 1 | 9 | 11 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 6 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 988 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 7 | 0
1988-01-28 | 1900-01-27 | 9:00 | 9 | 232 | 1410 | 121 | 1 | 13 | 517 | 1 | 9 | 35 | 1 | 13 | 122 | 1 | 13 | 383 | 1 | 9 | 58 | 1 | 13 | 65 | 1 | 21 | 7 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 988 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.84 | 7 | 0
1988-01-28 | 1900-01-27 | 10:00 | 10 | 446 | 1410 | 290 | 1 | 9 | 759 | 1 | 9 | 49 | 1 | 13 | 305 | 1 | 9 | 691 | 1 | 9 | 85 | 1 | 13 | 104 | 1 | 18 | 5 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.65 | A | 7 | 988 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.44 | 7 | 0
1988-01-28 | 1900-01-27 | 11:00 | 11 | 612 | 1410 | 428 | 1 | 9 | 840 | 1 | 9 | 63 | 1 | 13 | 449 | 1 | 9 | 805 | 1 | 9 | 99 | 1 | 13 | 136 | 1 | 18 | 5 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.56 | A | 7 | 989 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.52 | 7 | 0
1988-01-28 | 1900-01-27 | 12:00 | 12 | 717 | 1410 | 523 | 1 | 9 | 908 | 1 | 9 | 61 | 1 | 13 | 551 | 1 | 9 | 887 | 1 | 9 | 98 | 1 | 13 | 149 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.48 | A | 7 | 988 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.62 | 7 | 0
1988-01-28 | 1900-01-27 | 13:00 | 13 | 754 | 1410 | 560 | 1 | 9 | 954 | 1 | 9 | 50 | 1 | 13 | 594 | 1 | 9 | 938 | 1 | 9 | 91 | 1 | 13 | 138 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.45 | A | 7 | 987 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.02 | 7 | 0
1988-01-28 | 1900-01-27 | 14:00 | 14 | 721 | 1410 | 530 | 1 | 9 | 943 | 1 | 9 | 48 | 1 | 13 | 563 | 1 | 9 | 923 | 1 | 9 | 89 | 1 | 13 | 132 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.42 | A | 7 | 986 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.72 | 7 | 0
1988-01-28 | 1900-01-27 | 15:00 | 15 | 620 | 1410 | 441 | 1 | 9 | 908 | 1 | 9 | 43 | 1 | 13 | 471 | 1 | 9 | 874 | 1 | 9 | 85 | 1 | 13 | 117 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.42 | A | 7 | 986 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.48 | 7 | 0
1988-01-28 | 1900-01-27 | 16:00 | 16 | 458 | 1410 | 304 | 1 | 9 | 834 | 1 | 9 | 34 | 1 | 13 | 326 | 1 | 9 | 764 | 1 | 9 | 76 | 1 | 13 | 93 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 0 | 32 | A | 7 | 0.4 | A | 7 | 986 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.4 | 7 | 0
1988-01-28 | 1900-01-27 | 17:00 | 17 | 247 | 1410 | 137 | 1 | 13 | 656 | 1 | 9 | 24 | 1 | 13 | 148 | 1 | 13 | 516 | 1 | 9 | 57 | 1 | 13 | 61 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 0 | 32 | A | 7 | 0.45 | A | 7 | 985 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.9 | 7 | 0
1988-01-28 | 1900-01-27 | 18:00 | 18 | 34 | 764 | 27 | 1 | 13 | 171 | 1 | 9 | 10 | 1 | 13 | 19 | 1 | 13 | 85 | 1 | 9 | 15 | 1 | 13 | 21 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.72 | 7 | 0
1988-01-28 | 1900-01-27 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | 0 | 32 | A | 7 | 0.65 | A | 7 | 985 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.2 | 7 | 0
1988-01-28 | 1900-01-27 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.61 | A | 7 | 985 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.68 | 7 | 0
1988-01-28 | 1900-01-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.61 | A | 7 | 984 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.38 | 7 | 0
1988-01-28 | 1900-01-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 2.2 | 35.96 | A | 7 | 0.68 | A | 7 | 984 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.16 | 7 | 0
1988-01-28 | 1900-01-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 2.2 | 35.96 | A | 7 | 0.68 | A | 7 | 984 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.16 | 7 | 0
1988-01-28 | 1900-01-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | 2.8 | 37.04 | A | 7 | 0.8 | A | 7 | 983 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.64 | 7 | 0
1988-01-29 | 1900-01-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 3.9 | 39.02 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.12 | 1 | 0
1988-01-29 | 1900-01-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.83 | A | 7 | 982 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.72 | 1 | 0
1988-01-29 | 1900-01-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 5 | 41 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.1 | 1 | 0
1988-01-29 | 1900-01-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.78 | 1 | 0
1988-01-29 | 1900-01-28 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.78 | 1 | 0
1988-01-29 | 1900-01-28 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 980 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.78 | 1 | 0
1988-01-29 | 1900-01-28 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 980 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.78 | 1 | 0
1988-01-29 | 1900-01-28 | 8:00 | 8 | 28 | 693 | 16 | 1 | 13 | 8 | 1 | 13 | 15 | 1 | 13 | 17 | 1 | 13 | 4 | 1 | 13 | 17 | 1 | 13 | 36 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 8.9 | 48.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.83 | A | 7 | 980 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.58 | 1 | 0
1988-01-29 | 1900-01-28 | 9:00 | 9 | 236 | 1410 | 81 | 1 | 13 | 69 | 1 | 9 | 69 | 1 | 13 | 87 | 1 | 13 | 50 | 1 | 9 | 79 | 1 | 13 | 147 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 10 | 50 | A | 7 | 6.7 | 44.06 | A | 7 | 0.8 | A | 7 | 980 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 1.6 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.26 | 1 | 0
1988-01-29 | 1900-01-28 | 10:00 | 10 | 450 | 1410 | 251 | 1 | 13 | 523 | 1 | 13 | 84 | 1 | 13 | 259 | 1 | 13 | 468 | 1 | 13 | 109 | 1 | 13 | 156 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 11.7 | 53.06 | A | 7 | 7.2 | 44.96 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 200 | A | 7 | 9.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.16 | 1 | 0
1988-01-29 | 1900-01-28 | 11:00 | 11 | 616 | 1410 | 391 | 1 | 13 | 633 | 1 | 13 | 114 | 1 | 13 | 406 | 1 | 13 | 608 | 1 | 13 | 139 | 1 | 13 | 226 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 13.9 | 57.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 1 | 0
1988-01-29 | 1900-01-28 | 12:00 | 12 | 722 | 1410 | 448 | 1 | 13 | 565 | 1 | 13 | 159 | 1 | 13 | 479 | 1 | 13 | 569 | 1 | 13 | 187 | 1 | 13 | 337 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 13.3 | 55.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 200 | A | 7 | 14.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.44 | 1 | 0
1988-01-29 | 1900-01-28 | 13:00 | 13 | 760 | 1410 | 434 | 1 | 13 | 463 | 1 | 13 | 185 | 1 | 13 | 460 | 1 | 13 | 469 | 1 | 13 | 207 | 1 | 13 | 407 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 14.4 | 57.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 200 | A | 7 | 13.9 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.94 | 1 | 0
1988-01-29 | 1900-01-28 | 14:00 | 14 | 727 | 1410 | 324 | 1 | 13 | 239 | 1 | 13 | 201 | 1 | 13 | 349 | 1 | 13 | 249 | 1 | 13 | 220 | 1 | 13 | 456 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 14.4 | 57.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 200 | A | 7 | 14.9 | A | 7 | 32200 | A | 7 | 820 | A | 7 | 1.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.94 | 1 | 0
1988-01-29 | 1900-01-28 | 15:00 | 15 | 626 | 1410 | 237 | 1 | 9 | 62 | 1 | 9 | 210 | 1 | 13 | 260 | 1 | 9 | 61 | 1 | 9 | 233 | 1 | 13 | 587 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.72 | A | 7 | 976 | A | 7 | 200 | A | 7 | 13.4 | A | 7 | 32200 | A | 7 | 820 | A | 7 | 1.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.74 | 1 | 0
1988-01-29 | 1900-01-28 | 16:00 | 16 | 464 | 1410 | 137 | 1 | 9 | 69 | 1 | 9 | 115 | 1 | 13 | 151 | 1 | 9 | 64 | 1 | 9 | 130 | 1 | 13 | 317 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.72 | A | 7 | 976 | A | 7 | 180 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 760 | A | 7 | 1.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.74 | 1 | 0
1988-01-29 | 1900-01-28 | 17:00 | 17 | 252 | 1410 | 77 | 1 | 13 | 35 | 1 | 13 | 71 | 1 | 13 | 85 | 1 | 13 | 28 | 1 | 13 | 80 | 1 | 13 | 172 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 13.3 | 55.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.72 | A | 7 | 975 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 1.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.74 | 1 | 0
1988-01-29 | 1900-01-28 | 18:00 | 18 | 37 | 787 | 17 | 1 | 13 | 10 | 1 | 9 | 16 | 1 | 13 | 18 | 1 | 13 | 5 | 1 | 9 | 18 | 1 | 13 | 39 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 12.8 | 55.04 | A | 7 | 8.3 | 46.94 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 190 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 910 | A | 7 | 1.7 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.14 | 1 | 0
1988-01-29 | 1900-01-28 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 12.2 | 53.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.77 | A | 7 | 976 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.44 | 1 | 0
1988-01-29 | 1900-01-28 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 11.7 | 53.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.8 | A | 7 | 976 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 1370 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 1 | 0
1988-01-29 | 1900-01-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.77 | A | 7 | 975 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.64 | 1 | 0
1988-01-29 | 1900-01-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 12.2 | 53.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.34 | 1 | 0
1988-01-29 | 1900-01-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 12.2 | 53.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.72 | A | 7 | 975 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.86 | 1 | 0
1988-01-29 | 1900-01-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 11.7 | 53.06 | A | 7 | 7.2 | 44.96 | A | 7 | 0.74 | A | 7 | 974 | A | 7 | 190 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.16 | 1 | 0
1988-01-30 | 1900-01-29 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 12.2 | 53.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.75 | A | 7 | 973 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.34 | 2 | 0
1988-01-30 | 1900-01-29 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 12.2 | 53.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.75 | A | 7 | 973 | A | 7 | 190 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.34 | 2 | 0
1988-01-30 | 1900-01-29 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 12.2 | 53.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.75 | A | 7 | 973 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.34 | 2 | 0
1988-01-30 | 1900-01-29 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.77 | A | 7 | 972 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.64 | 2 | 0
1988-01-30 | 1900-01-29 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 11.1 | 51.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.8 | A | 7 | 972 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.04 | 2 | 0
1988-01-30 | 1900-01-29 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 11.1 | 51.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.8 | A | 7 | 972 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.04 | 2 | 0
1988-01-30 | 1900-01-29 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 4 | A | 7 | 11.7 | 53.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.8 | A | 7 | 971 | A | 7 | 190 | A | 7 | 13.4 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 2 | 0
1988-01-30 | 1900-01-29 | 8:00 | 8 | 30 | 717 | 11 | 1 | 13 | 4 | 1 | 9 | 10 | 1 | 13 | 11 | 1 | 13 | 2 | 1 | 9 | 11 | 1 | 13 | 25 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 12.2 | 53.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.83 | A | 7 | 971 | A | 7 | 190 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.22 | 2 | 0
1988-01-30 | 1900-01-29 | 9:00 | 9 | 240 | 1410 | 60 | 1 | 13 | 5 | 1 | 9 | 59 | 1 | 13 | 67 | 1 | 13 | 1 | 1 | 9 | 67 | 1 | 13 | 199 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 760 | A | 7 | 1.9 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.5 | 2 | 0
1988-01-30 | 1900-01-29 | 10:00 | 10 | 455 | 1410 | 104 | 1 | 9 | 29 | 1 | 9 | 94 | 1 | 13 | 114 | 1 | 9 | 27 | 1 | 9 | 105 | 1 | 13 | 266 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 10.6 | 51.08 | A | 7 | 0.75 | A | 7 | 971 | A | 7 | 190 | A | 7 | 13.9 | A | 7 | 32200 | A | 7 | 760 | A | 7 | 2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.98 | 2 | 0
1988-01-30 | 1900-01-29 | 11:00 | 11 | 621 | 1410 | 203 | 1 | 9 | 13 | 1 | 9 | 198 | 1 | 13 | 228 | 1 | 9 | 11 | 1 | 9 | 223 | 1 | 13 | 728 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 190 | A | 7 | 14.4 | A | 7 | 32200 | A | 7 | 760 | A | 7 | 2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.08 | 2 | 0
1988-01-30 | 1900-01-29 | 12:00 | 12 | 727 | 1410 | 226 | 1 | 9 | 7 | 1 | 9 | 223 | 1 | 13 | 257 | 1 | 9 | 6 | 1 | 9 | 253 | 1 | 13 | 870 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.7 | A | 7 | 970 | A | 7 | 200 | A | 7 | 13.4 | A | 7 | 32200 | A | 7 | 1070 | A | 7 | 2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.08 | 2 | 0
1988-01-30 | 1900-01-29 | 13:00 | 13 | 765 | 1410 | 192 | 1 | 9 | 2 | 1 | 9 | 191 | 1 | 13 | 222 | 1 | 9 | 2 | 1 | 9 | 221 | 1 | 13 | 807 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 970 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 1070 | A | 7 | 2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.28 | 2 | 0
1988-01-30 | 1900-01-29 | 14:00 | 14 | 732 | 1410 | 225 | 1 | 9 | 1 | 1 | 9 | 225 | 1 | 13 | 255 | 1 | 9 | 1 | 1 | 9 | 255 | 1 | 13 | 879 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 969 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.98 | 2 | 0
1988-01-30 | 1900-01-29 | 15:00 | 15 | 632 | 1410 | 181 | 1 | 9 | 3 | 1 | 9 | 179 | 1 | 13 | 204 | 1 | 9 | 2 | 1 | 9 | 203 | 1 | 13 | 691 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 969 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 1370 | A | 7 | 2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.98 | 2 | 0
1988-01-30 | 1900-01-29 | 16:00 | 16 | 469 | 1410 | 134 | 1 | 9 | 1 | 1 | 9 | 134 | 1 | 13 | 150 | 1 | 9 | 1 | 1 | 9 | 150 | 1 | 13 | 480 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.65 | A | 7 | 969 | A | 7 | 210 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 1370 | A | 7 | 2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.28 | 2 | 0
1988-01-30 | 1900-01-29 | 17:00 | 17 | 258 | 1410 | 43 | 1 | 13 | 0 | 1 | 9 | 43 | 1 | 13 | 50 | 1 | 13 | 0 | 1 | 9 | 50 | 1 | 13 | 162 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 969 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 1370 | A | 7 | 2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.98 | 2 | 0
1988-01-30 | 1900-01-29 | 18:00 | 18 | 40 | 811 | 12 | 1 | 13 | 3 | 1 | 9 | 12 | 1 | 13 | 14 | 1 | 13 | 0 | 1 | 9 | 14 | 1 | 13 | 43 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 970 | A | 7 | 190 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 1370 | A | 7 | 2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.98 | 2 | 0
1988-01-30 | 1900-01-29 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 11.1 | 51.98 | A | 7 | 0.75 | A | 7 | 971 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.78 | 2 | 0
1988-01-30 | 1900-01-29 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 15 | 59 | A | 7 | 11.1 | 51.98 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.28 | 2 | 0
1988-01-30 | 1900-01-29 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 11.7 | 53.06 | A | 7 | 0.81 | A | 7 | 971 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.86 | 2 | 0
1988-01-30 | 1900-01-29 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 11.7 | 53.06 | A | 7 | 0.81 | A | 7 | 971 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.86 | 2 | 0
1988-01-30 | 1900-01-29 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.93 | A | 7 | 971 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.76 | 2 | 0
1988-01-30 | 1900-01-29 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.93 | A | 7 | 970 | A | 7 | 230 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 760 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.76 | 2 | 0
1988-01-31 | 1900-01-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 10 | 50 | A | 7 | 0.96 | A | 7 | 971 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 4800 | A | 7 | 760 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 3 | 0
1988-01-31 | 1900-01-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 10 | 50 | A | 7 | 1 | A | 7 | 971 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50 | 3 | 0
1988-01-31 | 1900-01-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 971 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 790 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 3 | 0
1988-01-31 | 1900-01-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 971 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 820 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 3 | 0
1988-01-31 | 1900-01-30 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.28 | 3 | 0
1988-01-31 | 1900-01-30 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 10 | 50 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 400 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 3 | 0
1988-01-31 | 1900-01-30 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.86 | A | 7 | 974 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 700 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.24 | 3 | 0
1988-01-31 | 1900-01-30 | 8:00 | 8 | 32 | 740 | 7 | 1 | 13 | 8 | 1 | 9 | 7 | 1 | 13 | 9 | 1 | 13 | 3 | 1 | 9 | 8 | 1 | 13 | 14 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 977 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 2000 | A | 7 | 90 | A | 7 | 1.1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 3 | 0
1988-01-31 | 1900-01-30 | 9:00 | 9 | 244 | 1409 | 45 | 1 | 13 | 2 | 1 | 9 | 45 | 1 | 13 | 52 | 1 | 13 | 0 | 1 | 9 | 52 | 1 | 13 | 165 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 3 | 0
1988-01-31 | 1900-01-30 | 10:00 | 10 | 459 | 1409 | 122 | 1 | 9 | 0 | 1 | 9 | 122 | 1 | 13 | 137 | 1 | 9 | 0 | 1 | 9 | 137 | 1 | 13 | 446 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 350 | A | 7 | 8.2 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 3 | 0
1988-01-31 | 1900-01-30 | 11:00 | 11 | 626 | 1409 | 157 | 1 | 9 | 10 | 1 | 9 | 152 | 1 | 13 | 179 | 1 | 9 | 7 | 1 | 9 | 176 | 1 | 13 | 614 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 350 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.1 | 3 | 0
1988-01-31 | 1900-01-30 | 12:00 | 12 | 732 | 1409 | 177 | 1 | 9 | 1 | 1 | 9 | 176 | 1 | 13 | 204 | 1 | 9 | 1 | 1 | 9 | 203 | 1 | 13 | 743 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.89 | A | 7 | 981 | A | 7 | 360 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 340 | A | 7 | 1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 3 | 0
1988-01-31 | 1900-01-30 | 13:00 | 13 | 770 | 1409 | 234 | 1 | 9 | 3 | 1 | 9 | 232 | 1 | 13 | 266 | 1 | 9 | 3 | 1 | 9 | 264 | 1 | 13 | 926 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.85 | A | 7 | 981 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 400 | A | 7 | 1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 3 | 0
1988-01-31 | 1900-01-30 | 14:00 | 14 | 738 | 1409 | 210 | 1 | 9 | 3 | 1 | 9 | 208 | 1 | 13 | 239 | 1 | 9 | 3 | 1 | 9 | 238 | 1 | 13 | 839 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.85 | A | 7 | 981 | A | 7 | 350 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 430 | A | 7 | 1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.52 | 3 | 0
1988-01-31 | 1900-01-30 | 15:00 | 15 | 637 | 1409 | 206 | 1 | 9 | 1 | 1 | 9 | 205 | 1 | 13 | 230 | 1 | 9 | 1 | 1 | 9 | 230 | 1 | 13 | 756 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 10 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 430 | A | 7 | 1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.14 | 3 | 0
1988-01-31 | 1900-01-30 | 16:00 | 16 | 475 | 1409 | 138 | 1 | 9 | 2 | 1 | 9 | 138 | 1 | 13 | 155 | 1 | 9 | 1 | 1 | 9 | 154 | 1 | 13 | 492 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 982 | A | 7 | 10 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 430 | A | 7 | 0.9 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 3 | 0
1988-01-31 | 1900-01-30 | 17:00 | 17 | 263 | 1409 | 73 | 1 | 13 | 0 | 1 | 9 | 72 | 1 | 13 | 80 | 1 | 13 | 0 | 1 | 9 | 80 | 1 | 13 | 237 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.82 | A | 7 | 983 | A | 7 | 20 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 460 | A | 7 | 0.9 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 3 | 0
1988-01-31 | 1900-01-30 | 18:00 | 18 | 43 | 857 | 15 | 1 | 13 | 0 | 1 | 9 | 15 | 1 | 13 | 17 | 1 | 13 | 0 | 1 | 9 | 17 | 1 | 13 | 52 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 20 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 460 | A | 7 | 0.9 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 3 | 0
1988-01-31 | 1900-01-30 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 20 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 460 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.38 | 3 | 0
1988-01-31 | 1900-01-30 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -1.7 | 28.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 610 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 3 | 0
1988-01-31 | 1900-01-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 9140 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 3 | 0
1988-01-31 | 1900-01-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.6 | 27.32 | A | 7 | -5.3 | 22.46 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 610 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.96 | 3 | 0
1988-01-31 | 1900-01-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.7 | 25.34 | A | 7 | -6.4 | 20.48 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 20 | A | 7 | 4.7 | A | 7 | 32200 | A | 7 | 610 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.98 | 3 | 0
1988-01-31 | 1900-01-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.7 | 23.54 | A | 7 | -7.4 | 18.68 | A | 7 | 0.81 | A | 7 | 985 | A | 7 | 340 | A | 7 | 4.2 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.28 | 3 | 0
1994-02-01 | 1900-01-31 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.7 | 21.74 | A | 7 | -8.5 | 16.7 | A | 7 | 0.55 | A | 7 | 989 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 2286 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.7 | 4 | 0
1994-02-01 | 1900-01-31 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -6.7 | 19.94 | A | 7 | -9.5 | 14.9 | A | 7 | 0.71 | A | 7 | 989 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 1524 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.1 | 4 | 0
1994-02-01 | 1900-01-31 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | -7.8 | 17.96 | A | 7 | -10.6 | 12.92 | A | 7 | 0.78 | A | 7 | 988 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 2438 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.62 | 4 | 0
1994-02-01 | 1900-01-31 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.78 | A | 7 | 988 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 2438 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.74 | 4 | 0
1994-02-01 | 1900-01-31 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.78 | A | 7 | 987 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 2438 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.72 | 4 | 0
1994-02-01 | 1900-01-31 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.75 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 2134 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.62 | 4 | 0
1994-02-01 | 1900-01-31 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 1981 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.32 | 4 | 0
1994-02-01 | 1900-01-31 | 8:00 | 8 | 35 | 763 | 5 | 1 | 10 | 0 | 1 | 16 | 5 | 1 | 10 | 600 | 1 | 10 | 0 | 1 | 16 | 600 | 1 | 10 | 200 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -10.6 | 12.92 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 1981 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.22 | 4 | 0
1994-02-01 | 1900-01-31 | 9:00 | 9 | 250 | 1409 | 64 | 1 | 10 | 64 | 1 | 16 | 52 | 1 | 10 | 7000 | 1 | 10 | 4800 | 1 | 16 | 6200 | 1 | 10 | 1110 | 1 | 21 | 7 | A | 7 | 7 | A | 7 | -6.1 | 21.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.67 | A | 7 | 985 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 1981 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.02 | 4 | 0
1994-02-01 | 1900-01-31 | 10:00 | 10 | 467 | 1409 | 237 | 1 | 10 | 306 | 1 | 16 | 136 | 1 | 10 | 25100 | 1 | 10 | 28600 | 1 | 16 | 15600 | 1 | 10 | 2790 | 1 | 21 | 10 | A | 7 | 3 | A | 7 | -3.3 | 26.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.59 | A | 7 | 985 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.48 | 4 | 0
1994-02-01 | 1900-01-31 | 11:00 | 11 | 634 | 1409 | 396 | 1 | 10 | 547 | 1 | 16 | 150 | 1 | 10 | 41900 | 1 | 10 | 53800 | 1 | 16 | 17600 | 1 | 10 | 3040 | 1 | 21 | 4 | A | 7 | 2 | A | 7 | -1.1 | 30.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.49 | A | 7 | 985 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.88 | 4 | 0
1994-02-01 | 1900-01-31 | 12:00 | 12 | 740 | 1409 | 490 | 1 | 10 | 617 | 1 | 16 | 165 | 1 | 10 | 52300 | 1 | 10 | 62300 | 1 | 16 | 19400 | 1 | 10 | 3550 | 1 | 21 | 8 | A | 7 | 1 | A | 7 | 0 | 32 | A | 7 | -8.9 | 15.98 | A | 7 | 0.47 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.48 | 4 | 0
1994-02-01 | 1900-01-31 | 13:00 | 13 | 779 | 1409 | 518 | 1 | 10 | 624 | 1 | 16 | 172 | 1 | 10 | 53400 | 1 | 10 | 61400 | 1 | 16 | 19300 | 1 | 10 | 3680 | 1 | 21 | 7 | A | 7 | 1 | A | 7 | 1.7 | 35.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.4 | A | 7 | 983 | A | 7 | 240 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.28 | 4 | 0
1994-02-01 | 1900-01-31 | 14:00 | 14 | 747 | 1409 | 435 | 1 | 10 | 393 | 1 | 16 | 226 | 1 | 10 | 46500 | 1 | 10 | 41100 | 1 | 16 | 24600 | 1 | 10 | 5280 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 1.7 | 35.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.36 | A | 7 | 983 | A | 7 | 270 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.12 | 4 | 0
1994-02-01 | 1900-01-31 | 15:00 | 15 | 646 | 1409 | 308 | 1 | 10 | 212 | 1 | 16 | 210 | 1 | 10 | 33300 | 1 | 10 | 21400 | 1 | 16 | 23500 | 1 | 10 | 5090 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 1.7 | 35.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.34 | A | 7 | 982 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 6096 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.22 | 4 | 0
1994-02-01 | 1900-01-31 | 16:00 | 16 | 484 | 1409 | 79 | 1 | 10 | 0 | 1 | 16 | 79 | 1 | 10 | 9200 | 1 | 10 | 0 | 1 | 16 | 9200 | 1 | 10 | 3300 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.4 | A | 7 | 983 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 1524 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.28 | 4 | 0
1994-02-01 | 1900-01-31 | 17:00 | 17 | 272 | 1409 | 44 | 1 | 10 | 0 | 1 | 16 | 44 | 1 | 10 | 5100 | 1 | 10 | 0 | 1 | 16 | 5100 | 1 | 10 | 1680 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.49 | A | 7 | 983 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 1524 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.36 | 4 | 0
1994-02-01 | 1900-01-31 | 18:00 | 18 | 47 | 881 | 7 | 1 | 10 | 0 | 1 | 16 | 7 | 1 | 10 | 800 | 1 | 10 | 0 | 1 | 16 | 800 | 1 | 10 | 270 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -6.7 | 19.94 | A | 7 | 0.57 | A | 7 | 983 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 19200 | A | 7 | 1402 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.74 | 4 | 0
1994-02-01 | 1900-01-31 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.91 | A | 7 | 984 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 1200 | A | 7 | 305 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 25.26 | 4 | 0
1994-02-01 | 1900-01-31 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 984 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 1158 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.04 | 4 | 0
1994-02-01 | 1900-01-31 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -5 | 23 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.08 | 4 | 0
1994-02-01 | 1900-01-31 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.79 | A | 7 | 985 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.78 | 4 | 0
1994-02-01 | 1900-01-31 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -7.8 | 17.96 | A | 7 | -10 | 14 | A | 7 | 0.82 | A | 7 | 985 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.9 | 4 | 0
1994-02-01 | 1900-01-31 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.081 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.54 | 4 | 0
1994-02-02 | 1900-02-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 985 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.54 | 5 | 0
1994-02-02 | 1900-02-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 579 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.82 | 5 | 0
1994-02-02 | 1900-02-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 457 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.88 | 5 | 0
1994-02-02 | 1900-02-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -13.9 | 6.98 | A | 7 | 0.7 | A | 7 | 984 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.58 | 5 | 0
1994-02-02 | 1900-02-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -13.3 | 8.06 | A | 7 | 0.78 | A | 7 | 984 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.96 | 5 | 0
1994-02-02 | 1900-02-01 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.16 | 5 | 0
1994-02-02 | 1900-02-01 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.82 | A | 7 | 983 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.16 | 5 | 0
1994-02-02 | 1900-02-01 | 8:00 | 8 | 37 | 786 | 8 | 1 | 10 | 28 | 1 | 16 | 7 | 1 | 10 | 1000 | 1 | 10 | 800 | 1 | 16 | 900 | 1 | 10 | 110 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -12.8 | 8.96 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.86 | 5 | 0
1994-02-02 | 1900-02-01 | 9:00 | 9 | 255 | 1408 | 117 | 1 | 10 | 355 | 1 | 16 | 53 | 1 | 10 | 12400 | 1 | 10 | 25500 | 1 | 16 | 7700 | 1 | 10 | 950 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.32 | 5 | 0
1994-02-02 | 1900-02-01 | 10:00 | 10 | 471 | 1408 | 282 | 1 | 10 | 598 | 1 | 16 | 81 | 1 | 10 | 29200 | 1 | 10 | 54400 | 1 | 16 | 10900 | 1 | 10 | 1540 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -10 | 14 | A | 7 | 0.59 | A | 7 | 980 | A | 7 | 210 | A | 7 | 8.8 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.5 | 5 | 0
1994-02-02 | 1900-02-01 | 11:00 | 11 | 639 | 1408 | 427 | 1 | 10 | 714 | 1 | 16 | 103 | 1 | 10 | 44900 | 1 | 10 | 69500 | 1 | 16 | 13200 | 1 | 10 | 2120 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 230 | A | 7 | 8.8 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.76 | 5 | 0
1994-02-02 | 1900-02-01 | 12:00 | 12 | 746 | 1408 | 521 | 1 | 11 | 725 | 1 | 16 | 137 | 1 | 11 | 54500 | 1 | 11 | 71700 | 1 | 16 | 16400 | 1 | 11 | 2950 | 1 | 22 | 4 | B | 8 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 250 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.34 | 5 | 0
1994-02-02 | 1900-02-01 | 13:00 | 13 | 785 | 1408 | 367 | 1 | 10 | 326 | 1 | 16 | 185 | 1 | 10 | 40100 | 1 | 10 | 34400 | 1 | 16 | 20900 | 1 | 10 | 4230 | 1 | 21 | 8 | A | 7 | 6 | A | 7 | 2.8 | 37.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.49 | A | 7 | 981 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 32000 | A | 7 | 1402 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.02 | 5 | 0
1994-02-02 | 1900-02-01 | 14:00 | 14 | 753 | 1408 | 378 | 1 | 10 | 321 | 1 | 16 | 207 | 1 | 10 | 40900 | 1 | 10 | 33700 | 1 | 16 | 22800 | 1 | 10 | 4770 | 1 | 21 | 7 | A | 7 | 7 | A | 7 | 2.2 | 35.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 32000 | A | 7 | 1280 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.22 | 5 | 0
1994-02-02 | 1900-02-01 | 15:00 | 15 | 652 | 1408 | 370 | 1 | 10 | 180 | 1 | 16 | 286 | 1 | 10 | 39300 | 1 | 10 | 18000 | 1 | 16 | 30900 | 1 | 10 | 6970 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 3.9 | 39.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.45 | A | 7 | 981 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 1311 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.72 | 5 | 0
1994-02-02 | 1900-02-01 | 16:00 | 16 | 489 | 1408 | 293 | 1 | 10 | 594 | 1 | 16 | 86 | 1 | 10 | 30400 | 1 | 10 | 54500 | 1 | 16 | 11400 | 1 | 10 | 1640 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.02 | 5 | 0
1994-02-02 | 1900-02-01 | 17:00 | 17 | 277 | 1408 | 132 | 1 | 10 | 386 | 1 | 16 | 56 | 1 | 10 | 13500 | 1 | 10 | 29100 | 1 | 16 | 7700 | 1 | 10 | 990 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -7.8 | 17.96 | A | 7 | 0.44 | A | 7 | 981 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.96 | 5 | 0
1994-02-02 | 1900-02-01 | 18:00 | 18 | 51 | 927 | 17 | 1 | 10 | 15 | 1 | 16 | 16 | 1 | 10 | 1900 | 1 | 10 | 800 | 1 | 16 | 1800 | 1 | 10 | 390 | 1 | 21 | 5 | A | 7 | 5 | A | 7 | 0.6 | 33.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.49 | A | 7 | 982 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.36 | 5 | 0
1994-02-02 | 1900-02-01 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -7.8 | 17.96 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 2286 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.56 | 5 | 0
1994-02-02 | 1900-02-01 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.49 | A | 7 | 984 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 2286 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.58 | 5 | 0
1994-02-02 | 1900-02-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.49 | A | 7 | 984 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 1981 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.88 | 5 | 0
1994-02-02 | 1900-02-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.75 | A | 7 | 985 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 1981 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.24 | 5 | 0
1994-02-02 | 1900-02-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 3 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.83 | A | 7 | 986 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.76 | 5 | 0
1994-02-02 | 1900-02-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -9.4 | 15.08 | A | 7 | 0.72 | A | 7 | 987 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 2438 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.28 | 5 | 0
1994-02-03 | 1900-02-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -5.6 | 21.92 | A | 7 | -10.6 | 12.92 | A | 7 | 0.65 | A | 7 | 987 | A | 7 | 20 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 2438 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.82 | 6 | 0
1994-02-03 | 1900-02-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 10 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 2286 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.94 | 6 | 0
1994-02-03 | 1900-02-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.54 | 6 | 0
1994-02-03 | 1900-02-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -9.4 | 15.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.78 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.84 | 6 | 0
1994-02-03 | 1900-02-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.46 | 6 | 0
1994-02-03 | 1900-02-02 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.75 | A | 7 | 986 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.74 | 6 | 0
1994-02-03 | 1900-02-02 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.74 | A | 7 | 987 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.66 | 6 | 0
1994-02-03 | 1900-02-02 | 8:00 | 8 | 39 | 810 | 10 | 1 | 10 | 38 | 1 | 16 | 8 | 1 | 10 | 1100 | 1 | 10 | 1300 | 1 | 16 | 1100 | 1 | 10 | 130 | 1 | 21 | 3 | A | 7 | 3 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 987 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.54 | 6 | 0
1994-02-03 | 1900-02-02 | 9:00 | 9 | 259 | 1408 | 115 | 1 | 10 | 294 | 1 | 16 | 60 | 1 | 10 | 11900 | 1 | 10 | 21200 | 1 | 16 | 8000 | 1 | 10 | 1090 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | -6.1 | 21.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.67 | A | 7 | 987 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.02 | 6 | 0
1994-02-03 | 1900-02-02 | 10:00 | 10 | 476 | 1408 | 272 | 1 | 10 | 457 | 1 | 16 | 117 | 1 | 10 | 28400 | 1 | 10 | 41900 | 1 | 16 | 14200 | 1 | 10 | 2230 | 1 | 21 | 9 | A | 7 | 3 | A | 7 | -4.4 | 24.08 | A | 7 | -9.4 | 15.08 | A | 7 | 0.65 | A | 7 | 988 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.88 | 6 | 0
1994-02-03 | 1900-02-02 | 11:00 | 11 | 644 | 1408 | 406 | 1 | 10 | 538 | 1 | 16 | 160 | 1 | 10 | 42800 | 1 | 10 | 53100 | 1 | 16 | 18400 | 1 | 10 | 3270 | 1 | 21 | 9 | A | 7 | 2 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.98 | 6 | 0
1994-02-03 | 1900-02-02 | 12:00 | 12 | 751 | 1408 | 476 | 1 | 10 | 593 | 1 | 16 | 160 | 1 | 10 | 49300 | 1 | 10 | 58200 | 1 | 16 | 18100 | 1 | 10 | 3370 | 1 | 21 | 9 | A | 7 | 3 | A | 7 | 0 | 32 | A | 7 | -8.9 | 15.98 | A | 7 | 0.47 | A | 7 | 987 | A | 7 | 180 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.48 | 6 | 0
1994-02-03 | 1900-02-02 | 13:00 | 13 | 790 | 1408 | 561 | 1 | 10 | 728 | 1 | 16 | 152 | 1 | 10 | 58500 | 1 | 10 | 72300 | 1 | 16 | 17800 | 1 | 10 | 3370 | 1 | 21 | 9 | A | 7 | 2 | A | 7 | 2.8 | 37.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.37 | A | 7 | 985 | A | 7 | 200 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.08 | 6 | 0
1994-02-03 | 1900-02-02 | 14:00 | 14 | 758 | 1408 | 489 | 1 | 10 | 603 | 1 | 16 | 164 | 1 | 10 | 50500 | 1 | 10 | 59200 | 1 | 16 | 18500 | 1 | 10 | 3460 | 1 | 21 | 8 | A | 7 | 3 | A | 7 | 3.9 | 39.02 | A | 7 | -11.1 | 12.02 | A | 7 | 0.29 | A | 7 | 984 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.02 | 6 | 0
1994-02-03 | 1900-02-02 | 15:00 | 15 | 658 | 1408 | 443 | 1 | 10 | 677 | 1 | 16 | 126 | 1 | 10 | 45900 | 1 | 10 | 65600 | 1 | 16 | 15200 | 1 | 10 | 2540 | 1 | 21 | 9 | A | 7 | 2 | A | 7 | 4.4 | 39.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.34 | A | 7 | 983 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.58 | 6 | 0
1994-02-03 | 1900-02-02 | 16:00 | 16 | 495 | 1408 | 290 | 1 | 10 | 521 | 1 | 16 | 107 | 1 | 10 | 30800 | 1 | 10 | 48400 | 1 | 16 | 13700 | 1 | 10 | 2030 | 1 | 21 | 10 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | -7.8 | 17.96 | A | 7 | 0.36 | A | 7 | 982 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.46 | 6 | 0
1994-02-03 | 1900-02-02 | 17:00 | 17 | 282 | 1408 | 120 | 1 | 10 | 196 | 1 | 16 | 81 | 1 | 10 | 12600 | 1 | 10 | 14700 | 1 | 16 | 9700 | 1 | 10 | 1580 | 1 | 21 | 9 | A | 7 | 4 | A | 7 | 4.4 | 39.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.4 | A | 7 | 981 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.64 | 6 | 0
1994-02-03 | 1900-02-02 | 18:00 | 18 | 54 | 950 | 14 | 1 | 10 | 24 | 1 | 16 | 12 | 1 | 10 | 1500 | 1 | 10 | 1000 | 1 | 16 | 1500 | 1 | 10 | 250 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 2.2 | 35.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.48 | A | 7 | 981 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.04 | 6 | 0
1994-02-03 | 1900-02-02 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 1.1 | 33.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.5 | A | 7 | 981 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.34 | 6 | 0
1994-02-03 | 1900-02-02 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 0.6 | 33.08 | A | 7 | -7.2 | 19.04 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.54 | 6 | 0
1994-02-03 | 1900-02-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -1.1 | 30.02 | A | 7 | -7.2 | 19.04 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 2743 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.14 | 6 | 0
1994-02-03 | 1900-02-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.57 | A | 7 | 982 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 3048 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.96 | 6 | 0
1994-02-03 | 1900-02-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -1.1 | 30.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 2743 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.96 | 6 | 0
1994-02-03 | 1900-02-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.44 | A | 7 | 982 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 2438 | A | 7 | 0.8 | E | 8 | 0.082 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.62 | 6 | 0
1994-02-04 | 1900-02-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.44 | A | 7 | 982 | A | 7 | 50 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 2896 | A | 7 | 0.8 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.62 | 7 | 0
1994-02-04 | 1900-02-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -10 | 14 | A | 7 | 0.49 | A | 7 | 983 | A | 7 | 30 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 2743 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.9 | 7 | 0
1994-02-04 | 1900-02-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -2.2 | 28.04 | A | 7 | -7.2 | 19.04 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 40 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 2591 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.44 | 7 | 0
1994-02-04 | 1900-02-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 32000 | A | 7 | 2591 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.22 | 7 | 0
1994-02-04 | 1900-02-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -3.9 | 24.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.83 | A | 7 | 984 | A | 7 | 30 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.72 | 7 | 0
1994-02-04 | 1900-02-03 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.54 | 7 | 0
1994-02-04 | 1900-02-03 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.83 | A | 7 | 985 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.74 | 7 | 0
1994-02-04 | 1900-02-03 | 8:00 | 8 | 42 | 833 | 14 | 1 | 10 | 132 | 1 | 16 | 7 | 1 | 10 | 1500 | 1 | 10 | 6900 | 1 | 16 | 1200 | 1 | 10 | 170 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.75 | A | 7 | 986 | A | 7 | 30 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.28 | 7 | 0
1994-02-04 | 1900-02-03 | 9:00 | 9 | 264 | 1408 | 143 | 1 | 10 | 574 | 1 | 16 | 35 | 1 | 10 | 14700 | 1 | 10 | 44800 | 1 | 16 | 6300 | 1 | 10 | 690 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -11.1 | 12.02 | A | 7 | 0.59 | A | 7 | 987 | A | 7 | 30 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.72 | 7 | 0
1994-02-04 | 1900-02-03 | 10:00 | 10 | 481 | 1408 | 315 | 1 | 10 | 771 | 1 | 16 | 51 | 1 | 10 | 33200 | 1 | 10 | 71100 | 1 | 16 | 8800 | 1 | 10 | 1120 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.44 | A | 7 | 987 | A | 7 | 30 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.16 | 7 | 0
1994-02-04 | 1900-02-03 | 11:00 | 11 | 650 | 1408 | 453 | 1 | 10 | 837 | 1 | 16 | 66 | 1 | 10 | 47500 | 1 | 10 | 80800 | 1 | 16 | 10100 | 1 | 10 | 1440 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.36 | A | 7 | 988 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.96 | 7 | 0
1994-02-04 | 1900-02-03 | 12:00 | 12 | 757 | 1408 | 548 | 1 | 10 | 869 | 1 | 16 | 80 | 1 | 10 | 57200 | 1 | 10 | 85200 | 1 | 16 | 11300 | 1 | 10 | 1690 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.35 | A | 7 | 987 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.66 | 7 | 0
1994-02-04 | 1900-02-03 | 13:00 | 13 | 796 | 1408 | 582 | 1 | 10 | 892 | 1 | 16 | 77 | 1 | 10 | 60900 | 1 | 10 | 87800 | 1 | 16 | 11000 | 1 | 10 | 1750 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -13.3 | 8.06 | A | 7 | 0.29 | A | 7 | 985 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.56 | 7 | 0
1994-02-04 | 1900-02-03 | 14:00 | 14 | 764 | 1408 | 552 | 1 | 10 | 868 | 1 | 16 | 80 | 1 | 10 | 57700 | 1 | 10 | 85100 | 1 | 16 | 11300 | 1 | 10 | 1700 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -13.3 | 8.06 | A | 7 | 0.28 | A | 7 | 984 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.56 | 7 | 0
1994-02-04 | 1900-02-03 | 15:00 | 15 | 663 | 1408 | 467 | 1 | 10 | 763 | 1 | 16 | 107 | 1 | 10 | 49100 | 1 | 10 | 74700 | 1 | 16 | 13800 | 1 | 10 | 2230 | 1 | 21 | 8 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -12.8 | 8.96 | A | 7 | 0.28 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.36 | 7 | 0
1994-02-04 | 1900-02-03 | 16:00 | 16 | 501 | 1408 | 324 | 1 | 10 | 660 | 1 | 16 | 89 | 1 | 10 | 33600 | 1 | 10 | 60900 | 1 | 16 | 11900 | 1 | 10 | 1700 | 1 | 21 | 9 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.29 | A | 7 | 983 | A | 7 | 80 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.36 | 7 | 0
1994-02-04 | 1900-02-03 | 17:00 | 17 | 288 | 1408 | 143 | 1 | 10 | 53 | 1 | 16 | 132 | 1 | 10 | 15600 | 1 | 10 | 4500 | 1 | 16 | 14600 | 1 | 10 | 2750 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 1.1 | 33.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.32 | A | 7 | 983 | A | 7 | 20 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.44 | 7 | 0
1994-02-04 | 1900-02-03 | 18:00 | 18 | 57 | 974 | 14 | 1 | 10 | 35 | 1 | 16 | 12 | 1 | 10 | 1600 | 1 | 10 | 1200 | 1 | 16 | 1500 | 1 | 10 | 200 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 0 | 32 | A | 7 | -12.2 | 10.04 | A | 7 | 0.35 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.64 | 7 | 0
1994-02-04 | 1900-02-03 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -0.6 | 30.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.35 | A | 7 | 983 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.66 | 7 | 0
1994-02-04 | 1900-02-03 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 7 | A | 7 | -1.7 | 28.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.42 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.74 | 7 | 0
1994-02-04 | 1900-02-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | -2.2 | 28.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.44 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.84 | 7 | 0
1994-02-04 | 1900-02-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -2.2 | 28.04 | A | 7 | -10.6 | 12.92 | A | 7 | 0.48 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.82 | 7 | 0
1994-02-04 | 1900-02-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -2.8 | 26.96 | A | 7 | -10 | 14 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.2 | 7 | 0
1994-02-04 | 1900-02-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -3.3 | 26.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.12 | 7 | 0
1994-02-05 | 1900-02-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -3.3 | 26.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.46 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.24 | 1 | 0
1994-02-05 | 1900-02-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | -5.6 | 21.92 | A | 7 | -10.6 | 12.92 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.82 | 1 | 0
1994-02-05 | 1900-02-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.75 | A | 7 | 980 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.48 | 1 | 0
1994-02-05 | 1900-02-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -5 | 23 | A | 7 | -10 | 14 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.9 | 1 | 0
1994-02-05 | 1900-02-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -6.7 | 19.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.78 | 1 | 0
1994-02-05 | 1900-02-04 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.75 | A | 7 | 980 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.48 | 1 | 0
1994-02-05 | 1900-02-04 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.88 | 1 | 0
1994-02-05 | 1900-02-04 | 8:00 | 8 | 44 | 856 | 13 | 1 | 10 | 71 | 1 | 16 | 9 | 1 | 10 | 1500 | 1 | 10 | 2600 | 1 | 16 | 1300 | 1 | 10 | 150 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.75 | A | 7 | 982 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.28 | 1 | 0
1994-02-05 | 1900-02-04 | 9:00 | 9 | 269 | 1407 | 140 | 1 | 10 | 521 | 1 | 16 | 41 | 1 | 10 | 14600 | 1 | 10 | 39600 | 1 | 16 | 7000 | 1 | 10 | 760 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -7.8 | 17.96 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.26 | 1 | 0
1994-02-05 | 1900-02-04 | 10:00 | 10 | 487 | 1407 | 311 | 1 | 10 | 727 | 1 | 16 | 59 | 1 | 10 | 32400 | 1 | 10 | 67200 | 1 | 16 | 9100 | 1 | 10 | 1210 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -10 | 14 | A | 7 | 0.41 | A | 7 | 983 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.4 | 1 | 0
1994-02-05 | 1900-02-04 | 11:00 | 11 | 655 | 1407 | 456 | 1 | 10 | 821 | 1 | 16 | 74 | 1 | 10 | 48300 | 1 | 10 | 80100 | 1 | 16 | 10900 | 1 | 10 | 1610 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.3 | A | 7 | 983 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.34 | 1 | 0
1994-02-05 | 1900-02-04 | 12:00 | 12 | 763 | 1407 | 552 | 1 | 10 | 865 | 1 | 16 | 83 | 1 | 10 | 58800 | 1 | 10 | 86000 | 1 | 16 | 12100 | 1 | 10 | 1910 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -11.7 | 10.94 | A | 7 | 0.28 | A | 7 | 982 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.04 | 1 | 0
1994-02-05 | 1900-02-04 | 13:00 | 13 | 802 | 1407 | 587 | 1 | 10 | 879 | 1 | 16 | 86 | 1 | 10 | 61300 | 1 | 10 | 86500 | 1 | 16 | 11800 | 1 | 10 | 1810 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -11.1 | 12.02 | A | 7 | 0.27 | A | 7 | 981 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.82 | 1 | 0
1994-02-05 | 1900-02-04 | 14:00 | 14 | 770 | 1407 | 558 | 1 | 10 | 868 | 1 | 16 | 83 | 1 | 10 | 58300 | 1 | 10 | 85200 | 1 | 16 | 11500 | 1 | 10 | 1730 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.26 | A | 7 | 980 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.52 | 1 | 0
1994-02-05 | 1900-02-04 | 15:00 | 15 | 669 | 1407 | 469 | 1 | 10 | 828 | 1 | 16 | 75 | 1 | 10 | 49700 | 1 | 10 | 81000 | 1 | 16 | 11000 | 1 | 10 | 1640 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.24 | A | 7 | 980 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.72 | 1 | 0
1994-02-05 | 1900-02-04 | 16:00 | 16 | 507 | 1407 | 328 | 1 | 10 | 741 | 1 | 16 | 61 | 1 | 10 | 34300 | 1 | 10 | 69100 | 1 | 16 | 9300 | 1 | 10 | 1250 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.21 | A | 7 | 979 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.84 | 1 | 0
1994-02-05 | 1900-02-04 | 17:00 | 17 | 294 | 1407 | 158 | 1 | 10 | 553 | 1 | 16 | 43 | 1 | 10 | 16100 | 1 | 10 | 44300 | 1 | 16 | 6800 | 1 | 10 | 810 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.22 | A | 7 | 979 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.94 | 1 | 0
1994-02-05 | 1900-02-04 | 18:00 | 18 | 61 | 997 | 20 | 1 | 10 | 138 | 1 | 16 | 12 | 1 | 10 | 2200 | 1 | 10 | 6600 | 1 | 16 | 1800 | 1 | 10 | 230 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.26 | A | 7 | 979 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.26 | 1 | 0
1994-02-05 | 1900-02-04 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -10.6 | 12.92 | A | 7 | 0.42 | A | 7 | 979 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.52 | 1 | 0
1994-02-05 | 1900-02-04 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.39 | A | 7 | 978 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.32 | 1 | 0
1994-02-05 | 1900-02-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -10 | 14 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.9 | 1 | 0
1994-02-05 | 1900-02-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.88 | 1 | 0
1994-02-05 | 1900-02-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.98 | 1 | 0
1994-02-05 | 1900-02-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -10 | 14 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.083 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.9 | 1 | 0
1994-02-06 | 1900-02-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -10 | 14 | A | 7 | 0.41 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.4 | 2 | 0
1994-02-06 | 1900-02-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.39 | A | 7 | 977 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.32 | 2 | 0
1994-02-06 | 1900-02-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -10 | 14 | A | 7 | 0.49 | A | 7 | 977 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.9 | 2 | 0
1994-02-06 | 1900-02-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -7.8 | 17.96 | A | 7 | 0.52 | A | 7 | 977 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.56 | 2 | 0
1994-02-06 | 1900-02-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -7.8 | 17.96 | A | 7 | 0.52 | A | 7 | 977 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.56 | 2 | 0
1994-02-06 | 1900-02-05 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.96 | 2 | 0
1994-02-06 | 1900-02-05 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -7.2 | 19.04 | A | 7 | 0.63 | A | 7 | 977 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.34 | 2 | 0
1994-02-06 | 1900-02-05 | 8:00 | 8 | 47 | 879 | 12 | 1 | 10 | 54 | 1 | 16 | 9 | 1 | 10 | 1400 | 1 | 10 | 2000 | 1 | 16 | 1300 | 1 | 10 | 150 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -7.2 | 19.04 | A | 7 | 0.65 | A | 7 | 978 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.44 | 2 | 0
1994-02-06 | 1900-02-05 | 9:00 | 9 | 274 | 1407 | 133 | 1 | 10 | 421 | 1 | 16 | 51 | 1 | 10 | 13600 | 1 | 10 | 31800 | 1 | 16 | 7400 | 1 | 10 | 920 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.52 | 2 | 0
1994-02-06 | 1900-02-05 | 10:00 | 10 | 492 | 1407 | 302 | 1 | 10 | 644 | 1 | 16 | 76 | 1 | 10 | 31600 | 1 | 10 | 59500 | 1 | 16 | 10700 | 1 | 10 | 1480 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.49 | A | 7 | 979 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.82 | 2 | 0
1994-02-06 | 1900-02-05 | 11:00 | 11 | 661 | 1407 | 448 | 1 | 10 | 749 | 1 | 16 | 96 | 1 | 10 | 47500 | 1 | 10 | 73600 | 1 | 16 | 12800 | 1 | 10 | 2030 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -4.4 | 24.08 | A | 7 | 0.48 | A | 7 | 980 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.58 | 2 | 0
1994-02-06 | 1900-02-05 | 12:00 | 12 | 769 | 1407 | 544 | 1 | 10 | 799 | 1 | 16 | 107 | 1 | 10 | 56400 | 1 | 10 | 78600 | 1 | 16 | 13300 | 1 | 10 | 2250 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.4 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.88 | 2 | 0
1994-02-06 | 1900-02-05 | 13:00 | 13 | 808 | 1407 | 580 | 1 | 10 | 815 | 1 | 16 | 111 | 1 | 10 | 60300 | 1 | 10 | 80600 | 1 | 16 | 13800 | 1 | 10 | 2410 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.36 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.48 | 2 | 0
1994-02-06 | 1900-02-05 | 14:00 | 14 | 776 | 1407 | 551 | 1 | 10 | 802 | 1 | 16 | 108 | 1 | 10 | 57200 | 1 | 10 | 79000 | 1 | 16 | 13400 | 1 | 10 | 2280 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -5 | 23 | A | 7 | 0.3 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.1 | 2 | 0
1994-02-06 | 1900-02-05 | 15:00 | 15 | 675 | 1407 | 461 | 1 | 10 | 757 | 1 | 16 | 97 | 1 | 10 | 48900 | 1 | 10 | 74700 | 1 | 16 | 12900 | 1 | 10 | 2070 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.27 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.22 | 2 | 0
1994-02-06 | 1900-02-05 | 16:00 | 16 | 512 | 1407 | 319 | 1 | 10 | 659 | 1 | 16 | 79 | 1 | 10 | 33500 | 1 | 10 | 61500 | 1 | 16 | 11000 | 1 | 10 | 1550 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.26 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.34 | 2 | 0
1994-02-06 | 1900-02-05 | 17:00 | 17 | 299 | 1407 | 151 | 1 | 10 | 455 | 1 | 16 | 54 | 1 | 10 | 15500 | 1 | 10 | 35700 | 1 | 16 | 7900 | 1 | 10 | 980 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.29 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.42 | 2 | 0
1994-02-06 | 1900-02-05 | 18:00 | 18 | 65 | 1020 | 19 | 1 | 10 | 80 | 1 | 16 | 14 | 1 | 10 | 2100 | 1 | 10 | 3300 | 1 | 16 | 1900 | 1 | 10 | 240 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -5 | 23 | A | 7 | 0.41 | A | 7 | 980 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.1 | 2 | 0
1994-02-06 | 1900-02-05 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 3.3 | 37.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.18 | 2 | 0
1994-02-06 | 1900-02-05 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 0.6 | 33.08 | A | 7 | -5 | 23 | A | 7 | 0.63 | A | 7 | 983 | A | 7 | 10 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.9 | 2 | 0
1994-02-06 | 1900-02-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.68 | A | 7 | 983 | A | 7 | 30 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.32 | 2 | 0
1994-02-06 | 1900-02-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -3.3 | 26.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.68 | A | 7 | 985 | A | 7 | 40 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.66 | 2 | 0
1994-02-06 | 1900-02-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -10 | 14 | A | 7 | 0.65 | A | 7 | 986 | A | 7 | 40 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.9 | 2 | 0
1994-02-06 | 1900-02-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.53 | A | 7 | 987 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.76 | 2 | 0
1994-02-07 | 1900-02-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.14 | 3 | 0
1994-02-07 | 1900-02-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -13.3 | 8.06 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 20 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.26 | 3 | 0
1994-02-07 | 1900-02-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.75 | A | 7 | 987 | A | 7 | 40 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.74 | 3 | 0
1994-02-07 | 1900-02-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | -9.4 | 15.08 | A | 7 | -13.9 | 6.98 | A | 7 | 0.67 | A | 7 | 987 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.38 | 3 | 0
1994-02-07 | 1900-02-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | -10 | 14 | A | 7 | -15 | 5 | A | 7 | 0.64 | A | 7 | 988 | A | 7 | 50 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 6096 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 3.4 | 3 | 0
1994-02-07 | 1900-02-06 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.57 | A | 7 | 987 | A | 7 | 40 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 5486 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.34 | 3 | 0
1994-02-07 | 1900-02-06 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -16.7 | 1.94 | A | 7 | 0.6 | A | 7 | 988 | A | 7 | 50 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 4267 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.44 | 3 | 0
1994-02-07 | 1900-02-06 | 8:00 | 8 | 50 | 902 | 8 | 1 | 10 | 0 | 1 | 16 | 8 | 1 | 10 | 1000 | 1 | 10 | 0 | 1 | 16 | 1000 | 1 | 10 | 310 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -17.8 | -0.04 | A | 7 | 0.52 | A | 7 | 987 | A | 7 | 50 | A | 7 | 9.3 | A | 7 | 32000 | A | 7 | 4572 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -1.74 | 3 | 0
1994-02-07 | 1900-02-06 | 9:00 | 9 | 279 | 1406 | 65 | 1 | 10 | 0 | 1 | 16 | 65 | 1 | 10 | 7300 | 1 | 10 | 0 | 1 | 16 | 7300 | 1 | 10 | 2280 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -18.3 | -0.94 | A | 7 | 0.54 | A | 7 | 988 | A | 7 | 40 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 4572 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -2.44 | 3 | 0
1994-02-07 | 1900-02-06 | 10:00 | 10 | 497 | 1406 | 257 | 1 | 10 | 369 | 1 | 16 | 126 | 1 | 10 | 26800 | 1 | 10 | 34300 | 1 | 16 | 14600 | 1 | 10 | 2430 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | -10.6 | 12.92 | A | 7 | -17.8 | -0.04 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 50 | A | 7 | 8.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -1.74 | 3 | 0
1994-02-07 | 1900-02-06 | 11:00 | 11 | 666 | 1406 | 322 | 1 | 10 | 326 | 1 | 16 | 168 | 1 | 10 | 34900 | 1 | 10 | 33500 | 1 | 16 | 18900 | 1 | 10 | 3620 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | -9.4 | 15.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.44 | A | 7 | 987 | A | 7 | 50 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -2.84 | 3 | 0
1994-02-07 | 1900-02-06 | 12:00 | 12 | 774 | 1406 | 444 | 1 | 10 | 344 | 1 | 16 | 254 | 1 | 10 | 47300 | 1 | 10 | 36100 | 1 | 16 | 27300 | 1 | 10 | 6150 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -8.3 | 17.06 | A | 7 | -17.2 | 1.04 | A | 7 | 0.45 | A | 7 | 985 | A | 7 | 50 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.96 | 3 | 0
1994-02-07 | 1900-02-06 | 13:00 | 13 | 814 | 1406 | 511 | 1 | 10 | 560 | 1 | 16 | 187 | 1 | 10 | 54700 | 1 | 10 | 57200 | 1 | 16 | 21400 | 1 | 10 | 4280 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | -6.7 | 19.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.41 | A | 7 | 983 | A | 7 | 50 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.26 | 3 | 0
1994-02-07 | 1900-02-06 | 14:00 | 14 | 782 | 1406 | 471 | 1 | 10 | 611 | 1 | 16 | 131 | 1 | 10 | 49600 | 1 | 10 | 61000 | 1 | 16 | 15600 | 1 | 10 | 2950 | 1 | 21 | 10 | A | 7 | 4 | A | 7 | -6.7 | 19.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.41 | A | 7 | 983 | A | 7 | 60 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.26 | 3 | 0
1994-02-07 | 1900-02-06 | 15:00 | 15 | 681 | 1406 | 149 | 1 | 10 | 0 | 1 | 16 | 149 | 1 | 10 | 17300 | 1 | 10 | 0 | 1 | 16 | 17300 | 1 | 10 | 6330 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.41 | A | 7 | 983 | A | 7 | 60 | A | 7 | 6.7 | A | 7 | 24000 | A | 7 | 945 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.26 | 3 | 0
1994-02-07 | 1900-02-06 | 16:00 | 16 | 518 | 1406 | 109 | 1 | 10 | 0 | 1 | 16 | 109 | 1 | 10 | 12500 | 1 | 10 | 0 | 1 | 16 | 12500 | 1 | 10 | 4380 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.41 | A | 7 | 983 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 24000 | A | 7 | 914 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.26 | 3 | 0
1994-02-07 | 1900-02-06 | 17:00 | 17 | 305 | 1406 | 57 | 1 | 10 | 0 | 1 | 16 | 57 | 1 | 10 | 6500 | 1 | 10 | 0 | 1 | 16 | 6500 | 1 | 10 | 2140 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -16.7 | 1.94 | A | 7 | 0.42 | A | 7 | 982 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 24000 | A | 7 | 853 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.26 | 3 | 0
1994-02-07 | 1900-02-06 | 18:00 | 18 | 68 | 1043 | 9 | 1 | 10 | 0 | 1 | 16 | 9 | 1 | 10 | 1100 | 1 | 10 | 0 | 1 | 16 | 1100 | 1 | 10 | 350 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.45 | A | 7 | 982 | A | 7 | 30 | A | 7 | 6.2 | A | 7 | 24000 | A | 7 | 853 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.16 | 3 | 0
1994-02-07 | 1900-02-06 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.55 | A | 7 | 983 | A | 7 | 40 | A | 7 | 7.2 | A | 7 | 24000 | A | 7 | 762 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 2.02 | 3 | 0
1994-02-07 | 1900-02-06 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.55 | A | 7 | 982 | A | 7 | 50 | A | 7 | 7.2 | A | 7 | 24000 | A | 7 | 640 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 2.02 | 3 | 0
1994-02-07 | 1900-02-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.51 | A | 7 | 982 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 24000 | A | 7 | 701 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.04 | 3 | 0
1994-02-07 | 1900-02-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10 | 14 | A | 7 | -16.7 | 1.94 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 762 | A | 7 | 1.1 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.24 | 3 | 0
1994-02-07 | 1900-02-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 24000 | A | 7 | 762 | A | 7 | 1.2 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.34 | 3 | 0
1994-02-07 | 1900-02-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 762 | A | 7 | 1.2 | E | 8 | 0.084 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.34 | 3 | 0
1994-02-08 | 1900-02-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -16.1 | 3.02 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 30 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 671 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.52 | 4 | 0
1994-02-08 | 1900-02-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 24000 | A | 7 | 671 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.34 | 4 | 0
1994-02-08 | 1900-02-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -16.1 | 3.02 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 823 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.52 | 4 | 0
1994-02-08 | 1900-02-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -15.6 | 3.92 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 24000 | A | 7 | 914 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 2.42 | 4 | 0
1994-02-08 | 1900-02-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -14.4 | 6.08 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 12800 | A | 7 | 518 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.88 | 4 | 0
1994-02-08 | 1900-02-07 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -13.9 | 6.98 | A | 7 | 0.86 | A | 7 | 978 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 335 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.28 | 4 | 0
1994-02-08 | 1900-02-07 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -13.9 | 6.98 | A | 7 | 0.86 | A | 7 | 977 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 274 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.28 | 4 | 0
1994-02-08 | 1900-02-07 | 8:00 | 8 | 53 | 925 | 7 | 1 | 10 | 0 | 1 | 16 | 7 | 1 | 10 | 900 | 1 | 10 | 0 | 1 | 16 | 900 | 1 | 10 | 270 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -14.4 | 6.08 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 30 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 274 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.28 | 4 | 0
1994-02-08 | 1900-02-07 | 9:00 | 9 | 284 | 1406 | 35 | 1 | 10 | 0 | 1 | 16 | 35 | 1 | 10 | 4100 | 1 | 10 | 0 | 1 | 16 | 4100 | 1 | 10 | 1410 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -13.9 | 6.98 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 4000 | A | 7 | 366 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.08 | 4 | 0
1994-02-08 | 1900-02-07 | 10:00 | 10 | 503 | 1406 | 89 | 1 | 10 | 0 | 1 | 16 | 89 | 1 | 10 | 10400 | 1 | 10 | 0 | 1 | 16 | 10400 | 1 | 10 | 3690 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 4000 | A | 7 | 518 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.16 | 4 | 0
1994-02-08 | 1900-02-07 | 11:00 | 11 | 672 | 1406 | 132 | 1 | 10 | 0 | 1 | 16 | 132 | 1 | 10 | 15400 | 1 | 10 | 0 | 1 | 16 | 15400 | 1 | 10 | 5720 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 2400 | A | 7 | 518 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.16 | 4 | 0
1994-02-08 | 1900-02-07 | 12:00 | 12 | 780 | 1406 | 160 | 1 | 10 | 0 | 1 | 16 | 160 | 1 | 10 | 18800 | 1 | 10 | 0 | 1 | 16 | 18800 | 1 | 10 | 7140 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -13.3 | 8.06 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 2400 | A | 7 | 518 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.96 | 4 | 0
1994-02-08 | 1900-02-07 | 13:00 | 13 | 820 | 1406 | 170 | 1 | 10 | 0 | 1 | 16 | 170 | 1 | 10 | 20000 | 1 | 10 | 0 | 1 | 16 | 20000 | 1 | 10 | 7670 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -13.3 | 8.06 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 4000 | A | 7 | 518 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.96 | 4 | 0
1994-02-08 | 1900-02-07 | 14:00 | 14 | 788 | 1406 | 162 | 1 | 10 | 0 | 1 | 16 | 162 | 1 | 10 | 19000 | 1 | 10 | 0 | 1 | 16 | 19000 | 1 | 10 | 7250 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -10 | 14 | A | 7 | -13.3 | 8.06 | A | 7 | 0.74 | A | 7 | 976 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 945 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.76 | 4 | 0
1994-02-08 | 1900-02-07 | 15:00 | 15 | 687 | 1406 | 136 | 1 | 10 | 0 | 1 | 16 | 136 | 1 | 10 | 15900 | 1 | 10 | 0 | 1 | 16 | 15900 | 1 | 10 | 5920 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.7 | A | 7 | 975 | A | 7 | 330 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 853 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.56 | 4 | 0
1994-02-08 | 1900-02-07 | 16:00 | 16 | 524 | 1406 | 95 | 1 | 10 | 0 | 1 | 16 | 95 | 1 | 10 | 11100 | 1 | 10 | 0 | 1 | 16 | 11100 | 1 | 10 | 3950 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 884 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.78 | 4 | 0
1994-02-08 | 1900-02-07 | 17:00 | 17 | 310 | 1406 | 46 | 1 | 10 | 0 | 1 | 16 | 46 | 1 | 10 | 5400 | 1 | 10 | 0 | 1 | 16 | 5400 | 1 | 10 | 1820 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -15 | 5 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 518 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 3.7 | 4 | 0
1994-02-08 | 1900-02-07 | 18:00 | 18 | 72 | 1089 | 12 | 1 | 10 | 0 | 1 | 16 | 12 | 1 | 10 | 1400 | 1 | 10 | 0 | 1 | 16 | 1400 | 1 | 10 | 450 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -16.1 | 3.02 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 1372 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.72 | 4 | 0
1994-02-08 | 1900-02-07 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 579 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.54 | 4 | 0
1994-02-08 | 1900-02-07 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -16.7 | 1.94 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 330 | A | 7 | 8.8 | A | 7 | 11200 | A | 7 | 3048 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.64 | 4 | 0
1994-02-08 | 1900-02-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -17.2 | 1.04 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 610 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.16 | 4 | 0
1994-02-08 | 1900-02-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -13.3 | 8.06 | A | 7 | -17.2 | 1.04 | A | 7 | 0.7 | A | 7 | 982 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 11200 | A | 7 | 3962 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.06 | 4 | 0
1994-02-08 | 1900-02-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.81 | A | 7 | 983 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 3962 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.24 | 4 | 0
1994-02-08 | 1900-02-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -15 | 5 | A | 7 | -19.4 | -2.92 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 11200 | A | 7 | 3962 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -4.02 | 4 | 0
1994-02-09 | 1900-02-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -15.6 | 3.92 | A | 7 | -20 | -4 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 310 | A | 7 | 9.8 | A | 7 | 19200 | A | 7 | 549 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -5 | 5 | 0
1994-02-09 | 1900-02-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -16.1 | 3.02 | A | 7 | -21.1 | -5.98 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 320 | A | 7 | 10.8 | A | 7 | 19200 | A | 7 | 1280 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -6.98 | 5 | 0
1994-02-09 | 1900-02-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -16.1 | 3.02 | A | 7 | -21.1 | -5.98 | A | 7 | 0.62 | A | 7 | 985 | A | 7 | 330 | A | 7 | 9.3 | A | 7 | 24000 | A | 7 | 1341 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -6.98 | 5 | 0
1994-02-09 | 1900-02-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -16.1 | 3.02 | A | 7 | -21.1 | -5.98 | A | 7 | 0.62 | A | 7 | 986 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 24000 | A | 7 | 1829 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -6.98 | 5 | 0
1994-02-09 | 1900-02-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -16.1 | 3.02 | A | 7 | -21.1 | -5.98 | A | 7 | 0.62 | A | 7 | 987 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 19200 | A | 7 | 1981 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -6.98 | 5 | 0
1994-02-09 | 1900-02-08 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -16.7 | 1.94 | A | 7 | -21.1 | -5.98 | A | 7 | 0.66 | A | 7 | 988 | A | 7 | 330 | A | 7 | 8.2 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -6.88 | 5 | 0
1994-02-09 | 1900-02-08 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -17.2 | 1.04 | A | 7 | -22.2 | -7.96 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -8.86 | 5 | 0
1994-02-09 | 1900-02-08 | 8:00 | 8 | 56 | 949 | 18 | 1 | 10 | 112 | 1 | 16 | 11 | 1 | 10 | 1900 | 1 | 10 | 5300 | 1 | 16 | 1600 | 1 | 10 | 210 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -22.8 | -9.04 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -9.94 | 5 | 0
1994-02-09 | 1900-02-08 | 9:00 | 9 | 289 | 1405 | 152 | 1 | 10 | 523 | 1 | 16 | 45 | 1 | 10 | 15900 | 1 | 10 | 40900 | 1 | 16 | 7400 | 1 | 10 | 840 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -17.2 | 1.04 | A | 7 | -22.2 | -7.96 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -8.86 | 5 | 0
1994-02-09 | 1900-02-08 | 10:00 | 10 | 508 | 1405 | 326 | 1 | 10 | 722 | 1 | 16 | 65 | 1 | 10 | 33900 | 1 | 10 | 67200 | 1 | 16 | 9500 | 1 | 10 | 1300 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -21.7 | -7.06 | A | 7 | 0.62 | A | 7 | 990 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -8.06 | 5 | 0
1994-02-09 | 1900-02-08 | 11:00 | 11 | 678 | 1405 | 473 | 1 | 10 | 814 | 1 | 16 | 80 | 1 | 10 | 49800 | 1 | 10 | 79600 | 1 | 16 | 11300 | 1 | 10 | 1730 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -20.6 | -5.08 | A | 7 | 0.59 | A | 7 | 990 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -6.28 | 5 | 0
1994-02-09 | 1900-02-08 | 12:00 | 12 | 786 | 1405 | 570 | 1 | 10 | 857 | 1 | 16 | 90 | 1 | 10 | 60400 | 1 | 10 | 85200 | 1 | 16 | 12600 | 1 | 10 | 2070 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -20 | -4 | A | 7 | 0.53 | A | 7 | 991 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -5.4 | 5 | 0
1994-02-09 | 1900-02-08 | 13:00 | 13 | 826 | 1405 | 605 | 1 | 10 | 871 | 1 | 16 | 93 | 1 | 10 | 64400 | 1 | 10 | 87000 | 1 | 16 | 13000 | 1 | 10 | 2210 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -19.4 | -2.92 | A | 7 | 0.51 | A | 7 | 990 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -4.42 | 5 | 0
1994-02-09 | 1900-02-08 | 14:00 | 14 | 794 | 1405 | 577 | 1 | 10 | 860 | 1 | 16 | 90 | 1 | 10 | 61200 | 1 | 10 | 85700 | 1 | 16 | 12600 | 1 | 10 | 2090 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -18.9 | -2.02 | A | 7 | 0.47 | A | 7 | 990 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -3.72 | 5 | 0
1994-02-09 | 1900-02-08 | 15:00 | 15 | 693 | 1405 | 487 | 1 | 10 | 821 | 1 | 16 | 82 | 1 | 10 | 51300 | 1 | 10 | 80500 | 1 | 16 | 11500 | 1 | 10 | 1780 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -18.9 | -2.02 | A | 7 | 0.44 | A | 7 | 989 | A | 7 | 50 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -3.82 | 5 | 0
1994-02-09 | 1900-02-08 | 16:00 | 16 | 530 | 1405 | 345 | 1 | 10 | 737 | 1 | 16 | 67 | 1 | 10 | 35900 | 1 | 10 | 69200 | 1 | 16 | 9700 | 1 | 10 | 1350 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -18.3 | -0.94 | A | 7 | 0.42 | A | 7 | 989 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -2.84 | 5 | 0
1994-02-09 | 1900-02-08 | 17:00 | 17 | 316 | 1405 | 172 | 1 | 10 | 555 | 1 | 16 | 47 | 1 | 10 | 17900 | 1 | 10 | 44900 | 1 | 16 | 7800 | 1 | 10 | 880 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.44 | A | 7 | 990 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -2.84 | 5 | 0
1994-02-09 | 1900-02-08 | 18:00 | 18 | 76 | 1112 | 26 | 1 | 10 | 153 | 1 | 16 | 15 | 1 | 10 | 2700 | 1 | 10 | 7600 | 1 | 16 | 2200 | 1 | 10 | 280 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -18.3 | -0.94 | A | 7 | 0.49 | A | 7 | 989 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -2.64 | 5 | 0
1994-02-09 | 1900-02-08 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -17.8 | -0.04 | A | 7 | 0.57 | A | 7 | 990 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -1.54 | 5 | 0
1994-02-09 | 1900-02-08 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -17.8 | -0.04 | A | 7 | 0.6 | A | 7 | 990 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -1.44 | 5 | 0
1994-02-09 | 1900-02-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -17.8 | -0.04 | A | 7 | 0.63 | A | 7 | 989 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -1.34 | 5 | 0
1994-02-09 | 1900-02-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -17.8 | -0.04 | A | 7 | 0.66 | A | 7 | 989 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -1.24 | 5 | 0
1994-02-09 | 1900-02-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -17.8 | -0.04 | A | 7 | 0.7 | A | 7 | 989 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -1.14 | 5 | 0
1994-02-09 | 1900-02-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -20.6 | -5.08 | A | 7 | 0.53 | A | 7 | 989 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -6.38 | 5 | 0
1994-02-10 | 1900-02-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -17.8 | -0.04 | A | 7 | 0.73 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -1.04 | 6 | 0
1994-02-10 | 1900-02-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -17.8 | -0.04 | A | 7 | 0.73 | A | 7 | 989 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -1.04 | 6 | 0
1994-02-10 | 1900-02-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -17.2 | 1.04 | A | 7 | 0.74 | A | 7 | 989 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.04 | 6 | 0
1994-02-10 | 1900-02-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.24 | 6 | 0
1994-02-10 | 1900-02-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -16.7 | 1.94 | A | 7 | 0.77 | A | 7 | 989 | A | 7 | 100 | A | 7 | 1.5 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.04 | 6 | 0
1994-02-10 | 1900-02-09 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.81 | A | 7 | 989 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.24 | 6 | 0
1994-02-10 | 1900-02-09 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.81 | A | 7 | 989 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.24 | 6 | 0
1994-02-10 | 1900-02-09 | 8:00 | 8 | 59 | 972 | 20 | 1 | 10 | 144 | 1 | 16 | 11 | 1 | 10 | 2100 | 1 | 10 | 6900 | 1 | 16 | 1700 | 1 | 10 | 210 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -15.6 | 3.92 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 3.12 | 6 | 0
1994-02-10 | 1900-02-09 | 9:00 | 9 | 295 | 1405 | 161 | 1 | 10 | 568 | 1 | 16 | 41 | 1 | 10 | 16400 | 1 | 10 | 45800 | 1 | 16 | 6800 | 1 | 10 | 790 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -13.3 | 8.06 | A | 7 | 0.78 | A | 7 | 988 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.96 | 6 | 0
1994-02-10 | 1900-02-09 | 10:00 | 10 | 514 | 1405 | 336 | 1 | 10 | 756 | 1 | 16 | 59 | 1 | 10 | 35300 | 1 | 10 | 70900 | 1 | 16 | 9300 | 1 | 10 | 1240 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 988 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.34 | 6 | 0
1994-02-10 | 1900-02-09 | 11:00 | 11 | 684 | 1405 | 484 | 1 | 10 | 842 | 1 | 16 | 74 | 1 | 10 | 51500 | 1 | 10 | 82700 | 1 | 16 | 11100 | 1 | 10 | 1650 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.56 | A | 7 | 988 | A | 7 | 130 | A | 7 | 1.5 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.74 | 6 | 0
1994-02-10 | 1900-02-09 | 12:00 | 12 | 792 | 1405 | 580 | 1 | 10 | 883 | 1 | 16 | 82 | 1 | 10 | 60600 | 1 | 10 | 86900 | 1 | 16 | 11400 | 1 | 10 | 1770 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.44 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.16 | 6 | 0
1994-02-10 | 1900-02-09 | 13:00 | 13 | 832 | 1405 | 616 | 1 | 10 | 895 | 1 | 16 | 85 | 1 | 10 | 64200 | 1 | 10 | 88400 | 1 | 16 | 11700 | 1 | 10 | 1880 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -12.8 | 8.96 | A | 7 | 0.4 | A | 7 | 986 | A | 7 | 90 | A | 7 | 1.5 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.96 | 6 | 0
1994-02-10 | 1900-02-09 | 14:00 | 14 | 800 | 1405 | 587 | 1 | 10 | 885 | 1 | 16 | 83 | 1 | 10 | 61400 | 1 | 10 | 87100 | 1 | 16 | 11500 | 1 | 10 | 1790 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.35 | A | 7 | 985 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.66 | 6 | 0
1994-02-10 | 1900-02-09 | 15:00 | 15 | 699 | 1405 | 497 | 1 | 10 | 848 | 1 | 16 | 75 | 1 | 10 | 53000 | 1 | 10 | 83600 | 1 | 16 | 11200 | 1 | 10 | 1690 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.31 | A | 7 | 984 | A | 7 | 170 | A | 7 | 2.1 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.46 | 6 | 0
1994-02-10 | 1900-02-09 | 16:00 | 16 | 536 | 1405 | 354 | 1 | 10 | 768 | 1 | 16 | 61 | 1 | 10 | 37300 | 1 | 10 | 72600 | 1 | 16 | 9500 | 1 | 10 | 1290 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.31 | A | 7 | 985 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.46 | 6 | 0
1994-02-10 | 1900-02-09 | 17:00 | 17 | 321 | 1405 | 180 | 1 | 10 | 597 | 1 | 16 | 43 | 1 | 10 | 18500 | 1 | 10 | 49500 | 1 | 16 | 7100 | 1 | 10 | 840 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.31 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.46 | 6 | 0
1994-02-10 | 1900-02-09 | 18:00 | 18 | 80 | 1135 | 29 | 1 | 10 | 192 | 1 | 16 | 15 | 1 | 10 | 3100 | 1 | 10 | 9700 | 1 | 16 | 2300 | 1 | 10 | 280 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.37 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.74 | 6 | 0
1994-02-10 | 1900-02-09 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.44 | A | 7 | 985 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.84 | 6 | 0
1994-02-10 | 1900-02-09 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.53 | A | 7 | 985 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.32 | 6 | 0
1994-02-10 | 1900-02-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.52 | 6 | 0
1994-02-10 | 1900-02-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.53 | A | 7 | 985 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.32 | 6 | 0
1994-02-10 | 1900-02-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 985 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.22 | 6 | 0
1994-02-10 | 1900-02-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.61 | A | 7 | 985 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.94 | 6 | 0
1994-02-11 | 1900-02-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.67 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.02 | 7 | 0
1994-02-11 | 1900-02-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.22 | 7 | 0
1994-02-11 | 1900-02-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.02 | 7 | 0
1994-02-11 | 1900-02-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -11.7 | 10.94 | A | 7 | 0.86 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.14 | 7 | 0
1994-02-11 | 1900-02-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.06 | 7 | 0
1994-02-11 | 1900-02-10 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -11.7 | 10.94 | A | 7 | 0.86 | A | 7 | 984 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.14 | 7 | 0
1994-02-11 | 1900-02-10 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.02 | 7 | 0
1994-02-11 | 1900-02-10 | 8:00 | 8 | 63 | 995 | 19 | 1 | 10 | 84 | 1 | 16 | 13 | 1 | 10 | 2000 | 1 | 10 | 3400 | 1 | 16 | 1800 | 1 | 10 | 220 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -10.6 | 12.92 | A | 7 | 0.78 | A | 7 | 984 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.62 | 7 | 0
1994-02-11 | 1900-02-10 | 9:00 | 9 | 300 | 1404 | 153 | 1 | 10 | 466 | 1 | 16 | 53 | 1 | 10 | 15700 | 1 | 10 | 36700 | 1 | 16 | 7900 | 1 | 10 | 960 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 984 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.08 | 7 | 0
1994-02-11 | 1900-02-10 | 10:00 | 10 | 520 | 1404 | 326 | 1 | 10 | 671 | 1 | 16 | 77 | 1 | 10 | 34300 | 1 | 10 | 63000 | 1 | 16 | 10900 | 1 | 10 | 1520 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.56 | A | 7 | 984 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.08 | 7 | 0
1994-02-11 | 1900-02-10 | 11:00 | 11 | 690 | 1404 | 474 | 1 | 10 | 768 | 1 | 16 | 96 | 1 | 10 | 49000 | 1 | 10 | 74700 | 1 | 16 | 12200 | 1 | 10 | 1940 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -10 | 14 | A | 7 | 0.43 | A | 7 | 984 | A | 7 | 90 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.5 | 7 | 0
1994-02-11 | 1900-02-10 | 12:00 | 12 | 798 | 1404 | 528 | 1 | 10 | 723 | 1 | 16 | 116 | 1 | 10 | 56200 | 1 | 10 | 72800 | 1 | 16 | 14700 | 1 | 10 | 2700 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 2.2 | 35.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.33 | A | 7 | 983 | A | 7 | 110 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.22 | 7 | 0
1994-02-11 | 1900-02-10 | 13:00 | 13 | 838 | 1404 | 577 | 1 | 10 | 670 | 1 | 16 | 177 | 1 | 10 | 59900 | 1 | 10 | 66600 | 1 | 16 | 20100 | 1 | 10 | 4040 | 1 | 21 | 4 | A | 7 | 4 | A | 7 | 3.9 | 39.02 | A | 7 | -11.1 | 12.02 | A | 7 | 0.29 | A | 7 | 983 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.02 | 7 | 0
1994-02-11 | 1900-02-10 | 14:00 | 14 | 806 | 1404 | 462 | 1 | 10 | 279 | 1 | 16 | 302 | 1 | 10 | 50000 | 1 | 10 | 28900 | 1 | 16 | 33300 | 1 | 10 | 7980 | 1 | 21 | 6 | A | 7 | 6 | A | 7 | 5.6 | 42.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.26 | A | 7 | 981 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.82 | 7 | 0
1994-02-11 | 1900-02-10 | 15:00 | 15 | 705 | 1404 | 309 | 1 | 10 | 273 | 1 | 16 | 172 | 1 | 10 | 33600 | 1 | 10 | 28400 | 1 | 16 | 19300 | 1 | 10 | 3770 | 1 | 21 | 6 | A | 7 | 6 | A | 7 | 7.2 | 44.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.23 | A | 7 | 980 | A | 7 | 120 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 3658 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.62 | 7 | 0
1994-02-11 | 1900-02-10 | 16:00 | 16 | 541 | 1404 | 225 | 1 | 10 | 263 | 1 | 16 | 123 | 1 | 10 | 24300 | 1 | 10 | 25800 | 1 | 16 | 14300 | 1 | 10 | 2460 | 1 | 21 | 6 | A | 7 | 6 | A | 7 | 6.1 | 42.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.24 | A | 7 | 979 | A | 7 | 110 | A | 7 | 8.2 | A | 7 | 32000 | A | 7 | 3658 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.74 | 7 | 0
1994-02-11 | 1900-02-10 | 17:00 | 17 | 327 | 1404 | 140 | 1 | 10 | 157 | 1 | 16 | 103 | 1 | 10 | 15100 | 1 | 10 | 13000 | 1 | 16 | 12000 | 1 | 10 | 2240 | 1 | 21 | 7 | A | 7 | 7 | A | 7 | 5.6 | 42.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.26 | A | 7 | 978 | A | 7 | 130 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 3658 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.82 | 7 | 0
1994-02-11 | 1900-02-10 | 18:00 | 18 | 84 | 1158 | 23 | 1 | 10 | 27 | 1 | 16 | 21 | 1 | 10 | 2600 | 1 | 10 | 1300 | 1 | 16 | 2500 | 1 | 10 | 430 | 1 | 21 | 6 | A | 7 | 6 | A | 7 | 3.3 | 37.94 | A | 7 | -10 | 14 | A | 7 | 0.34 | A | 7 | 978 | A | 7 | 100 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 4572 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10 | 7 | 0
1994-02-11 | 1900-02-10 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 1.7 | 35.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.4 | A | 7 | 978 | A | 7 | 100 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.28 | 7 | 0
1994-02-11 | 1900-02-10 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 1.1 | 33.98 | A | 7 | -9.4 | 15.08 | A | 7 | 0.41 | A | 7 | 977 | A | 7 | 110 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.28 | 7 | 0
1994-02-11 | 1900-02-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 1.7 | 35.06 | A | 7 | -10 | 14 | A | 7 | 0.38 | A | 7 | 976 | A | 7 | 120 | A | 7 | 8.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.2 | 7 | 0
1994-02-11 | 1900-02-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 1.7 | 35.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.36 | A | 7 | 976 | A | 7 | 110 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 3658 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.12 | 7 | 0
1994-02-11 | 1900-02-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 1.7 | 35.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.36 | A | 7 | 975 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 4572 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.12 | 7 | 0
1994-02-11 | 1900-02-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 0.6 | 33.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.37 | A | 7 | 976 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 4572 | A | 7 | 1.2 | E | 8 | 0.085 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.42 | 7 | 0
1994-02-12 | 1900-02-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 0 | 32 | A | 7 | -10.6 | 12.92 | A | 7 | 0.4 | A | 7 | 976 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 3962 | A | 7 | 1.2 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.42 | 1 | 0
1994-02-12 | 1900-02-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -7.2 | 19.04 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 1981 | A | 7 | 1.2 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.64 | 1 | 0
1994-02-12 | 1900-02-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.66 | A | 7 | 975 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 19200 | A | 7 | 1829 | A | 7 | 1.2 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.18 | 1 | 0
1994-02-12 | 1900-02-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.83 | A | 7 | 975 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 1311 | A | 7 | 1.2 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.24 | 1 | 0
1994-02-12 | 1900-02-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 24000 | A | 7 | 1097 | A | 7 | 1.2 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.64 | 1 | 0
1994-02-12 | 1900-02-11 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.83 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19200 | A | 7 | 1006 | A | 7 | 1.2 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.44 | 1 | 0
1994-02-12 | 1900-02-11 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19200 | A | 7 | 1676 | A | 7 | 1.2 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.64 | 1 | 0
1994-02-12 | 1900-02-11 | 8:00 | 8 | 66 | 1041 | 10 | 1 | 10 | 0 | 1 | 16 | 10 | 1 | 10 | 1200 | 1 | 10 | 0 | 1 | 16 | 1200 | 1 | 10 | 380 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.87 | A | 7 | 977 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 11200 | A | 7 | 914 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.64 | 1 | 0
1994-02-12 | 1900-02-11 | 9:00 | 9 | 306 | 1404 | 46 | 1 | 10 | 0 | 1 | 16 | 46 | 1 | 10 | 5400 | 1 | 10 | 0 | 1 | 16 | 5400 | 1 | 10 | 1810 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.83 | A | 7 | 978 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 11200 | A | 7 | 914 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.24 | 1 | 0
1994-02-12 | 1900-02-11 | 10:00 | 10 | 526 | 1404 | 97 | 1 | 10 | 0 | 1 | 16 | 97 | 1 | 10 | 11300 | 1 | 10 | 0 | 1 | 16 | 11300 | 1 | 10 | 4030 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 427 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.64 | 1 | 0
1994-02-12 | 1900-02-11 | 11:00 | 11 | 696 | 1404 | 140 | 1 | 10 | 0 | 1 | 16 | 140 | 1 | 10 | 16400 | 1 | 10 | 0 | 1 | 16 | 16400 | 1 | 10 | 6100 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 330 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 1676 | A | 7 | 1.1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.66 | 1 | 0
1994-02-12 | 1900-02-11 | 12:00 | 12 | 805 | 1404 | 168 | 1 | 10 | 0 | 1 | 16 | 168 | 1 | 10 | 19700 | 1 | 10 | 0 | 1 | 16 | 19700 | 1 | 10 | 7530 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.66 | A | 7 | 981 | A | 7 | 340 | A | 7 | 7.7 | A | 7 | 9600 | A | 7 | 1676 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.18 | 1 | 0
1994-02-12 | 1900-02-11 | 13:00 | 13 | 844 | 1404 | 178 | 1 | 10 | 0 | 1 | 16 | 178 | 1 | 10 | 20900 | 1 | 10 | 0 | 1 | 16 | 20900 | 1 | 10 | 8070 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 340 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.08 | 1 | 0
1994-02-12 | 1900-02-11 | 14:00 | 14 | 812 | 1404 | 170 | 1 | 10 | 0 | 1 | 16 | 170 | 1 | 10 | 20000 | 1 | 10 | 0 | 1 | 16 | 20000 | 1 | 10 | 7640 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -5 | 23 | A | 7 | 0.61 | A | 7 | 982 | A | 7 | 350 | A | 7 | 9.3 | A | 7 | 11200 | A | 7 | 2438 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.8 | 1 | 0
1994-02-12 | 1900-02-11 | 15:00 | 15 | 711 | 1404 | 144 | 1 | 10 | 0 | 1 | 16 | 144 | 1 | 10 | 16800 | 1 | 10 | 0 | 1 | 16 | 16800 | 1 | 10 | 6300 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -5 | 23 | A | 7 | 0.58 | A | 7 | 983 | A | 7 | 330 | A | 7 | 10.3 | A | 7 | 11200 | A | 7 | 914 | A | 7 | 1 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.5 | 1 | 0
1994-02-12 | 1900-02-11 | 16:00 | 16 | 547 | 1404 | 102 | 1 | 10 | 0 | 1 | 16 | 102 | 1 | 10 | 11900 | 1 | 10 | 0 | 1 | 16 | 11900 | 1 | 10 | 4260 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.6 | A | 7 | 984 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 11200 | A | 7 | 914 | A | 7 | 0.9 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.72 | 1 | 0
1994-02-12 | 1900-02-11 | 17:00 | 17 | 332 | 1404 | 52 | 1 | 10 | 0 | 1 | 16 | 52 | 1 | 10 | 6000 | 1 | 10 | 0 | 1 | 16 | 6000 | 1 | 10 | 2050 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -6.1 | 21.02 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 330 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 792 | A | 7 | 0.9 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.92 | 1 | 0
1994-02-12 | 1900-02-11 | 18:00 | 18 | 89 | 1181 | 14 | 1 | 10 | 0 | 1 | 16 | 14 | 1 | 10 | 1600 | 1 | 10 | 0 | 1 | 16 | 1600 | 1 | 10 | 520 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 320 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 945 | A | 7 | 0.9 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.94 | 1 | 0
1994-02-12 | 1900-02-11 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.62 | A | 7 | 988 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 19200 | A | 7 | 914 | A | 7 | 0.9 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.04 | 1 | 0
1994-02-12 | 1900-02-11 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.65 | A | 7 | 989 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 19200 | A | 7 | 792 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.34 | 1 | 0
1994-02-12 | 1900-02-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -2.2 | 28.04 | A | 7 | -7.2 | 19.04 | A | 7 | 0.65 | A | 7 | 990 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 19200 | A | 7 | 732 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.44 | 1 | 0
1994-02-12 | 1900-02-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -2.8 | 26.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.69 | A | 7 | 990 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 19200 | A | 7 | 671 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.74 | 1 | 0
1994-02-12 | 1900-02-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.75 | A | 7 | 991 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.24 | 1 | 0
1994-02-12 | 1900-02-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.75 | A | 7 | 991 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.16 | 1 | 0
1994-02-13 | 1900-02-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -10 | 14 | A | 7 | 0.75 | A | 7 | 992 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.5 | 2 | 0
1994-02-13 | 1900-02-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -10.6 | 12.92 | A | 7 | 0.78 | A | 7 | 992 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.62 | 2 | 0
1994-02-13 | 1900-02-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.87 | A | 7 | 993 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.18 | 2 | 0
1994-02-13 | 1900-02-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.91 | A | 7 | 993 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.48 | 2 | 0
1994-02-13 | 1900-02-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -10 | 14 | A | 7 | 0.91 | A | 7 | 993 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.4 | 2 | 0
1994-02-13 | 1900-02-12 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -10 | 14 | A | 7 | 0.86 | A | 7 | 993 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.1 | 2 | 0
1994-02-13 | 1900-02-12 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.82 | A | 7 | 993 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.82 | 2 | 0
1994-02-13 | 1900-02-12 | 8:00 | 8 | 70 | 1064 | 27 | 1 | 10 | 233 | 1 | 16 | 12 | 1 | 10 | 3000 | 1 | 10 | 13100 | 1 | 16 | 2000 | 1 | 10 | 260 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.83 | A | 7 | 994 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.88 | 2 | 0
1994-02-13 | 1900-02-12 | 9:00 | 9 | 312 | 1403 | 183 | 1 | 10 | 661 | 1 | 16 | 36 | 1 | 10 | 19100 | 1 | 10 | 54700 | 1 | 16 | 6900 | 1 | 10 | 750 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.79 | A | 7 | 995 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.34 | 2 | 0
1994-02-13 | 1900-02-12 | 10:00 | 10 | 532 | 1403 | 364 | 1 | 10 | 826 | 1 | 16 | 51 | 1 | 10 | 38400 | 1 | 10 | 77600 | 1 | 16 | 8900 | 1 | 10 | 1190 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.66 | A | 7 | 995 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.32 | 2 | 0
1994-02-13 | 1900-02-12 | 11:00 | 11 | 702 | 1403 | 514 | 1 | 10 | 901 | 1 | 16 | 63 | 1 | 10 | 54100 | 1 | 10 | 87800 | 1 | 16 | 10000 | 1 | 10 | 1500 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.49 | A | 7 | 996 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.02 | 2 | 0
1994-02-13 | 1900-02-12 | 12:00 | 12 | 811 | 1403 | 611 | 1 | 10 | 936 | 1 | 16 | 70 | 1 | 10 | 64200 | 1 | 10 | 92400 | 1 | 16 | 10600 | 1 | 10 | 1720 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.38 | A | 7 | 995 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.24 | 2 | 0
1994-02-13 | 1900-02-12 | 13:00 | 13 | 851 | 1403 | 647 | 1 | 10 | 947 | 1 | 16 | 73 | 1 | 10 | 67900 | 1 | 10 | 93800 | 1 | 16 | 10800 | 1 | 10 | 1820 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | -7.2 | 19.04 | A | 7 | 0.31 | A | 7 | 994 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.94 | 2 | 0
1994-02-13 | 1900-02-12 | 14:00 | 14 | 819 | 1403 | 617 | 1 | 10 | 937 | 1 | 16 | 70 | 1 | 10 | 64800 | 1 | 10 | 92600 | 1 | 16 | 10600 | 1 | 10 | 1740 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.28 | A | 7 | 993 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.86 | 2 | 0
1994-02-13 | 1900-02-12 | 15:00 | 15 | 717 | 1403 | 526 | 1 | 10 | 904 | 1 | 16 | 64 | 1 | 10 | 55400 | 1 | 10 | 88300 | 1 | 16 | 10100 | 1 | 10 | 1530 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.27 | A | 7 | 992 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.76 | 2 | 0
1994-02-13 | 1900-02-12 | 16:00 | 16 | 553 | 1403 | 356 | 1 | 10 | 731 | 1 | 16 | 68 | 1 | 10 | 37200 | 1 | 10 | 69300 | 1 | 16 | 9800 | 1 | 10 | 1390 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 10.6 | 51.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.22 | A | 7 | 992 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.78 | 2 | 0
1994-02-13 | 1900-02-12 | 17:00 | 17 | 338 | 1403 | 197 | 1 | 10 | 656 | 1 | 16 | 39 | 1 | 10 | 20600 | 1 | 10 | 55600 | 1 | 16 | 7200 | 1 | 10 | 810 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | -9.4 | 15.08 | A | 7 | 0.22 | A | 7 | 991 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.08 | 2 | 0
1994-02-13 | 1900-02-12 | 18:00 | 18 | 93 | 1204 | 38 | 1 | 10 | 290 | 1 | 16 | 16 | 1 | 10 | 4100 | 1 | 10 | 16900 | 1 | 16 | 2700 | 1 | 10 | 330 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.25 | A | 7 | 991 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.52 | 2 | 0
1994-02-13 | 1900-02-12 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.4 | A | 7 | 991 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.28 | 2 | 0
1994-02-13 | 1900-02-12 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -9.4 | 15.08 | A | 7 | 0.33 | A | 7 | 990 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.78 | 2 | 0
1994-02-13 | 1900-02-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.39 | A | 7 | 989 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.86 | 2 | 0
1994-02-13 | 1900-02-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.35 | A | 7 | 989 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.68 | 2 | 0
1994-02-13 | 1900-02-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.35 | A | 7 | 988 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.68 | 2 | 0
1994-02-13 | 1900-02-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.35 | A | 7 | 988 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.086 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.98 | 2 | 0
1994-02-14 | 1900-02-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -10 | 14 | A | 7 | 0.34 | A | 7 | 987 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10 | 3 | 0
1994-02-14 | 1900-02-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -10 | 14 | A | 7 | 0.34 | A | 7 | 986 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10 | 3 | 0
1994-02-14 | 1900-02-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.35 | A | 7 | 985 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.98 | 3 | 0
1994-02-14 | 1900-02-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.35 | A | 7 | 984 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.98 | 3 | 0
1994-02-14 | 1900-02-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.37 | A | 7 | 984 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.08 | 3 | 0
1994-02-14 | 1900-02-13 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.38 | A | 7 | 983 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.08 | 3 | 0
1994-02-14 | 1900-02-13 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 2.2 | 35.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.38 | A | 7 | 983 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.08 | 3 | 0
1994-02-14 | 1900-02-13 | 8:00 | 8 | 74 | 1087 | 17 | 1 | 10 | 39 | 1 | 16 | 14 | 1 | 10 | 1900 | 1 | 10 | 1500 | 1 | 16 | 1800 | 1 | 10 | 230 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 2.2 | 35.96 | A | 7 | -8.9 | 15.98 | A | 7 | 0.4 | A | 7 | 983 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.98 | 3 | 0
1994-02-14 | 1900-02-13 | 9:00 | 9 | 317 | 1403 | 134 | 1 | 10 | 74 | 1 | 16 | 117 | 1 | 10 | 14600 | 1 | 10 | 6400 | 1 | 16 | 13200 | 1 | 10 | 2710 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 3.9 | 39.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.35 | A | 7 | 983 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.68 | 3 | 0
1994-02-14 | 1900-02-13 | 10:00 | 10 | 538 | 1403 | 287 | 1 | 10 | 383 | 1 | 16 | 140 | 1 | 10 | 29900 | 1 | 10 | 36300 | 1 | 16 | 15900 | 1 | 10 | 2750 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 7.2 | 44.96 | A | 7 | -8.3 | 17.06 | A | 7 | 0.3 | A | 7 | 983 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.26 | 3 | 0
1994-02-14 | 1900-02-13 | 11:00 | 11 | 708 | 1403 | 419 | 1 | 10 | 474 | 1 | 16 | 180 | 1 | 10 | 44200 | 1 | 10 | 47500 | 1 | 16 | 20100 | 1 | 10 | 3840 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 9.4 | 48.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.24 | A | 7 | 982 | A | 7 | 190 | A | 7 | 10.8 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.98 | 3 | 0
1994-02-14 | 1900-02-13 | 12:00 | 12 | 817 | 1403 | 574 | 1 | 10 | 656 | 1 | 16 | 192 | 1 | 10 | 59100 | 1 | 10 | 64600 | 1 | 16 | 21400 | 1 | 10 | 4210 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 13.9 | 57.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.19 | A | 7 | 981 | A | 7 | 210 | A | 7 | 11.3 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.46 | 3 | 0
1994-02-14 | 1900-02-13 | 13:00 | 13 | 857 | 1403 | 572 | 1 | 10 | 715 | 1 | 16 | 135 | 1 | 10 | 60700 | 1 | 10 | 72200 | 1 | 16 | 16500 | 1 | 10 | 3290 | 1 | 21 | 8 | A | 7 | 4 | A | 7 | 15 | 59 | A | 7 | -10.6 | 12.92 | A | 7 | 0.14 | A | 7 | 980 | A | 7 | 200 | A | 7 | 12.9 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.82 | 3 | 0
1994-02-14 | 1900-02-13 | 14:00 | 14 | 825 | 1403 | 452 | 1 | 10 | 331 | 1 | 16 | 257 | 1 | 10 | 48500 | 1 | 10 | 35100 | 1 | 16 | 27800 | 1 | 10 | 6380 | 1 | 21 | 9 | A | 7 | 4 | A | 7 | 15.6 | 60.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.21 | A | 7 | 979 | A | 7 | 210 | A | 7 | 14.4 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.72 | 3 | 0
1994-02-14 | 1900-02-13 | 15:00 | 15 | 723 | 1403 | 366 | 1 | 10 | 347 | 1 | 16 | 187 | 1 | 10 | 39600 | 1 | 10 | 36200 | 1 | 16 | 20900 | 1 | 10 | 4180 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 16.1 | 60.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.2 | A | 7 | 979 | A | 7 | 210 | A | 7 | 13.4 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.72 | 3 | 0
1994-02-14 | 1900-02-13 | 16:00 | 16 | 559 | 1403 | 252 | 1 | 10 | 284 | 1 | 16 | 139 | 1 | 10 | 27200 | 1 | 10 | 28100 | 1 | 16 | 15900 | 1 | 10 | 2850 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 15 | 59 | A | 7 | -12.2 | 10.04 | A | 7 | 0.13 | A | 7 | 979 | A | 7 | 220 | A | 7 | 9.3 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.44 | 3 | 0
1994-02-14 | 1900-02-13 | 17:00 | 17 | 344 | 1403 | 129 | 1 | 10 | 87 | 1 | 16 | 107 | 1 | 10 | 13900 | 1 | 10 | 7400 | 1 | 16 | 12000 | 1 | 10 | 2340 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 13.9 | 57.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.13 | A | 7 | 980 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.56 | 3 | 0
1994-02-14 | 1900-02-13 | 18:00 | 18 | 97 | 1251 | 19 | 1 | 10 | 34 | 1 | 16 | 16 | 1 | 10 | 2100 | 1 | 10 | 1700 | 1 | 16 | 2000 | 1 | 10 | 330 | 1 | 21 | 10 | A | 7 | 7 | A | 7 | 12.8 | 55.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.15 | A | 7 | 980 | A | 7 | 210 | A | 7 | 9.3 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.34 | 3 | 0
1994-02-14 | 1900-02-13 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 10.6 | 51.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.17 | A | 7 | 981 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.44 | 3 | 0
1994-02-14 | 1900-02-13 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 4 | A | 7 | 9.4 | 48.92 | A | 7 | -11.1 | 12.02 | A | 7 | 0.2 | A | 7 | 982 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.42 | 3 | 0
1994-02-14 | 1900-02-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 3 | A | 7 | 7.8 | 46.04 | A | 7 | -10.6 | 12.92 | A | 7 | 0.23 | A | 7 | 983 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.42 | 3 | 0
1994-02-14 | 1900-02-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 6.7 | 44.06 | A | 7 | -10 | 14 | A | 7 | 0.26 | A | 7 | 983 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.5 | 3 | 0
1994-02-14 | 1900-02-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 4.4 | 39.92 | A | 7 | -10 | 14 | A | 7 | 0.31 | A | 7 | 984 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.8 | 3 | 0
1994-02-14 | 1900-02-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 4 | A | 7 | 3.9 | 39.02 | A | 7 | -11.7 | 10.94 | A | 7 | 0.28 | A | 7 | 984 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.04 | 3 | 0
1994-02-15 | 1900-02-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 2.8 | 37.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.38 | A | 7 | 984 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.88 | 4 | 0
1994-02-15 | 1900-02-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | 0.6 | 33.08 | A | 7 | -7.2 | 19.04 | A | 7 | 0.52 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.54 | 4 | 0
1994-02-15 | 1900-02-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 1.1 | 33.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.55 | A | 7 | 986 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.52 | 4 | 0
1994-02-15 | 1900-02-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.68 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.32 | 4 | 0
1994-02-15 | 1900-02-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.66 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.22 | 4 | 0
1994-02-15 | 1900-02-14 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.62 | 4 | 0
1994-02-15 | 1900-02-14 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.72 | 4 | 0
1994-02-15 | 1900-02-14 | 8:00 | 8 | 79 | 1110 | 30 | 1 | 10 | 222 | 1 | 16 | 14 | 1 | 10 | 3100 | 1 | 10 | 12600 | 1 | 16 | 2200 | 1 | 10 | 290 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5 | 23 | A | 7 | 0.69 | A | 7 | 990 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.4 | 4 | 0
1994-02-15 | 1900-02-14 | 9:00 | 9 | 323 | 1402 | 189 | 1 | 10 | 641 | 1 | 16 | 41 | 1 | 10 | 19600 | 1 | 10 | 53400 | 1 | 16 | 7200 | 1 | 10 | 820 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.59 | A | 7 | 991 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.38 | 4 | 0
1994-02-15 | 1900-02-14 | 10:00 | 10 | 544 | 1402 | 371 | 1 | 10 | 808 | 1 | 16 | 58 | 1 | 10 | 39100 | 1 | 10 | 76100 | 1 | 16 | 9400 | 1 | 10 | 1240 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -3.9 | 24.98 | A | 7 | 0.51 | A | 7 | 991 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.58 | 4 | 0
1994-02-15 | 1900-02-14 | 11:00 | 11 | 714 | 1402 | 521 | 1 | 10 | 885 | 1 | 16 | 71 | 1 | 10 | 54700 | 1 | 10 | 86400 | 1 | 16 | 10600 | 1 | 10 | 1570 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.46 | A | 7 | 992 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.06 | 4 | 0
1994-02-15 | 1900-02-14 | 12:00 | 12 | 823 | 1402 | 619 | 1 | 10 | 920 | 1 | 16 | 78 | 1 | 10 | 64700 | 1 | 10 | 90900 | 1 | 16 | 11200 | 1 | 10 | 1820 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.41 | A | 7 | 992 | A | 7 | 350 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.56 | 4 | 0
1994-02-15 | 1900-02-14 | 13:00 | 13 | 863 | 1402 | 655 | 1 | 10 | 931 | 1 | 16 | 81 | 1 | 10 | 68400 | 1 | 10 | 92200 | 1 | 16 | 11400 | 1 | 10 | 1920 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | -4.4 | 24.08 | A | 7 | 0.34 | A | 7 | 991 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.28 | 4 | 0
1994-02-15 | 1900-02-14 | 14:00 | 14 | 831 | 1402 | 625 | 1 | 10 | 921 | 1 | 16 | 79 | 1 | 10 | 65400 | 1 | 10 | 91000 | 1 | 16 | 11300 | 1 | 10 | 1840 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.28 | A | 7 | 991 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.02 | 4 | 0
1994-02-15 | 1900-02-14 | 15:00 | 15 | 729 | 1402 | 533 | 1 | 10 | 887 | 1 | 16 | 72 | 1 | 10 | 55900 | 1 | 10 | 86700 | 1 | 16 | 10700 | 1 | 10 | 1600 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.21 | A | 7 | 991 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.78 | 4 | 0
1994-02-15 | 1900-02-14 | 16:00 | 16 | 565 | 1402 | 387 | 1 | 10 | 815 | 1 | 16 | 59 | 1 | 10 | 40800 | 1 | 10 | 77300 | 1 | 16 | 9500 | 1 | 10 | 1280 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -8.9 | 15.98 | A | 7 | 0.22 | A | 7 | 991 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.78 | 4 | 0
1994-02-15 | 1900-02-14 | 17:00 | 17 | 349 | 1402 | 207 | 1 | 10 | 661 | 1 | 16 | 43 | 1 | 10 | 21600 | 1 | 10 | 56400 | 1 | 16 | 7500 | 1 | 10 | 870 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -9.4 | 15.08 | A | 7 | 0.21 | A | 7 | 991 | A | 7 | 30 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.98 | 4 | 0
1994-02-15 | 1900-02-14 | 18:00 | 18 | 102 | 1273 | 41 | 1 | 10 | 277 | 1 | 16 | 19 | 1 | 10 | 4400 | 1 | 10 | 14600 | 1 | 16 | 3200 | 1 | 10 | 350 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -10 | 14 | A | 7 | 0.23 | A | 7 | 991 | A | 7 | 50 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.3 | 4 | 0
1994-02-15 | 1900-02-14 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -8.9 | 15.98 | A | 7 | 0.33 | A | 7 | 991 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.58 | 4 | 0
1994-02-15 | 1900-02-14 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -8.3 | 17.06 | A | 7 | 0.35 | A | 7 | 991 | A | 7 | 70 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.56 | 4 | 0
1994-02-15 | 1900-02-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -7.8 | 17.96 | A | 7 | 0.42 | A | 7 | 991 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.86 | 4 | 0
1994-02-15 | 1900-02-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -7.2 | 19.04 | A | 7 | 0.44 | A | 7 | 991 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.94 | 4 | 0
1994-02-15 | 1900-02-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.48 | A | 7 | 992 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.04 | 4 | 0
1994-02-15 | 1900-02-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -7.2 | 19.04 | A | 7 | 0.48 | A | 7 | 991 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.087 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.24 | 4 | 0
1994-02-16 | 1900-02-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -7.2 | 19.04 | A | 7 | 0.48 | A | 7 | 991 | A | 7 | 130 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.24 | 5 | 0
1994-02-16 | 1900-02-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.55 | A | 7 | 991 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.52 | 5 | 0
1994-02-16 | 1900-02-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -6.1 | 21.02 | A | 7 | 0.6 | A | 7 | 990 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.92 | 5 | 0
1994-02-16 | 1900-02-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 990 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.82 | 5 | 0
1994-02-16 | 1900-02-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.6 | A | 7 | 989 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.72 | 5 | 0
1994-02-16 | 1900-02-15 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -5 | 23 | A | 7 | 0.58 | A | 7 | 989 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.5 | 5 | 0
1994-02-16 | 1900-02-15 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 160 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.82 | 5 | 0
1994-02-16 | 1900-02-15 | 8:00 | 8 | 83 | 1133 | 32 | 1 | 10 | 138 | 1 | 16 | 22 | 1 | 10 | 3400 | 1 | 10 | 6100 | 1 | 16 | 3000 | 1 | 10 | 390 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | 1.1 | 33.98 | A | 7 | -5 | 23 | A | 7 | 0.61 | A | 7 | 989 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.8 | 5 | 0
1994-02-16 | 1900-02-15 | 9:00 | 9 | 329 | 1401 | 168 | 1 | 10 | 419 | 1 | 16 | 69 | 1 | 10 | 17700 | 1 | 10 | 33800 | 1 | 16 | 9700 | 1 | 10 | 1250 | 1 | 21 | 9 | A | 7 | 3 | A | 7 | 6.1 | 42.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.41 | A | 7 | 989 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.12 | 5 | 0
1994-02-16 | 1900-02-15 | 10:00 | 10 | 550 | 1401 | 362 | 1 | 10 | 767 | 1 | 16 | 61 | 1 | 10 | 38300 | 1 | 10 | 72900 | 1 | 16 | 9500 | 1 | 10 | 1300 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | 10 | 50 | A | 7 | -5 | 23 | A | 7 | 0.33 | A | 7 | 989 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.4 | 5 | 0
1994-02-16 | 1900-02-15 | 11:00 | 11 | 721 | 1401 | 487 | 1 | 10 | 777 | 1 | 16 | 87 | 1 | 10 | 51200 | 1 | 10 | 76500 | 1 | 16 | 11800 | 1 | 10 | 1900 | 1 | 21 | 6 | A | 7 | 1 | A | 7 | 12.8 | 55.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.29 | A | 7 | 989 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.88 | 5 | 0
1994-02-16 | 1900-02-15 | 12:00 | 12 | 830 | 1401 | 592 | 1 | 10 | 865 | 1 | 16 | 79 | 1 | 10 | 61900 | 1 | 10 | 85500 | 1 | 16 | 11100 | 1 | 10 | 1840 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.26 | A | 7 | 989 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.58 | 5 | 0
1994-02-16 | 1900-02-15 | 13:00 | 13 | 869 | 1401 | 654 | 1 | 10 | 898 | 1 | 16 | 96 | 1 | 10 | 68000 | 1 | 10 | 88900 | 1 | 16 | 12600 | 1 | 10 | 2020 | 1 | 21 | 4 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.3 | A | 7 | 988 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.62 | 5 | 0
1994-02-16 | 1900-02-15 | 14:00 | 14 | 837 | 1401 | 583 | 1 | 10 | 771 | 1 | 16 | 122 | 1 | 10 | 62200 | 1 | 10 | 78000 | 1 | 16 | 15500 | 1 | 10 | 2950 | 1 | 21 | 9 | A | 7 | 1 | A | 7 | 16.7 | 62.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.29 | A | 7 | 985 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.52 | 5 | 0
1994-02-16 | 1900-02-15 | 15:00 | 15 | 735 | 1401 | 492 | 1 | 10 | 661 | 1 | 16 | 145 | 1 | 10 | 51100 | 1 | 10 | 65000 | 1 | 16 | 16900 | 1 | 10 | 3070 | 1 | 21 | 9 | A | 7 | 1 | A | 7 | 16.7 | 62.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.31 | A | 7 | 985 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.42 | 5 | 0
1994-02-16 | 1900-02-15 | 16:00 | 16 | 571 | 1401 | 353 | 1 | 10 | 603 | 1 | 16 | 108 | 1 | 10 | 36600 | 1 | 10 | 57100 | 1 | 16 | 13300 | 1 | 10 | 2100 | 1 | 21 | 10 | A | 7 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.31 | A | 7 | 984 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.42 | 5 | 0
1994-02-16 | 1900-02-15 | 17:00 | 17 | 355 | 1401 | 194 | 1 | 10 | 515 | 1 | 16 | 64 | 1 | 10 | 20000 | 1 | 10 | 43000 | 1 | 16 | 9100 | 1 | 10 | 1170 | 1 | 21 | 10 | A | 7 | 1 | A | 7 | 15.6 | 60.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.31 | A | 7 | 984 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.72 | 5 | 0
1994-02-16 | 1900-02-15 | 18:00 | 18 | 107 | 1296 | 38 | 1 | 10 | 132 | 1 | 16 | 27 | 1 | 10 | 4000 | 1 | 10 | 6300 | 1 | 16 | 3500 | 1 | 10 | 480 | 1 | 21 | 10 | A | 7 | 1 | A | 7 | 13.9 | 57.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.37 | A | 7 | 984 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.12 | 5 | 0
1994-02-16 | 1900-02-15 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 4 | A | 7 | 12.8 | 55.04 | A | 7 | 0 | 32 | A | 7 | 0.41 | A | 7 | 984 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 25.5 | 5 | 0
1994-02-16 | 1900-02-15 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | 12.2 | 53.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.41 | A | 7 | 984 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.62 | 5 | 0
1994-02-16 | 1900-02-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 12.2 | 53.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.41 | A | 7 | 984 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.62 | 5 | 0
1994-02-16 | 1900-02-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | 11.7 | 53.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.42 | A | 7 | 984 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.72 | 5 | 0
1994-02-16 | 1900-02-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 11.1 | 51.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.44 | A | 7 | 984 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.92 | 5 | 0
1994-02-16 | 1900-02-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 10 | 50 | A | 7 | -0.6 | 30.92 | A | 7 | 0.47 | A | 7 | 983 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 25.22 | 5 | 0
1994-02-17 | 1900-02-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | 9.4 | 48.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.49 | A | 7 | 983 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 25.52 | 6 | 0
1994-02-17 | 1900-02-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 5 | A | 7 | 9.4 | 48.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.49 | A | 7 | 983 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 25.52 | 6 | 0
1994-02-17 | 1900-02-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 8.9 | 48.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.51 | A | 7 | 983 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 25.72 | 6 | 0
1994-02-17 | 1900-02-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 7.8 | 46.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.55 | A | 7 | 983 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.12 | 6 | 0
1994-02-17 | 1900-02-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 6.1 | 42.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.92 | 6 | 0
1994-02-17 | 1900-02-16 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 6.7 | 44.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.59 | A | 7 | 983 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.62 | 6 | 0
1994-02-17 | 1900-02-16 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.69 | A | 7 | 983 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.82 | 6 | 0
1994-02-17 | 1900-02-16 | 8:00 | 8 | 88 | 1179 | 32 | 1 | 10 | 86 | 1 | 16 | 25 | 1 | 10 | 3400 | 1 | 10 | 3500 | 1 | 16 | 3100 | 1 | 10 | 440 | 1 | 21 | 8 | A | 7 | 3 | A | 7 | 4.4 | 39.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.7 | A | 7 | 983 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.72 | 6 | 0
1994-02-17 | 1900-02-16 | 9:00 | 9 | 335 | 1401 | 181 | 1 | 10 | 464 | 1 | 16 | 70 | 1 | 10 | 18500 | 1 | 10 | 37600 | 1 | 16 | 9400 | 1 | 10 | 1240 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.58 | A | 7 | 984 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.28 | 6 | 0
1994-02-17 | 1900-02-16 | 10:00 | 10 | 556 | 1401 | 340 | 1 | 10 | 643 | 1 | 16 | 85 | 1 | 10 | 35800 | 1 | 10 | 61200 | 1 | 16 | 11400 | 1 | 10 | 1700 | 1 | 21 | 8 | A | 7 | 1 | A | 7 | 10.6 | 51.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.38 | 6 | 0
1994-02-17 | 1900-02-16 | 11:00 | 11 | 727 | 1401 | 482 | 1 | 10 | 766 | 1 | 16 | 85 | 1 | 10 | 51000 | 1 | 10 | 75600 | 1 | 16 | 11600 | 1 | 10 | 1880 | 1 | 21 | 5 | A | 7 | 1 | A | 7 | 12.2 | 53.96 | A | 7 | 2.2 | 35.96 | A | 7 | 0.5 | A | 7 | 983 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 29.76 | 6 | 0
1994-02-17 | 1900-02-16 | 12:00 | 12 | 836 | 1401 | 607 | 1 | 10 | 820 | 1 | 16 | 118 | 1 | 10 | 63100 | 1 | 10 | 81200 | 1 | 16 | 14500 | 1 | 10 | 2590 | 1 | 21 | 8 | A | 7 | 1 | A | 7 | 14.4 | 57.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.47 | A | 7 | 983 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 30.94 | 6 | 0
1994-02-17 | 1900-02-16 | 13:00 | 13 | 876 | 1401 | 610 | 1 | 10 | 793 | 1 | 16 | 114 | 1 | 10 | 64000 | 1 | 10 | 79100 | 1 | 16 | 14400 | 1 | 10 | 2680 | 1 | 21 | 7 | A | 7 | 1 | A | 7 | 16.1 | 60.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.44 | A | 7 | 982 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.32 | 6 | 0
1994-02-17 | 1900-02-16 | 14:00 | 14 | 843 | 1401 | 583 | 1 | 10 | 772 | 1 | 16 | 118 | 1 | 10 | 60600 | 1 | 10 | 76600 | 1 | 16 | 14400 | 1 | 10 | 2620 | 1 | 21 | 8 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 4.4 | 39.92 | A | 7 | 0.41 | A | 7 | 981 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.62 | 6 | 0
1994-02-17 | 1900-02-16 | 15:00 | 15 | 741 | 1401 | 461 | 1 | 10 | 398 | 1 | 16 | 250 | 1 | 10 | 48900 | 1 | 10 | 41500 | 1 | 16 | 26900 | 1 | 10 | 5970 | 1 | 21 | 10 | A | 7 | 4 | A | 7 | 17.8 | 64.04 | A | 7 | 5 | 41 | A | 7 | 0.43 | A | 7 | 980 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 33.2 | 6 | 0
1994-02-17 | 1900-02-16 | 16:00 | 16 | 576 | 1401 | 308 | 1 | 10 | 446 | 1 | 16 | 124 | 1 | 10 | 32800 | 1 | 10 | 43100 | 1 | 16 | 14900 | 1 | 10 | 2420 | 1 | 21 | 10 | A | 7 | 4 | A | 7 | 18.3 | 64.94 | A | 7 | 4.4 | 39.92 | A | 7 | 0.4 | A | 7 | 979 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.42 | 6 | 0
1994-02-17 | 1900-02-16 | 17:00 | 17 | 360 | 1401 | 189 | 1 | 10 | 394 | 1 | 16 | 88 | 1 | 10 | 19700 | 1 | 10 | 32900 | 1 | 16 | 11200 | 1 | 10 | 1630 | 1 | 21 | 10 | A | 7 | 4 | A | 7 | 16.1 | 60.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.46 | A | 7 | 979 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 32.72 | 6 | 0
1994-02-17 | 1900-02-16 | 18:00 | 18 | 111 | 1319 | 27 | 1 | 10 | 23 | 1 | 16 | 25 | 1 | 10 | 3000 | 1 | 10 | 1400 | 1 | 16 | 2800 | 1 | 10 | 620 | 1 | 21 | 10 | A | 7 | 6 | A | 7 | 13.9 | 57.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 33.72 | 6 | 0
1994-02-17 | 1900-02-16 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 14.4 | 57.92 | A | 7 | 5 | 41 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 34.6 | 6 | 0
1994-02-17 | 1900-02-16 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 13.9 | 57.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 36.08 | 6 | 0
1994-02-17 | 1900-02-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 5 | A | 7 | 13.9 | 57.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 36.08 | 6 | 0
1994-02-17 | 1900-02-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 13.9 | 57.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 36.08 | 6 | 0
1994-02-17 | 1900-02-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 13.9 | 57.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 36.08 | 6 | 0
1994-02-17 | 1900-02-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 13.3 | 55.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.6 | A | 7 | 978 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.088 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 36.58 | 6 | 0
1994-02-18 | 1900-02-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 12.2 | 53.96 | A | 7 | 5 | 41 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 150 | A | 7 | 7.2 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 35.8 | 7 | 0
1994-02-18 | 1900-02-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 7 | A | 7 | 12.8 | 55.04 | A | 7 | 5 | 41 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 35.5 | 7 | 0
1994-02-18 | 1900-02-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 12.2 | 53.96 | A | 7 | 3.9 | 39.02 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 33.52 | 7 | 0
1994-02-18 | 1900-02-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 5 | A | 7 | 11.7 | 53.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.56 | A | 7 | 977 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 32.44 | 7 | 0
1994-02-18 | 1900-02-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.58 | A | 7 | 977 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.64 | 7 | 0
1994-02-18 | 1900-02-17 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 10.6 | 51.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.58 | A | 7 | 977 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.64 | 7 | 0
1994-02-18 | 1900-02-17 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 10 | 50 | A | 7 | 2.8 | 37.04 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 32.24 | 7 | 0
1994-02-18 | 1900-02-17 | 8:00 | 8 | 93 | 1202 | 22 | 1 | 10 | 3 | 1 | 16 | 22 | 1 | 10 | 2500 | 1 | 10 | 0 | 1 | 16 | 2500 | 1 | 10 | 760 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 11.1 | 51.98 | A | 7 | 2.8 | 37.04 | A | 7 | 0.57 | A | 7 | 976 | A | 7 | 160 | A | 7 | 9.3 | A | 7 | 19200 | A | 7 | 3658 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.44 | 7 | 0
1994-02-18 | 1900-02-17 | 9:00 | 9 | 341 | 1400 | 71 | 1 | 10 | 0 | 1 | 16 | 71 | 1 | 10 | 8100 | 1 | 10 | 0 | 1 | 16 | 8100 | 1 | 10 | 2650 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 2.8 | 37.04 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 19200 | A | 7 | 4572 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.14 | 7 | 0
1994-02-18 | 1900-02-17 | 10:00 | 10 | 562 | 1400 | 121 | 1 | 10 | 0 | 1 | 16 | 121 | 1 | 10 | 13900 | 1 | 10 | 0 | 1 | 16 | 13900 | 1 | 10 | 4930 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.51 | A | 7 | 975 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 19200 | A | 7 | 4572 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 32.72 | 7 | 0
1994-02-18 | 1900-02-17 | 11:00 | 11 | 733 | 1400 | 191 | 1 | 10 | 42 | 1 | 16 | 169 | 1 | 10 | 21100 | 1 | 10 | 4200 | 1 | 16 | 18900 | 1 | 10 | 5430 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 15 | 59 | A | 7 | 5 | 41 | A | 7 | 0.51 | A | 7 | 975 | A | 7 | 160 | A | 7 | 13.4 | A | 7 | 19200 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 34.4 | 7 | 0
1994-02-18 | 1900-02-17 | 12:00 | 12 | 842 | 1400 | 395 | 1 | 10 | 288 | 1 | 16 | 221 | 1 | 10 | 42900 | 1 | 10 | 30700 | 1 | 16 | 24400 | 1 | 10 | 5400 | 1 | 21 | 7 | A | 7 | 7 | A | 7 | 16.7 | 62.06 | A | 7 | 5 | 41 | A | 7 | 0.46 | A | 7 | 974 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 33.6 | 7 | 0
1994-02-18 | 1900-02-17 | 13:00 | 13 | 882 | 1400 | 172 | 1 | 10 | 35 | 1 | 16 | 150 | 1 | 10 | 19100 | 1 | 10 | 3500 | 1 | 16 | 16900 | 1 | 10 | 5440 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 4.4 | 39.92 | A | 7 | 0.41 | A | 7 | 972 | A | 7 | 160 | A | 7 | 12.4 | A | 7 | 9600 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.62 | 7 | 0
1994-02-18 | 1900-02-17 | 14:00 | 14 | 849 | 1400 | 245 | 1 | 10 | 64 | 1 | 16 | 205 | 1 | 10 | 26900 | 1 | 10 | 6400 | 1 | 16 | 23000 | 1 | 10 | 6980 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 5 | 41 | A | 7 | 0.43 | A | 7 | 971 | A | 7 | 170 | A | 7 | 14.4 | A | 7 | 9600 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 33.2 | 7 | 0
1994-02-18 | 1900-02-17 | 15:00 | 15 | 747 | 1400 | 438 | 1 | 10 | 243 | 1 | 16 | 308 | 1 | 10 | 46900 | 1 | 10 | 24900 | 1 | 16 | 33600 | 1 | 10 | 7880 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 17.2 | 62.96 | A | 7 | 5 | 41 | A | 7 | 0.44 | A | 7 | 970 | A | 7 | 170 | A | 7 | 12.9 | A | 7 | 9600 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 33.3 | 7 | 0
1994-02-18 | 1900-02-17 | 16:00 | 16 | 582 | 1400 | 201 | 1 | 10 | 221 | 1 | 16 | 109 | 1 | 10 | 22100 | 1 | 10 | 22200 | 1 | 16 | 12900 | 1 | 10 | 2150 | 1 | 21 | 6 | A | 7 | 6 | A | 7 | 17.8 | 64.04 | A | 7 | 5 | 41 | A | 7 | 0.43 | A | 7 | 970 | A | 7 | 160 | A | 7 | 14.9 | A | 7 | 9600 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 33.2 | 7 | 0
1994-02-18 | 1900-02-17 | 17:00 | 17 | 366 | 1400 | 171 | 1 | 10 | 310 | 1 | 16 | 90 | 1 | 10 | 17800 | 1 | 10 | 26100 | 1 | 16 | 11000 | 1 | 10 | 1670 | 1 | 21 | 5 | A | 7 | 1 | A | 7 | 17.2 | 62.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.46 | A | 7 | 969 | A | 7 | 170 | A | 7 | 13.4 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 34.48 | 7 | 0
1994-02-18 | 1900-02-17 | 18:00 | 18 | 116 | 1342 | 28 | 1 | 10 | 0 | 1 | 16 | 28 | 1 | 10 | 3100 | 1 | 10 | 0 | 1 | 16 | 3100 | 1 | 10 | 940 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.5 | A | 7 | 969 | A | 7 | 170 | A | 7 | 12.9 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 35.88 | 7 | 0
1994-02-18 | 1900-02-17 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 16.1 | 60.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.51 | A | 7 | 969 | A | 7 | 170 | A | 7 | 10.8 | A | 7 | 24000 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 35.98 | 7 | 0
1994-02-18 | 1900-02-17 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 6 | A | 7 | 15.6 | 60.08 | A | 7 | 6.1 | 42.98 | A | 7 | 0.53 | A | 7 | 970 | A | 7 | 170 | A | 7 | 11.3 | A | 7 | 32000 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 36.28 | 7 | 0
1994-02-18 | 1900-02-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.51 | A | 7 | 970 | A | 7 | 170 | A | 7 | 11.8 | A | 7 | 32000 | A | 7 | 1463 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 35.98 | 7 | 0
1994-02-18 | 1900-02-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.54 | A | 7 | 970 | A | 7 | 170 | A | 7 | 13.4 | A | 7 | 24000 | A | 7 | 1433 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 37.36 | 7 | 0
1994-02-18 | 1900-02-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 15.6 | 60.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.57 | A | 7 | 969 | A | 7 | 170 | A | 7 | 11.8 | A | 7 | 32000 | A | 7 | 1829 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 38.66 | 7 | 0
1994-02-18 | 1900-02-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 15 | 59 | A | 7 | 7.2 | 44.96 | A | 7 | 0.6 | A | 7 | 969 | A | 7 | 170 | A | 7 | 9.8 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 39.06 | 7 | 0
1994-02-19 | 1900-02-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 7.8 | 46.04 | A | 7 | 0.62 | A | 7 | 970 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 32000 | A | 7 | 1676 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 40.34 | 1 | 0
1994-02-19 | 1900-02-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 7.8 | 46.04 | A | 7 | 0.62 | A | 7 | 970 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 1280 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 40.34 | 1 | 0
1994-02-19 | 1900-02-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.62 | A | 7 | 970 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 32000 | A | 7 | 1280 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 41.14 | 1 | 0
1994-02-19 | 1900-02-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.62 | A | 7 | 970 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 32000 | A | 7 | 1280 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 41.14 | 1 | 0
1994-02-19 | 1900-02-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.64 | A | 7 | 969 | A | 7 | 160 | A | 7 | 11.3 | A | 7 | 32000 | A | 7 | 2134 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 42.42 | 1 | 0
1994-02-19 | 1900-02-18 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.69 | A | 7 | 970 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 32000 | A | 7 | 945 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45 | 1 | 0
1994-02-19 | 1900-02-18 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.69 | A | 7 | 970 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 32000 | A | 7 | 945 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45 | 1 | 0
1994-02-19 | 1900-02-18 | 8:00 | 8 | 98 | 1225 | 17 | 1 | 10 | 0 | 1 | 16 | 17 | 1 | 10 | 2000 | 1 | 10 | 0 | 1 | 16 | 2000 | 1 | 10 | 620 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 32000 | A | 7 | 3658 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.08 | 1 | 0
1994-02-19 | 1900-02-18 | 9:00 | 9 | 348 | 1400 | 63 | 1 | 10 | 0 | 1 | 16 | 63 | 1 | 10 | 7300 | 1 | 10 | 0 | 1 | 16 | 7300 | 1 | 10 | 2440 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 32000 | A | 7 | 884 | A | 7 | 1.5 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.08 | 1 | 0
1994-02-19 | 1900-02-18 | 10:00 | 10 | 569 | 1400 | 116 | 1 | 10 | 0 | 1 | 16 | 116 | 1 | 10 | 13400 | 1 | 10 | 0 | 1 | 16 | 13400 | 1 | 10 | 4800 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 972 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 32000 | A | 7 | 701 | A | 7 | 1.5 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.28 | 1 | 0
1994-02-19 | 1900-02-18 | 11:00 | 11 | 740 | 1400 | 159 | 1 | 10 | 0 | 1 | 16 | 159 | 1 | 10 | 18500 | 1 | 10 | 0 | 1 | 16 | 18500 | 1 | 10 | 6940 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.8 | A | 7 | 972 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 32000 | A | 7 | 549 | A | 7 | 1.5 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.56 | 1 | 0
1994-02-19 | 1900-02-18 | 12:00 | 12 | 849 | 1400 | 186 | 1 | 10 | 0 | 1 | 16 | 186 | 1 | 10 | 21800 | 1 | 10 | 0 | 1 | 16 | 21800 | 1 | 10 | 8380 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 12.8 | 55.04 | A | 7 | 0.87 | A | 7 | 972 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 427 | A | 7 | 1.5 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.74 | 1 | 0
1994-02-19 | 1900-02-18 | 13:00 | 13 | 888 | 1400 | 164 | 1 | 10 | 0 | 1 | 16 | 164 | 1 | 10 | 19600 | 1 | 10 | 0 | 1 | 16 | 19600 | 1 | 10 | 7740 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 12.8 | 55.04 | A | 7 | 0.87 | A | 7 | 972 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 396 | A | 7 | 1.4 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.74 | 1 | 0
1994-02-19 | 1900-02-18 | 14:00 | 14 | 856 | 1400 | 158 | 1 | 10 | 0 | 1 | 16 | 158 | 1 | 10 | 18800 | 1 | 10 | 0 | 1 | 16 | 18800 | 1 | 10 | 7390 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 12.8 | 55.04 | A | 7 | 0.87 | A | 7 | 971 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 366 | A | 7 | 1.4 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.74 | 1 | 0
1994-02-19 | 1900-02-18 | 15:00 | 15 | 753 | 1400 | 136 | 1 | 10 | 0 | 1 | 16 | 136 | 1 | 10 | 16100 | 1 | 10 | 0 | 1 | 16 | 16100 | 1 | 10 | 6180 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 12.8 | 55.04 | A | 7 | 0.87 | A | 7 | 971 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 335 | A | 7 | 1.4 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.74 | 1 | 0
1994-02-19 | 1900-02-18 | 16:00 | 16 | 588 | 1400 | 101 | 1 | 10 | 0 | 1 | 16 | 101 | 1 | 10 | 11900 | 1 | 10 | 0 | 1 | 16 | 11900 | 1 | 10 | 4360 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 971 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 11200 | A | 7 | 335 | A | 7 | 1.4 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.14 | 1 | 0
1994-02-19 | 1900-02-18 | 17:00 | 17 | 371 | 1400 | 57 | 1 | 10 | 0 | 1 | 16 | 57 | 1 | 10 | 6700 | 1 | 10 | 0 | 1 | 16 | 6700 | 1 | 10 | 2300 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.96 | A | 7 | 971 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 19200 | A | 7 | 335 | A | 7 | 1.3 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.24 | 1 | 0
1994-02-19 | 1900-02-18 | 18:00 | 18 | 121 | 1365 | 14 | 1 | 10 | 0 | 1 | 16 | 14 | 1 | 10 | 1700 | 1 | 10 | 0 | 1 | 16 | 1700 | 1 | 10 | 540 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 971 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 396 | A | 7 | 1.3 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 55.84 | 1 | 0
1994-02-19 | 1900-02-18 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 10 | 50 | A | 7 | 0.93 | A | 7 | 972 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 9600 | A | 7 | 1524 | A | 7 | 1.3 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 4 | 1 | A | 7 | 48.9 | 1 | 0
1994-02-19 | 1900-02-18 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 973 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 1829 | A | 7 | 1.3 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 46.84 | 1 | 0
1994-02-19 | 1900-02-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 973 | A | 7 | 10 | A | 7 | 1.5 | A | 7 | 4800 | A | 7 | 1981 | A | 7 | 1.2 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 46.84 | 1 | 0
1994-02-19 | 1900-02-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 972 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 3200 | A | 7 | 61 | A | 7 | 1.2 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.86 | 1 | 0
1994-02-19 | 1900-02-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.97 | A | 7 | 973 | A | 7 | 30 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 122 | A | 7 | 1.2 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 41.68 | 1 | 0
1994-02-19 | 1900-02-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 4.4 | 39.92 | A | 7 | 0.96 | A | 7 | 976 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 152 | A | 7 | 1.2 | E | 8 | 0.089 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 39.32 | 1 | 0
1994-02-20 | 1900-02-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 183 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 36.14 | 2 | 0
1994-02-20 | 1900-02-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 978 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 183 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 34.16 | 2 | 0
1994-02-20 | 1900-02-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.96 | A | 7 | 978 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 4000 | A | 7 | 152 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 33.48 | 2 | 0
1994-02-20 | 1900-02-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 1.1 | 33.98 | A | 7 | 1 | A | 7 | 979 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 4000 | A | 7 | 91 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 33.88 | 2 | 0
1994-02-20 | 1900-02-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 4000 | A | 7 | 91 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 32.58 | 2 | 0
1994-02-20 | 1900-02-19 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.95 | A | 7 | 981 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 4000 | A | 7 | 152 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 30.32 | 2 | 0
1994-02-20 | 1900-02-19 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.95 | A | 7 | 981 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 91 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 30.32 | 2 | 0
1994-02-20 | 1900-02-19 | 8:00 | 8 | 103 | 1271 | 11 | 1 | 10 | 0 | 1 | 16 | 11 | 1 | 10 | 1300 | 1 | 10 | 0 | 1 | 16 | 1300 | 1 | 10 | 430 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.95 | A | 7 | 983 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 2400 | A | 7 | 91 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 30.32 | 2 | 0
1994-02-20 | 1900-02-19 | 9:00 | 9 | 354 | 1399 | 49 | 1 | 10 | 0 | 1 | 16 | 49 | 1 | 10 | 5800 | 1 | 10 | 0 | 1 | 16 | 5800 | 1 | 10 | 2000 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.95 | A | 7 | 983 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 2400 | A | 7 | 122 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 30.32 | 2 | 0
1994-02-20 | 1900-02-19 | 10:00 | 10 | 575 | 1399 | 87 | 1 | 10 | 0 | 1 | 16 | 87 | 1 | 10 | 10300 | 1 | 10 | 0 | 1 | 16 | 10300 | 1 | 10 | 3820 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.91 | A | 7 | 984 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 4000 | A | 7 | 122 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 29.92 | 2 | 0
1994-02-20 | 1900-02-19 | 11:00 | 11 | 746 | 1399 | 116 | 1 | 10 | 0 | 1 | 16 | 116 | 1 | 10 | 13900 | 1 | 10 | 0 | 1 | 16 | 13900 | 1 | 10 | 5400 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.91 | A | 7 | 985 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 4000 | A | 7 | 122 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 29.92 | 2 | 0
1994-02-20 | 1900-02-19 | 12:00 | 12 | 855 | 1399 | 135 | 1 | 10 | 0 | 1 | 16 | 135 | 1 | 10 | 16300 | 1 | 10 | 0 | 1 | 16 | 16300 | 1 | 10 | 6480 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 4000 | A | 7 | 91 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.1 | 2 | 0
1994-02-20 | 1900-02-19 | 13:00 | 13 | 895 | 1399 | 142 | 1 | 10 | 0 | 1 | 16 | 142 | 1 | 10 | 17100 | 1 | 10 | 0 | 1 | 16 | 17100 | 1 | 10 | 6890 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 4000 | A | 7 | 122 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.1 | 2 | 0
1994-02-20 | 1900-02-19 | 14:00 | 14 | 862 | 1399 | 136 | 1 | 10 | 0 | 1 | 16 | 136 | 1 | 10 | 16400 | 1 | 10 | 0 | 1 | 16 | 16400 | 1 | 10 | 6540 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 152 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.1 | 2 | 0
1994-02-20 | 1900-02-19 | 15:00 | 15 | 759 | 1399 | 142 | 1 | 10 | 0 | 1 | 16 | 142 | 1 | 10 | 16800 | 1 | 10 | 0 | 1 | 16 | 16800 | 1 | 10 | 6430 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 0 | 32 | A | 7 | 0.88 | A | 7 | 984 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 213 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 30.7 | 2 | 0
1994-02-20 | 1900-02-19 | 16:00 | 16 | 594 | 1399 | 108 | 1 | 10 | 0 | 1 | 16 | 108 | 1 | 10 | 12600 | 1 | 10 | 0 | 1 | 16 | 12600 | 1 | 10 | 4630 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.84 | A | 7 | 985 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 9600 | A | 7 | 274 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 29.22 | 2 | 0
1994-02-20 | 1900-02-19 | 17:00 | 17 | 377 | 1399 | 63 | 1 | 10 | 0 | 1 | 16 | 63 | 1 | 10 | 7300 | 1 | 10 | 0 | 1 | 16 | 7300 | 1 | 10 | 2510 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.84 | A | 7 | 985 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 11200 | A | 7 | 335 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 29.22 | 2 | 0
1994-02-20 | 1900-02-19 | 18:00 | 18 | 126 | 1387 | 16 | 1 | 10 | 0 | 1 | 16 | 16 | 1 | 10 | 1900 | 1 | 10 | 0 | 1 | 16 | 1900 | 1 | 10 | 610 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.87 | A | 7 | 986 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 335 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.72 | 2 | 0
1994-02-20 | 1900-02-19 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.83 | A | 7 | 987 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 366 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.24 | 2 | 0
1994-02-20 | 1900-02-19 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.87 | A | 7 | 988 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 305 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.64 | 2 | 0
1994-02-20 | 1900-02-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.83 | A | 7 | 988 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 11200 | A | 7 | 488 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.44 | 2 | 0
1994-02-20 | 1900-02-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.83 | A | 7 | 988 | A | 7 | 10 | A | 7 | 1.5 | A | 7 | 12800 | A | 7 | 518 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.44 | 2 | 0
1994-02-20 | 1900-02-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.83 | A | 7 | 988 | A | 7 | 20 | A | 7 | 2.1 | A | 7 | 12800 | A | 7 | 671 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.44 | 2 | 0
1994-02-20 | 1900-02-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.83 | A | 7 | 988 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 12800 | A | 7 | 640 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.44 | 2 | 0
1994-02-21 | 1900-02-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.83 | A | 7 | 989 | A | 7 | 320 | A | 7 | 1.5 | A | 7 | 11200 | A | 7 | 640 | A | 7 | 0.8 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 25.36 | 3 | 0
1994-02-21 | 1900-02-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | -1.1 | 30.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.83 | A | 7 | 989 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.46 | 3 | 0
1994-02-21 | 1900-02-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.87 | A | 7 | 989 | A | 7 | 20 | A | 7 | 2.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.78 | 3 | 0
1994-02-21 | 1900-02-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.87 | A | 7 | 990 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.98 | 3 | 0
1994-02-21 | 1900-02-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.82 | A | 7 | 990 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.42 | 3 | 0
1994-02-21 | 1900-02-20 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.82 | A | 7 | 991 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.42 | 3 | 0
1994-02-21 | 1900-02-20 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.86 | A | 7 | 991 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.82 | 3 | 0
1994-02-21 | 1900-02-20 | 8:00 | 8 | 108 | 1293 | 37 | 1 | 10 | 84 | 1 | 16 | 30 | 1 | 10 | 4000 | 1 | 10 | 3700 | 1 | 16 | 3600 | 1 | 10 | 540 | 1 | 21 | 6 | A | 7 | 3 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.82 | A | 7 | 991 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.42 | 3 | 0
1994-02-21 | 1900-02-20 | 9:00 | 9 | 360 | 1398 | 178 | 1 | 10 | 122 | 1 | 16 | 146 | 1 | 10 | 18800 | 1 | 10 | 10400 | 1 | 16 | 16100 | 1 | 10 | 3210 | 1 | 21 | 9 | A | 7 | 7 | A | 7 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 991 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.92 | 3 | 0
1994-02-21 | 1900-02-20 | 10:00 | 10 | 582 | 1398 | 294 | 1 | 10 | 192 | 1 | 16 | 214 | 1 | 10 | 31600 | 1 | 10 | 18900 | 1 | 16 | 23700 | 1 | 10 | 5060 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 991 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 19200 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.72 | 3 | 0
1994-02-21 | 1900-02-20 | 11:00 | 11 | 753 | 1398 | 336 | 1 | 10 | 189 | 1 | 16 | 235 | 1 | 10 | 36800 | 1 | 10 | 19600 | 1 | 16 | 26200 | 1 | 10 | 6030 | 1 | 21 | 10 | A | 7 | 7 | A | 7 | -0.6 | 30.92 | A | 7 | -5 | 23 | A | 7 | 0.69 | A | 7 | 991 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 19200 | A | 7 | 457 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.4 | 3 | 0
1994-02-21 | 1900-02-20 | 12:00 | 12 | 862 | 1398 | 384 | 1 | 10 | 107 | 1 | 16 | 317 | 1 | 10 | 42100 | 1 | 10 | 10900 | 1 | 16 | 35300 | 1 | 10 | 10020 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | -0.6 | 30.92 | A | 7 | -5 | 23 | A | 7 | 0.69 | A | 7 | 992 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 19200 | A | 7 | 518 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.4 | 3 | 0
1994-02-21 | 1900-02-20 | 13:00 | 13 | 901 | 1398 | 324 | 1 | 10 | 70 | 1 | 16 | 279 | 1 | 10 | 35700 | 1 | 10 | 7100 | 1 | 16 | 31100 | 1 | 10 | 9410 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 1.1 | 33.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.64 | A | 7 | 991 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19200 | A | 7 | 518 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.98 | 3 | 0
1994-02-21 | 1900-02-20 | 14:00 | 14 | 868 | 1398 | 235 | 1 | 10 | 13 | 1 | 16 | 226 | 1 | 10 | 27100 | 1 | 10 | 1100 | 1 | 16 | 26500 | 1 | 10 | 9810 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 1.7 | 35.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 990 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 19200 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.78 | 3 | 0
1994-02-21 | 1900-02-20 | 15:00 | 15 | 765 | 1398 | 254 | 1 | 10 | 82 | 1 | 16 | 209 | 1 | 10 | 28000 | 1 | 10 | 8200 | 1 | 16 | 23400 | 1 | 10 | 6640 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 1.7 | 35.06 | A | 7 | -3.3 | 26.06 | A | 7 | 0.67 | A | 7 | 989 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 19200 | A | 7 | 6096 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.06 | 3 | 0
1994-02-21 | 1900-02-20 | 16:00 | 16 | 599 | 1398 | 151 | 1 | 10 | 0 | 1 | 16 | 151 | 1 | 10 | 17200 | 1 | 10 | 0 | 1 | 16 | 17200 | 1 | 10 | 5990 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 988 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 19200 | A | 7 | 4572 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.08 | 3 | 0
1994-02-21 | 1900-02-20 | 17:00 | 17 | 382 | 1398 | 78 | 1 | 10 | 45 | 1 | 16 | 65 | 1 | 10 | 8500 | 1 | 10 | 3900 | 1 | 16 | 7400 | 1 | 10 | 1830 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 988 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 19200 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.08 | 3 | 0
1994-02-21 | 1900-02-20 | 18:00 | 18 | 131 | 1398 | 24 | 1 | 10 | 0 | 1 | 16 | 24 | 1 | 10 | 2700 | 1 | 10 | 0 | 1 | 16 | 2700 | 1 | 10 | 850 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.69 | A | 7 | 988 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.28 | 3 | 0
1994-02-21 | 1900-02-20 | 19:00 | 19 | 0 | 35 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -3.9 | 24.98 | A | 7 | 0.72 | A | 7 | 988 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 4572 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.48 | 3 | 0
1994-02-21 | 1900-02-20 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -3.3 | 26.06 | A | 7 | 0.76 | A | 7 | 987 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 24000 | A | 7 | 4572 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.86 | 3 | 0
1994-02-21 | 1900-02-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -3.3 | 26.06 | A | 7 | 0.76 | A | 7 | 987 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 24000 | A | 7 | 4572 | A | 7 | 1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.86 | 3 | 0
1994-02-21 | 1900-02-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.8 | 26.96 | A | 7 | 0.79 | A | 7 | 987 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 24000 | A | 7 | 4572 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.96 | 3 | 0
1994-02-21 | 1900-02-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 986 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 4572 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.66 | 3 | 0
1994-02-21 | 1900-02-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 985 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 4572 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.66 | 3 | 0
1994-02-22 | 1900-02-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 986 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 3658 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.66 | 4 | 0
1994-02-22 | 1900-02-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 984 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 2438 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.66 | 4 | 0
1994-02-22 | 1900-02-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.8 | A | 7 | 983 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 19200 | A | 7 | 2286 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.14 | 4 | 0
1994-02-22 | 1900-02-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.8 | A | 7 | 983 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 579 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.14 | 4 | 0
1994-02-22 | 1900-02-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.83 | A | 7 | 983 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 19200 | A | 7 | 2286 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.24 | 4 | 0
1994-02-22 | 1900-02-21 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 70 | A | 7 | 8.8 | A | 7 | 11200 | A | 7 | 2286 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.72 | 4 | 0
1994-02-22 | 1900-02-21 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.83 | A | 7 | 980 | A | 7 | 80 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 396 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.24 | 4 | 0
1994-02-22 | 1900-02-21 | 8:00 | 8 | 114 | 1316 | 15 | 1 | 10 | 0 | 1 | 16 | 15 | 1 | 10 | 1800 | 1 | 10 | 0 | 1 | 16 | 1800 | 1 | 10 | 570 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.95 | A | 7 | 979 | A | 7 | 60 | A | 7 | 8.2 | A | 7 | 1200 | A | 7 | 396 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 30.32 | 4 | 0
1994-02-22 | 1900-02-21 | 9:00 | 9 | 367 | 1398 | 62 | 1 | 10 | 0 | 1 | 16 | 62 | 1 | 10 | 7200 | 1 | 10 | 0 | 1 | 16 | 7200 | 1 | 10 | 2450 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.95 | A | 7 | 979 | A | 7 | 70 | A | 7 | 8.2 | A | 7 | 1200 | A | 7 | 396 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 30.32 | 4 | 0
1994-02-22 | 1900-02-21 | 10:00 | 10 | 588 | 1398 | 128 | 1 | 10 | 0 | 1 | 16 | 128 | 1 | 10 | 14800 | 1 | 10 | 0 | 1 | 16 | 14800 | 1 | 10 | 5260 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.91 | A | 7 | 978 | A | 7 | 70 | A | 7 | 8.8 | A | 7 | 3200 | A | 7 | 610 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 27.14 | 4 | 0
1994-02-22 | 1900-02-21 | 11:00 | 11 | 759 | 1398 | 170 | 1 | 10 | 0 | 1 | 16 | 170 | 1 | 10 | 19800 | 1 | 10 | 0 | 1 | 16 | 19800 | 1 | 10 | 7400 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.91 | A | 7 | 977 | A | 7 | 60 | A | 7 | 8.2 | A | 7 | 1200 | A | 7 | 701 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 27.14 | 4 | 0
1994-02-22 | 1900-02-21 | 12:00 | 12 | 868 | 1398 | 165 | 1 | 10 | 0 | 1 | 16 | 165 | 1 | 10 | 19600 | 1 | 10 | 0 | 1 | 16 | 19600 | 1 | 10 | 7710 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.88 | A | 7 | 976 | A | 7 | 60 | A | 7 | 7.7 | A | 7 | 4000 | A | 7 | 366 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 26.84 | 4 | 0
1994-02-22 | 1900-02-21 | 13:00 | 13 | 907 | 1398 | 173 | 1 | 10 | 0 | 1 | 16 | 173 | 1 | 10 | 20600 | 1 | 10 | 0 | 1 | 16 | 20600 | 1 | 10 | 8170 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.91 | A | 7 | 975 | A | 7 | 60 | A | 7 | 7.7 | A | 7 | 1600 | A | 7 | 244 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.04 | 4 | 0
1994-02-22 | 1900-02-21 | 14:00 | 14 | 874 | 1398 | 198 | 1 | 10 | 0 | 1 | 16 | 198 | 1 | 10 | 23200 | 1 | 10 | 0 | 1 | 16 | 23200 | 1 | 10 | 8930 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.91 | A | 7 | 974 | A | 7 | 60 | A | 7 | 5.7 | A | 7 | 2400 | A | 7 | 457 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.04 | 4 | 0
1994-02-22 | 1900-02-21 | 15:00 | 15 | 771 | 1398 | 173 | 1 | 10 | 0 | 1 | 16 | 173 | 1 | 10 | 20200 | 1 | 10 | 0 | 1 | 16 | 20200 | 1 | 10 | 7560 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.91 | A | 7 | 973 | A | 7 | 60 | A | 7 | 6.7 | A | 7 | 2400 | A | 7 | 457 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.04 | 4 | 0
1994-02-22 | 1900-02-21 | 16:00 | 16 | 605 | 1398 | 132 | 1 | 10 | 0 | 1 | 16 | 132 | 1 | 10 | 15200 | 1 | 10 | 0 | 1 | 16 | 15200 | 1 | 10 | 5460 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.91 | A | 7 | 973 | A | 7 | 70 | A | 7 | 6.2 | A | 7 | 2400 | A | 7 | 457 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.04 | 4 | 0
1994-02-22 | 1900-02-21 | 17:00 | 17 | 388 | 1398 | 66 | 1 | 10 | 0 | 1 | 16 | 66 | 1 | 10 | 7700 | 1 | 10 | 0 | 1 | 16 | 7700 | 1 | 10 | 2630 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 244 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 29.62 | 4 | 0
1994-02-22 | 1900-02-21 | 18:00 | 18 | 136 | 1398 | 15 | 1 | 10 | 0 | 1 | 16 | 15 | 1 | 10 | 1800 | 1 | 10 | 0 | 1 | 16 | 1800 | 1 | 10 | 580 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.95 | A | 7 | 973 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 2400 | A | 7 | 183 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.44 | 4 | 0
1994-02-22 | 1900-02-21 | 19:00 | 19 | 0 | 58 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.91 | A | 7 | 973 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 1600 | A | 7 | 1280 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 27.14 | 4 | 0
1994-02-22 | 1900-02-21 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.91 | A | 7 | 973 | A | 7 | 50 | A | 7 | 5.7 | A | 7 | 24000 | A | 7 | 366 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 26.06 | 4 | 0
1994-02-22 | 1900-02-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.87 | A | 7 | 973 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 366 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.78 | 4 | 0
1994-02-22 | 1900-02-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.87 | A | 7 | 973 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 335 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.98 | 4 | 0
1994-02-22 | 1900-02-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.91 | A | 7 | 973 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 4800 | A | 7 | 213 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.28 | 4 | 0
1994-02-22 | 1900-02-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.9 | A | 7 | 973 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 274 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.12 | 4 | 0
1994-02-23 | 1900-02-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.82 | A | 7 | 973 | A | 7 | 30 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 244 | A | 7 | 1.1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.54 | 5 | 0
1994-02-23 | 1900-02-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.86 | A | 7 | 973 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 244 | A | 7 | 1.1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.84 | 5 | 0
1994-02-23 | 1900-02-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.83 | A | 7 | 973 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 244 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.74 | 5 | 0
1994-02-23 | 1900-02-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.83 | A | 7 | 973 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 213 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.76 | 5 | 0
1994-02-23 | 1900-02-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.83 | A | 7 | 974 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 213 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.76 | 5 | 0
1994-02-23 | 1900-02-22 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.83 | A | 7 | 974 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 213 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.86 | 5 | 0
1994-02-23 | 1900-02-22 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.86 | A | 7 | 975 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 213 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.96 | 5 | 0
1994-02-23 | 1900-02-22 | 8:00 | 8 | 120 | 1362 | 16 | 1 | 10 | 0 | 1 | 16 | 16 | 1 | 10 | 1900 | 1 | 10 | 0 | 1 | 16 | 1900 | 1 | 10 | 600 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.91 | A | 7 | 976 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 274 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.26 | 5 | 0
1994-02-23 | 1900-02-22 | 9:00 | 9 | 373 | 1397 | 61 | 1 | 10 | 0 | 1 | 16 | 61 | 1 | 10 | 7100 | 1 | 10 | 0 | 1 | 16 | 7100 | 1 | 10 | 2440 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 518 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.16 | 5 | 0
1994-02-23 | 1900-02-22 | 10:00 | 10 | 595 | 1397 | 114 | 1 | 10 | 0 | 1 | 16 | 114 | 1 | 10 | 13300 | 1 | 10 | 0 | 1 | 16 | 13300 | 1 | 10 | 4840 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 320 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 610 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.48 | 5 | 0
1994-02-23 | 1900-02-22 | 11:00 | 11 | 766 | 1397 | 158 | 1 | 10 | 0 | 1 | 16 | 158 | 1 | 10 | 18500 | 1 | 10 | 0 | 1 | 16 | 18500 | 1 | 10 | 7030 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 610 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.2 | 5 | 0
1994-02-23 | 1900-02-22 | 12:00 | 12 | 874 | 1397 | 186 | 1 | 10 | 0 | 1 | 16 | 186 | 1 | 10 | 21900 | 1 | 10 | 0 | 1 | 16 | 21900 | 1 | 10 | 8510 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 320 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 549 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.2 | 5 | 0
1994-02-23 | 1900-02-22 | 13:00 | 13 | 914 | 1397 | 196 | 1 | 10 | 0 | 1 | 16 | 196 | 1 | 10 | 23200 | 1 | 10 | 0 | 1 | 16 | 23200 | 1 | 10 | 9050 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.02 | 5 | 0
1994-02-23 | 1900-02-22 | 14:00 | 14 | 880 | 1397 | 187 | 1 | 10 | 0 | 1 | 16 | 187 | 1 | 10 | 22100 | 1 | 10 | 0 | 1 | 16 | 22100 | 1 | 10 | 8570 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -10 | 14 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 330 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 884 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12 | 5 | 0
1994-02-23 | 1900-02-22 | 15:00 | 15 | 777 | 1397 | 161 | 1 | 10 | 0 | 1 | 16 | 161 | 1 | 10 | 18900 | 1 | 10 | 0 | 1 | 16 | 18900 | 1 | 10 | 7180 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -10 | 14 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 3200 | A | 7 | 762 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12 | 5 | 0
1994-02-23 | 1900-02-22 | 16:00 | 16 | 611 | 1397 | 118 | 1 | 10 | 0 | 1 | 16 | 118 | 1 | 10 | 13800 | 1 | 10 | 0 | 1 | 16 | 13800 | 1 | 10 | 5030 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -10 | 14 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 823 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12 | 5 | 0
1994-02-23 | 1900-02-22 | 17:00 | 17 | 393 | 1397 | 116 | 1 | 10 | 0 | 1 | 16 | 116 | 1 | 10 | 12900 | 1 | 10 | 0 | 1 | 16 | 12900 | 1 | 10 | 3970 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 1006 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.2 | 5 | 0
1994-02-23 | 1900-02-22 | 18:00 | 18 | 141 | 1397 | 38 | 1 | 10 | 18 | 1 | 16 | 36 | 1 | 10 | 4100 | 1 | 10 | 1200 | 1 | 16 | 4000 | 1 | 10 | 850 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 979 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24000 | A | 7 | 2286 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.22 | 5 | 0
1994-02-23 | 1900-02-22 | 19:00 | 19 | 0 | 81 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 10 | A | 7 | 7 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 980 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24000 | A | 7 | 853 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.22 | 5 | 0
1994-02-23 | 1900-02-22 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.34 | 5 | 0
1994-02-23 | 1900-02-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.54 | 5 | 0
1994-02-23 | 1900-02-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -9.4 | 15.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 671 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.84 | 5 | 0
1994-02-23 | 1900-02-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 579 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.72 | 5 | 0
1994-02-23 | 1900-02-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.58 | 5 | 0
1994-02-24 | 1900-02-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -13.9 | 6.98 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.98 | 6 | 0
1994-02-24 | 1900-02-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -14.4 | 6.08 | A | 7 | 0.86 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.38 | 6 | 0
1994-02-24 | 1900-02-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -15 | 5 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.2 | 6 | 0
1994-02-24 | 1900-02-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.4 | 6 | 0
1994-02-24 | 1900-02-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -15 | 5 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 170 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.5 | 6 | 0
1994-02-24 | 1900-02-23 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -12.2 | 10.04 | A | 7 | -13.9 | 6.98 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 170 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.28 | 6 | 0
1994-02-24 | 1900-02-23 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 4572 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.16 | 6 | 0
1994-02-24 | 1900-02-23 | 8:00 | 8 | 126 | 1385 | 23 | 1 | 10 | 0 | 1 | 16 | 23 | 1 | 10 | 2600 | 1 | 10 | 0 | 1 | 16 | 2600 | 1 | 10 | 820 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 4572 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.34 | 6 | 0
1994-02-24 | 1900-02-23 | 9:00 | 9 | 380 | 1396 | 84 | 1 | 10 | 0 | 1 | 16 | 84 | 1 | 10 | 9500 | 1 | 10 | 0 | 1 | 16 | 9500 | 1 | 10 | 3140 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 4572 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.74 | 6 | 0
1994-02-24 | 1900-02-23 | 10:00 | 10 | 601 | 1396 | 151 | 1 | 10 | 0 | 1 | 16 | 151 | 1 | 10 | 17200 | 1 | 10 | 0 | 1 | 16 | 17200 | 1 | 10 | 6010 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 4572 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.32 | 6 | 0
1994-02-24 | 1900-02-23 | 11:00 | 11 | 772 | 1396 | 205 | 1 | 10 | 0 | 1 | 16 | 205 | 1 | 10 | 23600 | 1 | 10 | 0 | 1 | 16 | 23600 | 1 | 10 | 8580 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 19200 | A | 7 | 4572 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 11.02 | 6 | 0
1994-02-24 | 1900-02-23 | 12:00 | 12 | 881 | 1396 | 240 | 1 | 10 | 0 | 1 | 16 | 240 | 1 | 10 | 27800 | 1 | 10 | 0 | 1 | 16 | 27800 | 1 | 10 | 10340 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -10.6 | 12.92 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 19200 | A | 7 | 4572 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.62 | 6 | 0
1994-02-24 | 1900-02-23 | 13:00 | 13 | 920 | 1396 | 252 | 1 | 10 | 0 | 1 | 16 | 252 | 1 | 10 | 29200 | 1 | 10 | 0 | 1 | 16 | 29200 | 1 | 10 | 10960 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -9.4 | 15.08 | A | 7 | 0.62 | A | 7 | 975 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 19200 | A | 7 | 4572 | A | 7 | 0.8 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.68 | 6 | 0
1994-02-24 | 1900-02-23 | 14:00 | 14 | 886 | 1396 | 242 | 1 | 10 | 0 | 1 | 16 | 242 | 1 | 10 | 28000 | 1 | 10 | 0 | 1 | 16 | 28000 | 1 | 10 | 10440 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 19200 | A | 7 | 3658 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.48 | 6 | 0
1994-02-24 | 1900-02-23 | 15:00 | 15 | 783 | 1396 | 209 | 1 | 10 | 0 | 1 | 16 | 209 | 1 | 10 | 24000 | 1 | 10 | 0 | 1 | 16 | 24000 | 1 | 10 | 8760 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.59 | A | 7 | 974 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 19200 | A | 7 | 3658 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.06 | 6 | 0
1994-02-24 | 1900-02-23 | 16:00 | 16 | 616 | 1396 | 178 | 1 | 10 | 81 | 1 | 16 | 142 | 1 | 10 | 19700 | 1 | 10 | 8200 | 1 | 16 | 16100 | 1 | 10 | 3410 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 19200 | A | 7 | 3658 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.34 | 6 | 0
1994-02-24 | 1900-02-23 | 17:00 | 17 | 399 | 1396 | 217 | 1 | 10 | 567 | 1 | 16 | 56 | 1 | 10 | 22900 | 1 | 10 | 49800 | 1 | 16 | 8700 | 1 | 10 | 1080 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.34 | 6 | 0
1994-02-24 | 1900-02-23 | 18:00 | 18 | 146 | 1396 | 61 | 1 | 10 | 318 | 1 | 16 | 27 | 1 | 10 | 6200 | 1 | 10 | 18300 | 1 | 16 | 4300 | 1 | 10 | 480 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.68 | A | 7 | 973 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.54 | 6 | 0
1994-02-24 | 1900-02-23 | 19:00 | 19 | 1 | 105 | 0 | 1 | 10 | 5 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -7.8 | 17.96 | A | 7 | 0.71 | A | 7 | 974 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.96 | 6 | 0
1994-02-24 | 1900-02-23 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.46 | 6 | 0
1994-02-24 | 1900-02-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.83 | A | 7 | 973 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.76 | 6 | 0
1994-02-24 | 1900-02-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.83 | A | 7 | 974 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 6096 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.74 | 6 | 0
1994-02-24 | 1900-02-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.82 | A | 7 | 971 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 24000 | A | 7 | 6096 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.54 | 6 | 0
1994-02-24 | 1900-02-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.79 | A | 7 | 972 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 24000 | A | 7 | 3048 | A | 7 | 1 | E | 8 | 0.092 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.34 | 6 | 0
1994-02-25 | 1900-02-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.79 | A | 7 | 972 | A | 7 | 70 | A | 7 | 2.1 | A | 7 | 24000 | A | 7 | 3962 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.34 | 7 | 0
1994-02-25 | 1900-02-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.82 | A | 7 | 974 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 24000 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.54 | 7 | 0
1994-02-25 | 1900-02-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.83 | A | 7 | 975 | A | 7 | 330 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 274 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.74 | 7 | 0
1994-02-25 | 1900-02-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 350 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 671 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.46 | 7 | 0
1994-02-25 | 1900-02-24 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 320 | A | 7 | 12.9 | A | 7 | 9600 | A | 7 | 457 | A | 7 | 1.1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.06 | 7 | 0
1994-02-25 | 1900-02-24 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 310 | A | 7 | 10.3 | A | 7 | 11200 | A | 7 | 2134 | A | 7 | 1.1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.54 | 7 | 0
1994-02-25 | 1900-02-24 | 7:00 | 7 | 0 | 35 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 7 | A | 7 | 7 | A | 7 | -10.6 | 12.92 | A | 7 | -13.9 | 6.98 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 290 | A | 7 | 9.8 | A | 7 | 11200 | A | 7 | 305 | A | 7 | 1.1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.78 | 7 | 0
1994-02-25 | 1900-02-24 | 8:00 | 8 | 132 | 1396 | 46 | 1 | 10 | 190 | 1 | 16 | 28 | 1 | 10 | 4800 | 1 | 10 | 9500 | 1 | 16 | 3900 | 1 | 10 | 500 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -11.1 | 12.02 | A | 7 | -16.1 | 3.02 | A | 7 | 0.63 | A | 7 | 983 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.52 | 7 | 0
1994-02-25 | 1900-02-24 | 9:00 | 9 | 386 | 1396 | 157 | 1 | 10 | 143 | 1 | 16 | 117 | 1 | 10 | 17000 | 1 | 10 | 12700 | 1 | 16 | 13400 | 1 | 10 | 2590 | 1 | 21 | 4 | A | 7 | 4 | A | 7 | -11.7 | 10.94 | A | 7 | -17.2 | 1.04 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 310 | A | 7 | 12.4 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.46 | 7 | 0
1994-02-25 | 1900-02-24 | 10:00 | 10 | 608 | 1396 | 407 | 1 | 10 | 744 | 1 | 16 | 83 | 1 | 10 | 42200 | 1 | 10 | 71300 | 1 | 16 | 11000 | 1 | 10 | 1650 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -18.9 | -2.02 | A | 7 | 0.51 | A | 7 | 986 | A | 7 | 300 | A | 7 | 13.4 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -3.62 | 7 | 0
1994-02-25 | 1900-02-24 | 11:00 | 11 | 779 | 1396 | 560 | 1 | 10 | 823 | 1 | 16 | 100 | 1 | 10 | 58600 | 1 | 10 | 81500 | 1 | 16 | 13000 | 1 | 10 | 2200 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -18.9 | -2.02 | A | 7 | 0.51 | A | 7 | 987 | A | 7 | 300 | A | 7 | 12.4 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -3.62 | 7 | 0
1994-02-25 | 1900-02-24 | 12:00 | 12 | 887 | 1396 | 557 | 1 | 10 | 616 | 1 | 16 | 165 | 1 | 10 | 58500 | 1 | 10 | 62000 | 1 | 16 | 19000 | 1 | 10 | 4080 | 1 | 21 | 5 | A | 7 | 3 | A | 7 | -11.1 | 12.02 | A | 7 | -18.3 | -0.94 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 310 | A | 7 | 12.4 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -2.54 | 7 | 0
1994-02-25 | 1900-02-24 | 13:00 | 13 | 926 | 1396 | 557 | 1 | 10 | 531 | 1 | 16 | 204 | 1 | 10 | 60100 | 1 | 10 | 55000 | 1 | 16 | 23500 | 1 | 10 | 5290 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | -10.6 | 12.92 | A | 7 | -17.2 | 1.04 | A | 7 | 0.55 | A | 7 | 988 | A | 7 | 300 | A | 7 | 11.8 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.56 | 7 | 0
1994-02-25 | 1900-02-24 | 14:00 | 14 | 893 | 1396 | 600 | 1 | 10 | 373 | 1 | 16 | 361 | 1 | 10 | 63300 | 1 | 10 | 39700 | 1 | 16 | 37800 | 1 | 10 | 10050 | 1 | 21 | 6 | A | 7 | 6 | A | 7 | -10 | 14 | A | 7 | -16.7 | 1.94 | A | 7 | 0.54 | A | 7 | 990 | A | 7 | 290 | A | 7 | 10.3 | A | 7 | 19200 | A | 7 | 1067 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.24 | 7 | 0
1994-02-25 | 1900-02-24 | 15:00 | 15 | 789 | 1396 | 559 | 1 | 10 | 815 | 1 | 16 | 98 | 1 | 10 | 58800 | 1 | 10 | 80900 | 1 | 16 | 12900 | 1 | 10 | 2200 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | -9.4 | 15.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.54 | A | 7 | 988 | A | 7 | 300 | A | 7 | 12.4 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.22 | 7 | 0
1994-02-25 | 1900-02-24 | 16:00 | 16 | 622 | 1396 | 370 | 1 | 10 | 517 | 1 | 16 | 139 | 1 | 10 | 39300 | 1 | 10 | 50800 | 1 | 16 | 16600 | 1 | 10 | 2790 | 1 | 21 | 3 | A | 7 | 3 | A | 7 | -8.9 | 15.98 | A | 7 | -16.1 | 3.02 | A | 7 | 0.52 | A | 7 | 989 | A | 7 | 300 | A | 7 | 11.3 | A | 7 | 19200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.12 | 7 | 0
1994-02-25 | 1900-02-24 | 17:00 | 17 | 404 | 1396 | 216 | 1 | 10 | 445 | 1 | 16 | 87 | 1 | 10 | 22800 | 1 | 10 | 38900 | 1 | 16 | 11500 | 1 | 10 | 1610 | 1 | 21 | 4 | A | 7 | 2 | A | 7 | -8.9 | 15.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.55 | A | 7 | 990 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 2.02 | 7 | 0
1994-02-25 | 1900-02-24 | 18:00 | 18 | 151 | 1396 | 43 | 1 | 10 | 73 | 1 | 16 | 35 | 1 | 10 | 4700 | 1 | 10 | 4200 | 1 | 16 | 4300 | 1 | 10 | 730 | 1 | 21 | 8 | A | 7 | 4 | A | 7 | -9.4 | 15.08 | A | 7 | -15.6 | 3.92 | A | 7 | 0.57 | A | 7 | 991 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 2.12 | 7 | 0
1994-02-25 | 1900-02-24 | 19:00 | 19 | 1 | 128 | 0 | 1 | 10 | 1 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 7 | A | 7 | 4 | A | 7 | -10 | 14 | A | 7 | -15.6 | 3.92 | A | 7 | 0.6 | A | 7 | 992 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 2.22 | 7 | 0
1994-02-25 | 1900-02-24 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 3 | A | 7 | -10.6 | 12.92 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 992 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 3.6 | 7 | 0
1994-02-25 | 1900-02-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 4 | A | 7 | -10.6 | 12.92 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 993 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 3.6 | 7 | 0
1994-02-25 | 1900-02-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -11.1 | 12.02 | A | 7 | -15 | 5 | A | 7 | 0.7 | A | 7 | 994 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 3.7 | 7 | 0
1994-02-25 | 1900-02-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -15 | 5 | A | 7 | 0.74 | A | 7 | 994 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 3.9 | 7 | 0
1994-02-25 | 1900-02-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -17.2 | 1.04 | A | 7 | 0.6 | A | 7 | 994 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.46 | 7 | 0
1994-02-26 | 1900-02-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -16.1 | 3.02 | A | 7 | 0.7 | A | 7 | 995 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.82 | 1 | 0
1994-02-26 | 1900-02-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -16.1 | 3.02 | A | 7 | 0.74 | A | 7 | 996 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.92 | 1 | 0
1994-02-26 | 1900-02-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -16.7 | 1.94 | A | 7 | 0.73 | A | 7 | 996 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.94 | 1 | 0
1994-02-26 | 1900-02-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -16.7 | 1.94 | A | 7 | 0.77 | A | 7 | 996 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.04 | 1 | 0
1994-02-26 | 1900-02-25 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.81 | A | 7 | 996 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 1.24 | 1 | 0
1994-02-26 | 1900-02-25 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -17.8 | -0.04 | A | 7 | 0.81 | A | 7 | 997 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | -0.74 | 1 | 0
1994-02-26 | 1900-02-25 | 7:00 | 7 | 0 | 58 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -15 | 5 | A | 7 | -17.2 | 1.04 | A | 7 | 0.81 | A | 7 | 997 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.34 | 1 | 0
1994-02-26 | 1900-02-25 | 8:00 | 8 | 139 | 1395 | 36 | 1 | 10 | 29 | 1 | 16 | 33 | 1 | 10 | 3900 | 1 | 10 | 1900 | 1 | 16 | 3700 | 1 | 10 | 790 | 1 | 21 | 6 | A | 7 | 6 | A | 7 | -13.3 | 8.06 | A | 7 | -16.7 | 1.94 | A | 7 | 0.73 | A | 7 | 997 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 3962 | A | 7 | 0.8 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 0.94 | 1 | 0
1994-02-26 | 1900-02-25 | 9:00 | 9 | 393 | 1395 | 136 | 1 | 10 | 55 | 1 | 16 | 120 | 1 | 10 | 14800 | 1 | 10 | 5000 | 1 | 16 | 13400 | 1 | 10 | 3060 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | -12.2 | 10.04 | A | 7 | -15.6 | 3.92 | A | 7 | 0.73 | A | 7 | 997 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 24000 | A | 7 | 3962 | A | 7 | 0.8 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 2.82 | 1 | 0
1994-02-26 | 1900-02-25 | 10:00 | 10 | 615 | 1395 | 204 | 1 | 10 | 164 | 1 | 16 | 131 | 1 | 10 | 22200 | 1 | 10 | 16600 | 1 | 16 | 14900 | 1 | 10 | 2680 | 1 | 21 | 7 | A | 7 | 7 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.71 | A | 7 | 998 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 24000 | A | 7 | 3962 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 4.78 | 1 | 0
1994-02-26 | 1900-02-25 | 11:00 | 11 | 785 | 1395 | 154 | 1 | 10 | 6 | 1 | 16 | 150 | 1 | 10 | 18100 | 1 | 10 | 400 | 1 | 16 | 17900 | 1 | 10 | 6830 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | -8.3 | 17.06 | A | 7 | -13.3 | 8.06 | A | 7 | 0.64 | A | 7 | 997 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 3962 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.26 | 1 | 0
1994-02-26 | 1900-02-25 | 12:00 | 12 | 894 | 1395 | 330 | 1 | 10 | 73 | 1 | 16 | 283 | 1 | 10 | 36300 | 1 | 10 | 7400 | 1 | 16 | 31500 | 1 | 10 | 9480 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -7.2 | 19.04 | A | 7 | -12.8 | 8.96 | A | 7 | 0.61 | A | 7 | 998 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 3962 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.96 | 1 | 0
1994-02-26 | 1900-02-25 | 13:00 | 13 | 933 | 1395 | 379 | 1 | 10 | 208 | 1 | 16 | 239 | 1 | 10 | 41500 | 1 | 10 | 22400 | 1 | 16 | 26400 | 1 | 10 | 6350 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | -5.6 | 21.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.53 | A | 7 | 997 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 3962 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.56 | 1 | 0
1994-02-26 | 1900-02-25 | 14:00 | 14 | 899 | 1395 | 448 | 1 | 10 | 383 | 1 | 16 | 201 | 1 | 10 | 48200 | 1 | 10 | 39600 | 1 | 16 | 22700 | 1 | 10 | 5040 | 1 | 21 | 7 | A | 7 | 5 | A | 7 | -3.9 | 24.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.48 | A | 7 | 995 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.34 | 1 | 0
1994-02-26 | 1900-02-25 | 15:00 | 15 | 795 | 1395 | 488 | 1 | 10 | 507 | 1 | 16 | 199 | 1 | 10 | 51700 | 1 | 10 | 51700 | 1 | 16 | 22200 | 1 | 10 | 4540 | 1 | 21 | 8 | A | 7 | 3 | A | 7 | -3.9 | 24.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.48 | A | 7 | 995 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.34 | 1 | 0
1994-02-26 | 1900-02-25 | 16:00 | 16 | 628 | 1395 | 335 | 1 | 10 | 449 | 1 | 16 | 133 | 1 | 10 | 35800 | 1 | 10 | 44200 | 1 | 16 | 15900 | 1 | 10 | 2660 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | -3.9 | 24.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.51 | A | 7 | 995 | A | 7 | 100 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.24 | 1 | 0
1994-02-26 | 1900-02-25 | 17:00 | 17 | 409 | 1395 | 113 | 1 | 10 | 121 | 1 | 16 | 77 | 1 | 10 | 12300 | 1 | 10 | 10900 | 1 | 16 | 9100 | 1 | 10 | 1430 | 1 | 21 | 6 | A | 7 | 6 | A | 7 | -4.4 | 24.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.53 | A | 7 | 994 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 3658 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.34 | 1 | 0
1994-02-26 | 1900-02-25 | 18:00 | 18 | 156 | 1395 | 52 | 1 | 10 | 120 | 1 | 16 | 38 | 1 | 10 | 5400 | 1 | 10 | 6300 | 1 | 16 | 4700 | 1 | 10 | 690 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | -5.6 | 21.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.59 | A | 7 | 994 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.74 | 1 | 0
1994-02-26 | 1900-02-25 | 19:00 | 19 | 1 | 151 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 4 | A | 7 | 4 | A | 7 | -6.1 | 21.02 | A | 7 | -11.7 | 10.94 | A | 7 | 0.61 | A | 7 | 994 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.84 | 1 | 0
1994-02-26 | 1900-02-25 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.64 | A | 7 | 994 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.94 | 1 | 0
1994-02-26 | 1900-02-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 994 | A | 7 | 90 | A | 7 | 1.5 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.34 | 1 | 0
1994-02-26 | 1900-02-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 994 | A | 7 | 70 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 9.54 | 1 | 0
1994-02-26 | 1900-02-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 994 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.54 | 1 | 0
1994-02-26 | 1900-02-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -13.9 | 6.98 | A | 7 | 0.64 | A | 7 | 993 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.093 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 5.28 | 1 | 0
1994-02-27 | 1900-02-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -8.9 | 15.98 | A | 7 | -13.3 | 8.06 | A | 7 | 0.67 | A | 7 | 993 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 6.46 | 2 | 0
1994-02-27 | 1900-02-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | -8.9 | 15.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 993 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.46 | 2 | 0
1994-02-27 | 1900-02-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 993 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.46 | 2 | 0
1994-02-27 | 1900-02-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.74 | A | 7 | 993 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.66 | 2 | 0
1994-02-27 | 1900-02-26 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -10 | 14 | A | 7 | -12.8 | 8.96 | A | 7 | 0.78 | A | 7 | 993 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.86 | 2 | 0
1994-02-27 | 1900-02-26 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -10 | 14 | A | 7 | -12.8 | 8.96 | A | 7 | 0.78 | A | 7 | 993 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 7.86 | 2 | 0
1994-02-27 | 1900-02-26 | 7:00 | 7 | 0 | 81 | 0 | 1 | 10 | 3 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.78 | A | 7 | 992 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 8.84 | 2 | 0
1994-02-27 | 1900-02-26 | 8:00 | 8 | 145 | 1394 | 53 | 1 | 10 | 93 | 1 | 16 | 43 | 1 | 10 | 5500 | 1 | 10 | 4600 | 1 | 16 | 5000 | 1 | 10 | 820 | 1 | 21 | 10 | A | 7 | 3 | A | 7 | -8.3 | 17.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.78 | A | 7 | 992 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 10.72 | 2 | 0
1994-02-27 | 1900-02-26 | 9:00 | 9 | 400 | 1394 | 216 | 1 | 10 | 453 | 1 | 16 | 86 | 1 | 10 | 22800 | 1 | 10 | 39500 | 1 | 16 | 11500 | 1 | 10 | 1580 | 1 | 21 | 9 | A | 7 | 1 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.71 | A | 7 | 992 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 12.2 | 2 | 0
1994-02-27 | 1900-02-26 | 10:00 | 10 | 621 | 1394 | 402 | 1 | 10 | 629 | 1 | 16 | 121 | 1 | 10 | 41600 | 1 | 10 | 60500 | 1 | 16 | 14600 | 1 | 10 | 2400 | 1 | 21 | 9 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -8.9 | 15.98 | A | 7 | 0.65 | A | 7 | 991 | A | 7 | 130 | A | 7 | 6.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 13.68 | 2 | 0
1994-02-27 | 1900-02-26 | 11:00 | 11 | 792 | 1394 | 545 | 1 | 10 | 696 | 1 | 16 | 149 | 1 | 10 | 57000 | 1 | 10 | 69300 | 1 | 16 | 17500 | 1 | 10 | 3350 | 1 | 21 | 10 | A | 7 | 2 | A | 7 | -2.2 | 28.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.59 | A | 7 | 991 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.26 | 2 | 0
1994-02-27 | 1900-02-26 | 12:00 | 12 | 900 | 1394 | 635 | 1 | 10 | 729 | 1 | 16 | 164 | 1 | 10 | 66900 | 1 | 10 | 73500 | 1 | 16 | 19300 | 1 | 10 | 4130 | 1 | 21 | 10 | A | 7 | 1 | A | 7 | 0 | 32 | A | 7 | -7.8 | 17.96 | A | 7 | 0.52 | A | 7 | 990 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 14.56 | 2 | 0
1994-02-27 | 1900-02-26 | 13:00 | 13 | 939 | 1394 | 557 | 1 | 10 | 570 | 1 | 16 | 173 | 1 | 10 | 58700 | 1 | 10 | 57600 | 1 | 16 | 19800 | 1 | 10 | 4570 | 1 | 21 | 10 | A | 7 | 2 | A | 7 | 1.7 | 35.06 | A | 7 | -7.2 | 19.04 | A | 7 | 0.48 | A | 7 | 989 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 15.24 | 2 | 0
1994-02-27 | 1900-02-26 | 14:00 | 14 | 905 | 1394 | 598 | 1 | 10 | 517 | 1 | 16 | 263 | 1 | 10 | 62800 | 1 | 10 | 53200 | 1 | 16 | 28100 | 1 | 10 | 6810 | 1 | 21 | 10 | A | 7 | 3 | A | 7 | 2.2 | 35.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.48 | A | 7 | 988 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 16.04 | 2 | 0
1994-02-27 | 1900-02-26 | 15:00 | 15 | 801 | 1394 | 497 | 1 | 10 | 618 | 1 | 16 | 142 | 1 | 10 | 52200 | 1 | 10 | 61800 | 1 | 16 | 16700 | 1 | 10 | 3240 | 1 | 21 | 10 | A | 7 | 5 | A | 7 | 2.2 | 35.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.51 | A | 7 | 987 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 17.22 | 2 | 0
1994-02-27 | 1900-02-26 | 16:00 | 16 | 633 | 1394 | 197 | 1 | 10 | 105 | 1 | 16 | 149 | 1 | 10 | 21800 | 1 | 10 | 10700 | 1 | 16 | 16900 | 1 | 10 | 3600 | 1 | 21 | 10 | A | 7 | 6 | A | 7 | 2.2 | 35.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.53 | A | 7 | 986 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 32000 | A | 7 | 6096 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 18.12 | 2 | 0
1994-02-27 | 1900-02-26 | 17:00 | 17 | 415 | 1394 | 92 | 1 | 10 | 0 | 1 | 16 | 92 | 1 | 10 | 10500 | 1 | 10 | 0 | 1 | 16 | 10500 | 1 | 10 | 3500 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.66 | A | 7 | 986 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 6096 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.18 | 2 | 0
1994-02-27 | 1900-02-26 | 18:00 | 18 | 161 | 1394 | 29 | 1 | 10 | 0 | 1 | 16 | 29 | 1 | 10 | 3300 | 1 | 10 | 0 | 1 | 16 | 3300 | 1 | 10 | 1040 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -5 | 23 | A | 7 | 0.66 | A | 7 | 985 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 6096 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.2 | 2 | 0
1994-02-27 | 1900-02-26 | 19:00 | 19 | 2 | 174 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -5 | 23 | A | 7 | 0.69 | A | 7 | 985 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 6096 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.4 | 2 | 0
1994-02-27 | 1900-02-26 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -5 | 23 | A | 7 | 0.72 | A | 7 | 985 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 32000 | A | 7 | 6096 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 20.7 | 2 | 0
1994-02-27 | 1900-02-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.68 | A | 7 | 986 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 32000 | A | 7 | 6096 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.32 | 2 | 0
1994-02-27 | 1900-02-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 985 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 6096 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.72 | 2 | 0
1994-02-27 | 1900-02-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.76 | A | 7 | 985 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 1524 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21 | 2 | 0
1994-02-27 | 1900-02-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 985 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 32000 | A | 7 | 1524 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.72 | 2 | 0
1994-02-28 | 1900-02-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 985 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 1463 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 19.72 | 3 | 0
1994-02-28 | 1900-02-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.76 | A | 7 | 984 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 32000 | A | 7 | 1433 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21 | 3 | 0
1994-02-28 | 1900-02-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.76 | A | 7 | 984 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 1311 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.98 | 3 | 0
1994-02-28 | 1900-02-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.76 | A | 7 | 984 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 1250 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.98 | 3 | 0
1994-02-28 | 1900-02-27 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.73 | A | 7 | 984 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32000 | A | 7 | 1250 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.78 | 3 | 0
1994-02-28 | 1900-02-27 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.73 | A | 7 | 984 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 975 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.78 | 3 | 0
1994-02-28 | 1900-02-27 | 7:00 | 7 | 1 | 128 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.73 | A | 7 | 984 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 19200 | A | 7 | 1067 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 21.78 | 3 | 0
1994-02-28 | 1900-02-27 | 8:00 | 8 | 152 | 1394 | 23 | 1 | 10 | 0 | 1 | 16 | 23 | 1 | 10 | 2700 | 1 | 10 | 0 | 1 | 16 | 2700 | 1 | 10 | 850 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -3.9 | 24.98 | A | 7 | 0.72 | A | 7 | 984 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 19200 | A | 7 | 1219 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 22.48 | 3 | 0
1994-02-28 | 1900-02-27 | 9:00 | 9 | 407 | 1394 | 80 | 1 | 10 | 0 | 1 | 16 | 80 | 1 | 10 | 9200 | 1 | 10 | 0 | 1 | 16 | 9200 | 1 | 10 | 3120 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.7 | A | 7 | 984 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 24000 | A | 7 | 1280 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.36 | 3 | 0
1994-02-28 | 1900-02-27 | 10:00 | 10 | 628 | 1394 | 135 | 1 | 10 | 0 | 1 | 16 | 135 | 1 | 10 | 15600 | 1 | 10 | 0 | 1 | 16 | 15600 | 1 | 10 | 5660 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 985 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 1829 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 24.16 | 3 | 0
1994-02-28 | 1900-02-27 | 11:00 | 11 | 799 | 1394 | 177 | 1 | 10 | 0 | 1 | 16 | 177 | 1 | 10 | 20700 | 1 | 10 | 0 | 1 | 16 | 20700 | 1 | 10 | 7840 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.68 | A | 7 | 984 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 32000 | A | 7 | 1341 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 23.96 | 3 | 0
1994-02-28 | 1900-02-27 | 12:00 | 12 | 907 | 1394 | 204 | 1 | 10 | 0 | 1 | 16 | 204 | 1 | 10 | 24000 | 1 | 10 | 0 | 1 | 16 | 24000 | 1 | 10 | 9320 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.84 | A | 7 | 984 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 1189 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 28.42 | 3 | 0
1994-02-28 | 1900-02-27 | 13:00 | 13 | 945 | 1394 | 214 | 1 | 10 | 0 | 1 | 16 | 214 | 1 | 10 | 25200 | 1 | 10 | 0 | 1 | 16 | 25200 | 1 | 10 | 9860 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 2400 | A | 7 | 1006 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.1 | 3 | 0
1994-02-28 | 1900-02-27 | 14:00 | 14 | 911 | 1394 | 143 | 1 | 10 | 0 | 1 | 16 | 143 | 1 | 10 | 17300 | 1 | 10 | 0 | 1 | 16 | 17300 | 1 | 10 | 6990 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 2400 | A | 7 | 152 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 32.58 | 3 | 0
1994-02-28 | 1900-02-27 | 15:00 | 15 | 806 | 1394 | 125 | 1 | 10 | 0 | 1 | 16 | 125 | 1 | 10 | 15000 | 1 | 10 | 0 | 1 | 16 | 15000 | 1 | 10 | 5940 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 2400 | A | 7 | 122 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 32.58 | 3 | 0
1994-02-28 | 1900-02-27 | 16:00 | 16 | 639 | 1394 | 96 | 1 | 10 | 0 | 1 | 16 | 96 | 1 | 10 | 11400 | 1 | 10 | 0 | 1 | 16 | 11400 | 1 | 10 | 4330 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 1200 | A | 7 | 122 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 31.5 | 3 | 0
1994-02-28 | 1900-02-27 | 17:00 | 17 | 420 | 1394 | 58 | 1 | 10 | 0 | 1 | 16 | 58 | 1 | 10 | 6900 | 1 | 10 | 0 | 1 | 16 | 6900 | 1 | 10 | 2430 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 400 | A | 7 | 122 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 4 | 1 | A | 7 | 31.5 | 3 | 0
1994-02-28 | 1900-02-27 | 18:00 | 18 | 166 | 1394 | 18 | 1 | 10 | 0 | 1 | 16 | 18 | 1 | 10 | 2100 | 1 | 10 | 0 | 1 | 16 | 2100 | 1 | 10 | 700 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 400 | A | 7 | 91 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 31.5 | 3 | 0
1994-02-28 | 1900-02-27 | 19:00 | 19 | 3 | 197 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 10 | 0 | 1 | 16 | 0 | 1 | 10 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 984 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 800 | A | 7 | 91 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.5 | 3 | 0
1994-02-28 | 1900-02-27 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 984 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 2400 | A | 7 | 122 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.9 | 3 | 0
1994-02-28 | 1900-02-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.95 | A | 7 | 985 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 152 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 30.32 | 3 | 0
1994-02-28 | 1900-02-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.2 | 32.36 | A | 7 | -0.3 | 31.46 | A | 7 | 0.95 | A | 7 | 985 | A | 7 | 60 | A | 7 | 4.5 | A | 7 | 3200 | A | 7 | 152 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 30.86 | 3 | 0
1994-02-28 | 1900-02-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.3 | 32.54 | A | 7 | -0.2 | 31.64 | A | 7 | 0.96 | A | 7 | 985 | A | 7 | 60 | A | 7 | 3.7 | A | 7 | 2000 | A | 7 | 183 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.14 | 3 | 0
1994-02-28 | 1900-02-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.5 | 32.9 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 985 | A | 7 | 60 | A | 7 | 3 | A | 7 | 1200 | A | 7 | 183 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 31.5 | 3 | 0
1982-03-01 | 1900-02-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | 0.1 | 32.18 | A | 7 | 0.86 | A | 7 | 990 | A | 7 | 270 | A | 7 | 2.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.68 | 4 | 0
1982-03-01 | 1900-02-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.8 | 33.44 | A | 7 | 0.3 | 32.54 | A | 7 | 0.85 | A | 7 | 990 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.84 | 4 | 0
1982-03-01 | 1900-02-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.9 | 33.62 | A | 7 | 0.4 | 32.72 | A | 7 | 0.92 | A | 7 | 989 | A | 7 | 280 | A | 7 | 0.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.82 | 4 | 0
1982-03-01 | 1900-02-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 4 | 0
1982-03-01 | 1900-02-28 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.96 | A | 7 | 990 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.54 | 4 | 0
1982-03-01 | 1900-02-28 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.54 | 4 | 0
1982-03-01 | 1900-02-28 | 7:00 | 7 | 1 | 151 | 2 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.56 | 4 | 0
1982-03-01 | 1900-02-28 | 8:00 | 8 | 157 | 1393 | 60 | 1 | 13 | 226 | 1 | 9 | 36 | 1 | 13 | 6400 | 1 | 13 | 12500 | 1 | 9 | 5000 | 1 | 13 | 640 | 1 | 21 | 4 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 990 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 4 | 0
1982-03-01 | 1900-02-28 | 9:00 | 9 | 413 | 1393 | 222 | 1 | 9 | 516 | 1 | 9 | 71 | 1 | 13 | 23200 | 1 | 9 | 45400 | 1 | 9 | 9700 | 1 | 13 | 1330 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 5.6 | 42.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.86 | A | 7 | 990 | A | 7 | 160 | A | 7 | 1.5 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.24 | 4 | 0
1982-03-01 | 1900-02-28 | 10:00 | 10 | 634 | 1393 | 419 | 1 | 9 | 721 | 1 | 9 | 93 | 1 | 13 | 44600 | 1 | 9 | 70500 | 1 | 9 | 12400 | 1 | 13 | 1940 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.71 | A | 7 | 989 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.32 | 4 | 0
1982-03-01 | 1900-02-28 | 11:00 | 11 | 805 | 1393 | 573 | 1 | 9 | 802 | 1 | 9 | 112 | 1 | 13 | 59900 | 1 | 9 | 79300 | 1 | 9 | 13900 | 1 | 13 | 2430 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 3.9 | 39.02 | A | 7 | 0.59 | A | 7 | 988 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.72 | 4 | 0
1982-03-01 | 1900-02-28 | 12:00 | 12 | 913 | 1393 | 657 | 1 | 9 | 811 | 1 | 9 | 128 | 1 | 13 | 68800 | 1 | 9 | 80900 | 1 | 9 | 15600 | 1 | 13 | 3060 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 14.4 | 57.92 | A | 7 | 5 | 41 | A | 7 | 0.53 | A | 7 | 986 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.6 | 4 | 0
1982-03-01 | 1900-02-28 | 13:00 | 13 | 951 | 1393 | 657 | 1 | 9 | 754 | 1 | 9 | 144 | 1 | 13 | 70500 | 1 | 9 | 76900 | 1 | 9 | 17800 | 1 | 13 | 3960 | 1 | 18 | 7 | A | 7 | 1 | A | 7 | 16.1 | 60.98 | A | 7 | 5 | 41 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.9 | 4 | 0
1982-03-01 | 1900-02-28 | 14:00 | 14 | 916 | 1393 | 647 | 1 | 9 | 811 | 1 | 9 | 116 | 1 | 13 | 68500 | 1 | 9 | 81300 | 1 | 9 | 14900 | 1 | 13 | 2890 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.43 | A | 7 | 984 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.08 | 4 | 0
1982-03-01 | 1900-02-28 | 15:00 | 15 | 812 | 1393 | 524 | 1 | 9 | 702 | 1 | 9 | 116 | 1 | 13 | 56100 | 1 | 9 | 70900 | 1 | 9 | 14600 | 1 | 13 | 2760 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.45 | A | 7 | 983 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.08 | 4 | 0
1982-03-01 | 1900-02-28 | 16:00 | 16 | 644 | 1393 | 390 | 1 | 9 | 514 | 1 | 9 | 153 | 1 | 13 | 41300 | 1 | 9 | 50800 | 1 | 9 | 17800 | 1 | 13 | 3120 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | 18.9 | 66.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.43 | A | 7 | 981 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.78 | 4 | 0
1982-03-01 | 1900-02-28 | 17:00 | 17 | 425 | 1393 | 201 | 1 | 13 | 329 | 1 | 13 | 102 | 1 | 13 | 21200 | 1 | 13 | 29200 | 1 | 13 | 12200 | 1 | 13 | 1910 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 18.9 | 66.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.39 | A | 7 | 980 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.32 | 4 | 0
1982-03-01 | 1900-02-28 | 18:00 | 18 | 171 | 1393 | 59 | 1 | 13 | 119 | 1 | 13 | 45 | 1 | 13 | 6300 | 1 | 13 | 6600 | 1 | 13 | 5500 | 1 | 13 | 840 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 16.1 | 60.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.46 | A | 7 | 980 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.72 | 4 | 0
1982-03-01 | 1900-02-28 | 19:00 | 19 | 3 | 221 | 1 | 1 | 13 | 2 | 1 | 13 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 15 | 59 | A | 7 | 5 | 41 | A | 7 | 0.51 | A | 7 | 979 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.4 | 4 | 0
1982-03-01 | 1900-02-28 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 5 | 41 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.9 | 4 | 0
1982-03-01 | 1900-02-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 1 | A | 7 | 13.9 | 57.02 | A | 7 | 5 | 41 | A | 7 | 0.55 | A | 7 | 977 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.9 | 4 | 0
1982-03-01 | 1900-02-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 1 | A | 7 | 12.8 | 55.04 | A | 7 | 5 | 41 | A | 7 | 0.59 | A | 7 | 976 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.5 | 4 | 0
1982-03-01 | 1900-02-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 6 | A | 7 | 12.8 | 55.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.62 | A | 7 | 975 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.88 | 4 | 0
1982-03-01 | 1900-02-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 3 | A | 7 | 12.8 | 55.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.88 | 4 | 0
1982-03-02 | 1900-03-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 12.8 | 55.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.62 | A | 7 | 973 | A | 7 | 210 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.88 | 5 | 0
1982-03-02 | 1900-03-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 12.8 | 55.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.62 | A | 7 | 972 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.88 | 5 | 0
1982-03-02 | 1900-03-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 12.2 | 53.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.64 | A | 7 | 971 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.08 | 5 | 0
1982-03-02 | 1900-03-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.64 | A | 7 | 971 | A | 7 | 210 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.08 | 5 | 0
1982-03-02 | 1900-03-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.69 | A | 7 | 971 | A | 7 | 210 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.88 | 5 | 0
1982-03-02 | 1900-03-01 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 971 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.08 | 5 | 0
1982-03-02 | 1900-03-01 | 7:00 | 7 | 2 | 197 | 1 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 971 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.5 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.08 | 5 | 0
1982-03-02 | 1900-03-01 | 8:00 | 8 | 164 | 1392 | 34 | 1 | 13 | 3 | 1 | 9 | 33 | 1 | 13 | 3800 | 1 | 13 | 0 | 1 | 9 | 3800 | 1 | 13 | 1150 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 5.6 | 42.08 | A | 7 | 0.74 | A | 7 | 971 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.5 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.58 | 5 | 0
1982-03-02 | 1900-03-01 | 9:00 | 9 | 420 | 1392 | 106 | 1 | 9 | 10 | 1 | 9 | 103 | 1 | 13 | 12000 | 1 | 9 | 600 | 1 | 9 | 11800 | 1 | 13 | 3810 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 971 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.5 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.08 | 5 | 0
1982-03-02 | 1900-03-01 | 10:00 | 10 | 641 | 1392 | 215 | 1 | 9 | 3 | 1 | 9 | 213 | 1 | 13 | 24000 | 1 | 9 | 300 | 1 | 9 | 23900 | 1 | 13 | 7830 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.69 | A | 7 | 971 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.5 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.88 | 5 | 0
1982-03-02 | 1900-03-01 | 11:00 | 11 | 811 | 1392 | 236 | 1 | 9 | 2 | 1 | 9 | 235 | 1 | 13 | 27100 | 1 | 9 | 200 | 1 | 9 | 27000 | 1 | 13 | 9720 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.5 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.38 | 5 | 0
1982-03-02 | 1900-03-01 | 12:00 | 12 | 919 | 1392 | 276 | 1 | 9 | 1 | 1 | 9 | 276 | 1 | 13 | 31900 | 1 | 9 | 100 | 1 | 9 | 31800 | 1 | 13 | 11690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 1.5 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.38 | 5 | 0
1982-03-02 | 1900-03-01 | 13:00 | 13 | 957 | 1392 | 313 | 1 | 9 | 2 | 1 | 9 | 312 | 1 | 13 | 35900 | 1 | 9 | 200 | 1 | 9 | 35800 | 1 | 13 | 12980 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.64 | A | 7 | 971 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 1.6 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.86 | 5 | 0
1982-03-02 | 1900-03-01 | 14:00 | 14 | 922 | 1392 | 290 | 1 | 9 | 5 | 1 | 9 | 287 | 1 | 13 | 33300 | 1 | 9 | 500 | 1 | 9 | 33000 | 1 | 13 | 12020 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 6.7 | 44.06 | A | 7 | 0.62 | A | 7 | 970 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 6100 | A | 7 | 1.6 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.56 | 5 | 0
1982-03-02 | 1900-03-01 | 15:00 | 15 | 817 | 1392 | 279 | 1 | 9 | 3 | 1 | 9 | 277 | 1 | 13 | 31600 | 1 | 9 | 300 | 1 | 9 | 31400 | 1 | 13 | 10850 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 5.6 | 42.08 | A | 7 | 0.74 | A | 7 | 971 | A | 7 | 20 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 1.5 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.58 | 5 | 0
1982-03-02 | 1900-03-01 | 16:00 | 16 | 649 | 1392 | 245 | 1 | 9 | 1 | 1 | 9 | 244 | 1 | 13 | 27100 | 1 | 9 | 100 | 1 | 9 | 27100 | 1 | 13 | 8510 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 4.4 | 39.92 | A | 7 | 0.77 | A | 7 | 971 | A | 7 | 30 | A | 7 | 7.2 | A | 7 | 6400 | A | 7 | 2440 | A | 7 | 1.4 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.92 | 5 | 0
1982-03-02 | 1900-03-01 | 17:00 | 17 | 430 | 1392 | 141 | 1 | 9 | 1 | 1 | 9 | 140 | 1 | 13 | 15500 | 1 | 9 | 100 | 1 | 9 | 15500 | 1 | 13 | 4690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.83 | A | 7 | 972 | A | 7 | 30 | A | 7 | 7.7 | A | 7 | 6400 | A | 7 | 370 | A | 7 | 1.2 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.94 | 5 | 0
1982-03-02 | 1900-03-01 | 18:00 | 18 | 176 | 1392 | 51 | 1 | 13 | 0 | 1 | 9 | 50 | 1 | 13 | 5500 | 1 | 13 | 0 | 1 | 9 | 5500 | 1 | 13 | 1570 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 2.2 | 35.96 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 40 | A | 7 | 9.3 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1.2 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.66 | 5 | 0
1982-03-02 | 1900-03-01 | 19:00 | 19 | 4 | 244 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 30 | A | 7 | 7.7 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 5 | 0
1982-03-02 | 1900-03-01 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.85 | A | 7 | 975 | A | 7 | 40 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.38 | 5 | 0
1982-03-02 | 1900-03-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 0 | 32 | A | 7 | 0.85 | A | 7 | 976 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 5 | 0
1982-03-02 | 1900-03-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.85 | A | 7 | 977 | A | 7 | 60 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 5 | 0
1982-03-02 | 1900-03-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 210 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 5 | 0
1982-03-02 | 1900-03-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.85 | A | 7 | 977 | A | 7 | 50 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 210 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.52 | 5 | 0
1982-03-03 | 1900-03-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 60 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 210 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.92 | 6 | 0
1982-03-03 | 1900-03-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 50 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 210 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.84 | 6 | 0
1982-03-03 | 1900-03-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 977 | A | 7 | 50 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 150 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 6 | 0
1982-03-03 | 1900-03-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 60 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 150 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.96 | 6 | 0
1982-03-03 | 1900-03-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.92 | A | 7 | 976 | A | 7 | 80 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 150 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 6 | 0
1982-03-03 | 1900-03-02 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 60 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.06 | 6 | 0
1982-03-03 | 1900-03-02 | 7:00 | 7 | 3 | 220 | 2 | 1 | 13 | 0 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 60 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 180 | A | 7 | 0.8 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1982-03-03 | 1900-03-02 | 8:00 | 8 | 171 | 1392 | 52 | 1 | 13 | 0 | 1 | 9 | 52 | 1 | 13 | 5700 | 1 | 13 | 0 | 1 | 9 | 5700 | 1 | 13 | 1580 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 60 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 210 | A | 7 | 0.8 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1982-03-03 | 1900-03-02 | 9:00 | 9 | 426 | 1392 | 147 | 1 | 9 | 1 | 1 | 9 | 146 | 1 | 13 | 16100 | 1 | 9 | 100 | 1 | 9 | 16100 | 1 | 13 | 4770 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 60 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 180 | A | 7 | 0.8 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1982-03-03 | 1900-03-02 | 10:00 | 10 | 648 | 1392 | 216 | 1 | 9 | 2 | 1 | 9 | 215 | 1 | 13 | 24200 | 1 | 9 | 200 | 1 | 9 | 24100 | 1 | 13 | 7930 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 70 | A | 7 | 8.2 | A | 7 | 12900 | A | 7 | 180 | A | 7 | 0.8 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1982-03-03 | 1900-03-02 | 11:00 | 11 | 818 | 1392 | 172 | 1 | 9 | 2 | 1 | 9 | 171 | 1 | 13 | 20300 | 1 | 9 | 200 | 1 | 9 | 20200 | 1 | 13 | 7730 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 80 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 150 | A | 7 | 0.8 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1982-03-03 | 1900-03-02 | 12:00 | 12 | 926 | 1392 | 195 | 1 | 9 | 0 | 1 | 9 | 194 | 1 | 13 | 23000 | 1 | 9 | 0 | 1 | 9 | 23000 | 1 | 13 | 9050 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.92 | A | 7 | 975 | A | 7 | 80 | A | 7 | 8.8 | A | 7 | 8000 | A | 7 | 150 | A | 7 | 0.9 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 6 | 0
1982-03-03 | 1900-03-02 | 13:00 | 13 | 963 | 1392 | 334 | 1 | 9 | 1 | 1 | 9 | 333 | 1 | 13 | 38100 | 1 | 9 | 100 | 1 | 9 | 38000 | 1 | 13 | 13580 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 80 | A | 7 | 8.8 | A | 7 | 9700 | A | 7 | 210 | A | 7 | 0.9 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 6 | 0
1982-03-03 | 1900-03-02 | 14:00 | 14 | 928 | 1392 | 356 | 1 | 9 | 1 | 1 | 9 | 355 | 1 | 13 | 40200 | 1 | 9 | 100 | 1 | 9 | 40100 | 1 | 13 | 13730 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 971 | A | 7 | 80 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.96 | 6 | 0
1982-03-03 | 1900-03-02 | 15:00 | 15 | 823 | 1392 | 314 | 1 | 9 | 2 | 1 | 9 | 313 | 1 | 13 | 35200 | 1 | 9 | 200 | 1 | 9 | 35100 | 1 | 13 | 11690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 971 | A | 7 | 70 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.96 | 6 | 0
1982-03-03 | 1900-03-02 | 16:00 | 16 | 655 | 1392 | 225 | 1 | 9 | 1 | 1 | 9 | 225 | 1 | 13 | 25200 | 1 | 9 | 100 | 1 | 9 | 25200 | 1 | 13 | 8200 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 970 | A | 7 | 60 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 6 | 0
1982-03-03 | 1900-03-02 | 17:00 | 17 | 435 | 1392 | 145 | 1 | 9 | 0 | 1 | 9 | 145 | 1 | 13 | 16000 | 1 | 9 | 0 | 1 | 9 | 16000 | 1 | 13 | 4820 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 970 | A | 7 | 50 | A | 7 | 7.2 | A | 7 | 6400 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 6 | 0
1982-03-03 | 1900-03-02 | 18:00 | 18 | 181 | 1392 | 54 | 1 | 13 | 0 | 1 | 9 | 54 | 1 | 13 | 5900 | 1 | 13 | 0 | 1 | 9 | 5900 | 1 | 13 | 1660 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.96 | A | 7 | 969 | A | 7 | 70 | A | 7 | 7.2 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 0.9 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.64 | 6 | 0
1982-03-03 | 1900-03-02 | 19:00 | 19 | 5 | 267 | 2 | 1 | 13 | 0 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -1.7 | 28.94 | A | 7 | 1 | A | 7 | 970 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 0.9 | E | 8 | 0.038 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.84 | 6 | 0
1982-03-03 | 1900-03-02 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.96 | A | 7 | 970 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.64 | 6 | 0
1982-03-03 | 1900-03-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.96 | A | 7 | 969 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.54 | 6 | 0
1982-03-03 | 1900-03-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.96 | A | 7 | 969 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.64 | 6 | 0
1982-03-03 | 1900-03-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.96 | A | 7 | 968 | A | 7 | 10 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.64 | 6 | 0
1982-03-03 | 1900-03-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.96 | A | 7 | 968 | A | 7 | 30 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.64 | 6 | 0
1982-03-04 | 1900-03-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.96 | A | 7 | 968 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.64 | 7 | 0
1982-03-04 | 1900-03-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.96 | A | 7 | 968 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 120 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.56 | 7 | 0
1982-03-04 | 1900-03-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.96 | A | 7 | 968 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 120 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.66 | 7 | 0
1982-03-04 | 1900-03-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.96 | A | 7 | 968 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.66 | 7 | 0
1982-03-04 | 1900-03-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.92 | A | 7 | 969 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.28 | 7 | 0
1982-03-04 | 1900-03-03 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5 | 23 | A | 7 | 0.88 | A | 7 | 970 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22 | 7 | 0
1982-03-04 | 1900-03-03 | 7:00 | 7 | 4 | 267 | 2 | 1 | 13 | 0 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.92 | A | 7 | 971 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 2400 | A | 7 | 180 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.22 | 7 | 0
1982-03-04 | 1900-03-03 | 8:00 | 8 | 178 | 1391 | 40 | 1 | 13 | 1 | 1 | 9 | 40 | 1 | 13 | 4500 | 1 | 13 | 0 | 1 | 9 | 4500 | 1 | 13 | 1360 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -6.1 | 21.02 | A | 7 | 0.92 | A | 7 | 972 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 200 | A | 7 | 30 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.32 | 7 | 0
1982-03-04 | 1900-03-03 | 9:00 | 9 | 433 | 1391 | 130 | 1 | 9 | 0 | 1 | 9 | 130 | 1 | 13 | 14500 | 1 | 9 | 0 | 1 | 9 | 14500 | 1 | 13 | 4520 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 60 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.62 | 7 | 0
1982-03-04 | 1900-03-03 | 10:00 | 10 | 654 | 1391 | 241 | 1 | 9 | 53 | 1 | 9 | 216 | 1 | 13 | 26400 | 1 | 9 | 5300 | 1 | 9 | 24000 | 1 | 13 | 6210 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -4.4 | 24.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.88 | A | 7 | 974 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 7 | 0
1982-03-04 | 1900-03-03 | 11:00 | 11 | 825 | 1391 | 344 | 1 | 9 | 128 | 1 | 9 | 269 | 1 | 13 | 37600 | 1 | 9 | 13400 | 1 | 9 | 29700 | 1 | 13 | 7230 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 340 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.54 | 7 | 0
1982-03-04 | 1900-03-03 | 12:00 | 12 | 932 | 1391 | 368 | 1 | 9 | 101 | 1 | 9 | 301 | 1 | 13 | 40600 | 1 | 9 | 10300 | 1 | 9 | 33700 | 1 | 13 | 10340 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 370 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 7 | 0
1982-03-04 | 1900-03-03 | 13:00 | 13 | 969 | 1391 | 338 | 1 | 9 | 45 | 1 | 9 | 307 | 1 | 13 | 37300 | 1 | 9 | 4600 | 1 | 9 | 34100 | 1 | 13 | 10880 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 7 | 0
1982-03-04 | 1900-03-03 | 14:00 | 14 | 934 | 1391 | 304 | 1 | 9 | 3 | 1 | 9 | 303 | 1 | 13 | 34900 | 1 | 9 | 300 | 1 | 9 | 34800 | 1 | 13 | 12560 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 430 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 7 | 0
1982-03-04 | 1900-03-03 | 15:00 | 15 | 829 | 1391 | 257 | 1 | 9 | 7 | 1 | 9 | 253 | 1 | 13 | 29400 | 1 | 9 | 600 | 1 | 9 | 29000 | 1 | 13 | 10350 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 460 | A | 7 | 0.8 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 7 | 0
1982-03-04 | 1900-03-03 | 16:00 | 16 | 660 | 1391 | 225 | 1 | 9 | 9 | 1 | 9 | 220 | 1 | 13 | 25100 | 1 | 9 | 800 | 1 | 9 | 24800 | 1 | 13 | 8150 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.75 | A | 7 | 976 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 7 | 0
1982-03-04 | 1900-03-03 | 17:00 | 17 | 440 | 1391 | 125 | 1 | 9 | 1 | 1 | 9 | 124 | 1 | 13 | 13900 | 1 | 9 | 100 | 1 | 9 | 13900 | 1 | 13 | 4430 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 7 | 0
1982-03-04 | 1900-03-03 | 18:00 | 18 | 186 | 1391 | 33 | 1 | 13 | 1 | 1 | 9 | 33 | 1 | 13 | 3800 | 1 | 13 | 0 | 1 | 9 | 3800 | 1 | 13 | 1190 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 7 | 0
1982-03-04 | 1900-03-03 | 19:00 | 19 | 6 | 290 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.087 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 7 | 0
1982-03-04 | 1900-03-03 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.44 | 7 | 0
1982-03-04 | 1900-03-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 1490 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.44 | 7 | 0
1982-03-04 | 1900-03-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 1490 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 7 | 0
1982-03-04 | 1900-03-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 1490 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.56 | 7 | 0
1982-03-04 | 1900-03-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.85 | A | 7 | 982 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 1490 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.94 | 7 | 0
1982-03-05 | 1900-03-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.85 | A | 7 | 983 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 1400 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.94 | 1 | 0
1982-03-05 | 1900-03-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 983 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 1400 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.04 | 1 | 0
1982-03-05 | 1900-03-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.88 | A | 7 | 983 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 1400 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.14 | 1 | 0
1982-03-05 | 1900-03-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.88 | A | 7 | 984 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 1400 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.14 | 1 | 0
1982-03-05 | 1900-03-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.88 | A | 7 | 984 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 1400 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.14 | 1 | 0
1982-03-05 | 1900-03-04 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -7.2 | 19.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 1340 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.46 | 1 | 0
1982-03-05 | 1900-03-04 | 7:00 | 7 | 5 | 290 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -8.9 | 15.98 | A | 7 | -9.4 | 15.08 | A | 7 | 0.96 | A | 7 | 985 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 0.6 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.78 | 1 | 0
1982-03-05 | 1900-03-04 | 8:00 | 8 | 185 | 1390 | 42 | 1 | 13 | 10 | 1 | 9 | 41 | 1 | 13 | 4800 | 1 | 13 | 100 | 1 | 9 | 4700 | 1 | 13 | 1400 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 1160 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.14 | 1 | 0
1982-03-05 | 1900-03-04 | 9:00 | 9 | 440 | 1390 | 112 | 1 | 9 | 15 | 1 | 9 | 107 | 1 | 13 | 12700 | 1 | 9 | 900 | 1 | 9 | 12400 | 1 | 13 | 4010 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.85 | A | 7 | 988 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 1040 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.94 | 1 | 0
1982-03-05 | 1900-03-04 | 10:00 | 10 | 661 | 1390 | 183 | 1 | 9 | 4 | 1 | 9 | 181 | 1 | 13 | 20800 | 1 | 9 | 300 | 1 | 9 | 20700 | 1 | 13 | 7210 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -7.2 | 19.04 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 330 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 760 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 1 | 0
1982-03-05 | 1900-03-04 | 11:00 | 11 | 831 | 1390 | 290 | 1 | 9 | 4 | 1 | 9 | 287 | 1 | 13 | 32700 | 1 | 9 | 400 | 1 | 9 | 32500 | 1 | 13 | 11230 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.78 | A | 7 | 989 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 400 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.44 | 1 | 0
1982-03-05 | 1900-03-04 | 12:00 | 12 | 939 | 1390 | 308 | 1 | 9 | 7 | 1 | 9 | 303 | 1 | 13 | 35300 | 1 | 9 | 700 | 1 | 9 | 34800 | 1 | 13 | 12600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.78 | A | 7 | 988 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 400 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 1 | 0
1982-03-05 | 1900-03-04 | 13:00 | 13 | 976 | 1390 | 462 | 1 | 9 | 174 | 1 | 9 | 341 | 1 | 13 | 50500 | 1 | 9 | 18400 | 1 | 9 | 37600 | 1 | 13 | 10370 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.72 | A | 7 | 988 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 910 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.04 | 1 | 0
1982-03-05 | 1900-03-04 | 14:00 | 14 | 940 | 1390 | 459 | 1 | 9 | 121 | 1 | 9 | 377 | 1 | 13 | 50400 | 1 | 9 | 12500 | 1 | 9 | 42000 | 1 | 13 | 12390 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -7.8 | 17.96 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 1010 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 1 | 0
1982-03-05 | 1900-03-04 | 15:00 | 15 | 834 | 1390 | 354 | 1 | 9 | 14 | 1 | 9 | 346 | 1 | 13 | 39500 | 1 | 9 | 1400 | 1 | 9 | 38700 | 1 | 13 | 12440 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -7.8 | 17.96 | A | 7 | 0.69 | A | 7 | 988 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 1040 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 1 | 0
1982-03-05 | 1900-03-04 | 16:00 | 16 | 666 | 1390 | 275 | 1 | 9 | 56 | 1 | 9 | 248 | 1 | 13 | 30100 | 1 | 9 | 5600 | 1 | 9 | 27400 | 1 | 13 | 6950 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -7.8 | 17.96 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 1040 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 1 | 0
1982-03-05 | 1900-03-04 | 17:00 | 17 | 446 | 1390 | 98 | 1 | 9 | 11 | 1 | 9 | 94 | 1 | 13 | 11200 | 1 | 9 | 600 | 1 | 9 | 11000 | 1 | 13 | 3670 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -3.9 | 24.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.72 | A | 7 | 987 | A | 7 | 330 | A | 7 | 5.7 | A | 7 | 12900 | A | 7 | 940 | A | 7 | 0.7 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.16 | 1 | 0
1982-03-05 | 1900-03-04 | 18:00 | 18 | 191 | 1390 | 74 | 1 | 13 | 37 | 1 | 9 | 69 | 1 | 13 | 8100 | 1 | 13 | 2700 | 1 | 9 | 7700 | 1 | 13 | 1520 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 987 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 3660 | A | 7 | 0.6 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 1 | 0
1982-03-05 | 1900-03-04 | 19:00 | 19 | 7 | 313 | 2 | 1 | 13 | 0 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | -5.6 | 21.92 | A | 7 | -9.4 | 15.08 | A | 7 | 0.74 | A | 7 | 987 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 0.6 | E | 8 | 0.14 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.38 | 1 | 0
1982-03-05 | 1900-03-04 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 3 | A | 7 | -6.7 | 19.94 | A | 7 | -10.6 | 12.92 | A | 7 | 0.74 | A | 7 | 987 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.42 | 1 | 0
1982-03-05 | 1900-03-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -8.9 | 15.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.84 | 1 | 0
1982-03-05 | 1900-03-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -9.4 | 15.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.8 | A | 7 | 987 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.94 | 1 | 0
1982-03-05 | 1900-03-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | -9.4 | 15.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.8 | A | 7 | 987 | A | 7 | 350 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.94 | 1 | 0
1982-03-05 | 1900-03-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -10 | 14 | A | 7 | -12.2 | 10.04 | A | 7 | 0.84 | A | 7 | 987 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 1 | 0
1982-03-06 | 1900-03-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | -10.6 | 12.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 2 | 0
1982-03-06 | 1900-03-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 4 | A | 7 | -10.6 | 12.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.88 | A | 7 | 986 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 2 | 0
1982-03-06 | 1900-03-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -11.1 | 12.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.88 | A | 7 | 985 | A | 7 | 300 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.36 | 2 | 0
1982-03-06 | 1900-03-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | -11.7 | 10.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.56 | 2 | 0
1982-03-06 | 1900-03-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -11.7 | 10.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.56 | 2 | 0
1982-03-06 | 1900-03-05 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -11.7 | 10.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.56 | 2 | 0
1982-03-06 | 1900-03-05 | 7:00 | 7 | 7 | 336 | 6 | 1 | 13 | 19 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -13.3 | 8.06 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.86 | 2 | 0
1982-03-06 | 1900-03-05 | 8:00 | 8 | 191 | 1389 | 88 | 1 | 13 | 423 | 1 | 9 | 32 | 1 | 13 | 9300 | 1 | 13 | 27800 | 1 | 9 | 5500 | 1 | 13 | 580 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.56 | 2 | 0
1982-03-06 | 1900-03-05 | 9:00 | 9 | 447 | 1389 | 284 | 1 | 9 | 723 | 1 | 9 | 55 | 1 | 13 | 30000 | 1 | 9 | 65800 | 1 | 9 | 8700 | 1 | 13 | 1120 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.84 | 2 | 0
1982-03-06 | 1900-03-05 | 10:00 | 10 | 668 | 1389 | 483 | 1 | 9 | 856 | 1 | 9 | 74 | 1 | 13 | 51600 | 1 | 9 | 83900 | 1 | 9 | 11100 | 1 | 13 | 1640 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 984 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.14 | 2 | 0
1982-03-06 | 1900-03-05 | 11:00 | 11 | 838 | 1389 | 632 | 1 | 9 | 906 | 1 | 9 | 88 | 1 | 13 | 66200 | 1 | 9 | 89600 | 1 | 9 | 12000 | 1 | 13 | 1930 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.72 | 2 | 0
1982-03-06 | 1900-03-05 | 12:00 | 12 | 945 | 1389 | 733 | 1 | 9 | 938 | 1 | 9 | 97 | 1 | 13 | 76500 | 1 | 9 | 93300 | 1 | 9 | 12800 | 1 | 13 | 2300 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.58 | 2 | 0
1982-03-06 | 1900-03-05 | 13:00 | 13 | 982 | 1389 | 768 | 1 | 9 | 949 | 1 | 9 | 100 | 1 | 13 | 80100 | 1 | 9 | 94600 | 1 | 9 | 13000 | 1 | 13 | 2460 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.58 | A | 7 | 982 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.18 | 2 | 0
1982-03-06 | 1900-03-05 | 14:00 | 14 | 946 | 1389 | 736 | 1 | 9 | 942 | 1 | 9 | 97 | 1 | 13 | 76800 | 1 | 9 | 93700 | 1 | 9 | 12800 | 1 | 13 | 2300 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.59 | A | 7 | 982 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 2 | 0
1982-03-06 | 1900-03-05 | 15:00 | 15 | 840 | 1389 | 636 | 1 | 9 | 909 | 1 | 9 | 89 | 1 | 13 | 66600 | 1 | 9 | 89900 | 1 | 9 | 12100 | 1 | 13 | 1940 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.64 | A | 7 | 982 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 2 | 0
1982-03-06 | 1900-03-05 | 16:00 | 16 | 671 | 1389 | 483 | 1 | 9 | 849 | 1 | 9 | 75 | 1 | 13 | 51500 | 1 | 9 | 83300 | 1 | 9 | 11100 | 1 | 13 | 1660 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 981 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.78 | 2 | 0
1982-03-06 | 1900-03-05 | 17:00 | 17 | 451 | 1389 | 258 | 1 | 13 | 513 | 1 | 13 | 93 | 1 | 13 | 26600 | 1 | 13 | 45800 | 1 | 13 | 11700 | 1 | 13 | 1700 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 1.7 | 35.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.08 | 2 | 0
1982-03-06 | 1900-03-05 | 18:00 | 18 | 195 | 1389 | 93 | 1 | 13 | 347 | 1 | 13 | 45 | 1 | 13 | 9400 | 1 | 13 | 22400 | 1 | 13 | 6300 | 1 | 13 | 770 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 0 | 32 | A | 7 | -6.1 | 21.02 | A | 7 | 0.64 | A | 7 | 982 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.22 | 2 | 0
1982-03-06 | 1900-03-05 | 19:00 | 19 | 8 | 359 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 983 | A | 7 | 350 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 640 | A | 7 | 0.7 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 2 | 0
1982-03-06 | 1900-03-05 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.72 | A | 7 | 984 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 580 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 2 | 0
1982-03-06 | 1900-03-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.72 | A | 7 | 985 | A | 7 | 340 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 610 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.04 | 2 | 0
1982-03-06 | 1900-03-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -3.9 | 24.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.72 | A | 7 | 986 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.16 | 2 | 0
1982-03-06 | 1900-03-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -8.3 | 17.06 | A | 7 | 0.78 | A | 7 | 987 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.56 | 2 | 0
1982-03-06 | 1900-03-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 2 | 0
1982-03-07 | 1900-03-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 3 | 0
1982-03-07 | 1900-03-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.84 | A | 7 | 987 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 3 | 0
1982-03-07 | 1900-03-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.88 | 3 | 0
1982-03-07 | 1900-03-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -10 | 14 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.8 | 3 | 0
1982-03-07 | 1900-03-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.92 | 3 | 0
1982-03-07 | 1900-03-06 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.81 | A | 7 | 989 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.84 | 3 | 0
1982-03-07 | 1900-03-06 | 7:00 | 7 | 8 | 359 | 9 | 1 | 13 | 38 | 1 | 9 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -12.2 | 10.04 | A | 7 | 0.84 | A | 7 | 989 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 3 | 0
1982-03-07 | 1900-03-06 | 8:00 | 8 | 198 | 1389 | 97 | 1 | 13 | 517 | 1 | 9 | 26 | 1 | 13 | 10300 | 1 | 13 | 36800 | 1 | 9 | 5000 | 1 | 13 | 530 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.77 | A | 7 | 989 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 3 | 0
1982-03-07 | 1900-03-06 | 9:00 | 9 | 454 | 1389 | 295 | 1 | 9 | 783 | 1 | 9 | 42 | 1 | 13 | 31600 | 1 | 9 | 71700 | 1 | 9 | 8100 | 1 | 13 | 1030 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -13.3 | 8.06 | A | 7 | 0.65 | A | 7 | 990 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.36 | 3 | 0
1982-03-07 | 1900-03-06 | 10:00 | 10 | 675 | 1389 | 488 | 1 | 9 | 895 | 1 | 9 | 57 | 1 | 13 | 51900 | 1 | 9 | 87000 | 1 | 9 | 9500 | 1 | 13 | 1410 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.57 | A | 7 | 990 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.96 | 3 | 0
1982-03-07 | 1900-03-06 | 11:00 | 11 | 845 | 1389 | 533 | 1 | 13 | 646 | 1 | 13 | 142 | 1 | 13 | 56600 | 1 | 13 | 65100 | 1 | 13 | 16900 | 1 | 13 | 3420 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | -5.6 | 21.92 | A | 7 | -13.3 | 8.06 | A | 7 | 0.55 | A | 7 | 989 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.86 | 3 | 0
1982-03-07 | 1900-03-06 | 12:00 | 12 | 951 | 1389 | 581 | 1 | 13 | 513 | 1 | 13 | 232 | 1 | 13 | 62500 | 1 | 13 | 53200 | 1 | 13 | 26000 | 1 | 13 | 6310 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | -4.4 | 24.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.5 | A | 7 | 989 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.66 | 3 | 0
1982-03-07 | 1900-03-06 | 13:00 | 13 | 988 | 1389 | 629 | 1 | 13 | 524 | 1 | 13 | 258 | 1 | 13 | 67200 | 1 | 13 | 54400 | 1 | 13 | 28400 | 1 | 13 | 7440 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | -3.3 | 26.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.48 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.36 | 3 | 0
1982-03-07 | 1900-03-06 | 14:00 | 14 | 952 | 1389 | 476 | 1 | 9 | 216 | 1 | 9 | 328 | 1 | 13 | 52000 | 1 | 9 | 22800 | 1 | 9 | 36300 | 1 | 13 | 9760 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -2.8 | 26.96 | A | 7 | -12.8 | 8.96 | A | 7 | 0.47 | A | 7 | 988 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 1980 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.26 | 3 | 0
1982-03-07 | 1900-03-06 | 15:00 | 15 | 845 | 1389 | 392 | 1 | 9 | 232 | 1 | 9 | 251 | 1 | 13 | 42300 | 1 | 9 | 24700 | 1 | 9 | 27300 | 1 | 13 | 6310 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -1.7 | 28.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.43 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.06 | 3 | 0
1982-03-07 | 1900-03-06 | 16:00 | 16 | 676 | 1389 | 284 | 1 | 9 | 180 | 1 | 9 | 197 | 1 | 13 | 31200 | 1 | 9 | 18400 | 1 | 9 | 22200 | 1 | 13 | 4860 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -1.7 | 28.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.49 | A | 7 | 987 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 1010 | A | 7 | 0.6 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.12 | 3 | 0
1982-03-07 | 1900-03-06 | 17:00 | 17 | 456 | 1389 | 116 | 1 | 9 | 0 | 1 | 9 | 116 | 1 | 13 | 13100 | 1 | 9 | 0 | 1 | 9 | 13100 | 1 | 13 | 4320 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.43 | A | 7 | 986 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.5 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.06 | 3 | 0
1982-03-07 | 1900-03-06 | 18:00 | 18 | 200 | 1389 | 62 | 1 | 13 | 22 | 1 | 9 | 59 | 1 | 13 | 6800 | 1 | 13 | 1600 | 1 | 9 | 6600 | 1 | 13 | 1380 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | -1.7 | 28.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.49 | A | 7 | 986 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 1490 | A | 7 | 0.6 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.12 | 3 | 0
1982-03-07 | 1900-03-06 | 19:00 | 19 | 9 | 382 | 5 | 1 | 13 | 3 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | -2.2 | 28.04 | A | 7 | -10.6 | 12.92 | A | 7 | 0.53 | A | 7 | 986 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 1490 | A | 7 | 0.6 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.12 | 3 | 0
1982-03-07 | 1900-03-06 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 3 | A | 7 | -2.8 | 26.96 | A | 7 | -10.6 | 12.92 | A | 7 | 0.55 | A | 7 | 986 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 3 | 0
1982-03-07 | 1900-03-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -10 | 14 | A | 7 | 0.66 | A | 7 | 986 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.9 | 3 | 0
1982-03-07 | 1900-03-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -9.4 | 15.08 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.18 | 3 | 0
1982-03-07 | 1900-03-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 3 | 0
1982-03-07 | 1900-03-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 984 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 3 | 0
1982-03-08 | 1900-03-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 984 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 4 | 0
1982-03-08 | 1900-03-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | -3.9 | 24.98 | A | 7 | -9.4 | 15.08 | A | 7 | 0.66 | A | 7 | 984 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.88 | 4 | 0
1982-03-08 | 1900-03-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -3.3 | 26.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.58 | A | 7 | 983 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.42 | 4 | 0
1982-03-08 | 1900-03-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -3.3 | 26.06 | A | 7 | -10 | 14 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.6 | 4 | 0
1982-03-08 | 1900-03-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 4 | A | 7 | -3.3 | 26.06 | A | 7 | -10 | 14 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.6 | 4 | 0
1982-03-08 | 1900-03-07 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.61 | A | 7 | 982 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.58 | 4 | 0
1982-03-08 | 1900-03-07 | 7:00 | 7 | 10 | 405 | 3 | 1 | 13 | 1 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -2.2 | 28.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 0.6 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.38 | 4 | 0
1982-03-08 | 1900-03-07 | 8:00 | 8 | 205 | 1388 | 54 | 1 | 13 | 19 | 1 | 9 | 51 | 1 | 13 | 5900 | 1 | 13 | 1400 | 1 | 9 | 5700 | 1 | 13 | 1250 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -1.7 | 28.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.61 | A | 7 | 981 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 0.7 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.36 | 4 | 0
1982-03-08 | 1900-03-07 | 9:00 | 9 | 461 | 1388 | 190 | 1 | 13 | 296 | 1 | 13 | 93 | 1 | 13 | 20400 | 1 | 13 | 27100 | 1 | 13 | 11400 | 1 | 13 | 1730 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 0.6 | 33.08 | A | 7 | -7.2 | 19.04 | A | 7 | 0.56 | A | 7 | 982 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.84 | 4 | 0
1982-03-08 | 1900-03-07 | 10:00 | 10 | 682 | 1388 | 279 | 1 | 13 | 215 | 1 | 13 | 174 | 1 | 13 | 30300 | 1 | 13 | 22300 | 1 | 13 | 19300 | 1 | 13 | 3800 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 982 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 0.8 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 4 | 0
1982-03-08 | 1900-03-07 | 11:00 | 11 | 851 | 1388 | 353 | 1 | 13 | 216 | 1 | 13 | 222 | 1 | 13 | 38700 | 1 | 13 | 23000 | 1 | 13 | 24500 | 1 | 13 | 5480 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 3.9 | 39.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 0.9 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 4 | 0
1982-03-08 | 1900-03-07 | 12:00 | 12 | 958 | 1388 | 671 | 1 | 9 | 829 | 1 | 9 | 101 | 1 | 13 | 69900 | 1 | 9 | 82500 | 1 | 9 | 12800 | 1 | 13 | 2370 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 5.6 | 42.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.55 | A | 7 | 982 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.76 | 4 | 0
1982-03-08 | 1900-03-07 | 13:00 | 13 | 994 | 1388 | 757 | 1 | 9 | 936 | 1 | 9 | 90 | 1 | 13 | 79300 | 1 | 9 | 93400 | 1 | 9 | 12200 | 1 | 13 | 2410 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.58 | A | 7 | 983 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.74 | 4 | 0
1982-03-08 | 1900-03-07 | 14:00 | 14 | 957 | 1388 | 726 | 1 | 13 | 843 | 1 | 13 | 146 | 1 | 13 | 75300 | 1 | 13 | 84000 | 1 | 13 | 17200 | 1 | 13 | 3580 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 5.6 | 42.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.6 | A | 7 | 984 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.94 | 4 | 0
1982-03-08 | 1900-03-07 | 15:00 | 15 | 851 | 1388 | 631 | 1 | 9 | 901 | 1 | 9 | 80 | 1 | 13 | 66100 | 1 | 9 | 89200 | 1 | 9 | 11300 | 1 | 13 | 1910 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -3.9 | 24.98 | A | 7 | 0.53 | A | 7 | 985 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.78 | 4 | 0
1982-03-08 | 1900-03-07 | 16:00 | 16 | 681 | 1388 | 486 | 1 | 9 | 854 | 1 | 9 | 68 | 1 | 13 | 51100 | 1 | 9 | 83000 | 1 | 9 | 10300 | 1 | 13 | 1510 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.51 | A | 7 | 987 | A | 7 | 360 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 4 | 0
1982-03-08 | 1900-03-07 | 17:00 | 17 | 461 | 1388 | 282 | 1 | 9 | 707 | 1 | 9 | 49 | 1 | 13 | 30100 | 1 | 9 | 65200 | 1 | 9 | 8400 | 1 | 13 | 1060 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 1.7 | 35.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.38 | A | 7 | 988 | A | 7 | 350 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.52 | 4 | 0
1982-03-08 | 1900-03-07 | 18:00 | 18 | 205 | 1388 | 95 | 1 | 13 | 413 | 1 | 9 | 35 | 1 | 13 | 9900 | 1 | 13 | 27900 | 1 | 9 | 5800 | 1 | 13 | 640 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -1.1 | 30.02 | A | 7 | -11.7 | 10.94 | A | 7 | 0.45 | A | 7 | 990 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.94 | 4 | 0
1982-03-08 | 1900-03-07 | 19:00 | 19 | 10 | 405 | 8 | 1 | 13 | 27 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -2.8 | 26.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.61 | A | 7 | 991 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.066 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.58 | 4 | 0
1982-03-08 | 1900-03-07 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -3.9 | 24.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.6 | A | 7 | 991 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 4 | 0
1982-03-08 | 1900-03-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.63 | A | 7 | 992 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.72 | 4 | 0
1982-03-08 | 1900-03-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -10 | 14 | A | 7 | 0.68 | A | 7 | 992 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12 | 4 | 0
1982-03-08 | 1900-03-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -10.6 | 12.92 | A | 7 | 0.68 | A | 7 | 993 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.02 | 4 | 0
1982-03-08 | 1900-03-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.71 | A | 7 | 993 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.22 | 4 | 0
1982-03-09 | 1900-03-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 993 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 5 | 0
1982-03-09 | 1900-03-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 992 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 5 | 0
1982-03-09 | 1900-03-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 992 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 5 | 0
1982-03-09 | 1900-03-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 992 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 5 | 0
1982-03-09 | 1900-03-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 992 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.54 | 5 | 0
1982-03-09 | 1900-03-08 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 992 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.54 | 5 | 0
1982-03-09 | 1900-03-08 | 7:00 | 7 | 12 | 428 | 9 | 1 | 13 | 6 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 992 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 5 | 0
1982-03-09 | 1900-03-08 | 8:00 | 8 | 212 | 1387 | 34 | 1 | 13 | 17 | 1 | 9 | 31 | 1 | 13 | 3700 | 1 | 13 | 1300 | 1 | 9 | 3500 | 1 | 13 | 830 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 991 | A | 7 | 120 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.6 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 5 | 0
1982-03-09 | 1900-03-08 | 9:00 | 9 | 468 | 1387 | 111 | 1 | 9 | 10 | 1 | 9 | 107 | 1 | 13 | 12600 | 1 | 9 | 600 | 1 | 9 | 12400 | 1 | 13 | 4140 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -11.1 | 12.02 | A | 7 | 0.65 | A | 7 | 991 | A | 7 | 120 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 0.6 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.02 | 5 | 0
1982-03-09 | 1900-03-08 | 10:00 | 10 | 689 | 1387 | 362 | 1 | 13 | 264 | 1 | 13 | 232 | 1 | 13 | 38500 | 1 | 13 | 27300 | 1 | 13 | 24900 | 1 | 13 | 5390 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | -3.9 | 24.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.6 | A | 7 | 990 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 0.6 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 5 | 0
1982-03-09 | 1900-03-08 | 11:00 | 11 | 858 | 1387 | 378 | 1 | 9 | 222 | 1 | 9 | 241 | 1 | 13 | 41000 | 1 | 9 | 23700 | 1 | 9 | 26300 | 1 | 13 | 6060 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -3.3 | 26.06 | A | 7 | -10 | 14 | A | 7 | 0.6 | A | 7 | 989 | A | 7 | 110 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.6 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.6 | 5 | 0
1982-03-09 | 1900-03-08 | 12:00 | 12 | 964 | 1387 | 255 | 1 | 9 | 7 | 1 | 9 | 250 | 1 | 13 | 29800 | 1 | 9 | 600 | 1 | 9 | 29400 | 1 | 13 | 11210 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 988 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 0.6 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 5 | 0
1982-03-09 | 1900-03-08 | 13:00 | 13 | 1000 | 1387 | 460 | 1 | 9 | 283 | 1 | 9 | 257 | 1 | 13 | 50800 | 1 | 9 | 30600 | 1 | 9 | 28600 | 1 | 13 | 7440 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 0 | 32 | A | 7 | -8.9 | 15.98 | A | 7 | 0.52 | A | 7 | 987 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.6 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.78 | 5 | 0
1982-03-09 | 1900-03-08 | 14:00 | 14 | 963 | 1387 | 309 | 1 | 9 | 26 | 1 | 9 | 291 | 1 | 13 | 35700 | 1 | 9 | 2400 | 1 | 9 | 34100 | 1 | 13 | 12480 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -7.8 | 17.96 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 80 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 0.7 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.86 | 5 | 0
1982-03-09 | 1900-03-08 | 15:00 | 15 | 856 | 1387 | 445 | 1 | 13 | 349 | 1 | 13 | 231 | 1 | 13 | 48600 | 1 | 13 | 37300 | 1 | 13 | 25500 | 1 | 13 | 5760 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 1.7 | 35.06 | A | 7 | -7.2 | 19.04 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.7 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.54 | 5 | 0
1982-03-09 | 1900-03-08 | 16:00 | 16 | 687 | 1387 | 465 | 1 | 9 | 745 | 1 | 9 | 98 | 1 | 13 | 49600 | 1 | 9 | 73900 | 1 | 9 | 13000 | 1 | 13 | 2120 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 3.3 | 37.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.48 | A | 7 | 983 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.04 | 5 | 0
1982-03-09 | 1900-03-08 | 17:00 | 17 | 466 | 1387 | 283 | 1 | 9 | 645 | 1 | 9 | 68 | 1 | 13 | 29900 | 1 | 9 | 59200 | 1 | 9 | 10000 | 1 | 13 | 1330 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 3.9 | 39.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.46 | A | 7 | 982 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.84 | 5 | 0
1982-03-09 | 1900-03-08 | 18:00 | 18 | 210 | 1387 | 75 | 1 | 13 | 142 | 1 | 13 | 54 | 1 | 13 | 8000 | 1 | 13 | 9100 | 1 | 13 | 6600 | 1 | 13 | 1010 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 2.8 | 37.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.52 | A | 7 | 982 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 0.7 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.22 | 5 | 0
1982-03-09 | 1900-03-08 | 19:00 | 19 | 11 | 428 | 7 | 1 | 13 | 10 | 1 | 13 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 1.7 | 35.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.59 | A | 7 | 982 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.06 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 5 | 0
1982-03-09 | 1900-03-08 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 0.6 | 33.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.64 | A | 7 | 982 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 5 | 0
1982-03-09 | 1900-03-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.22 | 5 | 0
1982-03-09 | 1900-03-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.42 | 5 | 0
1982-03-09 | 1900-03-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.72 | 5 | 0
1982-03-09 | 1900-03-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 5 | 0
1982-03-10 | 1900-03-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 6 | 0
1982-03-10 | 1900-03-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -3.3 | 26.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 6 | 0
1982-03-10 | 1900-03-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -3.3 | 26.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 6 | 0
1982-03-10 | 1900-03-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 6 | 0
1982-03-10 | 1900-03-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.82 | 6 | 0
1982-03-10 | 1900-03-09 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 6 | 0
1982-03-10 | 1900-03-09 | 7:00 | 7 | 14 | 474 | 6 | 1 | 13 | 14 | 1 | 9 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | -2.8 | 26.96 | A | 7 | -5 | 23 | A | 7 | 0.85 | A | 7 | 977 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.7 | 6 | 0
1982-03-10 | 1900-03-09 | 8:00 | 8 | 219 | 1386 | 90 | 1 | 13 | 234 | 1 | 9 | 54 | 1 | 13 | 9400 | 1 | 13 | 15600 | 1 | 9 | 7000 | 1 | 13 | 980 | 1 | 21 | 8 | A | 7 | 2 | A | 7 | 3.3 | 37.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 6 | 0
1982-03-10 | 1900-03-09 | 9:00 | 9 | 475 | 1386 | 244 | 1 | 13 | 399 | 1 | 13 | 109 | 1 | 13 | 25900 | 1 | 13 | 36800 | 1 | 13 | 13300 | 1 | 13 | 2060 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 6.1 | 42.98 | A | 7 | 0 | 32 | A | 7 | 0.65 | A | 7 | 976 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.2 | 6 | 0
1982-03-10 | 1900-03-09 | 10:00 | 10 | 695 | 1386 | 427 | 1 | 13 | 544 | 1 | 13 | 156 | 1 | 13 | 45800 | 1 | 13 | 54600 | 1 | 13 | 18300 | 1 | 13 | 3270 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 11.1 | 51.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.53 | A | 7 | 976 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.36 | 6 | 0
1982-03-10 | 1900-03-09 | 11:00 | 11 | 864 | 1386 | 628 | 1 | 13 | 762 | 1 | 13 | 155 | 1 | 13 | 66400 | 1 | 13 | 76700 | 1 | 13 | 18400 | 1 | 13 | 3780 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 12.8 | 55.04 | A | 7 | 2.8 | 37.04 | A | 7 | 0.51 | A | 7 | 975 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.74 | 6 | 0
1982-03-10 | 1900-03-09 | 12:00 | 12 | 970 | 1386 | 615 | 1 | 9 | 634 | 1 | 9 | 173 | 1 | 13 | 65300 | 1 | 9 | 64300 | 1 | 9 | 20200 | 1 | 13 | 4830 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 4.4 | 39.92 | A | 7 | 0.48 | A | 7 | 975 | A | 7 | 210 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.02 | 6 | 0
1982-03-10 | 1900-03-09 | 13:00 | 13 | 1006 | 1386 | 627 | 1 | 13 | 537 | 1 | 13 | 238 | 1 | 13 | 67600 | 1 | 13 | 55900 | 1 | 13 | 27000 | 1 | 13 | 7030 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 17.2 | 62.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.43 | A | 7 | 974 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.32 | 6 | 0
1982-03-10 | 1900-03-09 | 14:00 | 14 | 969 | 1386 | 499 | 1 | 13 | 336 | 1 | 13 | 264 | 1 | 13 | 54600 | 1 | 13 | 36200 | 1 | 13 | 29200 | 1 | 13 | 7420 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 18.3 | 64.94 | A | 7 | 5 | 41 | A | 7 | 0.42 | A | 7 | 972 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.1 | 6 | 0
1982-03-10 | 1900-03-09 | 15:00 | 15 | 862 | 1386 | 506 | 1 | 13 | 518 | 1 | 13 | 185 | 1 | 13 | 54800 | 1 | 13 | 53400 | 1 | 13 | 21500 | 1 | 13 | 4460 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 19.4 | 66.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.42 | A | 7 | 971 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.68 | 6 | 0
1982-03-10 | 1900-03-09 | 16:00 | 16 | 692 | 1386 | 367 | 1 | 13 | 412 | 1 | 13 | 162 | 1 | 13 | 39100 | 1 | 13 | 41300 | 1 | 13 | 18400 | 1 | 13 | 3400 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.32 | A | 7 | 971 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.38 | 6 | 0
1982-03-10 | 1900-03-09 | 17:00 | 17 | 471 | 1386 | 260 | 1 | 13 | 472 | 1 | 13 | 101 | 1 | 13 | 27700 | 1 | 13 | 43400 | 1 | 13 | 12900 | 1 | 13 | 1900 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 21.1 | 69.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.38 | A | 7 | 970 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.08 | 6 | 0
1982-03-10 | 1900-03-09 | 18:00 | 18 | 215 | 1386 | 67 | 1 | 13 | 90 | 1 | 13 | 53 | 1 | 13 | 7300 | 1 | 13 | 6300 | 1 | 13 | 6300 | 1 | 13 | 1120 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 20 | 68 | A | 7 | 6.1 | 42.98 | A | 7 | 0.41 | A | 7 | 969 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.48 | 6 | 0
1982-03-10 | 1900-03-09 | 19:00 | 19 | 13 | 451 | 6 | 1 | 13 | 2 | 1 | 13 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.52 | A | 7 | 970 | A | 7 | 210 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.86 | 6 | 0
1982-03-10 | 1900-03-09 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 17.2 | 62.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.52 | 6 | 0
1982-03-10 | 1900-03-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 15 | 59 | A | 7 | 10 | 50 | A | 7 | 0.72 | A | 7 | 971 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.5 | 6 | 0
1982-03-10 | 1900-03-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 13.3 | 55.94 | A | 7 | 10 | 50 | A | 7 | 0.8 | A | 7 | 972 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.8 | 6 | 0
1982-03-10 | 1900-03-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.83 | A | 7 | 972 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.28 | 6 | 0
1982-03-10 | 1900-03-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 9.4 | 48.92 | A | 7 | 0.78 | A | 7 | 973 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 1280 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.42 | 6 | 0
1982-03-11 | 1900-03-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 10 | 50 | A | 7 | 3.3 | 37.94 | A | 7 | 0.64 | A | 7 | 974 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.44 | 7 | 0
1982-03-11 | 1900-03-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | 2.8 | 37.04 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.14 | 7 | 0
1982-03-11 | 1900-03-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.8 | A | 7 | 976 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.44 | 7 | 0
1982-03-11 | 1900-03-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.74 | 7 | 0
1982-03-11 | 1900-03-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 7 | 0
1982-03-11 | 1900-03-10 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 978 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 240 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.16 | 7 | 0
1982-03-11 | 1900-03-10 | 7:00 | 7 | 16 | 497 | 5 | 1 | 13 | 0 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.89 | A | 7 | 979 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.76 | 7 | 0
1982-03-11 | 1900-03-10 | 8:00 | 8 | 227 | 1386 | 52 | 1 | 13 | 1 | 1 | 9 | 52 | 1 | 13 | 5900 | 1 | 13 | 0 | 1 | 9 | 5800 | 1 | 13 | 1800 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 240 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.76 | 7 | 0
1982-03-11 | 1900-03-10 | 9:00 | 9 | 482 | 1386 | 117 | 1 | 9 | 1 | 1 | 9 | 117 | 1 | 13 | 13300 | 1 | 9 | 100 | 1 | 9 | 13300 | 1 | 13 | 4480 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.86 | A | 7 | 981 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 270 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.46 | 7 | 0
1982-03-11 | 1900-03-10 | 10:00 | 10 | 702 | 1386 | 201 | 1 | 9 | 9 | 1 | 9 | 197 | 1 | 13 | 23000 | 1 | 9 | 700 | 1 | 9 | 22600 | 1 | 13 | 7930 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 270 | A | 7 | 1.1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 7 | 0
1982-03-11 | 1900-03-10 | 11:00 | 11 | 871 | 1386 | 245 | 1 | 9 | 7 | 1 | 9 | 241 | 1 | 13 | 28400 | 1 | 9 | 600 | 1 | 9 | 28000 | 1 | 13 | 10340 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.7 | 35.06 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 270 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.96 | 7 | 0
1982-03-11 | 1900-03-10 | 12:00 | 12 | 977 | 1386 | 343 | 1 | 9 | 48 | 1 | 9 | 309 | 1 | 13 | 37800 | 1 | 9 | 4900 | 1 | 9 | 34300 | 1 | 13 | 11050 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 5.6 | 42.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 340 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 370 | A | 7 | 1.1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.78 | 7 | 0
1982-03-11 | 1900-03-10 | 13:00 | 13 | 1012 | 1386 | 753 | 1 | 13 | 774 | 1 | 13 | 191 | 1 | 13 | 79900 | 1 | 13 | 78400 | 1 | 13 | 22400 | 1 | 13 | 5660 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 7.2 | 44.96 | A | 7 | 2.2 | 35.96 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.56 | 7 | 0
1982-03-11 | 1900-03-10 | 14:00 | 14 | 974 | 1386 | 657 | 1 | 9 | 829 | 1 | 9 | 75 | 1 | 13 | 69000 | 1 | 9 | 82800 | 1 | 9 | 10600 | 1 | 13 | 2150 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 2.2 | 35.96 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.36 | 7 | 0
1982-03-11 | 1900-03-10 | 15:00 | 15 | 867 | 1386 | 638 | 1 | 9 | 881 | 1 | 9 | 89 | 1 | 13 | 66800 | 1 | 9 | 87300 | 1 | 9 | 12000 | 1 | 13 | 2010 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.54 | 7 | 0
1982-03-11 | 1900-03-10 | 16:00 | 16 | 697 | 1386 | 456 | 1 | 9 | 749 | 1 | 9 | 80 | 1 | 13 | 48400 | 1 | 9 | 73700 | 1 | 9 | 11200 | 1 | 13 | 1770 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 10.6 | 51.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.56 | 7 | 0
1982-03-11 | 1900-03-10 | 17:00 | 17 | 476 | 1386 | 248 | 1 | 13 | 377 | 1 | 13 | 119 | 1 | 13 | 25900 | 1 | 13 | 34700 | 1 | 13 | 14000 | 1 | 13 | 2280 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 10.6 | 51.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 90 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.56 | 7 | 0
1982-03-11 | 1900-03-10 | 18:00 | 18 | 219 | 1386 | 87 | 1 | 13 | 184 | 1 | 13 | 58 | 1 | 13 | 9200 | 1 | 13 | 12100 | 1 | 13 | 7300 | 1 | 13 | 1090 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 10 | 50 | A | 7 | 2.8 | 37.04 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.24 | 7 | 0
1982-03-11 | 1900-03-10 | 19:00 | 19 | 14 | 473 | 9 | 1 | 13 | 7 | 1 | 13 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 8.3 | 46.94 | A | 7 | 3.3 | 37.94 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.34 | 7 | 0
1982-03-11 | 1900-03-10 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 7.2 | 44.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.04 | 7 | 0
1982-03-11 | 1900-03-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 5.6 | 42.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.83 | A | 7 | 976 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.94 | 7 | 0
1982-03-11 | 1900-03-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 4.4 | 39.92 | A | 7 | 2.2 | 35.96 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.26 | 7 | 0
1982-03-11 | 1900-03-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 4.4 | 39.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.74 | 7 | 0
1982-03-11 | 1900-03-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 2.8 | 37.04 | A | 7 | 0.86 | A | 7 | 974 | A | 7 | 110 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 1040 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.34 | 7 | 0
1982-03-12 | 1900-03-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 1 | 0
1982-03-12 | 1900-03-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 972 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 1340 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 1 | 0
1982-03-12 | 1900-03-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 970 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 1 | 0
1982-03-12 | 1900-03-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 969 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 430 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 1 | 0
1982-03-12 | 1900-03-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 5.6 | 42.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.86 | A | 7 | 968 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 430 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.24 | 1 | 0
1982-03-12 | 1900-03-11 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.86 | A | 7 | 967 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 210 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.12 | 1 | 0
1982-03-12 | 1900-03-11 | 7:00 | 7 | 19 | 542 | 6 | 1 | 13 | 2 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 965 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 180 | A | 7 | 1.6 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.06 | 1 | 0
1982-03-12 | 1900-03-11 | 8:00 | 8 | 234 | 1385 | 66 | 1 | 13 | 12 | 1 | 9 | 64 | 1 | 13 | 7300 | 1 | 13 | 300 | 1 | 9 | 7200 | 1 | 13 | 2090 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 965 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 210 | A | 7 | 1.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.92 | 1 | 0
1982-03-12 | 1900-03-11 | 9:00 | 9 | 489 | 1385 | 122 | 1 | 9 | 13 | 1 | 9 | 118 | 1 | 13 | 13900 | 1 | 9 | 800 | 1 | 9 | 13600 | 1 | 13 | 4540 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.93 | A | 7 | 963 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 4800 | A | 7 | 180 | A | 7 | 2.2 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.76 | 1 | 0
1982-03-12 | 1900-03-11 | 10:00 | 10 | 709 | 1385 | 245 | 1 | 9 | 2 | 1 | 9 | 244 | 1 | 13 | 27500 | 1 | 9 | 200 | 1 | 9 | 27400 | 1 | 13 | 9130 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.84 | A | 7 | 962 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 6400 | A | 7 | 310 | A | 7 | 2.3 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.14 | 1 | 0
1982-03-12 | 1900-03-11 | 11:00 | 11 | 877 | 1385 | 405 | 1 | 9 | 88 | 1 | 9 | 350 | 1 | 13 | 44600 | 1 | 9 | 9000 | 1 | 9 | 38800 | 1 | 13 | 11040 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 961 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 9700 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.44 | 1 | 0
1982-03-12 | 1900-03-11 | 12:00 | 12 | 983 | 1385 | 287 | 1 | 9 | 12 | 1 | 9 | 278 | 1 | 13 | 33300 | 1 | 9 | 1100 | 1 | 9 | 32600 | 1 | 13 | 12240 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.68 | A | 7 | 960 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 2290 | A | 7 | 2.2 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.34 | 1 | 0
1982-03-12 | 1900-03-11 | 13:00 | 13 | 1018 | 1385 | 190 | 1 | 9 | 18 | 1 | 9 | 176 | 1 | 13 | 21000 | 1 | 9 | 1800 | 1 | 9 | 19700 | 1 | 13 | 7050 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 13.9 | 57.02 | A | 7 | 0.68 | A | 7 | 959 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 12900 | A | 7 | 2290 | A | 7 | 2.4 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.12 | 1 | 0
1982-03-12 | 1900-03-11 | 14:00 | 14 | 980 | 1385 | 197 | 1 | 9 | 5 | 1 | 9 | 194 | 1 | 13 | 23600 | 1 | 9 | 400 | 1 | 9 | 23300 | 1 | 13 | 9290 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 13.3 | 55.94 | A | 7 | 0.66 | A | 7 | 959 | A | 7 | 270 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 2290 | A | 7 | 2.3 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.74 | 1 | 0
1982-03-12 | 1900-03-11 | 15:00 | 15 | 872 | 1385 | 327 | 1 | 9 | 102 | 1 | 9 | 263 | 1 | 13 | 36000 | 1 | 9 | 10300 | 1 | 9 | 29500 | 1 | 13 | 8810 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.53 | A | 7 | 959 | A | 7 | 230 | A | 7 | 9.3 | A | 7 | 12900 | A | 7 | 2440 | A | 7 | 2.2 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.44 | 1 | 0
1982-03-12 | 1900-03-11 | 16:00 | 16 | 702 | 1385 | 196 | 1 | 9 | 6 | 1 | 9 | 193 | 1 | 13 | 22400 | 1 | 9 | 500 | 1 | 9 | 22100 | 1 | 13 | 7820 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.51 | A | 7 | 959 | A | 7 | 230 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 2.1 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.46 | 1 | 0
1982-03-12 | 1900-03-11 | 17:00 | 17 | 480 | 1385 | 170 | 1 | 9 | 19 | 1 | 9 | 164 | 1 | 13 | 18800 | 1 | 9 | 1400 | 1 | 9 | 18300 | 1 | 13 | 5540 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.67 | A | 7 | 963 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 1.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.72 | 1 | 0
1982-03-12 | 1900-03-11 | 18:00 | 18 | 224 | 1385 | 64 | 1 | 13 | 65 | 1 | 13 | 53 | 1 | 13 | 7000 | 1 | 13 | 4600 | 1 | 13 | 6200 | 1 | 13 | 1130 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 12.8 | 55.04 | A | 7 | 8.3 | 46.94 | A | 7 | 0.75 | A | 7 | 965 | A | 7 | 310 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 1.7 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.14 | 1 | 0
1982-03-12 | 1900-03-11 | 19:00 | 19 | 16 | 496 | 10 | 1 | 13 | 2 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 7.8 | 46.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.89 | A | 7 | 968 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 1280 | A | 7 | 1.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.48 | 1 | 0
1982-03-12 | 1900-03-11 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 7.8 | 46.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.74 | A | 7 | 970 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1980 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.74 | 1 | 0
1982-03-12 | 1900-03-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 2.8 | 37.04 | A | 7 | 0.76 | A | 7 | 971 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.14 | 1 | 0
1982-03-12 | 1900-03-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 972 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 1 | 0
1982-03-12 | 1900-03-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 3.9 | 39.02 | A | 7 | 0 | 32 | A | 7 | 0.76 | A | 7 | 974 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.4 | 1 | 0
1982-03-12 | 1900-03-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.72 | 1 | 0
1982-03-13 | 1900-03-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.92 | 2 | 0
1982-03-13 | 1900-03-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.22 | 2 | 0
1982-03-13 | 1900-03-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.14 | 2 | 0
1982-03-13 | 1900-03-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 978 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.94 | 2 | 0
1982-03-13 | 1900-03-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 979 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 2 | 0
1982-03-13 | 1900-03-12 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 1.1 | 33.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.14 | 2 | 0
1982-03-13 | 1900-03-12 | 7:00 | 7 | 22 | 565 | 16 | 1 | 13 | 28 | 1 | 9 | 12 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 2 | 0
1982-03-13 | 1900-03-12 | 8:00 | 8 | 241 | 1384 | 109 | 1 | 13 | 316 | 1 | 9 | 56 | 1 | 13 | 11600 | 1 | 13 | 22200 | 1 | 9 | 7700 | 1 | 13 | 1010 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | 2.2 | 35.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.02 | 2 | 0
1982-03-13 | 1900-03-12 | 9:00 | 9 | 496 | 1384 | 279 | 1 | 9 | 544 | 1 | 9 | 87 | 1 | 13 | 29300 | 1 | 9 | 50300 | 1 | 9 | 11200 | 1 | 13 | 1670 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 6.1 | 42.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.68 | A | 7 | 982 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.48 | 2 | 0
1982-03-13 | 1900-03-12 | 10:00 | 10 | 716 | 1384 | 464 | 1 | 9 | 683 | 1 | 9 | 113 | 1 | 13 | 49300 | 1 | 9 | 67800 | 1 | 9 | 14100 | 1 | 13 | 2470 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 8.9 | 48.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.61 | A | 7 | 984 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.36 | 2 | 0
1982-03-13 | 1900-03-12 | 11:00 | 11 | 884 | 1384 | 587 | 1 | 13 | 663 | 1 | 13 | 166 | 1 | 13 | 62000 | 1 | 13 | 66700 | 1 | 13 | 19200 | 1 | 13 | 4120 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 11.7 | 53.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.49 | A | 7 | 984 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.98 | 2 | 0
1982-03-13 | 1900-03-12 | 12:00 | 12 | 989 | 1384 | 682 | 1 | 13 | 706 | 1 | 13 | 179 | 1 | 13 | 72300 | 1 | 13 | 71600 | 1 | 13 | 21000 | 1 | 13 | 5150 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 13.9 | 57.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.32 | A | 7 | 984 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.46 | 2 | 0
1982-03-13 | 1900-03-12 | 13:00 | 13 | 1024 | 1384 | 466 | 1 | 13 | 319 | 1 | 13 | 231 | 1 | 13 | 50600 | 1 | 13 | 33200 | 1 | 13 | 25900 | 1 | 13 | 7030 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 15.6 | 60.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.3 | A | 7 | 984 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.14 | 2 | 0
1982-03-13 | 1900-03-12 | 14:00 | 14 | 986 | 1384 | 712 | 1 | 13 | 752 | 1 | 13 | 178 | 1 | 13 | 75500 | 1 | 13 | 76300 | 1 | 13 | 21000 | 1 | 13 | 5090 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 15.6 | 60.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.28 | A | 7 | 983 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.06 | 2 | 0
1982-03-13 | 1900-03-12 | 15:00 | 15 | 877 | 1384 | 605 | 1 | 13 | 726 | 1 | 13 | 146 | 1 | 13 | 64300 | 1 | 13 | 73400 | 1 | 13 | 17600 | 1 | 13 | 3660 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 16.1 | 60.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.27 | A | 7 | 983 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.96 | 2 | 0
1982-03-13 | 1900-03-12 | 16:00 | 16 | 707 | 1384 | 393 | 1 | 13 | 317 | 1 | 13 | 232 | 1 | 13 | 41900 | 1 | 13 | 32900 | 1 | 13 | 25000 | 1 | 13 | 5410 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 16.1 | 60.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.25 | A | 7 | 983 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.18 | 2 | 0
1982-03-13 | 1900-03-12 | 17:00 | 17 | 485 | 1384 | 165 | 1 | 9 | 113 | 1 | 9 | 126 | 1 | 13 | 18200 | 1 | 9 | 10800 | 1 | 9 | 14400 | 1 | 13 | 2880 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 15.6 | 60.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.25 | A | 7 | 983 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.48 | 2 | 0
1982-03-13 | 1900-03-12 | 18:00 | 18 | 229 | 1384 | 90 | 1 | 13 | 210 | 1 | 13 | 56 | 1 | 13 | 9400 | 1 | 13 | 14300 | 1 | 13 | 7000 | 1 | 13 | 1020 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 14.4 | 57.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.25 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 6100 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.82 | 2 | 0
1982-03-13 | 1900-03-12 | 19:00 | 19 | 17 | 519 | 14 | 1 | 13 | 19 | 1 | 13 | 12 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 11.1 | 51.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.35 | A | 7 | 983 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.18 | 2 | 0
1982-03-13 | 1900-03-12 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 7.2 | 44.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.54 | A | 7 | 983 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 2 | 0
1982-03-13 | 1900-03-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 9.4 | 48.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.43 | A | 7 | 983 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.56 | 2 | 0
1982-03-13 | 1900-03-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 5 | A | 7 | 8.9 | 48.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.44 | A | 7 | 983 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.66 | 2 | 0
1982-03-13 | 1900-03-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 6 | A | 7 | 9.4 | 48.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.43 | A | 7 | 984 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.56 | 2 | 0
1982-03-13 | 1900-03-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 8.9 | 48.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.42 | A | 7 | 983 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.66 | 2 | 0
1982-03-14 | 1900-03-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.44 | 3 | 0
1982-03-14 | 1900-03-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.92 | 3 | 0
1982-03-14 | 1900-03-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.72 | 3 | 0
1982-03-14 | 1900-03-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.56 | A | 7 | 982 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.52 | 3 | 0
1982-03-14 | 1900-03-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 3 | 0
1982-03-14 | 1900-03-13 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.5 | A | 7 | 981 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.94 | 3 | 0
1982-03-14 | 1900-03-13 | 7:00 | 7 | 24 | 611 | 7 | 1 | 13 | 1 | 1 | 9 | 7 | 1 | 13 | 800 | 1 | 13 | 0 | 1 | 9 | 800 | 1 | 13 | 260 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.5 | A | 7 | 982 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1400 | A | 7 | 1 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.82 | 3 | 0
1982-03-14 | 1900-03-13 | 8:00 | 8 | 248 | 1383 | 44 | 1 | 13 | 1 | 1 | 9 | 44 | 1 | 13 | 5100 | 1 | 13 | 0 | 1 | 9 | 5100 | 1 | 13 | 1640 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 0 | 32 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1340 | A | 7 | 1.1 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.2 | 3 | 0
1982-03-14 | 1900-03-13 | 9:00 | 9 | 503 | 1383 | 63 | 1 | 9 | 8 | 1 | 9 | 60 | 1 | 13 | 7600 | 1 | 9 | 400 | 1 | 9 | 7400 | 1 | 13 | 2660 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 100 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 610 | A | 7 | 1.2 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.96 | 3 | 0
1982-03-14 | 1900-03-13 | 10:00 | 10 | 723 | 1383 | 128 | 1 | 9 | 1 | 1 | 9 | 128 | 1 | 13 | 15200 | 1 | 9 | 100 | 1 | 9 | 15200 | 1 | 13 | 5810 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.89 | A | 7 | 979 | A | 7 | 100 | A | 7 | 10.3 | A | 7 | 8000 | A | 7 | 610 | A | 7 | 1.4 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.52 | 3 | 0
1982-03-14 | 1900-03-13 | 11:00 | 11 | 890 | 1383 | 151 | 1 | 9 | 7 | 1 | 9 | 146 | 1 | 13 | 18100 | 1 | 9 | 500 | 1 | 9 | 17800 | 1 | 13 | 7070 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 100 | A | 7 | 11.8 | A | 7 | 11300 | A | 7 | 240 | A | 7 | 1.4 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40 | 3 | 0
1982-03-14 | 1900-03-13 | 12:00 | 12 | 995 | 1383 | 189 | 1 | 9 | 7 | 1 | 9 | 184 | 1 | 13 | 22700 | 1 | 9 | 500 | 1 | 9 | 22400 | 1 | 13 | 8960 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 100 | A | 7 | 12.9 | A | 7 | 16100 | A | 7 | 340 | A | 7 | 1.4 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.5 | 3 | 0
1982-03-14 | 1900-03-13 | 13:00 | 13 | 1029 | 1383 | 311 | 1 | 9 | 5 | 1 | 9 | 307 | 1 | 13 | 36100 | 1 | 9 | 500 | 1 | 9 | 35800 | 1 | 13 | 13440 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.86 | A | 7 | 975 | A | 7 | 90 | A | 7 | 12.9 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 1.4 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.12 | 3 | 0
1982-03-14 | 1900-03-13 | 14:00 | 14 | 991 | 1383 | 335 | 1 | 9 | 1 | 1 | 9 | 334 | 1 | 13 | 38400 | 1 | 9 | 100 | 1 | 9 | 38400 | 1 | 13 | 13900 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.86 | A | 7 | 974 | A | 7 | 100 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 1.4 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.12 | 3 | 0
1982-03-14 | 1900-03-13 | 15:00 | 15 | 883 | 1383 | 173 | 1 | 9 | 0 | 1 | 9 | 173 | 1 | 13 | 20600 | 1 | 9 | 0 | 1 | 9 | 20600 | 1 | 13 | 8100 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 100 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 1.4 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.5 | 3 | 0
1982-03-14 | 1900-03-13 | 16:00 | 16 | 712 | 1383 | 139 | 1 | 9 | 0 | 1 | 9 | 139 | 1 | 13 | 16300 | 1 | 9 | 0 | 1 | 9 | 16300 | 1 | 13 | 6160 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.96 | A | 7 | 974 | A | 7 | 90 | A | 7 | 6.7 | A | 7 | 4800 | A | 7 | 210 | A | 7 | 1.5 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.48 | 3 | 0
1982-03-14 | 1900-03-13 | 17:00 | 17 | 490 | 1383 | 87 | 1 | 9 | 0 | 1 | 9 | 87 | 1 | 13 | 10100 | 1 | 9 | 0 | 1 | 9 | 10100 | 1 | 13 | 3610 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 100 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 150 | A | 7 | 1.5 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.48 | 3 | 0
1982-03-14 | 1900-03-13 | 18:00 | 18 | 234 | 1383 | 57 | 1 | 13 | 0 | 1 | 9 | 57 | 1 | 13 | 6400 | 1 | 13 | 0 | 1 | 9 | 6400 | 1 | 13 | 1940 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 90 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 180 | A | 7 | 1.4 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40 | 3 | 0
1982-03-14 | 1900-03-13 | 19:00 | 19 | 19 | 542 | 10 | 1 | 13 | 0 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 90 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 120 | A | 7 | 1.5 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.48 | 3 | 0
1982-03-14 | 1900-03-13 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 90 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 120 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.48 | 3 | 0
1982-03-14 | 1900-03-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 80 | A | 7 | 6.7 | A | 7 | 4800 | A | 7 | 90 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.4 | 3 | 0
1982-03-14 | 1900-03-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 80 | A | 7 | 8.2 | A | 7 | 6400 | A | 7 | 90 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.4 | 3 | 0
1982-03-14 | 1900-03-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 90 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.4 | 3 | 0
1982-03-14 | 1900-03-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 60 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.4 | 3 | 0
1982-03-15 | 1900-03-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 2400 | A | 7 | 60 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.4 | 4 | 0
1982-03-15 | 1900-03-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 1600 | A | 7 | 60 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.4 | 4 | 0
1982-03-15 | 1900-03-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 800 | A | 7 | 30 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.4 | 4 | 0
1982-03-15 | 1900-03-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 972 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 800 | A | 7 | 30 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.9 | 4 | 0
1982-03-15 | 1900-03-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 972 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 400 | A | 7 | 30 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.9 | 4 | 0
1982-03-15 | 1900-03-14 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 972 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 200 | A | 7 | 30 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.9 | 4 | 0
1982-03-15 | 1900-03-14 | 7:00 | 7 | 27 | 634 | 12 | 1 | 13 | 0 | 1 | 9 | 12 | 1 | 13 | 1400 | 1 | 13 | 0 | 1 | 9 | 1400 | 1 | 13 | 420 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 971 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 100 | A | 7 | 30 | A | 7 | 1.4 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.9 | 4 | 0
1982-03-15 | 1900-03-14 | 8:00 | 8 | 255 | 1383 | 81 | 1 | 13 | 0 | 1 | 9 | 81 | 1 | 13 | 8900 | 1 | 13 | 0 | 1 | 9 | 8900 | 1 | 13 | 2520 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 971 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 200 | A | 7 | 30 | A | 7 | 1.4 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.4 | 4 | 0
1982-03-15 | 1900-03-14 | 9:00 | 9 | 510 | 1383 | 184 | 1 | 9 | 1 | 1 | 9 | 184 | 1 | 13 | 20300 | 1 | 9 | 100 | 1 | 9 | 20300 | 1 | 13 | 6150 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 6.1 | 42.98 | A | 7 | 1 | A | 7 | 971 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 3200 | A | 7 | 180 | A | 7 | 1.5 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.88 | 4 | 0
1982-03-15 | 1900-03-14 | 10:00 | 10 | 729 | 1383 | 411 | 1 | 13 | 444 | 1 | 13 | 179 | 1 | 13 | 43800 | 1 | 13 | 44800 | 1 | 13 | 20100 | 1 | 13 | 3880 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 7.8 | 46.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.96 | A | 7 | 971 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 210 | A | 7 | 1.6 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.36 | 4 | 0
1982-03-15 | 1900-03-14 | 11:00 | 11 | 897 | 1383 | 279 | 1 | 9 | 35 | 1 | 9 | 256 | 1 | 13 | 30700 | 1 | 9 | 3500 | 1 | 9 | 28400 | 1 | 13 | 8820 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 10.6 | 51.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.86 | A | 7 | 971 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 1.7 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.84 | 4 | 0
1982-03-15 | 1900-03-14 | 12:00 | 12 | 1001 | 1383 | 679 | 1 | 13 | 677 | 1 | 13 | 192 | 1 | 13 | 72000 | 1 | 13 | 68500 | 1 | 13 | 22200 | 1 | 13 | 5600 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 12.8 | 55.04 | A | 7 | 9.4 | 48.92 | A | 7 | 0.8 | A | 7 | 969 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.82 | 4 | 0
1982-03-15 | 1900-03-14 | 13:00 | 13 | 1035 | 1383 | 745 | 1 | 9 | 879 | 1 | 9 | 89 | 1 | 13 | 77900 | 1 | 9 | 87900 | 1 | 9 | 11900 | 1 | 13 | 2580 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.8 | A | 7 | 967 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.78 | 4 | 0
1982-03-15 | 1900-03-14 | 14:00 | 14 | 996 | 1383 | 719 | 1 | 9 | 823 | 1 | 9 | 127 | 1 | 13 | 76200 | 1 | 9 | 82800 | 1 | 9 | 16300 | 1 | 13 | 3540 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.73 | A | 7 | 966 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.46 | 4 | 0
1982-03-15 | 1900-03-14 | 15:00 | 15 | 888 | 1383 | 424 | 1 | 13 | 285 | 1 | 13 | 241 | 1 | 13 | 46200 | 1 | 13 | 30500 | 1 | 13 | 26600 | 1 | 13 | 6210 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 16.7 | 62.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.73 | A | 7 | 965 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 2.1 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.46 | 4 | 0
1982-03-15 | 1900-03-14 | 16:00 | 16 | 717 | 1383 | 376 | 1 | 9 | 342 | 1 | 9 | 199 | 1 | 13 | 40600 | 1 | 9 | 35700 | 1 | 9 | 22000 | 1 | 13 | 4510 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 18.9 | 66.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.68 | A | 7 | 964 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 820 | A | 7 | 2.2 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.34 | 4 | 0
1982-03-15 | 1900-03-14 | 17:00 | 17 | 495 | 1383 | 123 | 1 | 9 | 9 | 1 | 9 | 120 | 1 | 13 | 14000 | 1 | 9 | 600 | 1 | 9 | 13800 | 1 | 13 | 4630 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 963 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 2.3 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.04 | 4 | 0
1982-03-15 | 1900-03-14 | 18:00 | 18 | 238 | 1383 | 44 | 1 | 13 | 7 | 1 | 9 | 43 | 1 | 13 | 5100 | 1 | 13 | 100 | 1 | 9 | 5000 | 1 | 13 | 1590 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 961 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 2.3 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.44 | 4 | 0
1982-03-15 | 1900-03-14 | 19:00 | 19 | 20 | 565 | 6 | 1 | 13 | 1 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.81 | A | 7 | 961 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 760 | A | 7 | 2.3 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 4 | 0
1982-03-15 | 1900-03-14 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.84 | A | 7 | 960 | A | 7 | 100 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 1520 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.14 | 4 | 0
1982-03-15 | 1900-03-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 960 | A | 7 | 280 | A | 7 | 14.4 | A | 7 | 800 | A | 7 | 90 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.14 | 4 | 0
1982-03-15 | 1900-03-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.96 | A | 7 | 961 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1490 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.34 | 4 | 0
1982-03-15 | 1900-03-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.96 | A | 7 | 961 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 1370 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.36 | 4 | 0
1982-03-15 | 1900-03-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.96 | A | 7 | 959 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.28 | 4 | 0
1982-03-16 | 1900-03-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 12.2 | 53.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.93 | A | 7 | 959 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.78 | 5 | 0
1982-03-16 | 1900-03-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.96 | A | 7 | 959 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.28 | 5 | 0
1982-03-16 | 1900-03-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.93 | A | 7 | 959 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.78 | 5 | 0
1982-03-16 | 1900-03-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 10 | 50 | A | 7 | 0.86 | A | 7 | 960 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.8 | 5 | 0
1982-03-16 | 1900-03-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 10.6 | 51.08 | A | 7 | 10 | 50 | A | 7 | 0.96 | A | 7 | 961 | A | 7 | 240 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 240 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 5 | 0
1982-03-16 | 1900-03-15 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.96 | A | 7 | 963 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 90 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.42 | 5 | 0
1982-03-16 | 1900-03-15 | 7:00 | 7 | 31 | 679 | 8 | 1 | 13 | 1 | 1 | 9 | 8 | 1 | 13 | 1000 | 1 | 13 | 0 | 1 | 9 | 1000 | 1 | 13 | 300 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 9.4 | 48.92 | A | 7 | 1 | A | 7 | 964 | A | 7 | 270 | A | 7 | 5.7 | A | 7 | 3200 | A | 7 | 60 | A | 7 | 1.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.82 | 5 | 0
1982-03-16 | 1900-03-15 | 8:00 | 8 | 262 | 1382 | 68 | 1 | 13 | 1 | 1 | 9 | 68 | 1 | 13 | 7600 | 1 | 13 | 0 | 1 | 9 | 7600 | 1 | 13 | 2300 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 966 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 150 | A | 7 | 1.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 5 | 0
1982-03-16 | 1900-03-15 | 9:00 | 9 | 517 | 1382 | 146 | 1 | 9 | 45 | 1 | 9 | 129 | 1 | 13 | 16000 | 1 | 9 | 4300 | 1 | 9 | 14400 | 1 | 13 | 3670 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 10.6 | 51.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.93 | A | 7 | 967 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 180 | A | 7 | 1.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.82 | 5 | 0
1982-03-16 | 1900-03-15 | 10:00 | 10 | 736 | 1382 | 460 | 1 | 9 | 503 | 1 | 9 | 194 | 1 | 13 | 48600 | 1 | 9 | 50800 | 1 | 9 | 21500 | 1 | 13 | 4260 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 11.7 | 53.06 | A | 7 | 10 | 50 | A | 7 | 0.9 | A | 7 | 968 | A | 7 | 260 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.4 | 5 | 0
1982-03-16 | 1900-03-15 | 11:00 | 11 | 903 | 1382 | 633 | 1 | 9 | 768 | 1 | 9 | 134 | 1 | 13 | 68100 | 1 | 9 | 78200 | 1 | 9 | 16800 | 1 | 13 | 3510 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.83 | A | 7 | 969 | A | 7 | 240 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.28 | 5 | 0
1982-03-16 | 1900-03-15 | 12:00 | 12 | 1007 | 1382 | 700 | 1 | 9 | 802 | 1 | 9 | 117 | 1 | 13 | 75000 | 1 | 9 | 81100 | 1 | 9 | 15700 | 1 | 13 | 3410 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 969 | A | 7 | 260 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.48 | 5 | 0
1982-03-16 | 1900-03-15 | 13:00 | 13 | 1041 | 1382 | 794 | 1 | 9 | 950 | 1 | 9 | 80 | 1 | 13 | 83200 | 1 | 9 | 95100 | 1 | 9 | 11400 | 1 | 13 | 2460 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.65 | A | 7 | 970 | A | 7 | 260 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.28 | 5 | 0
1982-03-16 | 1900-03-15 | 14:00 | 14 | 1002 | 1382 | 750 | 1 | 9 | 930 | 1 | 9 | 78 | 1 | 13 | 78800 | 1 | 9 | 93000 | 1 | 9 | 11200 | 1 | 13 | 2290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.63 | A | 7 | 970 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.68 | 5 | 0
1982-03-16 | 1900-03-15 | 15:00 | 15 | 893 | 1382 | 659 | 1 | 9 | 911 | 1 | 9 | 72 | 1 | 13 | 69300 | 1 | 9 | 90600 | 1 | 9 | 10600 | 1 | 13 | 1920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.59 | A | 7 | 970 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.18 | 5 | 0
1982-03-16 | 1900-03-15 | 16:00 | 16 | 721 | 1382 | 512 | 1 | 9 | 867 | 1 | 9 | 61 | 1 | 13 | 54100 | 1 | 9 | 84900 | 1 | 9 | 9700 | 1 | 13 | 1520 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.59 | A | 7 | 971 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.18 | 5 | 0
1982-03-16 | 1900-03-15 | 17:00 | 17 | 499 | 1382 | 321 | 1 | 9 | 757 | 1 | 9 | 49 | 1 | 13 | 34100 | 1 | 9 | 70600 | 1 | 9 | 8500 | 1 | 13 | 1140 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 10 | 50 | A | 7 | 0.57 | A | 7 | 971 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.9 | 5 | 0
1982-03-16 | 1900-03-15 | 18:00 | 18 | 243 | 1382 | 124 | 1 | 13 | 524 | 1 | 9 | 33 | 1 | 13 | 12800 | 1 | 13 | 39900 | 1 | 9 | 5800 | 1 | 13 | 650 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 972 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.98 | 5 | 0
1982-03-16 | 1900-03-15 | 19:00 | 19 | 22 | 587 | 16 | 1 | 13 | 58 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 12.8 | 55.04 | A | 7 | 10 | 50 | A | 7 | 0.83 | A | 7 | 972 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.3 | 5 | 0
1982-03-16 | 1900-03-15 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 973 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.34 | 5 | 0
1982-03-16 | 1900-03-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 7.2 | 44.96 | A | 7 | 0.83 | A | 7 | 974 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.46 | 5 | 0
1982-03-16 | 1900-03-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.46 | 5 | 0
1982-03-16 | 1900-03-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.06 | 5 | 0
1982-03-16 | 1900-03-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.98 | 5 | 0
1982-03-17 | 1900-03-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.08 | 6 | 0
1982-03-17 | 1900-03-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 977 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.4 | 6 | 0
1982-03-17 | 1900-03-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 977 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 240 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.9 | 6 | 0
1982-03-17 | 1900-03-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 976 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.9 | 6 | 0
1982-03-17 | 1900-03-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 180 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40 | 6 | 0
1982-03-17 | 1900-03-16 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 150 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40 | 6 | 0
1982-03-17 | 1900-03-16 | 7:00 | 7 | 34 | 725 | 7 | 1 | 13 | 0 | 1 | 9 | 7 | 1 | 13 | 800 | 1 | 13 | 0 | 1 | 9 | 800 | 1 | 13 | 270 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 6.1 | 42.98 | A | 7 | 1 | A | 7 | 977 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 1.5 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.88 | 6 | 0
1982-03-17 | 1900-03-16 | 8:00 | 8 | 269 | 1381 | 92 | 1 | 13 | 16 | 1 | 9 | 89 | 1 | 13 | 10100 | 1 | 13 | 700 | 1 | 9 | 9900 | 1 | 13 | 2740 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 977 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 1.6 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 6 | 0
1982-03-17 | 1900-03-16 | 9:00 | 9 | 524 | 1381 | 153 | 1 | 9 | 9 | 1 | 9 | 149 | 1 | 13 | 17200 | 1 | 9 | 700 | 1 | 9 | 16900 | 1 | 13 | 5540 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 110 | A | 7 | 8.2 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 1.6 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.06 | 6 | 0
1982-03-17 | 1900-03-16 | 10:00 | 10 | 743 | 1381 | 218 | 1 | 9 | 13 | 1 | 9 | 211 | 1 | 13 | 24900 | 1 | 9 | 1100 | 1 | 9 | 24300 | 1 | 13 | 8610 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 110 | A | 7 | 8.2 | A | 7 | 4800 | A | 7 | 150 | A | 7 | 1.6 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.96 | 6 | 0
1982-03-17 | 1900-03-16 | 11:00 | 11 | 910 | 1381 | 515 | 1 | 9 | 294 | 1 | 9 | 322 | 1 | 13 | 55100 | 1 | 9 | 31500 | 1 | 9 | 34400 | 1 | 13 | 8910 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 120 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 210 | A | 7 | 1.7 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.24 | 6 | 0
1982-03-17 | 1900-03-16 | 12:00 | 12 | 1013 | 1381 | 722 | 1 | 9 | 850 | 1 | 9 | 101 | 1 | 13 | 75300 | 1 | 9 | 84800 | 1 | 9 | 12800 | 1 | 13 | 2630 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | 9.4 | 48.92 | A | 7 | 0.8 | A | 7 | 976 | A | 7 | 130 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.82 | 6 | 0
1982-03-17 | 1900-03-16 | 13:00 | 13 | 1046 | 1381 | 802 | 1 | 9 | 969 | 1 | 9 | 70 | 1 | 13 | 84500 | 1 | 9 | 97100 | 1 | 9 | 10700 | 1 | 13 | 2280 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 975 | A | 7 | 120 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.48 | 6 | 0
1982-03-17 | 1900-03-16 | 14:00 | 14 | 1007 | 1381 | 733 | 1 | 9 | 914 | 1 | 9 | 68 | 1 | 13 | 77200 | 1 | 9 | 91500 | 1 | 9 | 10300 | 1 | 13 | 2120 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.65 | A | 7 | 974 | A | 7 | 100 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.06 | 6 | 0
1982-03-17 | 1900-03-16 | 15:00 | 15 | 898 | 1381 | 667 | 1 | 9 | 932 | 1 | 9 | 63 | 1 | 13 | 70500 | 1 | 9 | 92800 | 1 | 9 | 10000 | 1 | 13 | 1790 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 11.7 | 53.06 | A | 7 | 0.59 | A | 7 | 974 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.96 | 6 | 0
1982-03-17 | 1900-03-16 | 16:00 | 16 | 726 | 1381 | 519 | 1 | 9 | 887 | 1 | 9 | 54 | 1 | 13 | 55000 | 1 | 9 | 87000 | 1 | 9 | 9100 | 1 | 13 | 1430 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.59 | A | 7 | 974 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.64 | 6 | 0
1982-03-17 | 1900-03-16 | 17:00 | 17 | 504 | 1381 | 332 | 1 | 9 | 801 | 1 | 9 | 41 | 1 | 13 | 35400 | 1 | 9 | 74900 | 1 | 9 | 8000 | 1 | 13 | 1070 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.51 | A | 7 | 974 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.16 | 6 | 0
1982-03-17 | 1900-03-16 | 18:00 | 18 | 247 | 1381 | 113 | 1 | 13 | 381 | 1 | 9 | 46 | 1 | 13 | 11700 | 1 | 13 | 27800 | 1 | 9 | 6700 | 1 | 13 | 830 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | 18.9 | 66.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.7 | A | 7 | 974 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.54 | 6 | 0
1982-03-17 | 1900-03-16 | 19:00 | 19 | 24 | 610 | 21 | 1 | 13 | 100 | 1 | 9 | 9 | 1 | 13 | 1400 | 1 | 13 | 4100 | 1 | 9 | 1200 | 1 | 13 | 170 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.64 | 6 | 0
1982-03-17 | 1900-03-16 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 12.8 | 55.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 60 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.28 | 6 | 0
1982-03-17 | 1900-03-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.88 | 6 | 0
1982-03-17 | 1900-03-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.82 | 6 | 0
1982-03-17 | 1900-03-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 4000 | A | 7 | 150 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.92 | 6 | 0
1982-03-17 | 1900-03-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 8.3 | 46.94 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 30 | A | 7 | 4.6 | A | 7 | 2400 | A | 7 | 90 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.34 | 6 | 0
1982-03-18 | 1900-03-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 980 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 100 | A | 7 | 30 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.84 | 7 | 0
1982-03-18 | 1900-03-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 7.8 | 46.04 | A | 7 | 1 | A | 7 | 980 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 100 | A | 7 | 30 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.94 | 7 | 0
1982-03-18 | 1900-03-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 980 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 100 | A | 7 | 30 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.86 | 7 | 0
1982-03-18 | 1900-03-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 980 | A | 7 | 70 | A | 7 | 6.2 | A | 7 | 800 | A | 7 | 30 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 7 | 0
1982-03-18 | 1900-03-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 981 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 2400 | A | 7 | 60 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 7 | 0
1982-03-18 | 1900-03-17 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 981 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 1600 | A | 7 | 60 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.86 | 7 | 0
1982-03-18 | 1900-03-17 | 7:00 | 7 | 38 | 748 | 5 | 1 | 13 | 2 | 1 | 9 | 5 | 1 | 13 | 600 | 1 | 13 | 100 | 1 | 9 | 600 | 1 | 13 | 130 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 982 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 1600 | A | 7 | 60 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.86 | 7 | 0
1982-03-18 | 1900-03-17 | 8:00 | 8 | 276 | 1380 | 31 | 1 | 13 | 17 | 1 | 9 | 28 | 1 | 13 | 3500 | 1 | 13 | 1400 | 1 | 9 | 3200 | 1 | 13 | 790 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 978 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.86 | 7 | 0
1982-03-18 | 1900-03-17 | 9:00 | 9 | 531 | 1380 | 81 | 1 | 9 | 8 | 1 | 9 | 78 | 1 | 13 | 9600 | 1 | 9 | 500 | 1 | 9 | 9400 | 1 | 13 | 3400 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.96 | A | 7 | 982 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 3200 | A | 7 | 90 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.36 | 7 | 0
1982-03-18 | 1900-03-17 | 10:00 | 10 | 749 | 1380 | 180 | 1 | 9 | 1 | 1 | 9 | 180 | 1 | 13 | 20900 | 1 | 9 | 100 | 1 | 9 | 20900 | 1 | 13 | 7730 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 7.8 | 46.04 | A | 7 | 1 | A | 7 | 982 | A | 7 | 50 | A | 7 | 5.7 | A | 7 | 4000 | A | 7 | 90 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.94 | 7 | 0
1982-03-18 | 1900-03-17 | 11:00 | 11 | 916 | 1380 | 271 | 1 | 9 | 7 | 1 | 9 | 266 | 1 | 13 | 31300 | 1 | 9 | 600 | 1 | 9 | 30900 | 1 | 13 | 11430 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.96 | A | 7 | 982 | A | 7 | 60 | A | 7 | 6.7 | A | 7 | 4800 | A | 7 | 150 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.44 | 7 | 0
1982-03-18 | 1900-03-17 | 12:00 | 12 | 1019 | 1380 | 361 | 1 | 9 | 8 | 1 | 9 | 355 | 1 | 13 | 41400 | 1 | 9 | 800 | 1 | 9 | 40800 | 1 | 13 | 14710 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 60 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.84 | 7 | 0
1982-03-18 | 1900-03-17 | 13:00 | 13 | 1052 | 1380 | 315 | 1 | 9 | 1 | 1 | 9 | 314 | 1 | 13 | 36600 | 1 | 9 | 100 | 1 | 9 | 36600 | 1 | 13 | 13810 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 70 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 270 | A | 7 | 1.8 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.92 | 7 | 0
1982-03-18 | 1900-03-17 | 14:00 | 14 | 1012 | 1380 | 313 | 1 | 9 | 3 | 1 | 9 | 311 | 1 | 13 | 36300 | 1 | 9 | 300 | 1 | 9 | 36100 | 1 | 13 | 13450 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.9 | A | 7 | 981 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 240 | A | 7 | 1.8 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.52 | 7 | 0
1982-03-18 | 1900-03-17 | 15:00 | 15 | 903 | 1380 | 289 | 1 | 9 | 3 | 1 | 9 | 287 | 1 | 13 | 33100 | 1 | 9 | 300 | 1 | 9 | 32900 | 1 | 13 | 11920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 1.8 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.52 | 7 | 0
1982-03-18 | 1900-03-17 | 16:00 | 16 | 731 | 1380 | 255 | 1 | 9 | 1 | 1 | 9 | 254 | 1 | 13 | 28600 | 1 | 9 | 100 | 1 | 9 | 28600 | 1 | 13 | 9580 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 980 | A | 7 | 80 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 340 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.34 | 7 | 0
1982-03-18 | 1900-03-17 | 17:00 | 17 | 509 | 1380 | 158 | 1 | 9 | 0 | 1 | 9 | 158 | 1 | 13 | 17600 | 1 | 9 | 0 | 1 | 9 | 17600 | 1 | 13 | 5650 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 979 | A | 7 | 70 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 400 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.34 | 7 | 0
1982-03-18 | 1900-03-17 | 18:00 | 18 | 252 | 1380 | 64 | 1 | 13 | 0 | 1 | 9 | 64 | 1 | 13 | 7100 | 1 | 13 | 0 | 1 | 9 | 7100 | 1 | 13 | 2170 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 980 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 430 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.34 | 7 | 0
1982-03-18 | 1900-03-17 | 19:00 | 19 | 26 | 633 | 11 | 1 | 13 | 0 | 1 | 9 | 11 | 1 | 13 | 1300 | 1 | 13 | 0 | 1 | 9 | 1300 | 1 | 13 | 390 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 70 | A | 7 | 6.7 | A | 7 | 9700 | A | 7 | 370 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.84 | 7 | 0
1982-03-18 | 1900-03-17 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 370 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.24 | 7 | 0
1982-03-18 | 1900-03-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.86 | A | 7 | 978 | A | 7 | 80 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.96 | 7 | 0
1982-03-18 | 1900-03-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 90 | A | 7 | 6.7 | A | 7 | 9700 | A | 7 | 310 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.96 | 7 | 0
1982-03-18 | 1900-03-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 100 | A | 7 | 8.8 | A | 7 | 9700 | A | 7 | 270 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.96 | 7 | 0
1982-03-18 | 1900-03-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 80 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 270 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.96 | 7 | 0
1982-03-19 | 1900-03-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 90 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 150 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.96 | 1 | 0
1982-03-19 | 1900-03-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 80 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 150 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.96 | 1 | 0
1982-03-19 | 1900-03-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 90 | A | 7 | 7.2 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.96 | 1 | 0
1982-03-19 | 1900-03-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 7.8 | 46.04 | A | 7 | 1 | A | 7 | 971 | A | 7 | 90 | A | 7 | 8.2 | A | 7 | 1600 | A | 7 | 60 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.94 | 1 | 0
1982-03-19 | 1900-03-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 7.8 | 46.04 | A | 7 | 1 | A | 7 | 971 | A | 7 | 110 | A | 7 | 9.3 | A | 7 | 1600 | A | 7 | 60 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.94 | 1 | 0
1982-03-19 | 1900-03-18 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 7.8 | 46.04 | A | 7 | 1 | A | 7 | 972 | A | 7 | 110 | A | 7 | 9.3 | A | 7 | 800 | A | 7 | 30 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.94 | 1 | 0
1982-03-19 | 1900-03-18 | 7:00 | 7 | 42 | 793 | 16 | 1 | 13 | 0 | 1 | 9 | 16 | 1 | 13 | 1800 | 1 | 13 | 0 | 1 | 9 | 1800 | 1 | 13 | 550 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 7.8 | 46.04 | A | 7 | 1 | A | 7 | 970 | A | 7 | 100 | A | 7 | 8.2 | A | 7 | 200 | A | 7 | 0 | A | 7 | 1.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.94 | 1 | 0
1982-03-19 | 1900-03-18 | 8:00 | 8 | 284 | 1379 | 83 | 1 | 13 | 1 | 1 | 9 | 83 | 1 | 13 | 9200 | 1 | 13 | 0 | 1 | 9 | 9200 | 1 | 13 | 2720 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 969 | A | 7 | 90 | A | 7 | 6.7 | A | 7 | 100 | A | 7 | 0 | A | 7 | 1.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.84 | 1 | 0
1982-03-19 | 1900-03-18 | 9:00 | 9 | 538 | 1379 | 105 | 1 | 9 | 1 | 1 | 9 | 105 | 1 | 13 | 12200 | 1 | 9 | 100 | 1 | 9 | 12200 | 1 | 13 | 4360 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 8.9 | 48.02 | A | 7 | 1 | A | 7 | 969 | A | 7 | 100 | A | 7 | 6.2 | A | 7 | 1600 | A | 7 | 30 | A | 7 | 1.8 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.02 | 1 | 0
1982-03-19 | 1900-03-18 | 10:00 | 10 | 756 | 1379 | 156 | 1 | 9 | 1 | 1 | 9 | 155 | 1 | 13 | 18300 | 1 | 9 | 100 | 1 | 9 | 18200 | 1 | 13 | 6920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 10 | 50 | A | 7 | 1 | A | 7 | 968 | A | 7 | 100 | A | 7 | 6.7 | A | 7 | 500 | A | 7 | 60 | A | 7 | 1.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50 | 1 | 0
1982-03-19 | 1900-03-18 | 11:00 | 11 | 922 | 1379 | 313 | 1 | 9 | 1 | 1 | 9 | 312 | 1 | 13 | 35700 | 1 | 9 | 100 | 1 | 9 | 35600 | 1 | 13 | 12750 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 11.1 | 51.98 | A | 7 | 1 | A | 7 | 967 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 800 | A | 7 | 60 | A | 7 | 2 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.88 | 1 | 0
1982-03-19 | 1900-03-18 | 12:00 | 12 | 1025 | 1379 | 368 | 1 | 9 | 0 | 1 | 9 | 368 | 1 | 13 | 42100 | 1 | 9 | 0 | 1 | 9 | 42100 | 1 | 13 | 15090 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 12.2 | 53.96 | A | 7 | 1 | A | 7 | 966 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 1600 | A | 7 | 520 | A | 7 | 2.2 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.86 | 1 | 0
1982-03-19 | 1900-03-18 | 13:00 | 13 | 1057 | 1379 | 416 | 1 | 9 | 108 | 1 | 9 | 334 | 1 | 13 | 45900 | 1 | 9 | 11500 | 1 | 9 | 37100 | 1 | 13 | 11240 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.96 | A | 7 | 965 | A | 7 | 80 | A | 7 | 5.7 | A | 7 | 3200 | A | 7 | 940 | A | 7 | 2.4 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.32 | 1 | 0
1982-03-19 | 1900-03-18 | 14:00 | 14 | 1017 | 1379 | 745 | 1 | 13 | 811 | 1 | 13 | 148 | 1 | 13 | 77900 | 1 | 13 | 81200 | 1 | 13 | 17800 | 1 | 13 | 4090 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 19.4 | 66.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.81 | A | 7 | 963 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.28 | 1 | 0
1982-03-19 | 1900-03-18 | 15:00 | 15 | 908 | 1379 | 585 | 1 | 13 | 622 | 1 | 13 | 177 | 1 | 13 | 61500 | 1 | 13 | 62600 | 1 | 13 | 20200 | 1 | 13 | 4520 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 26.1 | 78.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.39 | A | 7 | 962 | A | 7 | 210 | A | 7 | 11.3 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.28 | 1 | 0
1982-03-19 | 1900-03-18 | 16:00 | 16 | 736 | 1379 | 512 | 1 | 9 | 785 | 1 | 9 | 95 | 1 | 13 | 53800 | 1 | 9 | 77400 | 1 | 9 | 12400 | 1 | 13 | 2060 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.34 | A | 7 | 963 | A | 7 | 230 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.44 | 1 | 0
1982-03-19 | 1900-03-18 | 17:00 | 17 | 513 | 1379 | 336 | 1 | 9 | 770 | 1 | 9 | 51 | 1 | 13 | 35600 | 1 | 9 | 72100 | 1 | 9 | 8700 | 1 | 13 | 1170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.35 | A | 7 | 964 | A | 7 | 230 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.46 | 1 | 0
1982-03-19 | 1900-03-18 | 18:00 | 18 | 256 | 1379 | 134 | 1 | 13 | 551 | 1 | 9 | 33 | 1 | 13 | 14000 | 1 | 13 | 42900 | 1 | 9 | 6000 | 1 | 13 | 670 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.3 | A | 7 | 965 | A | 7 | 230 | A | 7 | 9.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.54 | 1 | 0
1982-03-19 | 1900-03-18 | 19:00 | 19 | 28 | 655 | 21 | 1 | 13 | 85 | 1 | 9 | 11 | 1 | 13 | 1600 | 1 | 13 | 2800 | 1 | 9 | 1500 | 1 | 13 | 190 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 4.4 | 39.92 | A | 7 | 0.4 | A | 7 | 966 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.42 | 1 | 0
1982-03-19 | 1900-03-18 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.87 | A | 7 | 968 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.78 | 1 | 0
1982-03-19 | 1900-03-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 969 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 1 | 0
1982-03-19 | 1900-03-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 8.9 | 48.02 | A | 7 | 8.9 | 48.02 | A | 7 | 1 | A | 7 | 970 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.02 | 1 | 0
1982-03-19 | 1900-03-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 7.8 | 46.04 | A | 7 | 7.8 | 46.04 | A | 7 | 1 | A | 7 | 969 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.94 | 1 | 0
1982-03-19 | 1900-03-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 969 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 1 | 0
1982-03-20 | 1900-03-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 969 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 2 | 0
1982-03-20 | 1900-03-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 969 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 2 | 0
1982-03-20 | 1900-03-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 969 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 100 | A | 7 | 0 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 2 | 0
1982-03-20 | 1900-03-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 969 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 100 | A | 7 | 0 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.86 | 2 | 0
1982-03-20 | 1900-03-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 969 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 100 | A | 7 | 0 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.86 | 2 | 0
1982-03-20 | 1900-03-19 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 971 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.86 | 2 | 0
1982-03-20 | 1900-03-19 | 7:00 | 7 | 46 | 816 | 14 | 1 | 13 | 3 | 1 | 9 | 14 | 1 | 13 | 1600 | 1 | 13 | 0 | 1 | 9 | 1600 | 1 | 13 | 500 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 971 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 2 | 0
1982-03-20 | 1900-03-19 | 8:00 | 8 | 291 | 1379 | 82 | 1 | 13 | 19 | 1 | 9 | 78 | 1 | 13 | 9000 | 1 | 13 | 1600 | 1 | 9 | 8600 | 1 | 13 | 1960 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 6.1 | 42.98 | A | 7 | 6.1 | 42.98 | A | 7 | 1 | A | 7 | 972 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.88 | 2 | 0
1982-03-20 | 1900-03-19 | 9:00 | 9 | 545 | 1379 | 347 | 1 | 9 | 705 | 1 | 9 | 72 | 1 | 13 | 36400 | 1 | 9 | 66700 | 1 | 9 | 10000 | 1 | 13 | 1440 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 972 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.9 | 2 | 0
1982-03-20 | 1900-03-19 | 10:00 | 10 | 763 | 1379 | 535 | 1 | 9 | 807 | 1 | 9 | 92 | 1 | 13 | 56900 | 1 | 9 | 80100 | 1 | 9 | 12500 | 1 | 13 | 2080 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.59 | A | 7 | 973 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.04 | 2 | 0
1982-03-20 | 1900-03-19 | 11:00 | 11 | 928 | 1379 | 661 | 1 | 9 | 827 | 1 | 9 | 107 | 1 | 13 | 70900 | 1 | 9 | 83400 | 1 | 9 | 14600 | 1 | 13 | 2830 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 10.6 | 51.08 | A | 7 | 0 | 32 | A | 7 | 0.48 | A | 7 | 973 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.3 | 2 | 0
1982-03-20 | 1900-03-19 | 12:00 | 12 | 1031 | 1379 | 779 | 1 | 9 | 877 | 1 | 9 | 126 | 1 | 13 | 83200 | 1 | 9 | 88600 | 1 | 9 | 16800 | 1 | 13 | 3770 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.47 | A | 7 | 974 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.78 | 2 | 0
1982-03-20 | 1900-03-19 | 13:00 | 13 | 1063 | 1379 | 813 | 1 | 9 | 906 | 1 | 9 | 117 | 1 | 13 | 84300 | 1 | 9 | 90500 | 1 | 9 | 14300 | 1 | 13 | 3070 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.47 | A | 7 | 974 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.66 | 2 | 0
1982-03-20 | 1900-03-19 | 14:00 | 14 | 1022 | 1379 | 777 | 1 | 9 | 897 | 1 | 9 | 114 | 1 | 13 | 80600 | 1 | 9 | 89500 | 1 | 9 | 14100 | 1 | 13 | 2790 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.42 | A | 7 | 974 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.18 | 2 | 0
1982-03-20 | 1900-03-19 | 15:00 | 15 | 912 | 1379 | 676 | 1 | 9 | 865 | 1 | 9 | 105 | 1 | 13 | 72300 | 1 | 9 | 87100 | 1 | 9 | 14500 | 1 | 13 | 2730 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 0 | 32 | A | 7 | 0.39 | A | 7 | 974 | A | 7 | 270 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.2 | 2 | 0
1982-03-20 | 1900-03-19 | 16:00 | 16 | 740 | 1379 | 527 | 1 | 9 | 815 | 1 | 9 | 90 | 1 | 13 | 55600 | 1 | 9 | 80600 | 1 | 9 | 12200 | 1 | 13 | 2000 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.35 | A | 7 | 973 | A | 7 | 300 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.22 | 2 | 0
1982-03-20 | 1900-03-19 | 17:00 | 17 | 518 | 1379 | 312 | 1 | 9 | 645 | 1 | 9 | 72 | 1 | 13 | 33300 | 1 | 9 | 60900 | 1 | 9 | 10300 | 1 | 13 | 1440 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 13.3 | 55.94 | A | 7 | -1.1 | 30.02 | A | 7 | 0.37 | A | 7 | 974 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.42 | 2 | 0
1982-03-20 | 1900-03-19 | 18:00 | 18 | 261 | 1379 | 124 | 1 | 13 | 395 | 1 | 9 | 50 | 1 | 13 | 12800 | 1 | 13 | 29500 | 1 | 9 | 7200 | 1 | 13 | 890 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 12.2 | 53.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.38 | A | 7 | 974 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.64 | 2 | 0
1982-03-20 | 1900-03-19 | 19:00 | 19 | 30 | 678 | 14 | 1 | 13 | 20 | 1 | 9 | 12 | 1 | 13 | 1500 | 1 | 13 | 800 | 1 | 9 | 1400 | 1 | 13 | 250 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | 10 | 50 | A | 7 | -1.1 | 30.02 | A | 7 | 0.46 | A | 7 | 974 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.42 | 2 | 0
1982-03-20 | 1900-03-19 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 8.3 | 46.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.02 | 2 | 0
1982-03-20 | 1900-03-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 7.2 | 44.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.56 | A | 7 | 977 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.52 | 2 | 0
1982-03-20 | 1900-03-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | -1.1 | 30.02 | A | 7 | 0.65 | A | 7 | 978 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.42 | 2 | 0
1982-03-20 | 1900-03-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 4.4 | 39.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 2 | 0
1982-03-20 | 1900-03-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.58 | 2 | 0
1982-03-21 | 1900-03-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -5 | 23 | A | 7 | 0.62 | A | 7 | 979 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.8 | 3 | 0
1982-03-21 | 1900-03-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 3 | 0
1982-03-21 | 1900-03-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.22 | 3 | 0
1982-03-21 | 1900-03-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 3 | 0
1982-03-21 | 1900-03-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -7.2 | 19.04 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.54 | 3 | 0
1982-03-21 | 1900-03-20 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.69 | A | 7 | 981 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 3 | 0
1982-03-21 | 1900-03-20 | 7:00 | 7 | 50 | 861 | 25 | 1 | 13 | 87 | 1 | 9 | 16 | 1 | 13 | 2300 | 1 | 13 | 3400 | 1 | 9 | 2100 | 1 | 13 | 280 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.72 | A | 7 | 982 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.84 | 3 | 0
1982-03-21 | 1900-03-20 | 8:00 | 8 | 298 | 1378 | 158 | 1 | 13 | 545 | 1 | 9 | 43 | 1 | 13 | 16400 | 1 | 13 | 44200 | 1 | 9 | 6800 | 1 | 13 | 820 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 3 | 0
1982-03-21 | 1900-03-20 | 9:00 | 9 | 552 | 1378 | 364 | 1 | 9 | 758 | 1 | 9 | 64 | 1 | 13 | 38700 | 1 | 9 | 72200 | 1 | 9 | 9700 | 1 | 13 | 1360 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 3 | 0
1982-03-21 | 1900-03-20 | 10:00 | 10 | 769 | 1378 | 463 | 1 | 13 | 610 | 1 | 13 | 124 | 1 | 13 | 49200 | 1 | 13 | 61100 | 1 | 13 | 15000 | 1 | 13 | 2820 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 1.7 | 35.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 3 | 0
1982-03-21 | 1900-03-20 | 11:00 | 11 | 934 | 1378 | 611 | 1 | 13 | 583 | 1 | 13 | 218 | 1 | 13 | 66000 | 1 | 13 | 60400 | 1 | 13 | 24900 | 1 | 13 | 5820 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 2.8 | 37.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.58 | 3 | 0
1982-03-21 | 1900-03-20 | 12:00 | 12 | 1036 | 1378 | 466 | 1 | 9 | 205 | 1 | 9 | 312 | 1 | 13 | 51500 | 1 | 9 | 21800 | 1 | 9 | 35000 | 1 | 13 | 10240 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 350 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 3 | 0
1982-03-21 | 1900-03-20 | 13:00 | 13 | 1068 | 1378 | 601 | 1 | 13 | 456 | 1 | 13 | 249 | 1 | 13 | 65300 | 1 | 13 | 47600 | 1 | 13 | 28300 | 1 | 13 | 8330 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 984 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 700 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 3 | 0
1982-03-21 | 1900-03-20 | 14:00 | 14 | 1027 | 1378 | 365 | 1 | 9 | 98 | 1 | 9 | 292 | 1 | 13 | 40500 | 1 | 9 | 10400 | 1 | 9 | 32600 | 1 | 13 | 9480 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 5 | 41 | A | 7 | -2.8 | 26.96 | A | 7 | 0.58 | A | 7 | 984 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 820 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.96 | 3 | 0
1982-03-21 | 1900-03-20 | 15:00 | 15 | 917 | 1378 | 237 | 1 | 9 | 4 | 1 | 9 | 234 | 1 | 13 | 27600 | 1 | 9 | 300 | 1 | 9 | 27400 | 1 | 13 | 10450 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.58 | A | 7 | 984 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.94 | 3 | 0
1982-03-21 | 1900-03-20 | 16:00 | 16 | 745 | 1378 | 177 | 1 | 9 | 5 | 1 | 9 | 175 | 1 | 13 | 20600 | 1 | 9 | 400 | 1 | 9 | 20400 | 1 | 13 | 7550 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 984 | A | 7 | 330 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 820 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 3 | 0
1982-03-21 | 1900-03-20 | 17:00 | 17 | 522 | 1378 | 110 | 1 | 9 | 5 | 1 | 9 | 108 | 1 | 13 | 12700 | 1 | 9 | 300 | 1 | 9 | 12600 | 1 | 13 | 4400 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 3 | 0
1982-03-21 | 1900-03-20 | 18:00 | 18 | 265 | 1378 | 72 | 1 | 13 | 51 | 1 | 9 | 63 | 1 | 13 | 8000 | 1 | 13 | 4100 | 1 | 9 | 7200 | 1 | 13 | 1600 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 3 | 0
1982-03-21 | 1900-03-20 | 19:00 | 19 | 32 | 700 | 9 | 1 | 13 | 1 | 1 | 9 | 9 | 1 | 13 | 1100 | 1 | 13 | 0 | 1 | 9 | 1100 | 1 | 13 | 340 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.67 | A | 7 | 985 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 790 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.84 | 3 | 0
1982-03-21 | 1900-03-20 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.67 | A | 7 | 985 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 790 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.86 | 3 | 0
1982-03-21 | 1900-03-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.65 | A | 7 | 986 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 790 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.86 | 3 | 0
1982-03-21 | 1900-03-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 987 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 790 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 3 | 0
1982-03-21 | 1900-03-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.75 | A | 7 | 987 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 880 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 3 | 0
1982-03-21 | 1900-03-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 940 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.04 | 3 | 0
1982-03-22 | 1900-03-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 880 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.04 | 4 | 0
1982-03-22 | 1900-03-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 987 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 880 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.84 | 4 | 0
1982-03-22 | 1900-03-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 880 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.84 | 4 | 0
1982-03-22 | 1900-03-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.96 | 4 | 0
1982-03-22 | 1900-03-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.96 | 4 | 0
1982-03-22 | 1900-03-21 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 4 | 0
1982-03-22 | 1900-03-21 | 7:00 | 7 | 54 | 907 | 29 | 1 | 13 | 122 | 1 | 9 | 16 | 1 | 13 | 2600 | 1 | 13 | 4800 | 1 | 9 | 2300 | 1 | 13 | 280 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 4 | 0
1982-03-22 | 1900-03-21 | 8:00 | 8 | 305 | 1377 | 165 | 1 | 13 | 579 | 1 | 9 | 40 | 1 | 13 | 17400 | 1 | 13 | 47600 | 1 | 9 | 6800 | 1 | 13 | 800 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 987 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 4 | 0
1982-03-22 | 1900-03-21 | 9:00 | 9 | 559 | 1377 | 376 | 1 | 9 | 786 | 1 | 9 | 60 | 1 | 13 | 40300 | 1 | 9 | 75300 | 1 | 9 | 9600 | 1 | 13 | 1310 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 988 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 4 | 0
1982-03-22 | 1900-03-21 | 10:00 | 10 | 776 | 1377 | 568 | 1 | 9 | 878 | 1 | 9 | 76 | 1 | 13 | 59700 | 1 | 9 | 86400 | 1 | 9 | 10900 | 1 | 13 | 1740 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -5.6 | 21.92 | A | 7 | 0.47 | A | 7 | 988 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 4 | 0
1982-03-22 | 1900-03-21 | 11:00 | 11 | 940 | 1377 | 718 | 1 | 9 | 927 | 1 | 9 | 88 | 1 | 13 | 75200 | 1 | 9 | 92300 | 1 | 9 | 12000 | 1 | 13 | 2230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.38 | A | 7 | 988 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.24 | 4 | 0
1982-03-22 | 1900-03-21 | 12:00 | 12 | 1042 | 1377 | 814 | 1 | 9 | 954 | 1 | 9 | 95 | 1 | 13 | 85000 | 1 | 9 | 95400 | 1 | 9 | 12600 | 1 | 13 | 2720 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.31 | A | 7 | 987 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.36 | 4 | 0
1982-03-22 | 1900-03-21 | 13:00 | 13 | 1073 | 1377 | 841 | 1 | 9 | 957 | 1 | 9 | 97 | 1 | 13 | 87700 | 1 | 9 | 95800 | 1 | 9 | 12800 | 1 | 13 | 2920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -7.2 | 19.04 | A | 7 | 0.32 | A | 7 | 986 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.04 | 4 | 0
1982-03-22 | 1900-03-21 | 14:00 | 14 | 1032 | 1377 | 805 | 1 | 9 | 951 | 1 | 9 | 94 | 1 | 13 | 84000 | 1 | 9 | 95100 | 1 | 9 | 12500 | 1 | 13 | 2660 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | -7.8 | 17.96 | A | 7 | 0.28 | A | 7 | 985 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.86 | 4 | 0
1982-03-22 | 1900-03-21 | 15:00 | 15 | 922 | 1377 | 706 | 1 | 9 | 926 | 1 | 9 | 87 | 1 | 13 | 73800 | 1 | 9 | 92100 | 1 | 9 | 11900 | 1 | 13 | 2170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.27 | A | 7 | 984 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.76 | 4 | 0
1982-03-22 | 1900-03-21 | 16:00 | 16 | 749 | 1377 | 550 | 1 | 9 | 875 | 1 | 9 | 75 | 1 | 13 | 57700 | 1 | 9 | 85900 | 1 | 9 | 10800 | 1 | 13 | 1680 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.25 | A | 7 | 984 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.86 | 4 | 0
1982-03-22 | 1900-03-21 | 17:00 | 17 | 527 | 1377 | 354 | 1 | 9 | 779 | 1 | 9 | 58 | 1 | 13 | 37700 | 1 | 9 | 73800 | 1 | 9 | 9400 | 1 | 13 | 1250 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.22 | A | 7 | 983 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.32 | 4 | 0
1982-03-22 | 1900-03-21 | 18:00 | 18 | 270 | 1377 | 145 | 1 | 13 | 554 | 1 | 9 | 38 | 1 | 13 | 15000 | 1 | 13 | 43700 | 1 | 9 | 6400 | 1 | 13 | 740 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | -8.9 | 15.98 | A | 7 | 0.26 | A | 7 | 983 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.08 | 4 | 0
1982-03-22 | 1900-03-21 | 19:00 | 19 | 34 | 723 | 22 | 1 | 13 | 84 | 1 | 9 | 13 | 1 | 13 | 1900 | 1 | 13 | 2900 | 1 | 9 | 1700 | 1 | 13 | 220 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | -10 | 14 | A | 7 | 0.26 | A | 7 | 982 | A | 7 | 20 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.5 | 4 | 0
1982-03-22 | 1900-03-21 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.45 | A | 7 | 982 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.52 | 4 | 0
1982-03-22 | 1900-03-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -7.2 | 19.04 | A | 7 | 0.41 | A | 7 | 982 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.74 | 4 | 0
1982-03-22 | 1900-03-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.43 | A | 7 | 982 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.96 | 4 | 0
1982-03-22 | 1900-03-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.48 | A | 7 | 982 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.04 | 4 | 0
1982-03-22 | 1900-03-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 2.2 | 35.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.5 | A | 7 | 982 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.34 | 4 | 0
1982-03-23 | 1900-03-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.44 | 5 | 0
1982-03-23 | 1900-03-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.42 | 5 | 0
1982-03-23 | 1900-03-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 5 | 0
1982-03-23 | 1900-03-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -6.1 | 21.02 | A | 7 | 0.64 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.22 | 5 | 0
1982-03-23 | 1900-03-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 5 | 0
1982-03-23 | 1900-03-22 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -5 | 23 | A | 7 | 0.62 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.8 | 5 | 0
1982-03-23 | 1900-03-22 | 7:00 | 7 | 59 | 929 | 32 | 1 | 13 | 133 | 1 | 9 | 18 | 1 | 13 | 2900 | 1 | 13 | 5400 | 1 | 9 | 2500 | 1 | 13 | 310 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.78 | 5 | 0
1982-03-23 | 1900-03-22 | 8:00 | 8 | 312 | 1376 | 172 | 1 | 13 | 590 | 1 | 9 | 41 | 1 | 13 | 18000 | 1 | 13 | 48800 | 1 | 9 | 6900 | 1 | 13 | 820 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.58 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.94 | 5 | 0
1982-03-23 | 1900-03-22 | 9:00 | 9 | 565 | 1376 | 380 | 1 | 9 | 784 | 1 | 9 | 61 | 1 | 13 | 40700 | 1 | 9 | 75300 | 1 | 9 | 9700 | 1 | 13 | 1330 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.48 | A | 7 | 977 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.74 | 5 | 0
1982-03-23 | 1900-03-22 | 10:00 | 10 | 782 | 1376 | 570 | 1 | 9 | 867 | 1 | 9 | 80 | 1 | 13 | 59900 | 1 | 9 | 85400 | 1 | 9 | 11200 | 1 | 13 | 1770 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.37 | A | 7 | 977 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.84 | 5 | 0
1982-03-23 | 1900-03-22 | 11:00 | 11 | 946 | 1376 | 646 | 1 | 9 | 685 | 1 | 9 | 177 | 1 | 13 | 68400 | 1 | 9 | 69300 | 1 | 9 | 20600 | 1 | 13 | 4800 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | 14.4 | 57.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.32 | A | 7 | 976 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.34 | 5 | 0
1982-03-23 | 1900-03-22 | 12:00 | 12 | 1048 | 1376 | 519 | 1 | 13 | 368 | 1 | 13 | 239 | 1 | 13 | 56300 | 1 | 13 | 38400 | 1 | 13 | 27000 | 1 | 13 | 7680 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 14.4 | 57.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.32 | A | 7 | 976 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.34 | 5 | 0
1982-03-23 | 1900-03-22 | 13:00 | 13 | 1079 | 1376 | 530 | 1 | 13 | 273 | 1 | 13 | 316 | 1 | 13 | 58100 | 1 | 13 | 29600 | 1 | 13 | 34800 | 1 | 13 | 10630 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 16.7 | 62.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.3 | A | 7 | 974 | A | 7 | 210 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.62 | 5 | 0
1982-03-23 | 1900-03-22 | 14:00 | 14 | 1037 | 1376 | 677 | 1 | 13 | 554 | 1 | 13 | 260 | 1 | 13 | 72800 | 1 | 13 | 57700 | 1 | 13 | 29200 | 1 | 13 | 8250 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 16.1 | 60.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.29 | A | 7 | 973 | A | 7 | 210 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.04 | 5 | 0
1982-03-23 | 1900-03-22 | 15:00 | 15 | 926 | 1376 | 260 | 1 | 9 | 7 | 1 | 9 | 255 | 1 | 13 | 30200 | 1 | 9 | 600 | 1 | 9 | 29800 | 1 | 13 | 11190 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.29 | A | 7 | 972 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 2290 | A | 7 | 0.9 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.46 | 5 | 0
1982-03-23 | 1900-03-22 | 16:00 | 16 | 754 | 1376 | 330 | 1 | 9 | 232 | 1 | 9 | 204 | 1 | 13 | 35800 | 1 | 9 | 24400 | 1 | 9 | 22400 | 1 | 13 | 4720 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 13.9 | 57.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.32 | A | 7 | 971 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 2290 | A | 7 | 0.9 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.46 | 5 | 0
1982-03-23 | 1900-03-22 | 17:00 | 17 | 531 | 1376 | 117 | 1 | 9 | 44 | 1 | 9 | 100 | 1 | 13 | 12900 | 1 | 9 | 4200 | 1 | 9 | 11300 | 1 | 13 | 3000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.4 | A | 7 | 971 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 1 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.72 | 5 | 0
1982-03-23 | 1900-03-22 | 18:00 | 18 | 274 | 1376 | 36 | 1 | 13 | 22 | 1 | 9 | 32 | 1 | 13 | 4000 | 1 | 13 | 1800 | 1 | 9 | 3700 | 1 | 13 | 900 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.54 | A | 7 | 971 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1490 | A | 7 | 1.2 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.46 | 5 | 0
1982-03-23 | 1900-03-22 | 19:00 | 19 | 37 | 745 | 21 | 1 | 13 | 23 | 1 | 13 | 18 | 1 | 13 | 2100 | 1 | 13 | 900 | 1 | 13 | 2100 | 1 | 13 | 370 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 10 | 50 | A | 7 | 1.7 | 35.06 | A | 7 | 0.57 | A | 7 | 970 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 1.2 | E | 8 | 0.069 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.86 | 5 | 0
1982-03-23 | 1900-03-22 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 4 | A | 7 | 8.3 | 46.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.63 | A | 7 | 970 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.56 | 5 | 0
1982-03-23 | 1900-03-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 3 | A | 7 | 7.2 | 44.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.63 | A | 7 | 971 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.88 | 5 | 0
1982-03-23 | 1900-03-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 6.1 | 42.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.68 | A | 7 | 971 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.48 | 5 | 0
1982-03-23 | 1900-03-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.65 | A | 7 | 971 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.08 | 5 | 0
1982-03-23 | 1900-03-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | 0.6 | 33.08 | A | 7 | 0.71 | A | 7 | 971 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.78 | 5 | 0
1982-03-24 | 1900-03-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | 0.6 | 33.08 | A | 7 | 0.73 | A | 7 | 971 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.08 | 6 | 0
1982-03-24 | 1900-03-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.76 | A | 7 | 971 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.38 | 6 | 0
1982-03-24 | 1900-03-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.76 | A | 7 | 971 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.38 | 6 | 0
1982-03-24 | 1900-03-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 971 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 6 | 0
1982-03-24 | 1900-03-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | 0 | 32 | A | 7 | 0.85 | A | 7 | 971 | A | 7 | 190 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 6 | 0
1982-03-24 | 1900-03-23 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | 0 | 32 | A | 7 | 0.85 | A | 7 | 971 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 6 | 0
1982-03-24 | 1900-03-23 | 7:00 | 7 | 64 | 974 | 26 | 1 | 13 | 51 | 1 | 13 | 20 | 1 | 13 | 2500 | 1 | 13 | 1900 | 1 | 13 | 2400 | 1 | 13 | 350 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 972 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.1 | 6 | 0
1982-03-24 | 1900-03-23 | 8:00 | 8 | 319 | 1375 | 162 | 1 | 13 | 446 | 1 | 9 | 60 | 1 | 13 | 16800 | 1 | 13 | 36000 | 1 | 9 | 8400 | 1 | 13 | 1090 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | 3.3 | 37.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.76 | 6 | 0
1982-03-24 | 1900-03-23 | 9:00 | 9 | 572 | 1375 | 328 | 1 | 9 | 474 | 1 | 9 | 132 | 1 | 13 | 34900 | 1 | 9 | 45900 | 1 | 9 | 15700 | 1 | 13 | 2600 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 7.2 | 44.96 | A | 7 | 3.9 | 39.02 | A | 7 | 0.8 | A | 7 | 974 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.52 | 6 | 0
1982-03-24 | 1900-03-23 | 10:00 | 10 | 788 | 1375 | 406 | 1 | 13 | 337 | 1 | 13 | 214 | 1 | 13 | 44200 | 1 | 13 | 35700 | 1 | 13 | 23700 | 1 | 13 | 5080 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 9.4 | 48.92 | A | 7 | 4.4 | 39.92 | A | 7 | 0.71 | A | 7 | 974 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.12 | 6 | 0
1982-03-24 | 1900-03-23 | 11:00 | 11 | 952 | 1375 | 304 | 1 | 9 | 75 | 1 | 9 | 253 | 1 | 13 | 33700 | 1 | 9 | 7600 | 1 | 9 | 28400 | 1 | 13 | 9210 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 9.4 | 48.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 6100 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.02 | 6 | 0
1982-03-24 | 1900-03-23 | 12:00 | 12 | 1053 | 1375 | 254 | 1 | 9 | 12 | 1 | 9 | 245 | 1 | 13 | 30200 | 1 | 9 | 1000 | 1 | 9 | 29400 | 1 | 13 | 11540 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 40 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.02 | 6 | 0
1982-03-24 | 1900-03-23 | 13:00 | 13 | 1084 | 1375 | 754 | 1 | 13 | 606 | 1 | 13 | 278 | 1 | 13 | 81100 | 1 | 13 | 63200 | 1 | 13 | 31200 | 1 | 13 | 9710 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 11.1 | 51.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.59 | A | 7 | 975 | A | 7 | 50 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.84 | 6 | 0
1982-03-24 | 1900-03-23 | 14:00 | 14 | 1042 | 1375 | 630 | 1 | 13 | 479 | 1 | 13 | 268 | 1 | 13 | 67600 | 1 | 13 | 49900 | 1 | 13 | 29700 | 1 | 13 | 8610 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 12.2 | 53.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.55 | A | 7 | 974 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.24 | 6 | 0
1982-03-24 | 1900-03-23 | 15:00 | 15 | 931 | 1375 | 551 | 1 | 13 | 363 | 1 | 13 | 306 | 1 | 13 | 59500 | 1 | 13 | 39000 | 1 | 13 | 33000 | 1 | 13 | 8560 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 13.3 | 55.94 | A | 7 | 3.3 | 37.94 | A | 7 | 0.51 | A | 7 | 973 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.44 | 6 | 0
1982-03-24 | 1900-03-23 | 16:00 | 16 | 758 | 1375 | 285 | 1 | 13 | 94 | 1 | 13 | 233 | 1 | 13 | 31300 | 1 | 13 | 9400 | 1 | 13 | 26100 | 1 | 13 | 7280 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 12.8 | 55.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.47 | A | 7 | 973 | A | 7 | 60 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.66 | 6 | 0
1982-03-24 | 1900-03-23 | 17:00 | 17 | 536 | 1375 | 252 | 1 | 13 | 261 | 1 | 13 | 151 | 1 | 13 | 26900 | 1 | 13 | 25600 | 1 | 13 | 16900 | 1 | 13 | 3150 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 11.7 | 53.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.47 | A | 7 | 974 | A | 7 | 40 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.08 | 6 | 0
1982-03-24 | 1900-03-23 | 18:00 | 18 | 279 | 1375 | 63 | 1 | 13 | 24 | 1 | 9 | 58 | 1 | 13 | 6900 | 1 | 13 | 1900 | 1 | 9 | 6500 | 1 | 13 | 1520 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 11.1 | 51.98 | A | 7 | 1.1 | 33.98 | A | 7 | 0.5 | A | 7 | 974 | A | 7 | 50 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 1.1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.08 | 6 | 0
1982-03-24 | 1900-03-23 | 19:00 | 19 | 39 | 768 | 7 | 1 | 13 | 5 | 1 | 9 | 6 | 1 | 13 | 700 | 1 | 13 | 300 | 1 | 9 | 700 | 1 | 13 | 160 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 1.7 | 35.06 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 1.2 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.86 | 6 | 0
1982-03-24 | 1900-03-23 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 1010 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.14 | 6 | 0
1982-03-24 | 1900-03-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 3.9 | 39.02 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 790 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.12 | 6 | 0
1982-03-24 | 1900-03-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.83 | A | 7 | 978 | A | 7 | 20 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 700 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.72 | 6 | 0
1982-03-24 | 1900-03-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 6.1 | 42.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.83 | A | 7 | 978 | A | 7 | 20 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.84 | 6 | 0
1982-03-24 | 1900-03-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.86 | A | 7 | 978 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 880 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.24 | 6 | 0
1982-03-25 | 1900-03-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.89 | A | 7 | 979 | A | 7 | 10 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 820 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.74 | 7 | 0
1982-03-25 | 1900-03-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 350 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 210 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.14 | 7 | 0
1982-03-25 | 1900-03-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 150 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.16 | 7 | 0
1982-03-25 | 1900-03-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 982 | A | 7 | 350 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 210 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.16 | 7 | 0
1982-03-25 | 1900-03-24 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.92 | A | 7 | 982 | A | 7 | 360 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.08 | 7 | 0
1982-03-25 | 1900-03-24 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 350 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.08 | 7 | 0
1982-03-25 | 1900-03-24 | 7:00 | 7 | 69 | 997 | 18 | 1 | 13 | 5 | 1 | 9 | 17 | 1 | 13 | 1900 | 1 | 13 | 300 | 1 | 9 | 1900 | 1 | 13 | 430 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 340 | A | 7 | 1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 7 | 0
1982-03-25 | 1900-03-24 | 8:00 | 8 | 326 | 1375 | 80 | 1 | 13 | 7 | 1 | 9 | 78 | 1 | 13 | 9000 | 1 | 13 | 300 | 1 | 9 | 8900 | 1 | 13 | 2800 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.73 | A | 7 | 987 | A | 7 | 360 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 7 | 0
1982-03-25 | 1900-03-24 | 9:00 | 9 | 579 | 1375 | 200 | 1 | 9 | 52 | 1 | 9 | 179 | 1 | 13 | 22000 | 1 | 9 | 5100 | 1 | 9 | 19900 | 1 | 13 | 5050 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 2.2 | 35.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.79 | A | 7 | 987 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 580 | A | 7 | 1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.92 | 7 | 0
1982-03-25 | 1900-03-24 | 10:00 | 10 | 795 | 1375 | 524 | 1 | 13 | 678 | 1 | 13 | 134 | 1 | 13 | 55500 | 1 | 13 | 68000 | 1 | 13 | 16100 | 1 | 13 | 3100 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 988 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 7 | 0
1982-03-25 | 1900-03-24 | 11:00 | 11 | 958 | 1375 | 674 | 1 | 13 | 667 | 1 | 13 | 211 | 1 | 13 | 70500 | 1 | 13 | 66900 | 1 | 13 | 23700 | 1 | 13 | 5690 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 5 | 41 | A | 7 | -3.3 | 26.06 | A | 7 | 0.55 | A | 7 | 988 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.96 | 7 | 0
1982-03-25 | 1900-03-24 | 12:00 | 12 | 1059 | 1375 | 743 | 1 | 13 | 664 | 1 | 13 | 234 | 1 | 13 | 78000 | 1 | 13 | 66900 | 1 | 13 | 26400 | 1 | 13 | 7520 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 6.1 | 42.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.49 | A | 7 | 988 | A | 7 | 330 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.9 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.48 | 7 | 0
1982-03-25 | 1900-03-24 | 13:00 | 13 | 1089 | 1375 | 626 | 1 | 13 | 453 | 1 | 13 | 268 | 1 | 13 | 67600 | 1 | 13 | 47300 | 1 | 13 | 30100 | 1 | 13 | 9450 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 6.7 | 44.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.42 | A | 7 | 988 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.22 | 7 | 0
1982-03-25 | 1900-03-24 | 14:00 | 14 | 1047 | 1375 | 659 | 1 | 13 | 596 | 1 | 13 | 206 | 1 | 13 | 69600 | 1 | 13 | 60400 | 1 | 13 | 23500 | 1 | 13 | 6560 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 7.2 | 44.96 | A | 7 | -5 | 23 | A | 7 | 0.42 | A | 7 | 988 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.1 | 7 | 0
1982-03-25 | 1900-03-24 | 15:00 | 15 | 936 | 1375 | 515 | 1 | 13 | 391 | 1 | 13 | 250 | 1 | 13 | 54800 | 1 | 13 | 40400 | 1 | 13 | 27200 | 1 | 13 | 6780 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 6.7 | 44.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.4 | A | 7 | 987 | A | 7 | 340 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.32 | 7 | 0
1982-03-25 | 1900-03-24 | 16:00 | 16 | 763 | 1375 | 436 | 1 | 13 | 517 | 1 | 13 | 150 | 1 | 13 | 47500 | 1 | 13 | 52700 | 1 | 13 | 18200 | 1 | 13 | 3280 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 7.8 | 46.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.37 | A | 7 | 987 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 0.8 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.02 | 7 | 0
1982-03-25 | 1900-03-24 | 17:00 | 17 | 540 | 1375 | 303 | 1 | 13 | 437 | 1 | 13 | 132 | 1 | 13 | 31900 | 1 | 13 | 41700 | 1 | 13 | 15500 | 1 | 13 | 2580 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 6.7 | 44.06 | A | 7 | -7.2 | 19.04 | A | 7 | 0.37 | A | 7 | 987 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.44 | 7 | 0
1982-03-25 | 1900-03-24 | 18:00 | 18 | 283 | 1375 | 128 | 1 | 13 | 339 | 1 | 13 | 59 | 1 | 13 | 13600 | 1 | 13 | 25800 | 1 | 13 | 8300 | 1 | 13 | 1060 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 6.1 | 42.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.4 | A | 7 | 988 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.44 | 7 | 0
1982-03-25 | 1900-03-24 | 19:00 | 19 | 41 | 790 | 22 | 1 | 13 | 50 | 1 | 9 | 16 | 1 | 13 | 2000 | 1 | 13 | 1600 | 1 | 9 | 1900 | 1 | 13 | 270 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 4.4 | 39.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.43 | A | 7 | 988 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.84 | 7 | 0
1982-03-25 | 1900-03-24 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.55 | A | 7 | 988 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.52 | 7 | 0
1982-03-25 | 1900-03-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.57 | A | 7 | 989 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.74 | 7 | 0
1982-03-25 | 1900-03-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -6.7 | 19.94 | A | 7 | 0.61 | A | 7 | 989 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.04 | 7 | 0
1982-03-25 | 1900-03-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 990 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 7 | 0
1982-03-25 | 1900-03-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 990 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 7 | 0
1982-03-26 | 1900-03-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.69 | A | 7 | 990 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 1 | 0
1982-03-26 | 1900-03-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 990 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 1 | 0
1982-03-26 | 1900-03-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -7.2 | 19.04 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.24 | 1 | 0
1982-03-26 | 1900-03-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.84 | 1 | 0
1982-03-26 | 1900-03-25 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.78 | A | 7 | 990 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 1 | 0
1982-03-26 | 1900-03-25 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 1 | 0
1982-03-26 | 1900-03-25 | 7:00 | 7 | 74 | 1042 | 31 | 1 | 13 | 91 | 1 | 9 | 22 | 1 | 13 | 3100 | 1 | 13 | 3500 | 1 | 9 | 2800 | 1 | 13 | 380 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.54 | 1 | 0
1982-03-26 | 1900-03-25 | 8:00 | 8 | 333 | 1374 | 164 | 1 | 13 | 444 | 1 | 9 | 58 | 1 | 13 | 17100 | 1 | 13 | 36600 | 1 | 9 | 8200 | 1 | 13 | 1070 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.78 | A | 7 | 991 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 1 | 0
1982-03-26 | 1900-03-25 | 9:00 | 9 | 586 | 1374 | 381 | 1 | 9 | 713 | 1 | 9 | 80 | 1 | 13 | 39800 | 1 | 9 | 68100 | 1 | 9 | 10700 | 1 | 13 | 1590 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 1.7 | 35.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.59 | A | 7 | 992 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 1 | 0
1982-03-26 | 1900-03-25 | 10:00 | 10 | 801 | 1374 | 482 | 1 | 13 | 522 | 1 | 13 | 179 | 1 | 13 | 51900 | 1 | 13 | 53400 | 1 | 13 | 20700 | 1 | 13 | 4100 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 3.3 | 37.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.43 | A | 7 | 991 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.16 | 1 | 0
1982-03-26 | 1900-03-25 | 11:00 | 11 | 964 | 1374 | 476 | 1 | 13 | 315 | 1 | 13 | 256 | 1 | 13 | 52400 | 1 | 13 | 34000 | 1 | 13 | 28400 | 1 | 13 | 7190 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 5 | 41 | A | 7 | -9.4 | 15.08 | A | 7 | 0.35 | A | 7 | 991 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.98 | 1 | 0
1982-03-26 | 1900-03-25 | 12:00 | 12 | 1064 | 1374 | 704 | 1 | 13 | 624 | 1 | 13 | 222 | 1 | 13 | 74200 | 1 | 13 | 63100 | 1 | 13 | 25200 | 1 | 13 | 7270 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 6.1 | 42.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.35 | A | 7 | 991 | A | 7 | 360 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.56 | 1 | 0
1982-03-26 | 1900-03-25 | 13:00 | 13 | 1094 | 1374 | 794 | 1 | 9 | 729 | 1 | 9 | 215 | 1 | 13 | 84100 | 1 | 9 | 74000 | 1 | 9 | 25000 | 1 | 13 | 7560 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 7.2 | 44.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.3 | A | 7 | 990 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.58 | 1 | 0
1982-03-26 | 1900-03-25 | 14:00 | 14 | 1052 | 1374 | 738 | 1 | 9 | 756 | 1 | 9 | 161 | 1 | 13 | 79500 | 1 | 9 | 77500 | 1 | 9 | 20000 | 1 | 13 | 5320 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 7.8 | 46.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.3 | A | 7 | 989 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.38 | 1 | 0
1982-03-26 | 1900-03-25 | 15:00 | 15 | 940 | 1374 | 697 | 1 | 9 | 844 | 1 | 9 | 121 | 1 | 13 | 73700 | 1 | 9 | 84800 | 1 | 9 | 15600 | 1 | 13 | 3140 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.28 | A | 7 | 988 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.18 | 1 | 0
1982-03-26 | 1900-03-25 | 16:00 | 16 | 767 | 1374 | 542 | 1 | 9 | 776 | 1 | 9 | 110 | 1 | 13 | 56300 | 1 | 9 | 76500 | 1 | 9 | 13500 | 1 | 13 | 2320 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | -9.4 | 15.08 | A | 7 | 0.26 | A | 7 | 988 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.38 | 1 | 0
1982-03-26 | 1900-03-25 | 17:00 | 17 | 544 | 1374 | 317 | 1 | 9 | 574 | 1 | 9 | 91 | 1 | 13 | 33300 | 1 | 9 | 54400 | 1 | 9 | 11700 | 1 | 13 | 1800 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 8.3 | 46.94 | A | 7 | -10 | 14 | A | 7 | 0.26 | A | 7 | 987 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.5 | 1 | 0
1982-03-26 | 1900-03-25 | 18:00 | 18 | 287 | 1374 | 135 | 1 | 13 | 372 | 1 | 9 | 58 | 1 | 13 | 14400 | 1 | 13 | 28600 | 1 | 9 | 8400 | 1 | 13 | 1040 | 1 | 21 | 4 | A | 7 | 2 | A | 7 | 8.3 | 46.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.29 | A | 7 | 987 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.28 | 1 | 0
1982-03-26 | 1900-03-25 | 19:00 | 19 | 44 | 813 | 22 | 1 | 13 | 19 | 1 | 13 | 20 | 1 | 13 | 2300 | 1 | 13 | 1000 | 1 | 13 | 2300 | 1 | 13 | 470 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 6.7 | 44.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.38 | A | 7 | 987 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.24 | 1 | 0
1982-03-26 | 1900-03-25 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 4.4 | 39.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.45 | A | 7 | 988 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.74 | 1 | 0
1982-03-26 | 1900-03-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 3.9 | 39.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.48 | A | 7 | 988 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.92 | 1 | 0
1982-03-26 | 1900-03-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 2.8 | 37.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.22 | 1 | 0
1982-03-26 | 1900-03-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 1.7 | 35.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.57 | A | 7 | 988 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 1 | 0
1982-03-26 | 1900-03-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 1.7 | 35.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.59 | A | 7 | 989 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 1 | 0
1982-03-27 | 1900-03-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.64 | A | 7 | 989 | A | 7 | 80 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 2 | 0
1982-03-27 | 1900-03-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 1.1 | 33.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.67 | A | 7 | 990 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.28 | 2 | 0
1982-03-27 | 1900-03-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 990 | A | 7 | 80 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 2 | 0
1982-03-27 | 1900-03-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.59 | A | 7 | 991 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.82 | 2 | 0
1982-03-27 | 1900-03-26 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.59 | A | 7 | 991 | A | 7 | 70 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.84 | 2 | 0
1982-03-27 | 1900-03-26 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 0 | 32 | A | 7 | -6.7 | 19.94 | A | 7 | 0.61 | A | 7 | 991 | A | 7 | 80 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.04 | 2 | 0
1982-03-27 | 1900-03-26 | 7:00 | 7 | 79 | 1087 | 31 | 1 | 13 | 7 | 1 | 9 | 30 | 1 | 13 | 3400 | 1 | 13 | 0 | 1 | 9 | 3400 | 1 | 13 | 930 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 992 | A | 7 | 80 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.24 | 2 | 0
1982-03-27 | 1900-03-26 | 8:00 | 8 | 340 | 1373 | 140 | 1 | 13 | 165 | 1 | 13 | 99 | 1 | 13 | 15200 | 1 | 13 | 14100 | 1 | 13 | 11700 | 1 | 13 | 2170 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 0.6 | 33.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.59 | A | 7 | 993 | A | 7 | 100 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.84 | 2 | 0
1982-03-27 | 1900-03-26 | 9:00 | 9 | 592 | 1373 | 330 | 1 | 13 | 404 | 1 | 13 | 158 | 1 | 13 | 34700 | 1 | 13 | 39300 | 1 | 13 | 17700 | 1 | 13 | 3190 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 1.7 | 35.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.57 | A | 7 | 993 | A | 7 | 100 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 2 | 0
1982-03-27 | 1900-03-26 | 10:00 | 10 | 807 | 1373 | 456 | 1 | 9 | 510 | 1 | 9 | 157 | 1 | 13 | 49800 | 1 | 9 | 52300 | 1 | 9 | 19000 | 1 | 13 | 3580 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 2.8 | 37.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.5 | A | 7 | 994 | A | 7 | 100 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.14 | 2 | 0
1982-03-27 | 1900-03-26 | 11:00 | 11 | 970 | 1373 | 625 | 1 | 9 | 590 | 1 | 9 | 210 | 1 | 13 | 65500 | 1 | 9 | 59300 | 1 | 9 | 23500 | 1 | 13 | 5790 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | 4.4 | 39.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.47 | A | 7 | 994 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.82 | 2 | 0
1982-03-27 | 1900-03-26 | 12:00 | 12 | 1069 | 1373 | 779 | 1 | 9 | 746 | 1 | 9 | 200 | 1 | 13 | 82800 | 1 | 9 | 75900 | 1 | 9 | 23600 | 1 | 13 | 6720 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 5.6 | 42.08 | A | 7 | -5 | 23 | A | 7 | 0.47 | A | 7 | 993 | A | 7 | 110 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.6 | 2 | 0
1982-03-27 | 1900-03-26 | 13:00 | 13 | 1099 | 1373 | 795 | 1 | 9 | 817 | 1 | 9 | 143 | 1 | 13 | 84500 | 1 | 9 | 82500 | 1 | 9 | 18300 | 1 | 13 | 4840 | 1 | 18 | 7 | A | 7 | 1 | A | 7 | 7.2 | 44.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.4 | A | 7 | 993 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.02 | 2 | 0
1982-03-27 | 1900-03-26 | 14:00 | 14 | 1056 | 1373 | 789 | 1 | 9 | 879 | 1 | 9 | 114 | 1 | 13 | 81800 | 1 | 9 | 87800 | 1 | 9 | 14000 | 1 | 13 | 3030 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 7.8 | 46.04 | A | 7 | -5 | 23 | A | 7 | 0.4 | A | 7 | 992 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18 | 2 | 0
1982-03-27 | 1900-03-26 | 15:00 | 15 | 944 | 1373 | 670 | 1 | 9 | 788 | 1 | 9 | 129 | 1 | 13 | 70400 | 1 | 9 | 78900 | 1 | 9 | 15900 | 1 | 13 | 3300 | 1 | 18 | 6 | A | 7 | 1 | A | 7 | 8.3 | 46.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.36 | A | 7 | 992 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.02 | 2 | 0
1982-03-27 | 1900-03-26 | 16:00 | 16 | 771 | 1373 | 518 | 1 | 9 | 695 | 1 | 9 | 129 | 1 | 13 | 54800 | 1 | 9 | 69500 | 1 | 9 | 15700 | 1 | 13 | 2930 | 1 | 18 | 8 | A | 7 | 1 | A | 7 | 8.3 | 46.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.3 | A | 7 | 992 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.26 | 2 | 0
1982-03-27 | 1900-03-26 | 17:00 | 17 | 548 | 1373 | 335 | 1 | 9 | 553 | 1 | 9 | 115 | 1 | 13 | 34500 | 1 | 9 | 51900 | 1 | 9 | 13800 | 1 | 13 | 2180 | 1 | 18 | 6 | A | 7 | 1 | A | 7 | 8.3 | 46.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.3 | A | 7 | 991 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.26 | 2 | 0
1982-03-27 | 1900-03-26 | 18:00 | 18 | 292 | 1373 | 143 | 1 | 13 | 455 | 1 | 9 | 47 | 1 | 13 | 14900 | 1 | 13 | 35900 | 1 | 9 | 7300 | 1 | 13 | 870 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 7.2 | 44.96 | A | 7 | -8.3 | 17.06 | A | 7 | 0.32 | A | 7 | 992 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.36 | 2 | 0
1982-03-27 | 1900-03-26 | 19:00 | 19 | 46 | 835 | 26 | 1 | 13 | 83 | 1 | 9 | 17 | 1 | 13 | 2300 | 1 | 13 | 3200 | 1 | 9 | 2200 | 1 | 13 | 300 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.41 | A | 7 | 991 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.76 | 2 | 0
1982-03-27 | 1900-03-26 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 3.3 | 37.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.44 | A | 7 | 992 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.96 | 2 | 0
1982-03-27 | 1900-03-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 2.2 | 35.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.5 | A | 7 | 992 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.34 | 2 | 0
1982-03-27 | 1900-03-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.54 | A | 7 | 992 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.64 | 2 | 0
1982-03-27 | 1900-03-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.59 | A | 7 | 992 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.84 | 2 | 0
1982-03-27 | 1900-03-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -6.7 | 19.94 | A | 7 | 0.61 | A | 7 | 992 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.04 | 2 | 0
1982-03-28 | 1900-03-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 0 | 32 | A | 7 | -6.1 | 21.02 | A | 7 | 0.64 | A | 7 | 992 | A | 7 | 110 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.22 | 3 | 0
1982-03-28 | 1900-03-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.66 | A | 7 | 992 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.32 | 3 | 0
1982-03-28 | 1900-03-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 991 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 3 | 0
1982-03-28 | 1900-03-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.69 | A | 7 | 991 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 3 | 0
1982-03-28 | 1900-03-27 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.69 | A | 7 | 991 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 3 | 0
1982-03-28 | 1900-03-27 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.69 | A | 7 | 991 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 3 | 0
1982-03-28 | 1900-03-27 | 7:00 | 7 | 85 | 1109 | 41 | 1 | 13 | 202 | 1 | 9 | 20 | 1 | 13 | 3700 | 1 | 13 | 10300 | 1 | 9 | 2900 | 1 | 13 | 360 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 991 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.24 | 3 | 0
1982-03-28 | 1900-03-27 | 8:00 | 8 | 347 | 1372 | 191 | 1 | 13 | 567 | 1 | 9 | 50 | 1 | 13 | 20300 | 1 | 13 | 47900 | 1 | 9 | 8100 | 1 | 13 | 950 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 1.7 | 35.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.57 | A | 7 | 991 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 3 | 0
1982-03-28 | 1900-03-27 | 9:00 | 9 | 599 | 1372 | 363 | 1 | 13 | 645 | 1 | 13 | 84 | 1 | 13 | 38800 | 1 | 13 | 62800 | 1 | 13 | 11300 | 1 | 13 | 1750 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 4.4 | 39.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.49 | A | 7 | 991 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.82 | 3 | 0
1982-03-28 | 1900-03-27 | 10:00 | 10 | 813 | 1372 | 512 | 1 | 13 | 671 | 1 | 13 | 117 | 1 | 13 | 55000 | 1 | 13 | 67900 | 1 | 13 | 14700 | 1 | 13 | 2820 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 6.7 | 44.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.45 | A | 7 | 991 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.28 | 3 | 0
1982-03-28 | 1900-03-27 | 11:00 | 11 | 976 | 1372 | 750 | 1 | 9 | 953 | 1 | 9 | 74 | 1 | 13 | 78800 | 1 | 9 | 95200 | 1 | 9 | 10900 | 1 | 13 | 2160 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.46 | A | 7 | 991 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.86 | 3 | 0
1982-03-28 | 1900-03-27 | 12:00 | 12 | 1075 | 1372 | 840 | 1 | 9 | 974 | 1 | 9 | 80 | 1 | 13 | 88100 | 1 | 9 | 97600 | 1 | 9 | 11500 | 1 | 13 | 2640 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | -1.1 | 30.02 | A | 7 | 0.46 | A | 7 | 990 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.42 | 3 | 0
1982-03-28 | 1900-03-27 | 13:00 | 13 | 1104 | 1372 | 842 | 1 | 13 | 843 | 1 | 13 | 165 | 1 | 13 | 88100 | 1 | 13 | 84500 | 1 | 13 | 19900 | 1 | 13 | 5440 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 11.7 | 53.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.43 | A | 7 | 989 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.82 | 3 | 0
1982-03-28 | 1900-03-27 | 14:00 | 14 | 1061 | 1372 | 656 | 1 | 13 | 548 | 1 | 13 | 233 | 1 | 13 | 71600 | 1 | 13 | 57200 | 1 | 13 | 27200 | 1 | 13 | 7710 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 11.7 | 53.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.4 | A | 7 | 988 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.84 | 3 | 0
1982-03-28 | 1900-03-27 | 15:00 | 15 | 949 | 1372 | 702 | 1 | 13 | 836 | 1 | 13 | 125 | 1 | 13 | 74100 | 1 | 13 | 83900 | 1 | 13 | 15900 | 1 | 13 | 3260 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 12.8 | 55.04 | A | 7 | -1.1 | 30.02 | A | 7 | 0.39 | A | 7 | 987 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.62 | 3 | 0
1982-03-28 | 1900-03-27 | 16:00 | 16 | 775 | 1372 | 538 | 1 | 9 | 816 | 1 | 9 | 78 | 1 | 13 | 56400 | 1 | 9 | 80300 | 1 | 9 | 10900 | 1 | 13 | 1750 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 12.2 | 53.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.38 | A | 7 | 985 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.64 | 3 | 0
1982-03-28 | 1900-03-27 | 17:00 | 17 | 553 | 1372 | 349 | 1 | 9 | 747 | 1 | 9 | 50 | 1 | 13 | 37100 | 1 | 9 | 70900 | 1 | 9 | 8400 | 1 | 13 | 1220 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 11.1 | 51.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.41 | A | 7 | 985 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.94 | 3 | 0
1982-03-28 | 1900-03-27 | 18:00 | 18 | 296 | 1372 | 150 | 1 | 13 | 419 | 1 | 9 | 61 | 1 | 13 | 15400 | 1 | 13 | 32800 | 1 | 9 | 8300 | 1 | 13 | 1080 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | 10.6 | 51.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.43 | A | 7 | 985 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.14 | 3 | 0
1982-03-28 | 1900-03-27 | 19:00 | 19 | 49 | 858 | 32 | 1 | 13 | 159 | 1 | 9 | 15 | 1 | 13 | 2600 | 1 | 13 | 7300 | 1 | 9 | 2100 | 1 | 13 | 280 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.48 | A | 7 | 984 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.94 | 3 | 0
1982-03-28 | 1900-03-27 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.47 | A | 7 | 984 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.16 | 3 | 0
1982-03-28 | 1900-03-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.47 | A | 7 | 984 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.48 | 3 | 0
1982-03-28 | 1900-03-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -5 | 23 | A | 7 | 0.49 | A | 7 | 984 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.7 | 3 | 0
1982-03-28 | 1900-03-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.49 | A | 7 | 984 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.82 | 3 | 0
1982-03-28 | 1900-03-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -5 | 23 | A | 7 | 0.51 | A | 7 | 984 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.9 | 3 | 0
1982-03-29 | 1900-03-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -5 | 23 | A | 7 | 0.45 | A | 7 | 983 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.4 | 4 | 0
1982-03-29 | 1900-03-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.49 | A | 7 | 983 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.68 | 4 | 0
1982-03-29 | 1900-03-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -4.4 | 24.08 | A | 7 | 0.51 | A | 7 | 982 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.88 | 4 | 0
1982-03-29 | 1900-03-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.98 | 4 | 0
1982-03-29 | 1900-03-28 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 4 | 0
1982-03-29 | 1900-03-28 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 5 | 41 | A | 7 | -4.4 | 24.08 | A | 7 | 0.51 | A | 7 | 982 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.88 | 4 | 0
1982-03-29 | 1900-03-28 | 7:00 | 7 | 90 | 1154 | 16 | 1 | 13 | 13 | 1 | 9 | 15 | 1 | 13 | 1800 | 1 | 13 | 800 | 1 | 9 | 1700 | 1 | 13 | 390 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 4.4 | 39.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.55 | A | 7 | 982 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 4 | 0
1982-03-29 | 1900-03-28 | 8:00 | 8 | 354 | 1371 | 126 | 1 | 13 | 73 | 1 | 13 | 108 | 1 | 13 | 13900 | 1 | 13 | 6400 | 1 | 13 | 12200 | 1 | 13 | 2720 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 6.1 | 42.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.56 | 4 | 0
1982-03-29 | 1900-03-28 | 9:00 | 9 | 605 | 1371 | 379 | 1 | 13 | 581 | 1 | 13 | 124 | 1 | 13 | 39300 | 1 | 13 | 55700 | 1 | 13 | 14700 | 1 | 13 | 2430 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 9.4 | 48.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.44 | A | 7 | 981 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.54 | 4 | 0
1982-03-29 | 1900-03-28 | 10:00 | 10 | 819 | 1371 | 402 | 1 | 13 | 377 | 1 | 13 | 178 | 1 | 13 | 43500 | 1 | 13 | 38700 | 1 | 13 | 20300 | 1 | 13 | 4140 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 9.4 | 48.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.44 | A | 7 | 981 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.54 | 4 | 0
1982-03-29 | 1900-03-28 | 11:00 | 11 | 981 | 1371 | 650 | 1 | 13 | 682 | 1 | 13 | 163 | 1 | 13 | 69400 | 1 | 13 | 69500 | 1 | 13 | 19500 | 1 | 13 | 4750 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 13.3 | 55.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.39 | A | 7 | 980 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.42 | 4 | 0
1982-03-29 | 1900-03-28 | 12:00 | 12 | 1080 | 1371 | 390 | 1 | 13 | 186 | 1 | 13 | 244 | 1 | 13 | 43700 | 1 | 13 | 20200 | 1 | 13 | 27700 | 1 | 13 | 8020 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 15 | 59 | A | 7 | 0.6 | 33.08 | A | 7 | 0.38 | A | 7 | 979 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.98 | 4 | 0
1982-03-29 | 1900-03-28 | 13:00 | 13 | 1109 | 1371 | 422 | 1 | 9 | 93 | 1 | 9 | 347 | 1 | 13 | 46600 | 1 | 9 | 9500 | 1 | 9 | 38900 | 1 | 13 | 14170 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 15 | 59 | A | 7 | 1.7 | 35.06 | A | 7 | 0.41 | A | 7 | 977 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 1.2 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.86 | 4 | 0
1982-03-29 | 1900-03-28 | 14:00 | 14 | 1065 | 1371 | 551 | 1 | 9 | 266 | 1 | 9 | 345 | 1 | 13 | 60000 | 1 | 9 | 28800 | 1 | 9 | 37500 | 1 | 13 | 11580 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 15.6 | 60.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.43 | A | 7 | 976 | A | 7 | 160 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.64 | 4 | 0
1982-03-29 | 1900-03-28 | 15:00 | 15 | 953 | 1371 | 641 | 1 | 13 | 655 | 1 | 13 | 187 | 1 | 13 | 67500 | 1 | 13 | 66100 | 1 | 13 | 21500 | 1 | 13 | 5110 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 16.7 | 62.06 | A | 7 | 3.9 | 39.02 | A | 7 | 0.43 | A | 7 | 974 | A | 7 | 160 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.22 | 4 | 0
1982-03-29 | 1900-03-28 | 16:00 | 16 | 779 | 1371 | 488 | 1 | 13 | 591 | 1 | 13 | 153 | 1 | 13 | 51000 | 1 | 13 | 58700 | 1 | 13 | 17600 | 1 | 13 | 3420 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 16.7 | 62.06 | A | 7 | 3.9 | 39.02 | A | 7 | 0.43 | A | 7 | 973 | A | 7 | 160 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.22 | 4 | 0
1982-03-29 | 1900-03-28 | 17:00 | 17 | 557 | 1371 | 331 | 1 | 13 | 543 | 1 | 13 | 112 | 1 | 13 | 34300 | 1 | 13 | 51200 | 1 | 13 | 13500 | 1 | 13 | 2150 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 16.1 | 60.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.44 | A | 7 | 971 | A | 7 | 160 | A | 7 | 10.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.32 | 4 | 0
1982-03-29 | 1900-03-28 | 18:00 | 18 | 300 | 1371 | 131 | 1 | 13 | 178 | 1 | 9 | 92 | 1 | 13 | 13700 | 1 | 13 | 14000 | 1 | 9 | 10600 | 1 | 13 | 1820 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 16.1 | 60.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.44 | A | 7 | 970 | A | 7 | 160 | A | 7 | 10.3 | A | 7 | 19300 | A | 7 | 2130 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.32 | 4 | 0
1982-03-29 | 1900-03-28 | 19:00 | 19 | 51 | 880 | 7 | 1 | 13 | 0 | 1 | 9 | 7 | 1 | 13 | 900 | 1 | 13 | 0 | 1 | 9 | 900 | 1 | 13 | 270 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 5 | 41 | A | 7 | 0.5 | A | 7 | 969 | A | 7 | 160 | A | 7 | 10.8 | A | 7 | 12900 | A | 7 | 1220 | A | 7 | 1.4 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.2 | 4 | 0
1982-03-29 | 1900-03-28 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 5.6 | 42.08 | A | 7 | 0.54 | A | 7 | 969 | A | 7 | 160 | A | 7 | 10.3 | A | 7 | 12900 | A | 7 | 1220 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.68 | 4 | 0
1982-03-29 | 1900-03-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.67 | A | 7 | 970 | A | 7 | 180 | A | 7 | 13.4 | A | 7 | 12900 | A | 7 | 1040 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 4 | 0
1982-03-29 | 1900-03-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.72 | A | 7 | 969 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.74 | 4 | 0
1982-03-29 | 1900-03-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 10 | 50 | A | 7 | 0.9 | A | 7 | 967 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 850 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.4 | 4 | 0
1982-03-29 | 1900-03-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 10 | 50 | A | 7 | 0.86 | A | 7 | 965 | A | 7 | 160 | A | 7 | 8.8 | A | 7 | 12900 | A | 7 | 880 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.8 | 4 | 0
1982-03-30 | 1900-03-29 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.8 | 55.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.86 | A | 7 | 964 | A | 7 | 170 | A | 7 | 9.8 | A | 7 | 8000 | A | 7 | 880 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.78 | 5 | 0
1982-03-30 | 1900-03-29 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 964 | A | 7 | 200 | A | 7 | 15.4 | A | 7 | 3200 | A | 7 | 310 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.92 | 5 | 0
1982-03-30 | 1900-03-29 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.93 | A | 7 | 962 | A | 7 | 200 | A | 7 | 18 | A | 7 | 4800 | A | 7 | 400 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.88 | 5 | 0
1982-03-30 | 1900-03-29 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.9 | A | 7 | 962 | A | 7 | 200 | A | 7 | 13.9 | A | 7 | 6400 | A | 7 | 880 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.48 | 5 | 0
1982-03-30 | 1900-03-29 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 13.3 | 55.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.9 | A | 7 | 961 | A | 7 | 200 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.36 | 5 | 0
1982-03-30 | 1900-03-29 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.87 | A | 7 | 962 | A | 7 | 220 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.76 | 5 | 0
1982-03-30 | 1900-03-29 | 7:00 | 7 | 96 | 1176 | 35 | 1 | 13 | 79 | 1 | 9 | 27 | 1 | 13 | 3600 | 1 | 13 | 3400 | 1 | 9 | 3300 | 1 | 13 | 480 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.78 | A | 7 | 963 | A | 7 | 210 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.5 | 5 | 0
1982-03-30 | 1900-03-29 | 8:00 | 8 | 361 | 1371 | 197 | 1 | 9 | 553 | 1 | 9 | 54 | 1 | 13 | 20900 | 1 | 9 | 47200 | 1 | 9 | 8400 | 1 | 13 | 1030 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.6 | A | 7 | 964 | A | 7 | 210 | A | 7 | 12.4 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.26 | 5 | 0
1982-03-30 | 1900-03-29 | 9:00 | 9 | 612 | 1371 | 408 | 1 | 9 | 743 | 1 | 9 | 79 | 1 | 13 | 42900 | 1 | 9 | 71700 | 1 | 9 | 10800 | 1 | 13 | 1630 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.49 | A | 7 | 965 | A | 7 | 240 | A | 7 | 13.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.42 | 5 | 0
1982-03-30 | 1900-03-29 | 10:00 | 10 | 825 | 1371 | 593 | 1 | 9 | 826 | 1 | 9 | 98 | 1 | 13 | 63200 | 1 | 9 | 82600 | 1 | 9 | 13300 | 1 | 13 | 2340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.39 | A | 7 | 967 | A | 7 | 240 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.08 | 5 | 0
1982-03-30 | 1900-03-29 | 11:00 | 11 | 987 | 1371 | 744 | 1 | 9 | 881 | 1 | 9 | 112 | 1 | 13 | 77300 | 1 | 9 | 87800 | 1 | 9 | 13900 | 1 | 13 | 2620 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.38 | A | 7 | 967 | A | 7 | 240 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.68 | 5 | 0
1982-03-30 | 1900-03-29 | 12:00 | 12 | 1085 | 1371 | 832 | 1 | 9 | 903 | 1 | 9 | 119 | 1 | 13 | 86100 | 1 | 9 | 90300 | 1 | 9 | 14500 | 1 | 13 | 3310 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.46 | A | 7 | 967 | A | 7 | 210 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.72 | 5 | 0
1982-03-30 | 1900-03-29 | 13:00 | 13 | 1113 | 1371 | 858 | 1 | 9 | 909 | 1 | 9 | 121 | 1 | 13 | 88700 | 1 | 9 | 90900 | 1 | 9 | 14700 | 1 | 13 | 3580 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.4 | A | 7 | 967 | A | 7 | 210 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.94 | 5 | 0
1982-03-30 | 1900-03-29 | 14:00 | 14 | 1070 | 1371 | 818 | 1 | 9 | 899 | 1 | 9 | 118 | 1 | 13 | 84700 | 1 | 9 | 89800 | 1 | 9 | 14400 | 1 | 13 | 3180 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.36 | A | 7 | 967 | A | 7 | 230 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.74 | 5 | 0
1982-03-30 | 1900-03-29 | 15:00 | 15 | 957 | 1371 | 724 | 1 | 9 | 882 | 1 | 9 | 110 | 1 | 13 | 75200 | 1 | 9 | 87800 | 1 | 9 | 13700 | 1 | 13 | 2460 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.28 | A | 7 | 968 | A | 7 | 230 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.12 | 5 | 0
1982-03-30 | 1900-03-29 | 16:00 | 16 | 784 | 1371 | 567 | 1 | 9 | 829 | 1 | 9 | 95 | 1 | 13 | 60100 | 1 | 9 | 82500 | 1 | 9 | 12900 | 1 | 13 | 2180 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.25 | A | 7 | 967 | A | 7 | 230 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.54 | 5 | 0
1982-03-30 | 1900-03-29 | 17:00 | 17 | 561 | 1371 | 369 | 1 | 9 | 725 | 1 | 9 | 74 | 1 | 13 | 38500 | 1 | 9 | 69000 | 1 | 9 | 10200 | 1 | 13 | 1490 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.24 | A | 7 | 968 | A | 7 | 230 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.66 | 5 | 0
1982-03-30 | 1900-03-29 | 18:00 | 18 | 304 | 1371 | 160 | 1 | 13 | 506 | 1 | 9 | 49 | 1 | 13 | 16800 | 1 | 13 | 40600 | 1 | 9 | 7700 | 1 | 13 | 910 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.26 | A | 7 | 969 | A | 7 | 230 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.64 | 5 | 0
1982-03-30 | 1900-03-29 | 19:00 | 19 | 54 | 902 | 28 | 1 | 13 | 83 | 1 | 9 | 19 | 1 | 13 | 2600 | 1 | 13 | 3300 | 1 | 9 | 2400 | 1 | 13 | 330 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | -0.6 | 30.92 | A | 7 | 0.35 | A | 7 | 970 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.92 | 5 | 0
1982-03-30 | 1900-03-29 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.42 | A | 7 | 970 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.48 | 5 | 0
1982-03-30 | 1900-03-29 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.49 | A | 7 | 970 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.86 | 5 | 0
1982-03-30 | 1900-03-29 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 0 | 32 | A | 7 | 0.34 | A | 7 | 971 | A | 7 | 220 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.7 | 5 | 0
1982-03-30 | 1900-03-29 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 13.9 | 57.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.42 | A | 7 | 971 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 2130 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.18 | 5 | 0
1982-03-30 | 1900-03-29 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.53 | A | 7 | 972 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 1340 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.94 | 5 | 0
1982-03-31 | 1900-03-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 11.1 | 51.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.59 | A | 7 | 973 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.84 | 6 | 0
1982-03-31 | 1900-03-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 12.2 | 53.96 | A | 7 | 2.2 | 35.96 | A | 7 | 0.51 | A | 7 | 973 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.86 | 6 | 0
1982-03-31 | 1900-03-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 0.6 | 33.08 | A | 7 | 0.5 | A | 7 | 974 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.38 | 6 | 0
1982-03-31 | 1900-03-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.5 | A | 7 | 977 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.82 | 6 | 0
1982-03-31 | 1900-03-30 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.58 | A | 7 | 978 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.72 | 6 | 0
1982-03-31 | 1900-03-30 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -1.7 | 28.94 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 6 | 0
1982-03-31 | 1900-03-30 | 7:00 | 7 | 102 | 1221 | 48 | 1 | 13 | 280 | 1 | 9 | 19 | 1 | 13 | 4500 | 1 | 13 | 15000 | 1 | 9 | 3200 | 1 | 13 | 350 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.72 | 6 | 0
1982-03-31 | 1900-03-30 | 8:00 | 8 | 368 | 1370 | 221 | 1 | 9 | 690 | 1 | 9 | 38 | 1 | 13 | 23600 | 1 | 9 | 60600 | 1 | 9 | 7300 | 1 | 13 | 900 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.58 | A | 7 | 982 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.28 | 6 | 0
1982-03-31 | 1900-03-30 | 9:00 | 9 | 618 | 1370 | 431 | 1 | 9 | 841 | 1 | 9 | 55 | 1 | 13 | 45800 | 1 | 9 | 81100 | 1 | 9 | 9200 | 1 | 13 | 1340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 0.6 | 33.08 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.58 | 6 | 0
1982-03-31 | 1900-03-30 | 10:00 | 10 | 831 | 1370 | 620 | 1 | 9 | 914 | 1 | 9 | 69 | 1 | 13 | 65500 | 1 | 9 | 90600 | 1 | 9 | 10400 | 1 | 13 | 1780 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 0 | 32 | A | 7 | 0.43 | A | 7 | 984 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.7 | 6 | 0
1982-03-31 | 1900-03-30 | 11:00 | 11 | 992 | 1370 | 766 | 1 | 9 | 953 | 1 | 9 | 78 | 1 | 13 | 80400 | 1 | 9 | 95300 | 1 | 9 | 11200 | 1 | 13 | 2280 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 0 | 32 | A | 7 | 0.39 | A | 7 | 984 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.2 | 6 | 0
1982-03-31 | 1900-03-30 | 12:00 | 12 | 1090 | 1370 | 854 | 1 | 9 | 971 | 1 | 9 | 84 | 1 | 13 | 89500 | 1 | 9 | 97300 | 1 | 9 | 11800 | 1 | 13 | 2810 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 0 | 32 | A | 7 | 0.37 | A | 7 | 984 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25 | 6 | 0
1982-03-31 | 1900-03-30 | 13:00 | 13 | 1118 | 1370 | 885 | 1 | 9 | 982 | 1 | 9 | 85 | 1 | 13 | 92500 | 1 | 9 | 98500 | 1 | 9 | 11900 | 1 | 13 | 3000 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.29 | A | 7 | 983 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.04 | 6 | 0
1982-03-31 | 1900-03-30 | 14:00 | 14 | 1074 | 1370 | 843 | 1 | 9 | 971 | 1 | 9 | 83 | 1 | 13 | 88200 | 1 | 9 | 97300 | 1 | 9 | 11700 | 1 | 13 | 2700 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.29 | A | 7 | 983 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.52 | 6 | 0
1982-03-31 | 1900-03-30 | 15:00 | 15 | 961 | 1370 | 743 | 1 | 9 | 952 | 1 | 9 | 77 | 1 | 13 | 78000 | 1 | 9 | 95000 | 1 | 9 | 11100 | 1 | 13 | 2170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.23 | A | 7 | 983 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.98 | 6 | 0
1982-03-31 | 1900-03-30 | 16:00 | 16 | 788 | 1370 | 587 | 1 | 9 | 908 | 1 | 9 | 66 | 1 | 13 | 61800 | 1 | 9 | 89600 | 1 | 9 | 10200 | 1 | 13 | 1670 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.23 | A | 7 | 982 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.86 | 6 | 0
1982-03-31 | 1900-03-30 | 17:00 | 17 | 565 | 1370 | 388 | 1 | 9 | 820 | 1 | 9 | 52 | 1 | 13 | 41200 | 1 | 9 | 78100 | 1 | 9 | 8900 | 1 | 13 | 1250 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | -1.1 | 30.02 | A | 7 | 0.27 | A | 7 | 982 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.32 | 6 | 0
1982-03-31 | 1900-03-30 | 18:00 | 18 | 309 | 1370 | 177 | 1 | 13 | 638 | 1 | 9 | 35 | 1 | 13 | 18700 | 1 | 13 | 53100 | 1 | 9 | 6800 | 1 | 13 | 740 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.29 | A | 7 | 982 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.52 | 6 | 0
1982-03-31 | 1900-03-30 | 19:00 | 19 | 57 | 925 | 34 | 1 | 13 | 170 | 1 | 9 | 16 | 1 | 13 | 2800 | 1 | 13 | 8000 | 1 | 9 | 2300 | 1 | 13 | 290 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.43 | A | 7 | 982 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.58 | 6 | 0
1982-03-31 | 1900-03-30 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 0 | 32 | A | 7 | 0.45 | A | 7 | 982 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.9 | 6 | 0
1982-03-31 | 1900-03-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 0 | 32 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.7 | 6 | 0
1982-03-31 | 1900-03-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.2 | 48.56 | A | 7 | 1 | 33.8 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 190 | A | 7 | 4.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.2 | 6 | 0
1982-03-31 | 1900-03-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 1.9 | 35.42 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 190 | A | 7 | 4.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.52 | 6 | 0
1982-03-31 | 1900-03-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.7 | 47.66 | A | 7 | 2.9 | 37.22 | A | 7 | 0.56 | A | 7 | 983 | A | 7 | 210 | A | 7 | 4.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.52 | 6 | 0
2000-04-01 | 1900-03-31 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 8.5 | 47.3 | A | 7 | 3.8 | 38.84 | A | 7 | 0.83 | A | 7 | 986 | A | 7 | 340 | A | 7 | 4 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 1.5 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.64 | 7 | 0
2000-04-01 | 1900-03-31 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | E | 9 | 8.3 | 46.94 | A | 7 | 4.8 | 40.64 | A | 7 | 0.9 | A | 7 | 985 | A | 7 | 350 | A | 7 | 3.9 | A | 7 | 12800 | A | 7 | 3353 | A | 7 | 1.5 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.34 | 7 | 0
2000-04-01 | 1900-03-31 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 8 | 46.4 | A | 7 | 5.7 | 42.26 | A | 7 | 0.9 | A | 7 | 985 | A | 7 | 360 | A | 7 | 3.7 | A | 7 | 11200 | A | 7 | 1981 | A | 7 | 1.4 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.86 | 7 | 0
2000-04-01 | 1900-03-31 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 1676 | A | 7 | 1.4 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.06 | 7 | 0
2000-04-01 | 1900-03-31 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 2743 | A | 7 | 1.3 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.06 | 7 | 0
2000-04-01 | 1900-03-31 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 7.8 | 46.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.89 | A | 7 | 984 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 14400 | A | 7 | 2134 | A | 7 | 1.2 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.48 | 7 | 0
2000-04-01 | 1900-03-31 | 7:00 | 7 | 112 | 1266 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 2286 | A | 7 | 1.2 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.98 | 7 | 0
2000-04-01 | 1900-03-31 | 8:00 | 8 | 379 | 1368 | 40 | 2 | 8 | 0 | 2 | 15 | 40 | 2 | 8 | 4800 | 2 | 8 | 0 | 2 | 15 | 4800 | 2 | 8 | 1720 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.9 | A | 7 | 985 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 2134 | A | 7 | 1.1 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.68 | 7 | 0
2000-04-01 | 1900-03-31 | 9:00 | 9 | 628 | 1368 | 75 | 2 | 8 | 0 | 2 | 15 | 75 | 2 | 8 | 9100 | 2 | 8 | 0 | 2 | 15 | 9100 | 2 | 8 | 3500 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.9 | A | 7 | 985 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 1829 | A | 7 | 1.1 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.68 | 7 | 0
2000-04-01 | 1900-03-31 | 10:00 | 10 | 841 | 1368 | 110 | 2 | 8 | 0 | 2 | 15 | 110 | 2 | 8 | 13500 | 2 | 8 | 0 | 2 | 15 | 13500 | 2 | 8 | 5440 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.8 | 46.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 1829 | A | 7 | 1 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.48 | 7 | 0
2000-04-01 | 1900-03-31 | 11:00 | 11 | 1001 | 1368 | 132 | 2 | 8 | 0 | 2 | 15 | 132 | 2 | 8 | 16300 | 2 | 8 | 0 | 2 | 15 | 16300 | 2 | 8 | 6780 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 8.3 | 46.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.86 | A | 7 | 984 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 2438 | A | 7 | 0.9 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.08 | 7 | 0
2000-04-01 | 1900-03-31 | 12:00 | 12 | 1098 | 1368 | 184 | 2 | 8 | 0 | 2 | 15 | 184 | 2 | 8 | 22500 | 2 | 8 | 0 | 2 | 15 | 22500 | 2 | 8 | 9270 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.8 | A | 7 | 982 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 2134 | A | 7 | 0.9 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.18 | 7 | 0
2000-04-01 | 1900-03-31 | 13:00 | 13 | 1125 | 1368 | 150 | 2 | 8 | 0 | 2 | 15 | 150 | 2 | 8 | 18700 | 2 | 8 | 0 | 2 | 15 | 18700 | 2 | 8 | 7800 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.83 | A | 7 | 983 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 11200 | A | 7 | 2134 | A | 7 | 0.9 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.66 | 7 | 0
2000-04-01 | 1900-03-31 | 14:00 | 14 | 1081 | 1368 | 135 | 2 | 8 | 0 | 2 | 15 | 135 | 2 | 8 | 16800 | 2 | 8 | 0 | 2 | 15 | 16800 | 2 | 8 | 7050 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10 | 50 | A | 7 | 6.1 | 42.98 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 360 | A | 7 | 1.5 | A | 7 | 11200 | A | 7 | 2134 | A | 7 | 1 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.78 | 7 | 0
2000-04-01 | 1900-03-31 | 15:00 | 15 | 968 | 1368 | 190 | 2 | 8 | 6 | 2 | 15 | 185 | 2 | 8 | 22700 | 2 | 8 | 500 | 2 | 15 | 22400 | 2 | 8 | 8940 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10 | 50 | A | 7 | 5.6 | 42.08 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11200 | A | 7 | 2134 | A | 7 | 1 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.58 | 7 | 0
2000-04-01 | 1900-03-31 | 16:00 | 16 | 794 | 1368 | 95 | 2 | 8 | 0 | 2 | 15 | 95 | 2 | 8 | 11700 | 2 | 8 | 0 | 2 | 15 | 11700 | 2 | 8 | 4680 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10 | 50 | A | 7 | 6.7 | 44.06 | A | 7 | 0.8 | A | 7 | 982 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 1981 | A | 7 | 1.1 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.26 | 7 | 0
2000-04-01 | 1900-03-31 | 17:00 | 17 | 571 | 1368 | 63 | 2 | 8 | 0 | 2 | 15 | 63 | 2 | 8 | 7700 | 2 | 8 | 0 | 2 | 15 | 7700 | 2 | 8 | 2900 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 9.4 | 48.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 12800 | A | 7 | 2134 | A | 7 | 1.1 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.66 | 7 | 0
2000-04-01 | 1900-03-31 | 18:00 | 18 | 315 | 1368 | 27 | 2 | 8 | 0 | 2 | 15 | 27 | 2 | 8 | 3300 | 2 | 8 | 0 | 2 | 15 | 3300 | 2 | 8 | 1150 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.83 | A | 7 | 979 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 2896 | A | 7 | 1.2 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.66 | 7 | 0
2000-04-01 | 1900-03-31 | 19:00 | 19 | 61 | 946 | 1 | 2 | 8 | 0 | 2 | 15 | 1 | 2 | 8 | 100 | 2 | 8 | 0 | 2 | 15 | 100 | 2 | 8 | 40 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 8.3 | 46.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.86 | A | 7 | 980 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 11200 | A | 7 | 1981 | A | 7 | 1.3 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.08 | 7 | 0
2000-04-01 | 1900-03-31 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 12800 | A | 7 | 2134 | A | 7 | 1.3 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.06 | 7 | 0
2000-04-01 | 1900-03-31 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 7.8 | 46.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11200 | A | 7 | 2134 | A | 7 | 1.4 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.48 | 7 | 0
2000-04-01 | 1900-03-31 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9600 | A | 7 | 2286 | A | 7 | 1.4 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.06 | 7 | 0
2000-04-01 | 1900-03-31 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 9600 | A | 7 | 2438 | A | 7 | 1.5 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.98 | 7 | 0
2000-04-01 | 1900-03-31 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 9600 | A | 7 | 2743 | A | 7 | 1.5 | E | 8 | 0.107 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.38 | 7 | 0
2000-04-02 | 1900-04-01 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 6.7 | 44.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 2743 | A | 7 | 1.5 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.08 | 1 | 0
2000-04-02 | 1900-04-01 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | B | 8 | 6 | B | 8 | 6.5 | 43.7 | B | 8 | 5.8 | 42.44 | B | 8 | 0.95 | A | 7 | 978 | B | 8 | 270 | B | 8 | 2.1 | B | 8 | -9900 | ? | 0 | 12372 | B | 8 | 1.4 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | -9900 | -9900 | ? | 0 | 41.74 | 1 | 0
2000-04-02 | 1900-04-01 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 6.1 | 42.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.97 | A | 7 | 977 | A | 7 | 250 | A | 7 | 1.5 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.68 | 1 | 0
2000-04-02 | 1900-04-01 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40 | 1 | 0
2000-04-02 | 1900-04-01 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 5 | 41 | A | 7 | 3.9 | 39.02 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 240 | A | 7 | 1.5 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.12 | 1 | 0
2000-04-02 | 1900-04-01 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 975 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.58 | 1 | 0
2000-04-02 | 1900-04-01 | 7:00 | 7 | 118 | 1310 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 977 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.9 | 1 | 0
2000-04-02 | 1900-04-01 | 8:00 | 8 | 385 | 1367 | 245 | 2 | 8 | 531 | 2 | 15 | 96 | 2 | 8 | 25600 | 2 | 8 | 45900 | 2 | 15 | 12600 | 2 | 8 | 1790 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.98 | 1 | 0
2000-04-02 | 1900-04-01 | 9:00 | 9 | 635 | 1367 | 445 | 2 | 8 | 725 | 2 | 15 | 107 | 2 | 8 | 46500 | 2 | 8 | 70700 | 2 | 15 | 13600 | 2 | 8 | 2210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 5.6 | 42.08 | A | 7 | 0.74 | A | 7 | 977 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.58 | 1 | 0
2000-04-02 | 1900-04-01 | 10:00 | 10 | 847 | 1367 | 608 | 2 | 8 | 768 | 2 | 15 | 131 | 2 | 8 | 64600 | 2 | 8 | 77800 | 2 | 15 | 16300 | 2 | 8 | 3240 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 12.2 | 53.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.59 | A | 7 | 977 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.52 | 1 | 0
2000-04-02 | 1900-04-01 | 11:00 | 11 | 1006 | 1367 | 720 | 2 | 8 | 726 | 2 | 15 | 185 | 2 | 8 | 76200 | 2 | 8 | 73700 | 2 | 15 | 21800 | 2 | 8 | 5570 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 13.3 | 55.94 | A | 7 | 5 | 41 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.2 | 1 | 0
2000-04-02 | 1900-04-01 | 12:00 | 12 | 1103 | 1367 | 808 | 2 | 8 | 771 | 2 | 15 | 185 | 2 | 8 | 86400 | 2 | 8 | 78900 | 2 | 15 | 22600 | 2 | 8 | 6820 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 15 | 59 | A | 7 | 5.6 | 42.08 | A | 7 | 0.53 | A | 7 | 975 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.58 | 1 | 0
2000-04-02 | 1900-04-01 | 13:00 | 13 | 1130 | 1367 | 852 | 2 | 8 | 822 | 2 | 15 | 171 | 2 | 8 | 88800 | 2 | 8 | 82500 | 2 | 15 | 20500 | 2 | 8 | 6050 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 15.6 | 60.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.51 | A | 7 | 976 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.28 | 1 | 0
2000-04-02 | 1900-04-01 | 14:00 | 14 | 1085 | 1367 | 806 | 2 | 8 | 789 | 2 | 15 | 178 | 2 | 8 | 86200 | 2 | 8 | 80800 | 2 | 15 | 21900 | 2 | 8 | 6310 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 16.7 | 62.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.48 | A | 7 | 975 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.78 | 1 | 0
2000-04-02 | 1900-04-01 | 15:00 | 15 | 972 | 1367 | 707 | 2 | 8 | 768 | 2 | 15 | 160 | 2 | 8 | 75300 | 2 | 8 | 78300 | 2 | 15 | 19500 | 2 | 8 | 4620 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 16.7 | 62.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.44 | A | 7 | 974 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.42 | 1 | 0
2000-04-02 | 1900-04-01 | 16:00 | 16 | 798 | 1367 | 562 | 2 | 8 | 685 | 2 | 15 | 162 | 2 | 8 | 58500 | 2 | 8 | 68200 | 2 | 15 | 18700 | 2 | 8 | 3670 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 16.1 | 60.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.44 | A | 7 | 974 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.32 | 1 | 0
2000-04-02 | 1900-04-01 | 17:00 | 17 | 575 | 1367 | 263 | 2 | 8 | 174 | 2 | 15 | 190 | 2 | 8 | 28500 | 2 | 8 | 17300 | 2 | 15 | 21200 | 2 | 8 | 4510 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 16.1 | 60.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.42 | A | 7 | 974 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.24 | 1 | 0
2000-04-02 | 1900-04-01 | 18:00 | 18 | 319 | 1367 | 173 | 2 | 8 | 373 | 2 | 15 | 85 | 2 | 8 | 17800 | 2 | 8 | 29900 | 2 | 15 | 10800 | 2 | 8 | 1580 | 2 | 19 | 7 | E | 9 | 7 | A | 7 | 15.6 | 60.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.44 | A | 7 | 972 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.54 | 1 | 0
2000-04-02 | 1900-04-01 | 19:00 | 19 | 64 | 969 | 12 | 2 | 8 | 95 | 2 | 15 | 9 | 2 | 8 | 1700 | 2 | 8 | 4800 | 2 | 15 | 1400 | 2 | 8 | 180 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 11.1 | 51.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.61 | A | 7 | 973 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.02 | 1 | 0
2000-04-02 | 1900-04-01 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 8.9 | 48.02 | A | 7 | 3.3 | 37.94 | A | 7 | 0.68 | A | 7 | 973 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.94 | 1 | 0
2000-04-02 | 1900-04-01 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 7 | E | 9 | 10.6 | 51.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.58 | A | 7 | 976 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.64 | 1 | 0
2000-04-02 | 1900-04-01 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 10 | 50 | A | 7 | 2.2 | 35.96 | A | 7 | 0.58 | A | 7 | 976 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 1.1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.76 | 1 | 0
2000-04-02 | 1900-04-01 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.66 | A | 7 | 977 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.1 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.74 | 1 | 0
2000-04-02 | 1900-04-01 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 1433 | A | 7 | 1.2 | E | 8 | 0.108 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.62 | 1 | 0
2000-04-03 | 1900-04-02 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.1 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.5 | 2 | 0
2000-04-03 | 1900-04-02 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.85 | A | 7 | 977 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.02 | 2 | 0
2000-04-03 | 1900-04-02 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 7 | E | 9 | 7.2 | 44.96 | A | 7 | 3.9 | 39.02 | A | 7 | 0.8 | A | 7 | 977 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.52 | 2 | 0
2000-04-03 | 1900-04-02 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 6.7 | 44.06 | A | 7 | 1.7 | 35.06 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 0.9 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.36 | 2 | 0
2000-04-03 | 1900-04-02 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 6.1 | 42.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 0.9 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.48 | 2 | 0
2000-04-03 | 1900-04-02 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 5.6 | 42.08 | A | 7 | 0 | 32 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 0.8 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.4 | 2 | 0
2000-04-03 | 1900-04-02 | 7:00 | 7 | 125 | 1355 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 0 | 32 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 0.7 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.9 | 2 | 0
2000-04-03 | 1900-04-02 | 8:00 | 8 | 392 | 1367 | 142 | 2 | 8 | 59 | 2 | 15 | 125 | 2 | 8 | 15500 | 2 | 8 | 5300 | 2 | 15 | 14000 | 2 | 8 | 3170 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 6.7 | 44.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 1097 | A | 7 | 0.7 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.08 | 2 | 0
2000-04-03 | 1900-04-02 | 9:00 | 9 | 641 | 1367 | 198 | 2 | 8 | 19 | 2 | 15 | 189 | 2 | 8 | 22400 | 2 | 8 | 1600 | 2 | 15 | 21700 | 2 | 8 | 7350 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 7.8 | 46.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 1067 | A | 7 | 0.6 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.68 | 2 | 0
2000-04-03 | 1900-04-02 | 10:00 | 10 | 852 | 1367 | 523 | 2 | 8 | 390 | 2 | 15 | 279 | 2 | 8 | 56100 | 2 | 8 | 41600 | 2 | 15 | 30100 | 2 | 8 | 7250 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 8.9 | 48.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.56 | A | 7 | 982 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 1036 | A | 7 | 0.6 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.08 | 2 | 0
2000-04-03 | 1900-04-02 | 11:00 | 11 | 1011 | 1367 | 726 | 2 | 8 | 611 | 2 | 15 | 273 | 2 | 8 | 77300 | 2 | 8 | 63500 | 2 | 15 | 30100 | 2 | 8 | 8410 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 10 | 50 | A | 7 | 0.6 | 33.08 | A | 7 | 0.52 | A | 7 | 982 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 0.5 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.58 | 2 | 0
2000-04-03 | 1900-04-02 | 12:00 | 12 | 1107 | 1367 | 269 | 2 | 8 | 30 | 2 | 15 | 245 | 2 | 8 | 29800 | 2 | 8 | 3000 | 2 | 15 | 27400 | 2 | 8 | 10510 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 10.6 | 51.08 | A | 7 | 0 | 32 | A | 7 | 0.48 | A | 7 | 980 | A | 7 | 330 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 1433 | A | 7 | 0.4 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.3 | 2 | 0
2000-04-03 | 1900-04-02 | 13:00 | 13 | 1134 | 1367 | 744 | 2 | 8 | 438 | 2 | 15 | 380 | 2 | 8 | 77900 | 2 | 8 | 45500 | 2 | 15 | 40000 | 2 | 8 | 15470 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 10.6 | 51.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.44 | A | 7 | 982 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 24.22 | 2 | 0
2000-04-03 | 1900-04-02 | 14:00 | 14 | 1089 | 1367 | 288 | 2 | 8 | 42 | 2 | 15 | 255 | 2 | 8 | 31900 | 2 | 8 | 4300 | 2 | 15 | 28500 | 2 | 8 | 10670 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 11.7 | 53.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.37 | A | 7 | 981 | A | 7 | 320 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 0.5 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.84 | 2 | 0
2000-04-03 | 1900-04-02 | 15:00 | 15 | 976 | 1367 | 730 | 2 | 8 | 595 | 2 | 15 | 304 | 2 | 8 | 76400 | 2 | 8 | 61600 | 2 | 15 | 32300 | 2 | 8 | 8940 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 11.7 | 53.06 | A | 7 | -3.3 | 26.06 | A | 7 | 0.34 | A | 7 | 981 | A | 7 | 310 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 1981 | A | 7 | 0.6 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.96 | 2 | 0
2000-04-03 | 1900-04-02 | 16:00 | 16 | 802 | 1367 | 474 | 2 | 8 | 378 | 2 | 15 | 251 | 2 | 8 | 50800 | 2 | 8 | 40100 | 2 | 15 | 27200 | 2 | 8 | 6200 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 11.1 | 51.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.32 | A | 7 | 981 | A | 7 | 330 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 0.6 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.18 | 2 | 0
2000-04-03 | 1900-04-02 | 17:00 | 17 | 579 | 1367 | 369 | 2 | 8 | 587 | 2 | 15 | 120 | 2 | 8 | 38000 | 2 | 8 | 55800 | 2 | 15 | 14300 | 2 | 8 | 2320 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 11.7 | 53.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.28 | A | 7 | 981 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.02 | 2 | 0
2000-04-03 | 1900-04-02 | 18:00 | 18 | 323 | 1367 | 183 | 2 | 8 | 528 | 2 | 15 | 57 | 2 | 8 | 18800 | 2 | 8 | 43100 | 2 | 15 | 8600 | 2 | 8 | 1050 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 10.6 | 51.08 | A | 7 | -7.2 | 19.04 | A | 7 | 0.26 | A | 7 | 980 | A | 7 | 320 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 13.54 | 2 | 0
2000-04-03 | 1900-04-02 | 19:00 | 19 | 67 | 991 | 15 | 2 | 8 | 140 | 2 | 15 | 9 | 2 | 8 | 2100 | 2 | 8 | 7100 | 2 | 15 | 1600 | 2 | 8 | 180 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 8.9 | 48.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.26 | A | 7 | 982 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 11.96 | 2 | 0
2000-04-03 | 1900-04-02 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 4 | E | 9 | 8.3 | 46.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.29 | A | 7 | 983 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 12.96 | 2 | 0
2000-04-03 | 1900-04-02 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 6.7 | 44.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.35 | A | 7 | 983 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 15.04 | 2 | 0
2000-04-03 | 1900-04-02 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.38 | A | 7 | 983 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 15.24 | 2 | 0
2000-04-03 | 1900-04-02 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | A | 7 | 4.4 | 39.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.41 | A | 7 | 983 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 15.44 | 2 | 0
2000-04-03 | 1900-04-02 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.47 | A | 7 | 983 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.109 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 17.62 | 2 | 0
2000-04-04 | 1900-04-03 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.2 | 35.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.53 | A | 7 | 984 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.12 | 3 | 0
2000-04-04 | 1900-04-03 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 1.7 | 35.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.32 | 3 | 0
2000-04-04 | 1900-04-03 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 0.6 | 33.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.6 | A | 7 | 984 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.72 | 3 | 0
2000-04-04 | 1900-04-03 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.82 | 3 | 0
2000-04-04 | 1900-04-03 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.66 | A | 7 | 984 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.22 | 3 | 0
2000-04-04 | 1900-04-03 | 6:00 | 6 | 0 | 11 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 1 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 1 | 0 | E | 9 | 0 | E | 9 | -1.7 | 28.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 985 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.62 | 3 | 0
2000-04-04 | 1900-04-03 | 7:00 | 7 | 132 | 1366 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 0 | 32 | A | 7 | -6.1 | 21.02 | A | 7 | 0.6 | A | 7 | 986 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 17.92 | 3 | 0
2000-04-04 | 1900-04-03 | 8:00 | 8 | 398 | 1366 | 250 | 2 | 8 | 522 | 2 | 15 | 98 | 2 | 8 | 26100 | 2 | 8 | 45700 | 2 | 15 | 12800 | 2 | 8 | 1830 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | -5 | 23 | A | 7 | 0.52 | A | 7 | 986 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19 | 3 | 0
2000-04-04 | 1900-04-03 | 9:00 | 9 | 647 | 1366 | 443 | 2 | 8 | 675 | 2 | 15 | 123 | 2 | 8 | 46100 | 2 | 8 | 65700 | 2 | 15 | 14900 | 2 | 8 | 2510 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.42 | A | 7 | 987 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 17.22 | 3 | 0
2000-04-04 | 1900-04-03 | 10:00 | 10 | 858 | 1366 | 607 | 2 | 8 | 725 | 2 | 15 | 150 | 2 | 8 | 64000 | 2 | 8 | 73100 | 2 | 15 | 17900 | 2 | 8 | 3710 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.33 | A | 7 | 987 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 14.14 | 3 | 0
2000-04-04 | 1900-04-03 | 11:00 | 11 | 1017 | 1366 | 751 | 2 | 8 | 774 | 2 | 15 | 173 | 2 | 8 | 79800 | 2 | 8 | 78900 | 2 | 15 | 20900 | 2 | 8 | 5360 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | -7.2 | 19.04 | A | 7 | 0.29 | A | 7 | 987 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 13.84 | 3 | 0
2000-04-04 | 1900-04-03 | 12:00 | 12 | 1112 | 1366 | 844 | 2 | 8 | 855 | 2 | 15 | 146 | 2 | 8 | 89300 | 2 | 8 | 86300 | 2 | 15 | 18800 | 2 | 8 | 5160 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.28 | A | 7 | 985 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 12.86 | 3 | 0
2000-04-04 | 1900-04-03 | 13:00 | 13 | 1138 | 1366 | 876 | 2 | 8 | 870 | 2 | 15 | 149 | 2 | 8 | 92800 | 2 | 8 | 87900 | 2 | 15 | 19300 | 2 | 8 | 5630 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.29 | A | 7 | 986 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.12 | 3 | 0
2000-04-04 | 1900-04-03 | 14:00 | 14 | 1093 | 1366 | 835 | 2 | 8 | 855 | 2 | 15 | 149 | 2 | 8 | 87900 | 2 | 8 | 86100 | 2 | 15 | 18800 | 2 | 8 | 4990 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.27 | A | 7 | 985 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 15.22 | 3 | 0
2000-04-04 | 1900-04-03 | 15:00 | 15 | 979 | 1366 | 736 | 2 | 8 | 845 | 2 | 15 | 128 | 2 | 8 | 77500 | 2 | 8 | 85000 | 2 | 15 | 16400 | 2 | 8 | 3530 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.27 | A | 7 | 984 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.02 | 3 | 0
2000-04-04 | 1900-04-03 | 16:00 | 16 | 805 | 1366 | 591 | 2 | 8 | 816 | 2 | 15 | 109 | 2 | 8 | 61700 | 2 | 8 | 81000 | 2 | 15 | 13800 | 2 | 8 | 2440 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | -5 | 23 | A | 7 | 0.26 | A | 7 | 983 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.7 | 3 | 0
2000-04-04 | 1900-04-03 | 17:00 | 17 | 583 | 1366 | 385 | 2 | 8 | 663 | 2 | 15 | 102 | 2 | 8 | 40200 | 2 | 8 | 63700 | 2 | 15 | 13000 | 2 | 8 | 2040 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | -5 | 23 | A | 7 | 0.27 | A | 7 | 983 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.8 | 3 | 0
2000-04-04 | 1900-04-03 | 18:00 | 18 | 328 | 1366 | 193 | 2 | 8 | 546 | 2 | 15 | 62 | 2 | 8 | 19800 | 2 | 8 | 44600 | 2 | 15 | 9100 | 2 | 8 | 1120 | 2 | 19 | 7 | E | 9 | 7 | A | 7 | 11.1 | 51.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.33 | A | 7 | 980 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.1 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.98 | 3 | 0
2000-04-04 | 1900-04-03 | 19:00 | 19 | 70 | 1013 | 16 | 2 | 8 | 136 | 2 | 15 | 10 | 2 | 8 | 2200 | 2 | 8 | 6900 | 2 | 15 | 1600 | 2 | 8 | 200 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.48 | A | 7 | 981 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 22.06 | 3 | 0
2000-04-04 | 1900-04-03 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 22.36 | 3 | 0
2000-04-04 | 1900-04-03 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.94 | 3 | 0
2000-04-04 | 1900-04-03 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 25.62 | 3 | 0
2000-04-04 | 1900-04-03 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | A | 7 | 7.2 | 44.96 | A | 7 | 0 | 32 | A | 7 | 0.6 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.6 | 3 | 0
2000-04-04 | 1900-04-03 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | A | 7 | 7.2 | 44.96 | A | 7 | 0 | 32 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.11 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.6 | 3 | 0
2000-04-05 | 1900-04-04 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 0 | 32 | A | 7 | 0.56 | A | 7 | 977 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.2 | 4 | 0
2000-04-05 | 1900-04-04 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 0 | 32 | A | 7 | 0.56 | A | 7 | 975 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.2 | 4 | 0
2000-04-05 | 1900-04-04 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.8 | 46.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.6 | A | 7 | 974 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.58 | 4 | 0
2000-04-05 | 1900-04-04 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 8.3 | 46.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | A | 7 | 972 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.28 | 4 | 0
2000-04-05 | 1900-04-04 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 8.9 | 48.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.61 | A | 7 | 971 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.36 | 4 | 0
2000-04-05 | 1900-04-04 | 6:00 | 6 | 0 | 57 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 2.2 | 35.96 | A | 7 | 0.58 | A | 7 | 969 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.76 | 4 | 0
2000-04-05 | 1900-04-04 | 7:00 | 7 | 138 | 1365 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 2 | E | 9 | 2 | E | 9 | 11.1 | 51.98 | A | 7 | 2.8 | 37.04 | A | 7 | 0.57 | A | 7 | 969 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.44 | 4 | 0
2000-04-05 | 1900-04-04 | 8:00 | 8 | 405 | 1365 | 233 | 2 | 8 | 416 | 2 | 15 | 109 | 2 | 8 | 24000 | 2 | 8 | 36500 | 2 | 15 | 13200 | 2 | 8 | 2060 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.52 | A | 7 | 969 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.54 | 4 | 0
2000-04-05 | 1900-04-04 | 9:00 | 9 | 653 | 1365 | 449 | 2 | 8 | 650 | 2 | 15 | 138 | 2 | 8 | 46400 | 2 | 8 | 63000 | 2 | 15 | 16200 | 2 | 8 | 2770 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 5 | 41 | A | 7 | 0.48 | A | 7 | 969 | A | 7 | 200 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.9 | 4 | 0
2000-04-05 | 1900-04-04 | 10:00 | 10 | 863 | 1365 | 613 | 2 | 8 | 731 | 2 | 15 | 149 | 2 | 8 | 64700 | 2 | 8 | 73800 | 2 | 15 | 17900 | 2 | 8 | 3710 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.43 | A | 7 | 968 | A | 7 | 200 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.08 | 4 | 0
2000-04-05 | 1900-04-04 | 11:00 | 11 | 1022 | 1365 | 757 | 2 | 8 | 804 | 2 | 15 | 153 | 2 | 8 | 78600 | 2 | 8 | 80500 | 2 | 15 | 18200 | 2 | 8 | 4310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.39 | A | 7 | 968 | A | 7 | 210 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.06 | 4 | 0
2000-04-05 | 1900-04-04 | 12:00 | 12 | 1117 | 1365 | 832 | 2 | 8 | 807 | 2 | 15 | 170 | 2 | 8 | 86600 | 2 | 8 | 80900 | 2 | 15 | 20300 | 2 | 8 | 5840 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.35 | A | 7 | 965 | A | 7 | 220 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.16 | 4 | 0
2000-04-05 | 1900-04-04 | 13:00 | 13 | 1142 | 1365 | 882 | 2 | 8 | 876 | 2 | 15 | 147 | 2 | 8 | 93600 | 2 | 8 | 88600 | 2 | 15 | 19300 | 2 | 8 | 5650 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 8.9 | 48.02 | A | 7 | 0.36 | A | 7 | 967 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.62 | 4 | 0
2000-04-05 | 1900-04-04 | 14:00 | 14 | 1097 | 1365 | 841 | 2 | 8 | 861 | 2 | 15 | 148 | 2 | 8 | 88700 | 2 | 8 | 86800 | 2 | 15 | 18800 | 2 | 8 | 5020 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.33 | A | 7 | 967 | A | 7 | 210 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.12 | 4 | 0
2000-04-05 | 1900-04-04 | 15:00 | 15 | 983 | 1365 | 731 | 2 | 8 | 810 | 2 | 15 | 146 | 2 | 8 | 76000 | 2 | 8 | 81000 | 2 | 15 | 17500 | 2 | 8 | 3870 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 27.8 | 82.04 | A | 7 | 9.4 | 48.92 | A | 7 | 0.32 | A | 7 | 966 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.62 | 4 | 0
2000-04-05 | 1900-04-04 | 16:00 | 16 | 809 | 1365 | 580 | 2 | 8 | 792 | 2 | 15 | 109 | 2 | 8 | 60500 | 2 | 8 | 78700 | 2 | 15 | 13800 | 2 | 8 | 2460 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 28.9 | 84.02 | A | 7 | 9.4 | 48.92 | A | 7 | 0.3 | A | 7 | 966 | A | 7 | 210 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.22 | 4 | 0
2000-04-05 | 1900-04-04 | 17:00 | 17 | 587 | 1365 | 385 | 2 | 8 | 651 | 2 | 15 | 105 | 2 | 8 | 40100 | 2 | 8 | 62500 | 2 | 15 | 13200 | 2 | 8 | 2100 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 28.9 | 84.02 | A | 7 | 10 | 50 | A | 7 | 0.31 | A | 7 | 966 | A | 7 | 210 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.2 | 4 | 0
2000-04-05 | 1900-04-04 | 18:00 | 18 | 332 | 1365 | 193 | 2 | 8 | 535 | 2 | 15 | 63 | 2 | 8 | 19800 | 2 | 8 | 43900 | 2 | 15 | 9100 | 2 | 8 | 1140 | 2 | 19 | 10 | E | 9 | 5 | A | 7 | 27.2 | 80.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.25 | A | 7 | 965 | A | 7 | 330 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.78 | 4 | 0
2000-04-05 | 1900-04-04 | 19:00 | 19 | 73 | 1035 | 17 | 2 | 8 | 120 | 2 | 15 | 11 | 2 | 8 | 2100 | 2 | 8 | 6200 | 2 | 15 | 1700 | 2 | 8 | 210 | 2 | 19 | 7 | E | 9 | 7 | E | 9 | 23.9 | 75.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.32 | A | 7 | 969 | A | 7 | 350 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.08 | 4 | 0
2000-04-05 | 1900-04-04 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 7 | E | 9 | 22.8 | 73.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.33 | A | 7 | 971 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.58 | 4 | 0
2000-04-05 | 1900-04-04 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 7 | E | 9 | 20 | 68 | A | 7 | -2.8 | 26.96 | A | 7 | 0.21 | A | 7 | 972 | A | 7 | 360 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1.4 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.36 | 4 | 0
2000-04-05 | 1900-04-04 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 2 | E | 9 | 18.3 | 64.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.22 | A | 7 | 974 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.76 | 4 | 0
2000-04-05 | 1900-04-04 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 16.1 | 60.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.24 | A | 7 | 974 | A | 7 | 360 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.08 | 4 | 0
2000-04-05 | 1900-04-04 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 8 | A | 7 | 14.4 | 57.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.31 | A | 7 | 973 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.111 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.24 | 4 | 0
2000-04-06 | 1900-04-05 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | E | 9 | 15 | 59 | A | 7 | -3.3 | 26.06 | A | 7 | 0.27 | A | 7 | 975 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.26 | 5 | 0
2000-04-06 | 1900-04-05 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 4 | E | 9 | 13.3 | 55.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.28 | A | 7 | 975 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 17.78 | 5 | 0
2000-04-06 | 1900-04-05 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 7 | E | 9 | 12.8 | 55.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.3 | A | 7 | 975 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.68 | 5 | 0
2000-04-06 | 1900-04-05 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 7 | E | 9 | 12.8 | 55.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.31 | A | 7 | 976 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.66 | 5 | 0
2000-04-06 | 1900-04-05 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | E | 9 | 10.6 | 51.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.38 | A | 7 | 976 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.06 | 5 | 0
2000-04-06 | 1900-04-05 | 6:00 | 6 | 0 | 80 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 7 | E | 9 | 5 | E | 9 | 10 | 50 | A | 7 | -2.8 | 26.96 | A | 7 | 0.39 | A | 7 | 976 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1.5 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.16 | 5 | 0
2000-04-06 | 1900-04-05 | 7:00 | 7 | 145 | 1364 | 51 | 2 | 8 | 0 | 2 | 15 | 51 | 2 | 8 | 5500 | 2 | 8 | 0 | 2 | 15 | 5500 | 2 | 8 | 1450 | 2 | 19 | 6 | E | 9 | 5 | E | 9 | 10.6 | 51.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.42 | A | 7 | 977 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1.5 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.04 | 5 | 0
2000-04-06 | 1900-04-05 | 8:00 | 8 | 411 | 1364 | 193 | 2 | 8 | 182 | 2 | 15 | 138 | 2 | 8 | 20800 | 2 | 8 | 16500 | 2 | 15 | 15800 | 2 | 8 | 3090 | 2 | 19 | 9 | E | 9 | 5 | E | 9 | 11.7 | 53.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.32 | A | 7 | 977 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1.5 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.88 | 5 | 0
2000-04-06 | 1900-04-05 | 9:00 | 9 | 659 | 1364 | 190 | 2 | 8 | 6 | 2 | 15 | 187 | 2 | 8 | 21600 | 2 | 8 | 500 | 2 | 15 | 21400 | 2 | 8 | 7430 | 2 | 19 | 10 | E | 9 | 4 | E | 9 | 11.7 | 53.06 | A | 7 | -3.3 | 26.06 | A | 7 | 0.34 | A | 7 | 976 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1.6 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.96 | 5 | 0
2000-04-06 | 1900-04-05 | 10:00 | 10 | 869 | 1364 | 206 | 2 | 8 | 6 | 2 | 15 | 202 | 2 | 8 | 24200 | 2 | 8 | 500 | 2 | 15 | 23900 | 2 | 8 | 9140 | 2 | 19 | 9 | E | 9 | 4 | E | 9 | 12.2 | 53.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.36 | A | 7 | 977 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1.6 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.74 | 5 | 0
2000-04-06 | 1900-04-05 | 11:00 | 11 | 1026 | 1364 | 575 | 2 | 8 | 260 | 2 | 15 | 379 | 2 | 8 | 62700 | 2 | 8 | 27500 | 2 | 15 | 41900 | 2 | 8 | 12450 | 2 | 19 | 10 | E | 9 | 5 | E | 9 | 13.9 | 57.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.29 | A | 7 | 978 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.6 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.46 | 5 | 0
2000-04-06 | 1900-04-05 | 12:00 | 12 | 1121 | 1364 | 648 | 2 | 8 | 313 | 2 | 15 | 390 | 2 | 8 | 70300 | 2 | 8 | 33900 | 2 | 15 | 42300 | 2 | 8 | 14820 | 2 | 19 | 7 | E | 9 | 4 | E | 9 | 14.4 | 57.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.28 | A | 7 | 975 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.6 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.36 | 5 | 0
2000-04-06 | 1900-04-05 | 13:00 | 13 | 1147 | 1364 | 486 | 2 | 8 | 108 | 2 | 15 | 395 | 2 | 8 | 53600 | 2 | 8 | 11100 | 2 | 15 | 44200 | 2 | 8 | 16720 | 2 | 19 | 7 | E | 9 | 5 | E | 9 | 16.1 | 60.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.29 | A | 7 | 976 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.6 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.74 | 5 | 0
2000-04-06 | 1900-04-05 | 14:00 | 14 | 1101 | 1364 | 683 | 2 | 8 | 413 | 2 | 15 | 349 | 2 | 8 | 74500 | 2 | 8 | 44800 | 2 | 15 | 38300 | 2 | 8 | 12560 | 2 | 19 | 6 | E | 9 | 3 | E | 9 | 16.7 | 62.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.31 | A | 7 | 975 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.6 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.42 | 5 | 0
2000-04-06 | 1900-04-05 | 15:00 | 15 | 987 | 1364 | 621 | 2 | 8 | 453 | 2 | 15 | 293 | 2 | 8 | 65400 | 2 | 8 | 46900 | 2 | 15 | 31400 | 2 | 8 | 8760 | 2 | 19 | 3 | E | 9 | 2 | E | 9 | 17.2 | 62.96 | A | 7 | 0 | 32 | A | 7 | 0.31 | A | 7 | 974 | A | 7 | 30 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.5 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 24.3 | 5 | 0
2000-04-06 | 1900-04-05 | 16:00 | 16 | 813 | 1364 | 552 | 2 | 8 | 609 | 2 | 15 | 189 | 2 | 8 | 59100 | 2 | 8 | 62400 | 2 | 15 | 21900 | 2 | 8 | 4410 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 17.2 | 62.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.3 | A | 7 | 974 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.5 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.32 | 5 | 0
2000-04-06 | 1900-04-05 | 17:00 | 17 | 591 | 1364 | 349 | 2 | 8 | 442 | 2 | 15 | 157 | 2 | 8 | 36400 | 2 | 8 | 43100 | 2 | 15 | 17700 | 2 | 8 | 3170 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 17.2 | 62.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.3 | A | 7 | 973 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.32 | 5 | 0
2000-04-06 | 1900-04-05 | 18:00 | 18 | 336 | 1364 | 166 | 2 | 8 | 348 | 2 | 15 | 81 | 2 | 8 | 17400 | 2 | 8 | 28600 | 2 | 15 | 10300 | 2 | 8 | 1490 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 16.7 | 62.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.29 | A | 7 | 971 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 22.52 | 5 | 0
2000-04-06 | 1900-04-05 | 19:00 | 19 | 77 | 1057 | 19 | 2 | 8 | 118 | 2 | 15 | 13 | 2 | 8 | 2300 | 2 | 8 | 6100 | 2 | 15 | 1900 | 2 | 8 | 250 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 14.4 | 57.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.35 | A | 7 | 972 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.92 | 5 | 0
2000-04-06 | 1900-04-05 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | -1.1 | 30.02 | A | 7 | 0.37 | A | 7 | 972 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.42 | 5 | 0
2000-04-06 | 1900-04-05 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 0 | 32 | A | 7 | 0.5 | A | 7 | 973 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.5 | 5 | 0
2000-04-06 | 1900-04-05 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.42 | A | 7 | 972 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 24.72 | 5 | 0
2000-04-06 | 1900-04-05 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | A | 7 | 11.1 | 51.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.42 | A | 7 | 971 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 24.02 | 5 | 0
2000-04-06 | 1900-04-05 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | A | 7 | 10.6 | 51.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.46 | A | 7 | 969 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 25.12 | 5 | 0
2000-04-07 | 1900-04-06 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 2 | E | 9 | 9.4 | 48.92 | A | 7 | 0 | 32 | A | 7 | 0.52 | A | 7 | 969 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.7 | 6 | 0
2000-04-07 | 1900-04-06 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 9.4 | 48.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.54 | A | 7 | 969 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 1981 | A | 7 | 1.2 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.88 | 6 | 0
2000-04-07 | 1900-04-06 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | E | 9 | 9.4 | 48.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.56 | A | 7 | 969 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.88 | 6 | 0
2000-04-07 | 1900-04-06 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 5 | E | 9 | 8.9 | 48.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.56 | A | 7 | 967 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.08 | 6 | 0
2000-04-07 | 1900-04-06 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 7 | E | 9 | 8.9 | 48.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.58 | A | 7 | 969 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.08 | 6 | 0
2000-04-07 | 1900-04-06 | 6:00 | 6 | 1 | 125 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 8.9 | 48.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.58 | A | 7 | 968 | A | 7 | 20 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.08 | 6 | 0
2000-04-07 | 1900-04-06 | 7:00 | 7 | 151 | 1363 | 80 | 2 | 8 | 178 | 2 | 15 | 60 | 2 | 8 | 8100 | 2 | 8 | 9100 | 2 | 15 | 7100 | 2 | 8 | 1230 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 9.4 | 48.92 | A | 7 | 1.7 | 35.06 | A | 7 | 0.59 | A | 7 | 970 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.06 | 6 | 0
2000-04-07 | 1900-04-06 | 8:00 | 8 | 418 | 1363 | 223 | 2 | 8 | 253 | 2 | 15 | 145 | 2 | 8 | 23200 | 2 | 8 | 22900 | 2 | 15 | 16200 | 2 | 8 | 3050 | 2 | 19 | 6 | E | 9 | 4 | E | 9 | 10.6 | 51.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.54 | A | 7 | 970 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.46 | 6 | 0
2000-04-07 | 1900-04-06 | 9:00 | 9 | 665 | 1363 | 203 | 2 | 8 | 19 | 2 | 15 | 194 | 2 | 8 | 23100 | 2 | 8 | 1600 | 2 | 15 | 22300 | 2 | 8 | 7660 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 12.2 | 53.96 | A | 7 | 2.2 | 35.96 | A | 7 | 0.5 | A | 7 | 969 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 4877 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.76 | 6 | 0
2000-04-07 | 1900-04-06 | 10:00 | 10 | 874 | 1363 | 219 | 2 | 8 | 12 | 2 | 15 | 211 | 2 | 8 | 25600 | 2 | 8 | 1000 | 2 | 15 | 25000 | 2 | 8 | 9490 | 2 | 19 | 7 | E | 9 | 7 | E | 9 | 13.3 | 55.94 | A | 7 | 3.3 | 37.94 | A | 7 | 0.51 | A | 7 | 971 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 4877 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.44 | 6 | 0
2000-04-07 | 1900-04-06 | 11:00 | 11 | 1031 | 1363 | 625 | 2 | 8 | 338 | 2 | 15 | 368 | 2 | 8 | 67200 | 2 | 8 | 36500 | 2 | 15 | 39600 | 2 | 8 | 11990 | 2 | 19 | 6 | E | 9 | 5 | E | 9 | 16.7 | 62.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.41 | A | 7 | 972 | A | 7 | 270 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.04 | 6 | 0
2000-04-07 | 1900-04-06 | 12:00 | 12 | 1126 | 1363 | 801 | 2 | 8 | 638 | 2 | 15 | 273 | 2 | 8 | 83500 | 2 | 8 | 64100 | 2 | 15 | 30400 | 2 | 8 | 10330 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 15 | 59 | A | 7 | 2.2 | 35.96 | A | 7 | 0.42 | A | 7 | 971 | A | 7 | 290 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.66 | 6 | 0
2000-04-07 | 1900-04-06 | 13:00 | 13 | 1151 | 1363 | 792 | 2 | 8 | 588 | 2 | 15 | 294 | 2 | 8 | 85300 | 2 | 8 | 61500 | 2 | 15 | 33300 | 2 | 8 | 12390 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 14.4 | 57.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.46 | A | 7 | 973 | A | 7 | 290 | A | 7 | 11.3 | A | 7 | 14400 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.04 | 6 | 0
2000-04-07 | 1900-04-06 | 14:00 | 14 | 1104 | 1363 | 653 | 2 | 8 | 335 | 2 | 15 | 381 | 2 | 8 | 70800 | 2 | 8 | 36300 | 2 | 15 | 41300 | 2 | 8 | 14000 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 12.8 | 55.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.52 | A | 7 | 975 | A | 7 | 300 | A | 7 | 15.5 | A | 7 | 12800 | A | 7 | 1433 | A | 7 | 1.3 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.54 | 6 | 0
2000-04-07 | 1900-04-06 | 15:00 | 15 | 990 | 1363 | 679 | 2 | 8 | 536 | 2 | 15 | 289 | 2 | 8 | 71600 | 2 | 8 | 55600 | 2 | 15 | 31200 | 2 | 8 | 8680 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 10.6 | 51.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.58 | A | 7 | 976 | A | 7 | 300 | A | 7 | 14.4 | A | 7 | 16000 | A | 7 | 1067 | A | 7 | 1.2 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.64 | 6 | 0
2000-04-07 | 1900-04-06 | 16:00 | 16 | 816 | 1363 | 357 | 2 | 8 | 136 | 2 | 15 | 275 | 2 | 8 | 38900 | 2 | 8 | 14200 | 2 | 15 | 30300 | 2 | 8 | 7430 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 7.8 | 46.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.6 | A | 7 | 978 | A | 7 | 310 | A | 7 | 15.5 | A | 7 | 16000 | A | 7 | 884 | A | 7 | 1.2 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.58 | 6 | 0
2000-04-07 | 1900-04-06 | 17:00 | 17 | 594 | 1363 | 201 | 2 | 8 | 29 | 2 | 15 | 188 | 2 | 8 | 22500 | 2 | 8 | 2400 | 2 | 15 | 21500 | 2 | 8 | 6990 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 4.4 | 39.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 330 | A | 7 | 12.4 | A | 7 | 16000 | A | 7 | 671 | A | 7 | 1.1 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.72 | 6 | 0
2000-04-07 | 1900-04-06 | 18:00 | 18 | 339 | 1363 | 70 | 2 | 8 | 0 | 2 | 15 | 70 | 2 | 8 | 8000 | 2 | 8 | 0 | 2 | 15 | 8000 | 2 | 8 | 2640 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.66 | A | 7 | 982 | A | 7 | 330 | A | 7 | 12.4 | A | 7 | 16000 | A | 7 | 732 | A | 7 | 1.1 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 25.54 | 6 | 0
2000-04-07 | 1900-04-06 | 19:00 | 19 | 80 | 1079 | 6 | 2 | 8 | 0 | 2 | 15 | 6 | 2 | 8 | 800 | 2 | 8 | 0 | 2 | 15 | 800 | 2 | 8 | 240 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.68 | A | 7 | 984 | A | 7 | 320 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 671 | A | 7 | 1 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 24.94 | 6 | 0
2000-04-07 | 1900-04-06 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.68 | A | 7 | 986 | A | 7 | 330 | A | 7 | 14.4 | A | 7 | 16000 | A | 7 | 792 | A | 7 | 1 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.96 | 6 | 0
2000-04-07 | 1900-04-06 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 1.7 | 35.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.61 | A | 7 | 987 | A | 7 | 330 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 884 | A | 7 | 0.9 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 20.68 | 6 | 0
2000-04-07 | 1900-04-06 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 0.6 | 33.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.57 | A | 7 | 988 | A | 7 | 330 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 17.62 | 6 | 0
2000-04-07 | 1900-04-06 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 988 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 18.82 | 6 | 0
2000-04-07 | 1900-04-06 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5 | 23 | A | 7 | 0.69 | A | 7 | 988 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.112 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 20.4 | 6 | 0
2000-04-08 | 1900-04-07 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.73 | A | 7 | 989 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.78 | 7 | 0
2000-04-08 | 1900-04-07 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.73 | A | 7 | 989 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.78 | 7 | 0
2000-04-08 | 1900-04-07 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | -1.1 | 30.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.76 | A | 7 | 990 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.98 | 7 | 0
2000-04-08 | 1900-04-07 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.76 | A | 7 | 991 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21 | 7 | 0
2000-04-08 | 1900-04-07 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 992 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.92 | 7 | 0
2000-04-08 | 1900-04-07 | 6:00 | 6 | 1 | 148 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 992 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.92 | 7 | 0
2000-04-08 | 1900-04-07 | 7:00 | 7 | 158 | 1362 | 90 | 2 | 8 | 234 | 2 | 15 | 63 | 2 | 8 | 9200 | 2 | 8 | 12300 | 2 | 15 | 7700 | 2 | 8 | 1290 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.66 | A | 7 | 993 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.22 | 7 | 0
2000-04-08 | 1900-04-07 | 8:00 | 8 | 424 | 1362 | 275 | 2 | 8 | 595 | 2 | 15 | 90 | 2 | 8 | 28100 | 2 | 8 | 52500 | 2 | 15 | 11800 | 2 | 8 | 1630 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 1.7 | 35.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.5 | A | 7 | 994 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.14 | 7 | 0
2000-04-08 | 1900-04-07 | 9:00 | 9 | 670 | 1362 | 460 | 2 | 8 | 679 | 2 | 15 | 125 | 2 | 8 | 47900 | 2 | 8 | 66500 | 2 | 15 | 15100 | 2 | 8 | 2600 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 3.9 | 39.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.37 | A | 7 | 995 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 12.76 | 7 | 0
2000-04-08 | 1900-04-07 | 10:00 | 10 | 879 | 1362 | 624 | 2 | 8 | 742 | 2 | 15 | 144 | 2 | 8 | 66200 | 2 | 8 | 75200 | 2 | 15 | 17500 | 2 | 8 | 3690 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.33 | A | 7 | 995 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 12.46 | 7 | 0
2000-04-08 | 1900-04-07 | 11:00 | 11 | 1036 | 1362 | 756 | 2 | 8 | 761 | 2 | 15 | 175 | 2 | 8 | 80500 | 2 | 8 | 77700 | 2 | 15 | 21200 | 2 | 8 | 5650 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.38 | A | 7 | 995 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.92 | 7 | 0
2000-04-08 | 1900-04-07 | 12:00 | 12 | 1130 | 1362 | 849 | 2 | 8 | 825 | 2 | 15 | 164 | 2 | 8 | 89000 | 2 | 8 | 83000 | 2 | 15 | 20100 | 2 | 8 | 5950 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.33 | A | 7 | 992 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.52 | 7 | 0
2000-04-08 | 1900-04-07 | 13:00 | 13 | 1155 | 1362 | 888 | 2 | 8 | 864 | 2 | 15 | 154 | 2 | 8 | 94000 | 2 | 8 | 87300 | 2 | 15 | 19800 | 2 | 8 | 6100 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | -5.6 | 21.92 | A | 7 | 0.31 | A | 7 | 993 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.32 | 7 | 0
2000-04-08 | 1900-04-07 | 14:00 | 14 | 1108 | 1362 | 836 | 2 | 8 | 819 | 2 | 15 | 167 | 2 | 8 | 87000 | 2 | 8 | 82200 | 2 | 15 | 20000 | 2 | 8 | 5660 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.3 | A | 7 | 993 | A | 7 | 270 | B | 8 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.22 | 7 | 0
2000-04-08 | 1900-04-07 | 15:00 | 15 | 994 | 1362 | 737 | 2 | 8 | 804 | 2 | 15 | 149 | 2 | 8 | 76600 | 2 | 8 | 80400 | 2 | 15 | 17800 | 2 | 8 | 4020 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.27 | A | 7 | 992 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 15.22 | 7 | 0
2000-04-08 | 1900-04-07 | 16:00 | 16 | 820 | 1362 | 597 | 2 | 8 | 804 | 2 | 15 | 112 | 2 | 8 | 62300 | 2 | 8 | 79900 | 2 | 15 | 14100 | 2 | 8 | 2540 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.3 | A | 7 | 991 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 17.98 | 7 | 0
2000-04-08 | 1900-04-07 | 17:00 | 17 | 598 | 1362 | 387 | 2 | 8 | 611 | 2 | 15 | 118 | 2 | 8 | 40000 | 2 | 8 | 58600 | 2 | 15 | 14200 | 2 | 8 | 2330 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.28 | A | 7 | 990 | A | 7 | 260 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.02 | 7 | 0
2000-04-08 | 1900-04-07 | 18:00 | 18 | 343 | 1362 | 200 | 2 | 8 | 532 | 2 | 15 | 66 | 2 | 8 | 20500 | 2 | 8 | 44200 | 2 | 15 | 9400 | 2 | 8 | 1200 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.28 | A | 7 | 987 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 15.32 | 7 | 0
2000-04-08 | 1900-04-07 | 19:00 | 19 | 83 | 1101 | 23 | 2 | 8 | 174 | 2 | 15 | 14 | 2 | 8 | 2900 | 2 | 8 | 9100 | 2 | 15 | 2200 | 2 | 8 | 270 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 9.4 | 48.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.31 | A | 7 | 989 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 15.62 | 7 | 0
2000-04-08 | 1900-04-07 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.36 | A | 7 | 988 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 16.02 | 7 | 0
2000-04-08 | 1900-04-07 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | -5 | 23 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19 | 7 | 0
2000-04-08 | 1900-04-07 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.57 | A | 7 | 987 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.18 | 7 | 0
2000-04-08 | 1900-04-07 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 986 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 20.38 | 7 | 0
2000-04-08 | 1900-04-07 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.45 | A | 7 | 985 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.113 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.28 | 7 | 0
2000-04-09 | 1900-04-08 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -3.3 | 26.06 | A | 7 | 0.47 | A | 7 | 985 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.16 | 1 | 0
2000-04-09 | 1900-04-08 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 22.06 | 1 | 0
2000-04-09 | 1900-04-08 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.54 | 1 | 0
2000-04-09 | 1900-04-08 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.52 | A | 7 | 984 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.34 | 1 | 0
2000-04-09 | 1900-04-08 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.54 | 1 | 0
2000-04-09 | 1900-04-08 | 6:00 | 6 | 2 | 193 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.56 | A | 7 | 983 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.74 | 1 | 0
2000-04-09 | 1900-04-08 | 7:00 | 7 | 164 | 1362 | 86 | 2 | 8 | 179 | 2 | 15 | 65 | 2 | 8 | 8800 | 2 | 8 | 9700 | 2 | 15 | 7700 | 2 | 8 | 1330 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.57 | A | 7 | 984 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 25.62 | 1 | 0
2000-04-09 | 1900-04-08 | 8:00 | 8 | 430 | 1362 | 282 | 2 | 8 | 593 | 2 | 15 | 94 | 2 | 8 | 28700 | 2 | 8 | 52400 | 2 | 15 | 12100 | 2 | 8 | 1700 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 9.4 | 48.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.49 | A | 7 | 984 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 25.52 | 1 | 0
2000-04-09 | 1900-04-08 | 9:00 | 9 | 676 | 1362 | 473 | 2 | 8 | 722 | 2 | 15 | 114 | 2 | 8 | 49700 | 2 | 8 | 71200 | 2 | 15 | 14300 | 2 | 8 | 2420 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 0 | 32 | A | 7 | 0.43 | A | 7 | 985 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 25.7 | 1 | 0
2000-04-09 | 1900-04-08 | 10:00 | 10 | 885 | 1362 | 617 | 2 | 8 | 688 | 2 | 15 | 170 | 2 | 8 | 64800 | 2 | 8 | 69300 | 2 | 15 | 19700 | 2 | 8 | 4290 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | -0.6 | 30.92 | A | 7 | 0.34 | A | 7 | 985 | A | 7 | 240 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 23.82 | 1 | 0
2000-04-09 | 1900-04-08 | 11:00 | 11 | 1041 | 1362 | 762 | 2 | 8 | 749 | 2 | 15 | 188 | 2 | 8 | 80800 | 2 | 8 | 76300 | 2 | 15 | 22400 | 2 | 8 | 6090 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.34 | A | 7 | 985 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.18 | 1 | 0
2000-04-09 | 1900-04-08 | 12:00 | 12 | 1134 | 1362 | 849 | 2 | 8 | 818 | 2 | 15 | 166 | 2 | 8 | 88900 | 2 | 8 | 82200 | 2 | 15 | 20200 | 2 | 8 | 6090 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.33 | A | 7 | 982 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.86 | 1 | 0
2000-04-09 | 1900-04-08 | 13:00 | 13 | 1158 | 1362 | 875 | 2 | 8 | 822 | 2 | 15 | 174 | 2 | 8 | 91400 | 2 | 8 | 82600 | 2 | 15 | 21000 | 2 | 8 | 6780 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 1.7 | 35.06 | A | 7 | 0.3 | A | 7 | 983 | A | 7 | 210 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.46 | 1 | 0
2000-04-09 | 1900-04-08 | 14:00 | 14 | 1112 | 1362 | 853 | 2 | 8 | 861 | 2 | 15 | 148 | 2 | 8 | 90100 | 2 | 8 | 86900 | 2 | 15 | 19000 | 2 | 8 | 5250 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.28 | A | 7 | 982 | A | 7 | 240 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.16 | 1 | 0
2000-04-09 | 1900-04-08 | 15:00 | 15 | 998 | 1362 | 748 | 2 | 8 | 804 | 2 | 15 | 158 | 2 | 8 | 77300 | 2 | 8 | 80200 | 2 | 15 | 18400 | 2 | 8 | 4200 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 2.2 | 35.96 | A | 7 | 0.29 | A | 7 | 981 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.96 | 1 | 0
2000-04-09 | 1900-04-08 | 16:00 | 16 | 823 | 1362 | 592 | 2 | 8 | 792 | 2 | 15 | 112 | 2 | 8 | 61800 | 2 | 8 | 78800 | 2 | 15 | 14100 | 2 | 8 | 2550 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 2.2 | 35.96 | A | 7 | 0.29 | A | 7 | 981 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.96 | 1 | 0
2000-04-09 | 1900-04-08 | 17:00 | 17 | 602 | 1362 | 408 | 2 | 8 | 716 | 2 | 15 | 91 | 2 | 8 | 43000 | 2 | 8 | 69600 | 2 | 15 | 12200 | 2 | 8 | 1880 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20.6 | 69.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.28 | A | 7 | 980 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.16 | 1 | 0
2000-04-09 | 1900-04-08 | 18:00 | 18 | 347 | 1362 | 205 | 2 | 8 | 550 | 2 | 15 | 65 | 2 | 8 | 21100 | 2 | 8 | 46000 | 2 | 15 | 9400 | 2 | 8 | 1190 | 2 | 19 | 10 | E | 9 | 3 | A | 7 | 18.3 | 64.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.33 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.86 | 1 | 0
2000-04-09 | 1900-04-08 | 19:00 | 19 | 86 | 1123 | 24 | 2 | 8 | 176 | 2 | 15 | 14 | 2 | 8 | 3000 | 2 | 8 | 9300 | 2 | 15 | 2200 | 2 | 8 | 270 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 1.7 | 35.06 | A | 7 | 0.41 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.86 | 1 | 0
2000-04-09 | 1900-04-08 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.48 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.88 | 1 | 0
2000-04-09 | 1900-04-08 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 1.7 | 35.06 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.76 | 1 | 0
2000-04-09 | 1900-04-08 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.46 | 1 | 0
2000-04-09 | 1900-04-08 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.08 | 1 | 0
2000-04-09 | 1900-04-08 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 3 | A | 7 | 8.3 | 46.94 | A | 7 | 0 | 32 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.114 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.2 | 1 | 0
2000-04-10 | 1900-04-09 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 0 | 32 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.2 | 2 | 0
2000-04-10 | 1900-04-09 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 8.3 | 46.94 | A | 7 | 0 | 32 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.2 | 2 | 0
2000-04-10 | 1900-04-09 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 3 | E | 9 | 8.9 | 48.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.08 | 2 | 0
2000-04-10 | 1900-04-09 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | E | 9 | 7.8 | 46.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.6 | A | 7 | 979 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.58 | 2 | 0
2000-04-10 | 1900-04-09 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 3 | E | 9 | 8.9 | 48.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.08 | 2 | 0
2000-04-10 | 1900-04-09 | 6:00 | 6 | 3 | 215 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 8.9 | 48.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.08 | 2 | 0
2000-04-10 | 1900-04-09 | 7:00 | 7 | 171 | 1361 | 96 | 2 | 8 | 225 | 2 | 15 | 68 | 2 | 8 | 9800 | 2 | 8 | 12600 | 2 | 15 | 8200 | 2 | 8 | 1400 | 2 | 19 | 7 | E | 9 | 4 | E | 9 | 10 | 50 | A | 7 | 1.1 | 33.98 | A | 7 | 0.54 | A | 7 | 979 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.58 | 2 | 0
2000-04-10 | 1900-04-09 | 8:00 | 8 | 436 | 1361 | 265 | 2 | 8 | 444 | 2 | 15 | 122 | 2 | 8 | 27300 | 2 | 8 | 40000 | 2 | 15 | 14400 | 2 | 8 | 2340 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 10.6 | 51.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.54 | A | 7 | 979 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.46 | 2 | 0
2000-04-10 | 1900-04-09 | 9:00 | 9 | 682 | 1361 | 452 | 2 | 8 | 617 | 2 | 15 | 142 | 2 | 8 | 46700 | 2 | 8 | 60200 | 2 | 15 | 16500 | 2 | 8 | 2920 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.49 | A | 7 | 979 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.44 | 2 | 0
2000-04-10 | 1900-04-09 | 10:00 | 10 | 890 | 1361 | 623 | 2 | 8 | 693 | 2 | 15 | 169 | 2 | 8 | 65400 | 2 | 8 | 69800 | 2 | 15 | 19700 | 2 | 8 | 4300 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 15.6 | 60.08 | A | 7 | 5 | 41 | A | 7 | 0.49 | A | 7 | 979 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.1 | 2 | 0
2000-04-10 | 1900-04-09 | 11:00 | 11 | 1045 | 1361 | 755 | 2 | 8 | 737 | 2 | 15 | 188 | 2 | 8 | 80200 | 2 | 8 | 75100 | 2 | 15 | 22400 | 2 | 8 | 6160 | 2 | 19 | 4 | E | 9 | 3 | E | 9 | 17.8 | 64.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.5 | A | 7 | 978 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.56 | 2 | 0
2000-04-10 | 1900-04-09 | 12:00 | 12 | 1138 | 1361 | 843 | 2 | 8 | 770 | 2 | 15 | 197 | 2 | 8 | 90000 | 2 | 8 | 78800 | 2 | 15 | 24000 | 2 | 8 | 8020 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 19.4 | 66.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.49 | A | 7 | 975 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.04 | 2 | 0
2000-04-10 | 1900-04-09 | 13:00 | 13 | 1162 | 1361 | 827 | 2 | 8 | 558 | 2 | 15 | 350 | 2 | 8 | 87800 | 2 | 8 | 58200 | 2 | 15 | 37900 | 2 | 8 | 15490 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 20.6 | 69.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.47 | A | 7 | 977 | A | 7 | 130 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.52 | 2 | 0
2000-04-10 | 1900-04-09 | 14:00 | 14 | 1115 | 1361 | 200 | 2 | 8 | 6 | 2 | 15 | 195 | 2 | 8 | 24400 | 2 | 8 | 500 | 2 | 15 | 24000 | 2 | 8 | 9780 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 19.4 | 66.92 | A | 7 | 10 | 50 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 1.3 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.4 | 2 | 0
2000-04-10 | 1900-04-09 | 15:00 | 15 | 1001 | 1361 | 121 | 2 | 8 | 0 | 2 | 15 | 121 | 2 | 8 | 15100 | 2 | 8 | 0 | 2 | 15 | 15100 | 2 | 8 | 6280 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 19.4 | 66.92 | A | 7 | 10 | 50 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 1.3 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.4 | 2 | 0
2000-04-10 | 1900-04-09 | 16:00 | 16 | 827 | 1361 | 128 | 2 | 8 | 0 | 2 | 15 | 128 | 2 | 8 | 15500 | 2 | 8 | 0 | 2 | 15 | 15500 | 2 | 8 | 6180 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 11.7 | 53.06 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1280 | A | 7 | 1.4 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.36 | 2 | 0
2000-04-10 | 1900-04-09 | 17:00 | 17 | 605 | 1361 | 117 | 2 | 8 | 0 | 2 | 15 | 117 | 2 | 8 | 13700 | 2 | 8 | 0 | 2 | 15 | 13700 | 2 | 8 | 5030 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.86 | A | 7 | 977 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 12800 | A | 7 | 1036 | A | 7 | 1.4 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 53.44 | 2 | 0
2000-04-10 | 1900-04-09 | 18:00 | 18 | 351 | 1361 | 66 | 2 | 8 | 0 | 2 | 15 | 66 | 2 | 8 | 7600 | 2 | 8 | 0 | 2 | 15 | 7600 | 2 | 8 | 2560 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 30 | A | 7 | 10.3 | A | 7 | 11200 | A | 7 | 975 | A | 7 | 1.5 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.22 | 2 | 0
2000-04-10 | 1900-04-09 | 19:00 | 19 | 90 | 1145 | 16 | 2 | 8 | 16 | 2 | 15 | 15 | 2 | 8 | 1900 | 2 | 8 | 800 | 2 | 15 | 1800 | 2 | 8 | 310 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10 | 50 | A | 7 | 6.1 | 42.98 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 30 | A | 7 | 8.2 | A | 7 | 11200 | A | 7 | 671 | A | 7 | 1.6 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.78 | 2 | 0
2000-04-10 | 1900-04-09 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.68 | A | 7 | 980 | A | 7 | 20 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 732 | A | 7 | 1.6 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.92 | 2 | 0
2000-04-10 | 1900-04-09 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 8.3 | 46.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 20 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 792 | A | 7 | 1.7 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.14 | 2 | 0
2000-04-10 | 1900-04-09 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 732 | A | 7 | 1.7 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.94 | 2 | 0
2000-04-10 | 1900-04-09 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 30 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 1.8 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.94 | 2 | 0
2000-04-10 | 1900-04-09 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 7 | A | 7 | 6.1 | 42.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 30 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.8 | E | 8 | 0.115 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.22 | 2 | 0
2000-04-11 | 1900-04-10 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | E | 9 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 983 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.54 | 3 | 0
2000-04-11 | 1900-04-10 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 3.9 | 39.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.93 | A | 7 | 983 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.14 | 3 | 0
2000-04-11 | 1900-04-10 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.9 | 39.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.14 | 3 | 0
2000-04-11 | 1900-04-10 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.9 | 39.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.14 | 3 | 0
2000-04-11 | 1900-04-10 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 3.3 | 37.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.97 | A | 7 | 985 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 244 | A | 7 | 1.3 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.64 | 3 | 0
2000-04-11 | 1900-04-10 | 6:00 | 6 | 4 | 261 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 3.9 | 39.02 | A | 7 | 3.3 | 37.94 | A | 7 | 0.96 | A | 7 | 985 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 122 | A | 7 | 1.2 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.44 | 3 | 0
2000-04-11 | 1900-04-10 | 7:00 | 7 | 177 | 1360 | 92 | 2 | 8 | 98 | 2 | 15 | 79 | 2 | 8 | 9700 | 2 | 8 | 6100 | 2 | 15 | 8900 | 2 | 8 | 1670 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 4.4 | 39.92 | A | 7 | 4.4 | 39.92 | A | 7 | 1 | A | 7 | 987 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 400 | A | 7 | 30 | A | 7 | 1 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.92 | 3 | 0
2000-04-11 | 1900-04-10 | 8:00 | 8 | 442 | 1360 | 136 | 2 | 8 | 13 | 2 | 15 | 132 | 2 | 8 | 15200 | 2 | 8 | 900 | 2 | 15 | 14900 | 2 | 8 | 4680 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 988 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 1600 | A | 7 | 91 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.9 | 3 | 0
2000-04-11 | 1900-04-10 | 9:00 | 9 | 687 | 1360 | 148 | 2 | 8 | 0 | 2 | 15 | 148 | 2 | 8 | 17300 | 2 | 8 | 0 | 2 | 15 | 17300 | 2 | 8 | 6420 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 989 | A | 7 | 350 | A | 7 | 7.2 | A | 7 | 4000 | A | 7 | 213 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.5 | 3 | 0
2000-04-11 | 1900-04-10 | 10:00 | 10 | 895 | 1360 | 122 | 2 | 8 | 0 | 2 | 15 | 122 | 2 | 8 | 14900 | 2 | 8 | 0 | 2 | 15 | 14900 | 2 | 8 | 6100 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6 | 42.8 | A | 7 | 4 | 39.2 | A | 7 | 0.87 | A | 7 | 990 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 180 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.5 | 3 | 0
2000-04-11 | 1900-04-10 | 11:00 | 11 | 1050 | 1360 | 125 | 2 | 8 | 0 | 2 | 15 | 125 | 2 | 8 | 15600 | 2 | 8 | 0 | 2 | 15 | 15600 | 2 | 8 | 6550 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 991 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 213 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.5 | 3 | 0
2000-04-11 | 1900-04-10 | 12:00 | 12 | 1142 | 1360 | 159 | 2 | 8 | 0 | 2 | 15 | 159 | 2 | 8 | 19800 | 2 | 8 | 0 | 2 | 15 | 19800 | 2 | 8 | 8230 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.8 | 46.04 | A | 7 | 5 | 41 | A | 7 | 0.82 | A | 7 | 990 | A | 7 | 10 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 335 | A | 7 | 0.5 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.6 | 3 | 0
2000-04-11 | 1900-04-10 | 13:00 | 13 | 1166 | 1360 | 150 | 2 | 8 | 0 | 2 | 15 | 150 | 2 | 8 | 18800 | 2 | 8 | 0 | 2 | 15 | 18800 | 2 | 8 | 7840 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 5 | 41 | A | 7 | 0.74 | A | 7 | 991 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 732 | A | 7 | 0.5 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.5 | 3 | 0
2000-04-11 | 1900-04-10 | 14:00 | 14 | 1119 | 1360 | 177 | 2 | 8 | 6 | 2 | 15 | 172 | 2 | 8 | 21800 | 2 | 8 | 400 | 2 | 15 | 21500 | 2 | 8 | 8790 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10 | 50 | A | 7 | 3.9 | 39.02 | A | 7 | 0.66 | A | 7 | 992 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 1036 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.72 | 3 | 0
2000-04-11 | 1900-04-10 | 15:00 | 15 | 1004 | 1360 | 438 | 2 | 8 | 125 | 2 | 15 | 345 | 2 | 8 | 47900 | 2 | 8 | 13300 | 2 | 15 | 38100 | 2 | 8 | 11070 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10.6 | 51.08 | A | 7 | 3.9 | 39.02 | A | 7 | 0.63 | A | 7 | 992 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 14400 | A | 7 | 1189 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.32 | 3 | 0
2000-04-11 | 1900-04-10 | 16:00 | 16 | 830 | 1360 | 229 | 2 | 8 | 18 | 2 | 15 | 218 | 2 | 8 | 26600 | 2 | 8 | 1500 | 2 | 15 | 25600 | 2 | 8 | 9470 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 11.1 | 51.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.59 | A | 7 | 992 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1280 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.84 | 3 | 0
2000-04-11 | 1900-04-10 | 17:00 | 17 | 609 | 1360 | 388 | 2 | 8 | 489 | 2 | 15 | 168 | 2 | 8 | 40300 | 2 | 8 | 48000 | 2 | 15 | 18800 | 2 | 8 | 3440 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 12.2 | 53.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.54 | A | 7 | 992 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.84 | 3 | 0
2000-04-11 | 1900-04-10 | 18:00 | 18 | 355 | 1360 | 188 | 2 | 8 | 429 | 2 | 15 | 76 | 2 | 8 | 19900 | 2 | 8 | 36100 | 2 | 15 | 10400 | 2 | 8 | 1390 | 2 | 19 | 8 | E | 9 | 8 | A | 7 | 10 | 50 | A | 7 | 3.3 | 37.94 | A | 7 | 0.63 | A | 7 | 990 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.34 | 3 | 0
2000-04-11 | 1900-04-10 | 19:00 | 19 | 93 | 1167 | 28 | 2 | 8 | 140 | 2 | 15 | 19 | 2 | 8 | 3300 | 2 | 8 | 6500 | 2 | 15 | 2800 | 2 | 8 | 330 | 2 | 19 | 4 | E | 9 | 2 | E | 9 | 7.8 | 46.04 | A | 7 | 2.2 | 35.96 | A | 7 | 0.68 | A | 7 | 992 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.16 | 3 | 0
2000-04-11 | 1900-04-10 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 3 | E | 9 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 993 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.76 | 3 | 0
2000-04-11 | 1900-04-10 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 2 | E | 9 | 5.6 | 42.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.73 | A | 7 | 994 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.78 | 3 | 0
2000-04-11 | 1900-04-10 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 2 | E | 9 | 4.4 | 39.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.76 | A | 7 | 994 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.38 | 3 | 0
2000-04-11 | 1900-04-10 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 3.9 | 39.02 | A | 7 | 0 | 32 | A | 7 | 0.76 | A | 7 | 993 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.4 | 3 | 0
2000-04-11 | 1900-04-10 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.78 | A | 7 | 993 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.62 | 3 | 0
2000-04-12 | 1900-04-11 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.2 | 35.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.81 | A | 7 | 994 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.92 | 4 | 0
2000-04-12 | 1900-04-11 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 1.7 | 35.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.81 | A | 7 | 994 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.12 | 4 | 0
2000-04-12 | 1900-04-11 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 2.2 | 35.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.78 | A | 7 | 994 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.72 | 4 | 0
2000-04-12 | 1900-04-11 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.74 | A | 7 | 995 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.34 | 4 | 0
2000-04-12 | 1900-04-11 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.74 | A | 7 | 995 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.34 | 4 | 0
2000-04-12 | 1900-04-11 | 6:00 | 6 | 5 | 283 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.87 | A | 7 | 995 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.64 | 4 | 0
2000-04-12 | 1900-04-11 | 7:00 | 7 | 184 | 1359 | 102 | 2 | 8 | 250 | 2 | 15 | 68 | 2 | 8 | 10400 | 2 | 8 | 14700 | 2 | 15 | 8400 | 2 | 8 | 1380 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 2.8 | 37.04 | A | 7 | -1.1 | 30.02 | A | 7 | 0.75 | A | 7 | 996 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.42 | 4 | 0
2000-04-12 | 1900-04-11 | 8:00 | 8 | 448 | 1359 | 293 | 2 | 8 | 596 | 2 | 15 | 96 | 2 | 8 | 29900 | 2 | 8 | 53400 | 2 | 15 | 12300 | 2 | 8 | 1750 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 5 | 41 | A | 7 | -1.1 | 30.02 | A | 7 | 0.64 | A | 7 | 996 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.32 | 4 | 0
2000-04-12 | 1900-04-11 | 9:00 | 9 | 693 | 1359 | 478 | 2 | 8 | 684 | 2 | 15 | 128 | 2 | 8 | 49800 | 2 | 8 | 67400 | 2 | 15 | 15400 | 2 | 8 | 2720 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.52 | A | 7 | 996 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 24.14 | 4 | 0
2000-04-12 | 1900-04-11 | 10:00 | 10 | 900 | 1359 | 642 | 2 | 8 | 730 | 2 | 15 | 158 | 2 | 8 | 67900 | 2 | 8 | 73900 | 2 | 15 | 18800 | 2 | 8 | 4120 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.46 | A | 7 | 996 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 22.74 | 4 | 0
2000-04-12 | 1900-04-11 | 11:00 | 11 | 1054 | 1359 | 780 | 2 | 8 | 791 | 2 | 15 | 164 | 2 | 8 | 80800 | 2 | 8 | 79100 | 2 | 15 | 19300 | 2 | 8 | 4900 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | -3.3 | 26.06 | A | 7 | 0.38 | A | 7 | 995 | A | 7 | 120 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 20.36 | 4 | 0
2000-04-12 | 1900-04-11 | 12:00 | 12 | 1146 | 1359 | 867 | 2 | 8 | 836 | 2 | 15 | 160 | 2 | 8 | 91300 | 2 | 8 | 84300 | 2 | 15 | 20000 | 2 | 8 | 6180 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.38 | A | 7 | 992 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 21.06 | 4 | 0
2000-04-12 | 1900-04-11 | 13:00 | 13 | 1170 | 1359 | 899 | 2 | 8 | 858 | 2 | 15 | 159 | 2 | 8 | 95000 | 2 | 8 | 86600 | 2 | 15 | 20300 | 2 | 8 | 6610 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.33 | A | 7 | 993 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 20.56 | 4 | 0
2000-04-12 | 1900-04-11 | 14:00 | 14 | 1122 | 1359 | 865 | 2 | 8 | 867 | 2 | 15 | 147 | 2 | 8 | 91600 | 2 | 8 | 87600 | 2 | 15 | 19100 | 2 | 8 | 5410 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.3 | A | 7 | 993 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.56 | 4 | 0
2000-04-12 | 1900-04-11 | 15:00 | 15 | 1008 | 1359 | 766 | 2 | 8 | 864 | 2 | 15 | 124 | 2 | 8 | 81400 | 2 | 8 | 87300 | 2 | 15 | 16500 | 2 | 8 | 3670 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 14.4 | 57.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.3 | A | 7 | 991 | A | 7 | 140 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 20.26 | 4 | 0
2000-04-12 | 1900-04-11 | 16:00 | 16 | 834 | 1359 | 609 | 2 | 8 | 804 | 2 | 15 | 115 | 2 | 8 | 63600 | 2 | 8 | 80000 | 2 | 15 | 14400 | 2 | 8 | 2630 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | -2.8 | 26.96 | A | 7 | 0.28 | A | 7 | 990 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 20.06 | 4 | 0
2000-04-12 | 1900-04-11 | 17:00 | 17 | 612 | 1359 | 415 | 2 | 8 | 705 | 2 | 15 | 96 | 2 | 8 | 43600 | 2 | 8 | 68700 | 2 | 15 | 12600 | 2 | 8 | 1990 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 14.4 | 57.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.28 | A | 7 | 990 | A | 7 | 130 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 19.36 | 4 | 0
2000-04-12 | 1900-04-11 | 18:00 | 18 | 359 | 1359 | 212 | 2 | 8 | 541 | 2 | 15 | 69 | 2 | 8 | 21800 | 2 | 8 | 45700 | 2 | 15 | 9700 | 2 | 8 | 1260 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.3 | A | 7 | 987 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 20.26 | 4 | 0
2000-04-12 | 1900-04-11 | 19:00 | 19 | 97 | 1189 | 29 | 2 | 8 | 188 | 2 | 15 | 16 | 2 | 8 | 3400 | 2 | 8 | 10100 | 2 | 15 | 2500 | 2 | 8 | 300 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.4 | A | 7 | 989 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 22.14 | 4 | 0
2000-04-12 | 1900-04-11 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.45 | A | 7 | 988 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 22.64 | 4 | 0
2000-04-12 | 1900-04-11 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 24.14 | 4 | 0
2000-04-12 | 1900-04-11 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 24.14 | 4 | 0
2000-04-12 | 1900-04-11 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.59 | A | 7 | 987 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 25.82 | 4 | 0
2000-04-12 | 1900-04-11 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 4.4 | 39.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.67 | A | 7 | 986 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.116 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.62 | 4 | 0
2000-04-13 | 1900-04-12 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.9 | 39.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 26.82 | 5 | 0
2000-04-13 | 1900-04-12 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.75 | A | 7 | 986 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.32 | 5 | 0
2000-04-13 | 1900-04-12 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 986 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.1 | 5 | 0
2000-04-13 | 1900-04-12 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 986 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.1 | 5 | 0
2000-04-13 | 1900-04-12 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.2 | 35.96 | A | 7 | 0 | 32 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.4 | 5 | 0
2000-04-13 | 1900-04-12 | 6:00 | 6 | 7 | 328 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 2.8 | 37.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.38 | 5 | 0
2000-04-13 | 1900-04-12 | 7:00 | 7 | 190 | 1359 | 110 | 2 | 8 | 294 | 2 | 15 | 69 | 2 | 8 | 10900 | 2 | 8 | 18100 | 2 | 15 | 8400 | 2 | 8 | 1320 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | 2.8 | 37.04 | A | 7 | 0.76 | A | 7 | 986 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.14 | 5 | 0
2000-04-13 | 1900-04-12 | 8:00 | 8 | 454 | 1359 | 299 | 2 | 8 | 615 | 2 | 15 | 93 | 2 | 8 | 30700 | 2 | 8 | 55500 | 2 | 15 | 12100 | 2 | 8 | 1720 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 2.8 | 37.04 | A | 7 | 0.61 | A | 7 | 986 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.24 | 5 | 0
2000-04-13 | 1900-04-12 | 9:00 | 9 | 698 | 1359 | 491 | 2 | 8 | 696 | 2 | 15 | 132 | 2 | 8 | 51100 | 2 | 8 | 68500 | 2 | 15 | 15800 | 2 | 8 | 2800 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.52 | A | 7 | 986 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.54 | 5 | 0
2000-04-13 | 1900-04-12 | 10:00 | 10 | 904 | 1359 | 635 | 2 | 8 | 693 | 2 | 15 | 172 | 2 | 8 | 66700 | 2 | 8 | 69900 | 2 | 15 | 20000 | 2 | 8 | 4470 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 4.4 | 39.92 | A | 7 | 0.49 | A | 7 | 986 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.12 | 5 | 0
2000-04-13 | 1900-04-12 | 11:00 | 11 | 1059 | 1359 | 779 | 2 | 8 | 755 | 2 | 15 | 190 | 2 | 8 | 82800 | 2 | 8 | 77000 | 2 | 15 | 22700 | 2 | 8 | 6420 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.43 | A | 7 | 985 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.32 | 5 | 0
2000-04-13 | 1900-04-12 | 12:00 | 12 | 1150 | 1359 | 873 | 2 | 8 | 842 | 2 | 15 | 158 | 2 | 8 | 92100 | 2 | 8 | 84900 | 2 | 15 | 20000 | 2 | 8 | 6210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 5 | 41 | A | 7 | 0.41 | A | 7 | 982 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.9 | 5 | 0
2000-04-13 | 1900-04-12 | 13:00 | 13 | 1173 | 1359 | 899 | 2 | 8 | 852 | 2 | 15 | 162 | 2 | 8 | 94900 | 2 | 8 | 85900 | 2 | 15 | 20500 | 2 | 8 | 6810 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 5.6 | 42.08 | A | 7 | 0.39 | A | 7 | 983 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.48 | 5 | 0
2000-04-13 | 1900-04-12 | 14:00 | 14 | 1126 | 1359 | 859 | 2 | 8 | 843 | 2 | 15 | 159 | 2 | 8 | 90300 | 2 | 8 | 84900 | 2 | 15 | 19800 | 2 | 8 | 5800 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 21.1 | 69.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.38 | A | 7 | 983 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.08 | 5 | 0
2000-04-13 | 1900-04-12 | 15:00 | 15 | 1011 | 1359 | 743 | 2 | 8 | 756 | 2 | 15 | 179 | 2 | 8 | 78800 | 2 | 8 | 77000 | 2 | 15 | 21400 | 2 | 8 | 5530 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 21.1 | 69.98 | A | 7 | 7.2 | 44.96 | A | 7 | 0.41 | A | 7 | 982 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.06 | 5 | 0
2000-04-13 | 1900-04-12 | 16:00 | 16 | 837 | 1359 | 598 | 2 | 8 | 769 | 2 | 15 | 123 | 2 | 8 | 61900 | 2 | 8 | 76300 | 2 | 15 | 14800 | 2 | 8 | 2750 | 2 | 19 | 1 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.41 | A | 7 | 981 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.7 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.94 | 5 | 0
2000-04-13 | 1900-04-12 | 17:00 | 17 | 616 | 1359 | 415 | 2 | 8 | 694 | 2 | 15 | 100 | 2 | 8 | 43600 | 2 | 8 | 67600 | 2 | 15 | 12900 | 2 | 8 | 2060 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 8.9 | 48.02 | A | 7 | 0.46 | A | 7 | 981 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.42 | 5 | 0
2000-04-13 | 1900-04-12 | 18:00 | 18 | 363 | 1359 | 208 | 2 | 8 | 513 | 2 | 15 | 71 | 2 | 8 | 21300 | 2 | 8 | 43400 | 2 | 15 | 9700 | 2 | 8 | 1290 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 19.4 | 66.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.04 | 5 | 0
2000-04-13 | 1900-04-12 | 19:00 | 19 | 100 | 1211 | 33 | 2 | 8 | 208 | 2 | 15 | 18 | 2 | 8 | 3800 | 2 | 8 | 11200 | 2 | 15 | 2800 | 2 | 8 | 340 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 8.3 | 46.94 | A | 7 | 0.54 | A | 7 | 980 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.84 | 5 | 0
2000-04-13 | 1900-04-12 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15.6 | 60.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.14 | 5 | 0
2000-04-13 | 1900-04-12 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15.6 | 60.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.64 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.42 | 5 | 0
2000-04-13 | 1900-04-12 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.9 | 57.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.72 | 5 | 0
2000-04-13 | 1900-04-12 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.42 | 5 | 0
2000-04-13 | 1900-04-12 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.117 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.34 | 5 | 0
2000-04-14 | 1900-04-13 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 8.9 | 48.02 | A | 7 | 0.8 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.92 | 6 | 0
2000-04-14 | 1900-04-13 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 8.9 | 48.02 | A | 7 | 0.8 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.92 | 6 | 0
2000-04-14 | 1900-04-13 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 8.9 | 48.02 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.82 | 6 | 0
2000-04-14 | 1900-04-13 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.89 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.22 | 6 | 0
2000-04-14 | 1900-04-13 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.89 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.22 | 6 | 0
2000-04-14 | 1900-04-13 | 6:00 | 6 | 8 | 351 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.89 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.22 | 6 | 0
2000-04-14 | 1900-04-13 | 7:00 | 7 | 196 | 1358 | 95 | 2 | 8 | 173 | 2 | 15 | 70 | 2 | 8 | 9800 | 2 | 8 | 10600 | 2 | 15 | 8200 | 2 | 8 | 1410 | 2 | 19 | 0 | B | 8 | 0 | B | 8 | 12.8 | 55.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.78 | 6 | 0
2000-04-14 | 1900-04-13 | 8:00 | 8 | 460 | 1358 | 298 | 2 | 8 | 569 | 2 | 15 | 105 | 2 | 8 | 30300 | 2 | 8 | 51100 | 2 | 15 | 13000 | 2 | 8 | 1900 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 10.6 | 51.08 | A | 7 | 0.75 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.98 | 6 | 0
2000-04-14 | 1900-04-13 | 9:00 | 9 | 703 | 1358 | 490 | 2 | 8 | 677 | 2 | 15 | 138 | 2 | 8 | 50900 | 2 | 8 | 66600 | 2 | 15 | 16300 | 2 | 8 | 2920 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.38 | 6 | 0
2000-04-14 | 1900-04-13 | 10:00 | 10 | 909 | 1358 | 641 | 2 | 8 | 705 | 2 | 15 | 168 | 2 | 8 | 67500 | 2 | 8 | 71300 | 2 | 15 | 19700 | 2 | 8 | 4420 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.9 | 66.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.38 | 6 | 0
2000-04-14 | 1900-04-13 | 11:00 | 11 | 1063 | 1358 | 798 | 2 | 8 | 797 | 2 | 15 | 172 | 2 | 8 | 82400 | 2 | 8 | 79600 | 2 | 15 | 19900 | 2 | 8 | 5180 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.16 | 6 | 0
2000-04-14 | 1900-04-13 | 12:00 | 12 | 1154 | 1358 | 873 | 2 | 8 | 812 | 2 | 15 | 181 | 2 | 8 | 90800 | 2 | 8 | 81400 | 2 | 15 | 21500 | 2 | 8 | 6960 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 22.8 | 73.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.48 | A | 7 | 975 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.98 | 6 | 0
2000-04-14 | 1900-04-13 | 13:00 | 13 | 1177 | 1358 | 839 | 2 | 8 | 636 | 2 | 15 | 287 | 2 | 8 | 87700 | 2 | 8 | 63900 | 2 | 15 | 32100 | 2 | 8 | 12760 | 2 | 19 | 3 | E | 9 | 1 | E | 9 | 23.3 | 73.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.46 | A | 7 | 976 | A | 7 | 170 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.58 | 6 | 0
2000-04-14 | 1900-04-13 | 14:00 | 14 | 1129 | 1358 | 812 | 2 | 8 | 670 | 2 | 15 | 254 | 2 | 8 | 85200 | 2 | 8 | 67600 | 2 | 15 | 28800 | 2 | 8 | 9900 | 2 | 19 | 2 | E | 9 | 1 | E | 9 | 23.9 | 75.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.45 | A | 7 | 976 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.38 | 6 | 0
2000-04-14 | 1900-04-13 | 15:00 | 15 | 1014 | 1358 | 749 | 2 | 8 | 786 | 2 | 15 | 160 | 2 | 8 | 77400 | 2 | 8 | 78500 | 2 | 15 | 18700 | 2 | 8 | 4410 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.42 | A | 7 | 975 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.08 | 6 | 0
2000-04-14 | 1900-04-13 | 16:00 | 16 | 840 | 1358 | 610 | 2 | 8 | 805 | 2 | 15 | 111 | 2 | 8 | 64000 | 2 | 8 | 80300 | 2 | 15 | 14200 | 2 | 8 | 2610 | 2 | 19 | 1 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 10 | 50 | A | 7 | 0.4 | A | 7 | 974 | A | 7 | 180 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.9 | 6 | 0
2000-04-14 | 1900-04-13 | 17:00 | 17 | 619 | 1358 | 426 | 2 | 8 | 735 | 2 | 15 | 90 | 2 | 8 | 45100 | 2 | 8 | 72000 | 2 | 15 | 12200 | 2 | 8 | 1890 | 2 | 19 | 3 | E | 9 | 2 | E | 9 | 23.9 | 75.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.43 | A | 7 | 974 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.28 | 6 | 0
2000-04-14 | 1900-04-13 | 18:00 | 18 | 366 | 1358 | 209 | 2 | 8 | 497 | 2 | 15 | 74 | 2 | 8 | 21300 | 2 | 8 | 42100 | 2 | 15 | 9900 | 2 | 8 | 1340 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 22.8 | 73.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.46 | A | 7 | 971 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.88 | 6 | 0
2000-04-14 | 1900-04-13 | 19:00 | 19 | 104 | 1233 | 34 | 2 | 8 | 202 | 2 | 15 | 19 | 2 | 8 | 3800 | 2 | 8 | 10900 | 2 | 15 | 2900 | 2 | 8 | 350 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20.6 | 69.08 | A | 7 | 10 | 50 | A | 7 | 0.51 | A | 7 | 973 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.9 | 6 | 0
2000-04-14 | 1900-04-13 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 10 | 50 | A | 7 | 0.53 | A | 7 | 973 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.2 | 6 | 0
2000-04-14 | 1900-04-13 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 10 | 50 | A | 7 | 0.6 | A | 7 | 974 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.5 | 6 | 0
2000-04-14 | 1900-04-13 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 974 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.08 | 6 | 0
2000-04-14 | 1900-04-13 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 3 | A | 7 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 973 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.96 | 6 | 0
2000-04-14 | 1900-04-13 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 11.1 | 51.98 | A | 7 | 0.77 | A | 7 | 973 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.118 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.18 | 6 | 0
2000-04-15 | 1900-04-14 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.48 | 7 | 0
2000-04-15 | 1900-04-14 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.86 | A | 7 | 974 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.78 | 7 | 0
2000-04-15 | 1900-04-14 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.86 | 7 | 0
2000-04-15 | 1900-04-14 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 12.2 | 53.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 518 | A | 7 | 2.1 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.48 | 7 | 0
2000-04-15 | 1900-04-14 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 14400 | A | 7 | 518 | A | 7 | 2.1 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.48 | 7 | 0
2000-04-15 | 1900-04-14 | 6:00 | 6 | 10 | 396 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 518 | A | 7 | 2.1 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.48 | 7 | 0
2000-04-15 | 1900-04-14 | 7:00 | 7 | 202 | 1357 | 93 | 2 | 8 | 147 | 2 | 15 | 71 | 2 | 8 | 9600 | 2 | 8 | 9200 | 2 | 15 | 8200 | 2 | 8 | 1420 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 13.9 | 57.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.8 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 12800 | A | 7 | 6096 | A | 7 | 2.2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.78 | 7 | 0
2000-04-15 | 1900-04-14 | 8:00 | 8 | 465 | 1357 | 208 | 2 | 8 | 140 | 2 | 15 | 159 | 2 | 8 | 22300 | 2 | 8 | 13200 | 2 | 15 | 17800 | 2 | 8 | 3620 | 2 | 19 | 6 | E | 9 | 5 | E | 9 | 15.6 | 60.08 | A | 7 | 11.1 | 51.98 | A | 7 | 0.75 | A | 7 | 976 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 14400 | A | 7 | 6096 | A | 7 | 2.2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.78 | 7 | 0
2000-04-15 | 1900-04-14 | 9:00 | 9 | 709 | 1357 | 255 | 2 | 8 | 49 | 2 | 15 | 229 | 2 | 8 | 28000 | 2 | 8 | 4900 | 2 | 15 | 25400 | 2 | 8 | 6930 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 16.7 | 62.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.72 | A | 7 | 976 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.26 | 7 | 0
2000-04-15 | 1900-04-14 | 10:00 | 10 | 914 | 1357 | 602 | 2 | 8 | 504 | 2 | 15 | 262 | 2 | 8 | 63400 | 2 | 8 | 52000 | 2 | 15 | 28300 | 2 | 8 | 7050 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 18.3 | 64.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.36 | 7 | 0
2000-04-15 | 1900-04-14 | 11:00 | 11 | 1067 | 1357 | 748 | 2 | 8 | 610 | 2 | 15 | 267 | 2 | 8 | 80500 | 2 | 8 | 63600 | 2 | 15 | 30300 | 2 | 8 | 9250 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 18.9 | 66.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.34 | 7 | 0
2000-04-15 | 1900-04-14 | 12:00 | 12 | 1158 | 1357 | 769 | 2 | 8 | 542 | 2 | 15 | 306 | 2 | 8 | 82700 | 2 | 8 | 56600 | 2 | 15 | 34300 | 2 | 8 | 13400 | 2 | 19 | 7 | E | 9 | 6 | E | 9 | 20.6 | 69.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.63 | A | 7 | 975 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.14 | 7 | 0
2000-04-15 | 1900-04-14 | 13:00 | 13 | 1180 | 1357 | 731 | 2 | 8 | 378 | 2 | 15 | 402 | 2 | 8 | 79800 | 2 | 8 | 41000 | 2 | 15 | 44000 | 2 | 8 | 17760 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 20 | 68 | A | 7 | 13.3 | 55.94 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 2.3 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.54 | 7 | 0
2000-04-15 | 1900-04-14 | 14:00 | 14 | 1132 | 1357 | 394 | 2 | 8 | 30 | 2 | 15 | 369 | 2 | 8 | 43500 | 2 | 8 | 3100 | 2 | 15 | 40900 | 2 | 8 | 15610 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 19.4 | 66.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 2.3 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.14 | 7 | 0
2000-04-15 | 1900-04-14 | 15:00 | 15 | 1017 | 1357 | 363 | 2 | 8 | 36 | 2 | 15 | 336 | 2 | 8 | 40000 | 2 | 8 | 3700 | 2 | 15 | 37200 | 2 | 8 | 12580 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 19.4 | 66.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.68 | A | 7 | 976 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 2.2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.14 | 7 | 0
2000-04-15 | 1900-04-14 | 16:00 | 16 | 844 | 1357 | 464 | 2 | 8 | 266 | 2 | 15 | 299 | 2 | 8 | 49600 | 2 | 8 | 28300 | 2 | 15 | 31900 | 2 | 8 | 7860 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 20 | 68 | A | 7 | 13.3 | 55.94 | A | 7 | 0.65 | A | 7 | 976 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 2.2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.54 | 7 | 0
2000-04-15 | 1900-04-14 | 17:00 | 17 | 623 | 1357 | 208 | 2 | 8 | 41 | 2 | 15 | 189 | 2 | 8 | 22800 | 2 | 8 | 4000 | 2 | 15 | 21000 | 2 | 8 | 5520 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 18.9 | 66.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.68 | A | 7 | 976 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1036 | A | 7 | 2.2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.34 | 7 | 0
2000-04-15 | 1900-04-14 | 18:00 | 18 | 370 | 1357 | 76 | 2 | 8 | 0 | 2 | 15 | 76 | 2 | 8 | 8700 | 2 | 8 | 0 | 2 | 15 | 8700 | 2 | 8 | 2920 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.7 | A | 7 | 974 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 2.1 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.74 | 7 | 0
2000-04-15 | 1900-04-14 | 19:00 | 19 | 107 | 1255 | 5 | 2 | 8 | 0 | 2 | 15 | 5 | 2 | 8 | 600 | 2 | 8 | 0 | 2 | 15 | 600 | 2 | 8 | 210 | 2 | 19 | 7 | E | 9 | 6 | E | 9 | 17.2 | 62.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.72 | A | 7 | 976 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 2.1 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.06 | 7 | 0
2000-04-15 | 1900-04-14 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 16.7 | 62.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.75 | A | 7 | 977 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 1006 | A | 7 | 2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.66 | 7 | 0
2000-04-15 | 1900-04-14 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | E | 9 | 16.7 | 62.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.75 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.66 | 7 | 0
2000-04-15 | 1900-04-14 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 4 | E | 9 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 6096 | A | 7 | 2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.16 | 7 | 0
2000-04-15 | 1900-04-14 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 15 | 59 | A | 7 | 11.7 | 53.06 | A | 7 | 0.81 | A | 7 | 976 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 12800 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.86 | 7 | 0
2000-04-15 | 1900-04-14 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 15 | 59 | A | 7 | 12.2 | 53.96 | A | 7 | 0.83 | A | 7 | 974 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 12800 | A | 7 | 1676 | A | 7 | 1.9 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 51.06 | 7 | 0
2000-04-16 | 1900-04-15 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.8 | A | 7 | 976 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1158 | A | 7 | 1.8 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.56 | 1 | 0
2000-04-16 | 1900-04-15 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.8 | A | 7 | 975 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1341 | A | 7 | 1.8 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.56 | 1 | 0
2000-04-16 | 1900-04-15 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 14.4 | 57.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 975 | A | 7 | 1.7 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 51.76 | 1 | 0
2000-04-16 | 1900-04-15 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 2743 | A | 7 | 1.7 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 52.06 | 1 | 0
2000-04-16 | 1900-04-15 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 210 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 610 | A | 7 | 1.6 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.48 | 1 | 0
2000-04-16 | 1900-04-15 | 6:00 | 6 | 12 | 418 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 11200 | A | 7 | 305 | A | 7 | 1.6 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.32 | 1 | 0
2000-04-16 | 1900-04-15 | 7:00 | 7 | 208 | 1356 | 23 | 2 | 8 | 0 | 2 | 15 | 23 | 2 | 8 | 2700 | 2 | 8 | 0 | 2 | 15 | 2700 | 2 | 8 | 910 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 305 | A | 7 | 1.5 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.54 | 1 | 0
2000-04-16 | 1900-04-15 | 8:00 | 8 | 471 | 1356 | 52 | 2 | 8 | 0 | 2 | 15 | 52 | 2 | 8 | 6300 | 2 | 8 | 0 | 2 | 15 | 6300 | 2 | 8 | 2310 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.8 | 46.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 305 | A | 7 | 1.4 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.48 | 1 | 0
2000-04-16 | 1900-04-15 | 9:00 | 9 | 714 | 1356 | 121 | 2 | 8 | 0 | 2 | 15 | 121 | 2 | 8 | 14400 | 2 | 8 | 0 | 2 | 15 | 14400 | 2 | 8 | 5560 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 230 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 305 | A | 7 | 1.4 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.68 | 1 | 0
2000-04-16 | 1900-04-15 | 10:00 | 10 | 918 | 1356 | 269 | 2 | 8 | 18 | 2 | 15 | 257 | 2 | 8 | 31300 | 2 | 8 | 1600 | 2 | 15 | 30200 | 2 | 8 | 11280 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 3.9 | 39.02 | A | 7 | 0.8 | A | 7 | 978 | A | 7 | 250 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 427 | A | 7 | 1.3 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.52 | 1 | 0
2000-04-16 | 1900-04-15 | 11:00 | 11 | 1071 | 1356 | 193 | 2 | 8 | 0 | 2 | 15 | 193 | 2 | 8 | 23500 | 2 | 8 | 0 | 2 | 15 | 23500 | 2 | 8 | 9610 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.8 | 46.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.73 | A | 7 | 978 | A | 7 | 250 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 457 | A | 7 | 1.3 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.54 | 1 | 0
2000-04-16 | 1900-04-15 | 12:00 | 12 | 1162 | 1356 | 250 | 2 | 8 | 0 | 2 | 15 | 250 | 2 | 8 | 30200 | 2 | 8 | 0 | 2 | 15 | 30200 | 2 | 8 | 12080 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 230 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 579 | A | 7 | 1.2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.84 | 1 | 0
2000-04-16 | 1900-04-15 | 13:00 | 13 | 1183 | 1356 | 180 | 2 | 8 | 0 | 2 | 15 | 180 | 2 | 8 | 22300 | 2 | 8 | 0 | 2 | 15 | 22300 | 2 | 8 | 9210 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 240 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 640 | A | 7 | 1.3 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.84 | 1 | 0
2000-04-16 | 1900-04-15 | 14:00 | 14 | 1135 | 1356 | 165 | 2 | 8 | 0 | 2 | 15 | 165 | 2 | 8 | 20500 | 2 | 8 | 0 | 2 | 15 | 20500 | 2 | 8 | 8500 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 2.2 | 35.96 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 260 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 640 | A | 7 | 1.3 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.36 | 1 | 0
2000-04-16 | 1900-04-15 | 15:00 | 15 | 1020 | 1356 | 184 | 2 | 8 | 0 | 2 | 15 | 184 | 2 | 8 | 22300 | 2 | 8 | 0 | 2 | 15 | 22300 | 2 | 8 | 9100 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 2.2 | 35.96 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 250 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 640 | A | 7 | 1.4 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.76 | 1 | 0
2000-04-16 | 1900-04-15 | 16:00 | 16 | 847 | 1356 | 157 | 2 | 8 | 0 | 2 | 15 | 157 | 2 | 8 | 18700 | 2 | 8 | 0 | 2 | 15 | 18700 | 2 | 8 | 7410 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 1.7 | 35.06 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 260 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 701 | A | 7 | 1.5 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.36 | 1 | 0
2000-04-16 | 1900-04-15 | 17:00 | 17 | 626 | 1356 | 64 | 2 | 8 | 0 | 2 | 15 | 64 | 2 | 8 | 7900 | 2 | 8 | 0 | 2 | 15 | 7900 | 2 | 8 | 3040 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 270 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 701 | A | 7 | 1.5 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.76 | 1 | 0
2000-04-16 | 1900-04-15 | 18:00 | 18 | 374 | 1356 | 33 | 2 | 8 | 0 | 2 | 15 | 33 | 2 | 8 | 4000 | 2 | 8 | 0 | 2 | 15 | 4000 | 2 | 8 | 1440 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.76 | A | 7 | 979 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 701 | A | 7 | 1.6 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.26 | 1 | 0
2000-04-16 | 1900-04-15 | 19:00 | 19 | 111 | 1277 | 38 | 2 | 8 | 127 | 2 | 15 | 28 | 2 | 8 | 4200 | 2 | 8 | 6200 | 2 | 15 | 3600 | 2 | 8 | 500 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 5.6 | 42.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 270 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 640 | A | 7 | 1.7 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.26 | 1 | 0
2000-04-16 | 1900-04-15 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 5 | 41 | A | 7 | 1.7 | 35.06 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 549 | A | 7 | 1.7 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.66 | 1 | 0
2000-04-16 | 1900-04-15 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 5 | 41 | A | 7 | 2.2 | 35.96 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 457 | A | 7 | 1.8 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.86 | 1 | 0
2000-04-16 | 1900-04-15 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 5 | 41 | A | 7 | 2.2 | 35.96 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 457 | A | 7 | 1.8 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.86 | 1 | 0
2000-04-16 | 1900-04-15 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 2.2 | 35.96 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 396 | A | 7 | 1.9 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.26 | 1 | 0
2000-04-16 | 1900-04-15 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 4.4 | 39.92 | A | 7 | 2.2 | 35.96 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 335 | A | 7 | 2 | E | 8 | 0.119 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.26 | 1 | 0
2000-04-17 | 1900-04-16 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 3.9 | 39.02 | A | 7 | 2.2 | 35.96 | A | 7 | 0.89 | A | 7 | 982 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 305 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.66 | 2 | 0
2000-04-17 | 1900-04-16 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 3.9 | 39.02 | A | 7 | 2.2 | 35.96 | A | 7 | 0.89 | A | 7 | 983 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 12800 | A | 7 | 305 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.66 | 2 | 0
2000-04-17 | 1900-04-16 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 3.9 | 39.02 | A | 7 | 2.2 | 35.96 | A | 7 | 0.89 | A | 7 | 983 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 244 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.66 | 2 | 0
2000-04-17 | 1900-04-16 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 3.3 | 37.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.89 | A | 7 | 983 | A | 7 | 320 | A | 7 | 6.7 | A | 7 | 9600 | A | 7 | 183 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.76 | 2 | 0
2000-04-17 | 1900-04-16 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 9600 | A | 7 | 183 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.16 | 2 | 0
2000-04-17 | 1900-04-16 | 6:00 | 6 | 13 | 463 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 183 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.16 | 2 | 0
2000-04-17 | 1900-04-16 | 7:00 | 7 | 214 | 1355 | 55 | 2 | 8 | 0 | 2 | 15 | 55 | 2 | 8 | 6100 | 2 | 8 | 0 | 2 | 15 | 6100 | 2 | 8 | 1840 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 183 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.16 | 2 | 0
2000-04-17 | 1900-04-16 | 8:00 | 8 | 477 | 1355 | 125 | 2 | 8 | 0 | 2 | 15 | 125 | 2 | 8 | 14100 | 2 | 8 | 0 | 2 | 15 | 14100 | 2 | 8 | 4720 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 3.3 | 37.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 244 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.76 | 2 | 0
2000-04-17 | 1900-04-16 | 9:00 | 9 | 719 | 1355 | 134 | 2 | 8 | 0 | 2 | 15 | 134 | 2 | 8 | 15800 | 2 | 8 | 0 | 2 | 15 | 15800 | 2 | 8 | 6060 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 4.4 | 39.92 | A | 7 | 1.7 | 35.06 | A | 7 | 0.83 | A | 7 | 985 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 305 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.06 | 2 | 0
2000-04-17 | 1900-04-16 | 10:00 | 10 | 923 | 1355 | 256 | 2 | 8 | 12 | 2 | 15 | 248 | 2 | 8 | 29900 | 2 | 8 | 1000 | 2 | 15 | 29200 | 2 | 8 | 11030 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 5.6 | 42.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.79 | A | 7 | 985 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 366 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.46 | 2 | 0
2000-04-17 | 1900-04-16 | 11:00 | 11 | 1075 | 1355 | 299 | 2 | 8 | 12 | 2 | 15 | 289 | 2 | 8 | 35200 | 2 | 8 | 1000 | 2 | 15 | 34400 | 2 | 8 | 13240 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.1 | 42.98 | A | 7 | 2.8 | 37.04 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 427 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.54 | 2 | 0
2000-04-17 | 1900-04-16 | 12:00 | 12 | 1165 | 1355 | 391 | 2 | 8 | 48 | 2 | 15 | 349 | 2 | 8 | 43100 | 2 | 8 | 4900 | 2 | 15 | 38900 | 2 | 8 | 15650 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.74 | A | 7 | 984 | A | 7 | 290 | B | 8 | 2.1 | A | 7 | 16000 | A | 7 | 488 | A | 7 | 2.1 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.84 | 2 | 0
2000-04-17 | 1900-04-16 | 13:00 | 13 | 1187 | 1355 | 875 | 2 | 8 | 636 | 2 | 15 | 317 | 2 | 8 | 94100 | 2 | 8 | 66500 | 2 | 15 | 35800 | 2 | 8 | 15270 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 10.6 | 51.08 | A | 7 | 4.4 | 39.92 | A | 7 | 0.65 | A | 7 | 985 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.32 | 2 | 0
2000-04-17 | 1900-04-16 | 14:00 | 14 | 1138 | 1355 | 859 | 2 | 8 | 789 | 2 | 15 | 195 | 2 | 8 | 91900 | 2 | 8 | 80800 | 2 | 15 | 23900 | 2 | 8 | 8040 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 12.2 | 53.96 | A | 7 | 5 | 41 | A | 7 | 0.61 | A | 7 | 984 | A | 7 | 310 | B | 8 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.8 | 2 | 0
2000-04-17 | 1900-04-16 | 15:00 | 15 | 1023 | 1355 | 755 | 2 | 8 | 780 | 2 | 15 | 164 | 2 | 8 | 80700 | 2 | 8 | 79800 | 2 | 15 | 20300 | 2 | 8 | 5250 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 13.9 | 57.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.57 | A | 7 | 984 | A | 7 | 350 | B | 8 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.08 | 2 | 0
2000-04-17 | 1900-04-16 | 16:00 | 16 | 850 | 1355 | 616 | 2 | 8 | 799 | 2 | 15 | 114 | 2 | 8 | 64500 | 2 | 8 | 79700 | 2 | 15 | 14400 | 2 | 8 | 2690 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 13.9 | 57.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.57 | A | 7 | 983 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.08 | 2 | 0
2000-04-17 | 1900-04-16 | 17:00 | 17 | 629 | 1355 | 427 | 2 | 8 | 700 | 2 | 15 | 101 | 2 | 8 | 44900 | 2 | 8 | 68500 | 2 | 15 | 13000 | 2 | 8 | 2110 | 2 | 19 | 2 | B | 8 | 2 | B | 8 | 14.4 | 57.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.55 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.88 | 2 | 0
2000-04-17 | 1900-04-16 | 18:00 | 18 | 378 | 1355 | 225 | 2 | 8 | 544 | 2 | 15 | 73 | 2 | 8 | 23100 | 2 | 8 | 46700 | 2 | 15 | 10100 | 2 | 8 | 1340 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 15 | 59 | A | 7 | 5.6 | 42.08 | A | 7 | 0.53 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.58 | 2 | 0
2000-04-17 | 1900-04-16 | 19:00 | 19 | 115 | 1299 | 39 | 2 | 8 | 226 | 2 | 15 | 20 | 2 | 8 | 4200 | 2 | 8 | 12500 | 2 | 15 | 3100 | 2 | 8 | 370 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.88 | 2 | 0
2000-04-17 | 1900-04-16 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 5 | 41 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.8 | 2 | 0
2000-04-17 | 1900-04-16 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.08 | 2 | 0
2000-04-17 | 1900-04-16 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 5 | 41 | A | 7 | 0.8 | A | 7 | 982 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.3 | 2 | 0
2000-04-17 | 1900-04-16 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | A | 7 | 7.8 | 46.04 | A | 7 | 4.4 | 39.92 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.22 | 2 | 0
2000-04-17 | 1900-04-16 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.12 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.62 | 2 | 0
2000-04-18 | 1900-04-17 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.85 | A | 7 | 981 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.02 | 3 | 0
2000-04-18 | 1900-04-17 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 5 | 41 | A | 7 | 0.86 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.1 | 3 | 0
2000-04-18 | 1900-04-17 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.5 | 3 | 0
2000-04-18 | 1900-04-17 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.68 | 3 | 0
2000-04-18 | 1900-04-17 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.5 | 3 | 0
2000-04-18 | 1900-04-17 | 6:00 | 6 | 15 | 485 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40 | 3 | 0
2000-04-18 | 1900-04-17 | 7:00 | 7 | 220 | 1355 | 129 | 2 | 8 | 338 | 2 | 15 | 74 | 2 | 8 | 12900 | 2 | 8 | 22600 | 2 | 15 | 9200 | 2 | 8 | 1400 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 6.7 | 44.06 | A | 7 | 0.86 | A | 7 | 980 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.06 | 3 | 0
2000-04-18 | 1900-04-17 | 8:00 | 8 | 482 | 1355 | 323 | 2 | 8 | 617 | 2 | 15 | 103 | 2 | 8 | 33100 | 2 | 8 | 56400 | 2 | 15 | 13000 | 2 | 8 | 1910 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.44 | 3 | 0
2000-04-18 | 1900-04-17 | 9:00 | 9 | 724 | 1355 | 521 | 2 | 8 | 750 | 2 | 15 | 119 | 2 | 8 | 54900 | 2 | 8 | 74700 | 2 | 15 | 14900 | 2 | 8 | 2630 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 15.6 | 60.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.64 | A | 7 | 980 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.42 | 3 | 0
2000-04-18 | 1900-04-17 | 10:00 | 10 | 927 | 1355 | 672 | 2 | 8 | 772 | 2 | 15 | 142 | 2 | 8 | 71800 | 2 | 8 | 78800 | 2 | 15 | 17700 | 2 | 8 | 3920 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.12 | 3 | 0
2000-04-18 | 1900-04-17 | 11:00 | 11 | 1079 | 1355 | 809 | 2 | 8 | 791 | 2 | 15 | 178 | 2 | 8 | 86600 | 2 | 8 | 81000 | 2 | 15 | 21900 | 2 | 8 | 6370 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20.6 | 69.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.49 | A | 7 | 979 | A | 7 | 130 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.62 | 3 | 0
2000-04-18 | 1900-04-17 | 12:00 | 12 | 1169 | 1355 | 909 | 2 | 8 | 860 | 2 | 15 | 165 | 2 | 8 | 95700 | 2 | 8 | 86700 | 2 | 15 | 20700 | 2 | 8 | 6870 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 10 | 50 | A | 7 | 0.46 | A | 7 | 976 | A | 7 | 140 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41 | 3 | 0
2000-04-18 | 1900-04-17 | 13:00 | 13 | 1190 | 1355 | 911 | 2 | 8 | 756 | 2 | 15 | 245 | 2 | 8 | 96300 | 2 | 8 | 76800 | 2 | 15 | 28700 | 2 | 8 | 11660 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.48 | A | 7 | 977 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 2743 | A | 7 | 2.7 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.98 | 3 | 0
2000-04-18 | 1900-04-17 | 14:00 | 14 | 1141 | 1355 | 647 | 2 | 8 | 263 | 2 | 15 | 425 | 2 | 8 | 70000 | 2 | 8 | 28500 | 2 | 15 | 45900 | 2 | 8 | 17320 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 25.6 | 78.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.45 | A | 7 | 976 | A | 7 | 150 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.7 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.84 | 3 | 0
2000-04-18 | 1900-04-17 | 15:00 | 15 | 1026 | 1355 | 767 | 2 | 8 | 727 | 2 | 15 | 214 | 2 | 8 | 80400 | 2 | 8 | 73500 | 2 | 15 | 24600 | 2 | 8 | 6710 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25.6 | 78.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.5 | A | 7 | 974 | A | 7 | 130 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.22 | 3 | 0
2000-04-18 | 1900-04-17 | 16:00 | 16 | 853 | 1355 | 599 | 2 | 8 | 704 | 2 | 15 | 155 | 2 | 8 | 63100 | 2 | 8 | 70900 | 2 | 15 | 18300 | 2 | 8 | 3820 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 26.1 | 78.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.48 | A | 7 | 973 | A | 7 | 140 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.82 | 3 | 0
2000-04-18 | 1900-04-17 | 17:00 | 17 | 633 | 1355 | 417 | 2 | 8 | 642 | 2 | 15 | 116 | 2 | 8 | 43400 | 2 | 8 | 62500 | 2 | 15 | 14200 | 2 | 8 | 2370 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25.6 | 78.08 | A | 7 | 15 | 59 | A | 7 | 0.52 | A | 7 | 973 | A | 7 | 130 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.6 | 3 | 0
2000-04-18 | 1900-04-17 | 18:00 | 18 | 381 | 1355 | 221 | 2 | 8 | 522 | 2 | 15 | 73 | 2 | 8 | 22600 | 2 | 8 | 45000 | 2 | 15 | 9900 | 2 | 8 | 1340 | 2 | 19 | 7 | E | 9 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.54 | A | 7 | 969 | A | 7 | 150 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.88 | 3 | 0
2000-04-18 | 1900-04-17 | 19:00 | 19 | 118 | 1321 | 43 | 2 | 8 | 242 | 2 | 15 | 22 | 2 | 8 | 4600 | 2 | 8 | 13300 | 2 | 15 | 3400 | 2 | 8 | 400 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 23.9 | 75.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 140 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 52.18 | 3 | 0
2000-04-18 | 1900-04-17 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 23.3 | 73.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.64 | A | 7 | 972 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 53.78 | 3 | 0
2000-04-18 | 1900-04-17 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 22.8 | 73.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.66 | A | 7 | 972 | A | 7 | 140 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 54.18 | 3 | 0
2000-04-18 | 1900-04-17 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 22.2 | 71.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.68 | A | 7 | 972 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 54.68 | 3 | 0
2000-04-18 | 1900-04-17 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 5 | A | 7 | 22.2 | 71.96 | A | 7 | 15.6 | 60.08 | A | 7 | 0.66 | A | 7 | 971 | A | 7 | 150 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 53.48 | 3 | 0
2000-04-18 | 1900-04-17 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 22.2 | 71.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.68 | A | 7 | 969 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.121 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 54.68 | 3 | 0
2000-04-19 | 1900-04-18 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 22.2 | 71.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.71 | A | 7 | 970 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 1036 | A | 7 | 2.4 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 56.26 | 4 | 0
2000-04-19 | 1900-04-18 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 22.2 | 71.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.73 | A | 7 | 969 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 14400 | A | 7 | 975 | A | 7 | 2.3 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 57.46 | 4 | 0
2000-04-19 | 1900-04-18 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 968 | A | 7 | 170 | A | 7 | 9.8 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 58.16 | 4 | 0
2000-04-19 | 1900-04-18 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 20.6 | 69.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.81 | A | 7 | 967 | A | 7 | 170 | A | 7 | 9.8 | A | 7 | 12800 | A | 7 | 762 | A | 7 | 2.1 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 59.16 | 4 | 0
2000-04-19 | 1900-04-18 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 969 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 701 | A | 7 | 2 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 60.14 | 4 | 0
2000-04-19 | 1900-04-18 | 6:00 | 6 | 17 | 508 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 967 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 8000 | A | 7 | 823 | A | 7 | 1.8 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 60.14 | 4 | 0
2000-04-19 | 1900-04-18 | 7:00 | 7 | 226 | 1354 | 53 | 2 | 8 | 0 | 2 | 15 | 53 | 2 | 8 | 5900 | 2 | 8 | 0 | 2 | 15 | 5900 | 2 | 8 | 1830 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 968 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 8000 | A | 7 | 732 | A | 7 | 1.7 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 60.64 | 4 | 0
2000-04-19 | 1900-04-18 | 8:00 | 8 | 487 | 1354 | 102 | 2 | 8 | 0 | 2 | 15 | 102 | 2 | 8 | 11800 | 2 | 8 | 0 | 2 | 15 | 11800 | 2 | 8 | 4110 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 968 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 8000 | A | 7 | 1158 | A | 7 | 1.6 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 60.64 | 4 | 0
2000-04-19 | 1900-04-18 | 9:00 | 9 | 728 | 1354 | 113 | 2 | 8 | 0 | 2 | 15 | 113 | 2 | 8 | 13600 | 2 | 8 | 0 | 2 | 15 | 13600 | 2 | 8 | 5290 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 969 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 8000 | A | 7 | 1189 | A | 7 | 1.5 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 62.22 | 4 | 0
2000-04-19 | 1900-04-18 | 10:00 | 10 | 932 | 1354 | 217 | 2 | 8 | 6 | 2 | 15 | 213 | 2 | 8 | 25700 | 2 | 8 | 500 | 2 | 15 | 25300 | 2 | 8 | 9880 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 969 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 1372 | A | 7 | 1.4 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 60.92 | 4 | 0
2000-04-19 | 1900-04-18 | 11:00 | 11 | 1083 | 1354 | 741 | 2 | 8 | 556 | 2 | 15 | 295 | 2 | 8 | 79100 | 2 | 8 | 58000 | 2 | 15 | 32600 | 2 | 8 | 10700 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25.6 | 78.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.56 | A | 7 | 969 | A | 7 | 230 | A | 7 | 8.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 52.08 | 4 | 0
2000-04-19 | 1900-04-18 | 12:00 | 12 | 1172 | 1354 | 872 | 2 | 8 | 770 | 2 | 15 | 204 | 2 | 8 | 93300 | 2 | 8 | 78800 | 2 | 15 | 24900 | 2 | 8 | 9300 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 26.1 | 78.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.48 | A | 7 | 967 | A | 7 | 250 | A | 7 | 7.2 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.82 | 4 | 0
2000-04-19 | 1900-04-18 | 13:00 | 13 | 1193 | 1354 | 905 | 2 | 8 | 792 | 2 | 15 | 205 | 2 | 8 | 97000 | 2 | 8 | 81200 | 2 | 15 | 25300 | 2 | 8 | 10020 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 27.2 | 80.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.45 | A | 7 | 969 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.12 | 4 | 0
2000-04-19 | 1900-04-18 | 14:00 | 14 | 1144 | 1354 | 830 | 2 | 8 | 658 | 2 | 15 | 272 | 2 | 8 | 86700 | 2 | 8 | 66200 | 2 | 15 | 30600 | 2 | 8 | 11100 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 27.8 | 82.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.47 | A | 7 | 968 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.38 | 4 | 0
2000-04-19 | 1900-04-18 | 15:00 | 15 | 1029 | 1354 | 686 | 2 | 8 | 560 | 2 | 15 | 259 | 2 | 8 | 73600 | 2 | 8 | 58300 | 2 | 15 | 29200 | 2 | 8 | 8340 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 28.3 | 82.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.46 | A | 7 | 967 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.08 | 4 | 0
2000-04-19 | 1900-04-18 | 16:00 | 16 | 856 | 1354 | 594 | 2 | 8 | 639 | 2 | 15 | 189 | 2 | 8 | 61600 | 2 | 8 | 63700 | 2 | 15 | 21200 | 2 | 8 | 4540 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 28.3 | 82.94 | A | 7 | 15 | 59 | A | 7 | 0.44 | A | 7 | 966 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.8 | 4 | 0
2000-04-19 | 1900-04-18 | 17:00 | 17 | 636 | 1354 | 396 | 2 | 8 | 514 | 2 | 15 | 154 | 2 | 8 | 41900 | 2 | 8 | 51000 | 2 | 15 | 17900 | 2 | 8 | 3160 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 27.2 | 80.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.51 | A | 7 | 966 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.98 | 4 | 0
2000-04-19 | 1900-04-18 | 18:00 | 18 | 385 | 1354 | 231 | 2 | 8 | 562 | 2 | 15 | 71 | 2 | 8 | 23800 | 2 | 8 | 48700 | 2 | 15 | 10000 | 2 | 8 | 1310 | 2 | 19 | 8 | E | 9 | 5 | A | 7 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 962 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 56.84 | 4 | 0
2000-04-19 | 1900-04-18 | 19:00 | 19 | 122 | 1343 | 44 | 2 | 8 | 244 | 2 | 15 | 22 | 2 | 8 | 4700 | 2 | 8 | 13600 | 2 | 15 | 3400 | 2 | 8 | 400 | 2 | 19 | 7 | E | 9 | 6 | E | 9 | 25 | 77 | A | 7 | 18.3 | 64.94 | A | 7 | 0.66 | A | 7 | 964 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 57.74 | 4 | 0
2000-04-19 | 1900-04-18 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 965 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 11200 | A | 7 | 1372 | A | 7 | 1.6 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 60.52 | 4 | 0
2000-04-19 | 1900-04-18 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 966 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 60.14 | 4 | 0
2000-04-19 | 1900-04-18 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 19.4 | 66.92 | A | 7 | 15 | 59 | A | 7 | 0.76 | A | 7 | 965 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 54.5 | 4 | 0
2000-04-19 | 1900-04-18 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 963 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 58.36 | 4 | 0
2000-04-19 | 1900-04-18 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 6 | E | 9 | 20.6 | 69.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.81 | A | 7 | 961 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 59.16 | 4 | 0
2000-04-20 | 1900-04-19 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | E | 9 | 14.4 | 57.92 | A | 7 | 5 | 41 | A | 7 | 0.53 | A | 7 | 964 | A | 7 | 270 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.6 | 5 | 0
2000-04-20 | 1900-04-19 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 10 | 50 | A | 7 | 1.7 | 35.06 | A | 7 | 0.56 | A | 7 | 964 | A | 7 | 250 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.76 | 5 | 0
2000-04-20 | 1900-04-19 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.63 | A | 7 | 964 | A | 7 | 250 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.56 | 5 | 0
2000-04-20 | 1900-04-19 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.68 | A | 7 | 965 | A | 7 | 250 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.16 | 5 | 0
2000-04-20 | 1900-04-19 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | E | 9 | 6.7 | 44.06 | A | 7 | 1.7 | 35.06 | A | 7 | 0.7 | A | 7 | 965 | A | 7 | 240 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.36 | 5 | 0
2000-04-20 | 1900-04-19 | 6:00 | 6 | 20 | 553 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 6.7 | 44.06 | A | 7 | 1.7 | 35.06 | A | 7 | 0.7 | A | 7 | 964 | A | 7 | 240 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.36 | 5 | 0
2000-04-20 | 1900-04-19 | 7:00 | 7 | 231 | 1353 | 83 | 2 | 8 | 59 | 2 | 15 | 73 | 2 | 8 | 9100 | 2 | 8 | 4600 | 2 | 15 | 8300 | 2 | 8 | 1720 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 8.3 | 46.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.65 | A | 7 | 966 | A | 7 | 250 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 884 | A | 7 | 1.9 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.56 | 5 | 0
2000-04-20 | 1900-04-19 | 8:00 | 8 | 493 | 1353 | 58 | 2 | 8 | 0 | 2 | 15 | 58 | 2 | 8 | 7000 | 2 | 8 | 0 | 2 | 15 | 7000 | 2 | 8 | 2580 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 966 | A | 7 | 240 | A | 7 | 7.2 | A | 7 | 9600 | A | 7 | 701 | A | 7 | 1.9 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.5 | 5 | 0
2000-04-20 | 1900-04-19 | 9:00 | 9 | 733 | 1353 | 87 | 2 | 8 | 0 | 2 | 15 | 87 | 2 | 8 | 10700 | 2 | 8 | 0 | 2 | 15 | 10700 | 2 | 8 | 4230 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.97 | A | 7 | 967 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 4000 | A | 7 | 305 | A | 7 | 2 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 6 | 1 | A | 7 | 43.56 | 5 | 0
2000-04-20 | 1900-04-19 | 10:00 | 10 | 936 | 1353 | 121 | 2 | 8 | 0 | 2 | 15 | 121 | 2 | 8 | 14900 | 2 | 8 | 0 | 2 | 15 | 14900 | 2 | 8 | 6160 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.89 | A | 7 | 969 | A | 7 | 320 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 457 | A | 7 | 2 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 1 | 1 | A | 7 | 46.32 | 5 | 0
2000-04-20 | 1900-04-19 | 11:00 | 11 | 1087 | 1353 | 236 | 2 | 8 | 6 | 2 | 15 | 232 | 2 | 8 | 28500 | 2 | 8 | 500 | 2 | 15 | 28100 | 2 | 8 | 11220 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.89 | A | 7 | 972 | A | 7 | 320 | A | 7 | 12.4 | A | 7 | 12800 | A | 7 | 396 | A | 7 | 2 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.24 | 5 | 0
2000-04-20 | 1900-04-19 | 12:00 | 12 | 1175 | 1353 | 189 | 2 | 8 | 0 | 2 | 15 | 189 | 2 | 8 | 23300 | 2 | 8 | 0 | 2 | 15 | 23300 | 2 | 8 | 9600 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 8.9 | 48.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 310 | A | 7 | 12.4 | A | 7 | 4000 | A | 7 | 488 | A | 7 | 2.1 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.36 | 5 | 0
2000-04-20 | 1900-04-19 | 13:00 | 13 | 1196 | 1353 | 186 | 2 | 8 | 0 | 2 | 15 | 186 | 2 | 8 | 23100 | 2 | 8 | 0 | 2 | 15 | 23100 | 2 | 8 | 9500 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 8.9 | 48.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.83 | A | 7 | 975 | A | 7 | 320 | A | 7 | 12.4 | A | 7 | 16000 | A | 7 | 488 | A | 7 | 2 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.58 | 5 | 0
2000-04-20 | 1900-04-19 | 14:00 | 14 | 1147 | 1353 | 171 | 2 | 8 | 0 | 2 | 15 | 171 | 2 | 8 | 21200 | 2 | 8 | 0 | 2 | 15 | 21200 | 2 | 8 | 8780 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.8 | A | 7 | 977 | A | 7 | 300 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 549 | A | 7 | 1.9 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.18 | 5 | 0
2000-04-20 | 1900-04-19 | 15:00 | 15 | 1032 | 1353 | 202 | 2 | 8 | 0 | 2 | 15 | 202 | 2 | 8 | 24300 | 2 | 8 | 0 | 2 | 15 | 24300 | 2 | 8 | 9880 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.77 | A | 7 | 978 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 732 | A | 7 | 1.8 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.98 | 5 | 0
2000-04-20 | 1900-04-19 | 16:00 | 16 | 859 | 1353 | 135 | 2 | 8 | 0 | 2 | 15 | 135 | 2 | 8 | 16300 | 2 | 8 | 0 | 2 | 15 | 16300 | 2 | 8 | 6580 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 978 | A | 7 | 300 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 732 | A | 7 | 1.7 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.9 | 5 | 0
2000-04-20 | 1900-04-19 | 17:00 | 17 | 639 | 1353 | 134 | 2 | 8 | 0 | 2 | 15 | 134 | 2 | 8 | 15600 | 2 | 8 | 0 | 2 | 15 | 15600 | 2 | 8 | 5750 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 8.9 | 48.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 945 | A | 7 | 1.6 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.42 | 5 | 0
2000-04-20 | 1900-04-19 | 18:00 | 18 | 388 | 1353 | 58 | 2 | 8 | 0 | 2 | 15 | 58 | 2 | 8 | 6800 | 2 | 8 | 0 | 2 | 15 | 6800 | 2 | 8 | 2390 | 2 | 19 | 10 | B | 8 | 10 | B | 8 | 8.9 | 48.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 945 | A | 7 | 1.5 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.42 | 5 | 0
2000-04-20 | 1900-04-19 | 19:00 | 19 | 126 | 1353 | 15 | 2 | 8 | 0 | 2 | 15 | 15 | 2 | 8 | 1800 | 2 | 8 | 0 | 2 | 15 | 1800 | 2 | 8 | 570 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 8.9 | 48.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 945 | A | 7 | 1.4 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.42 | 5 | 0
2000-04-20 | 1900-04-19 | 20:00 | 20 | 0 | 11 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 1 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 1 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 5 | 41 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 945 | A | 7 | 1.4 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.5 | 5 | 0
2000-04-20 | 1900-04-19 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.68 | A | 7 | 982 | A | 7 | 330 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 1097 | A | 7 | 1.3 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.92 | 5 | 0
2000-04-20 | 1900-04-19 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 8.9 | 48.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 1097 | A | 7 | 1.2 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.32 | 5 | 0
2000-04-20 | 1900-04-19 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | A | 7 | 8.3 | 46.94 | A | 7 | 3.9 | 39.02 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 330 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 1097 | A | 7 | 1.1 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.72 | 5 | 0
2000-04-20 | 1900-04-19 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 7.8 | 46.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 340 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 914 | A | 7 | 1 | E | 8 | 0.122 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.54 | 5 | 0
2000-04-21 | 1900-04-20 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 6.7 | 44.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.34 | 6 | 0
2000-04-21 | 1900-04-20 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 6.1 | 42.98 | A | 7 | 2.8 | 37.04 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.54 | 6 | 0
2000-04-21 | 1900-04-20 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.73 | A | 7 | 983 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.78 | 6 | 0
2000-04-21 | 1900-04-20 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 4.4 | 39.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.76 | A | 7 | 984 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.38 | 6 | 0
2000-04-21 | 1900-04-20 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 4.4 | 39.92 | A | 7 | 0 | 32 | A | 7 | 0.73 | A | 7 | 984 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.1 | 6 | 0
2000-04-21 | 1900-04-20 | 6:00 | 6 | 22 | 575 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 3.9 | 39.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.72 | A | 7 | 984 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.02 | 6 | 0
2000-04-21 | 1900-04-20 | 7:00 | 7 | 237 | 1352 | 132 | 2 | 8 | 314 | 2 | 15 | 77 | 2 | 8 | 13300 | 2 | 8 | 21900 | 2 | 15 | 9500 | 2 | 8 | 1450 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.68 | A | 7 | 985 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.48 | 6 | 0
2000-04-21 | 1900-04-20 | 8:00 | 8 | 498 | 1352 | 334 | 2 | 8 | 621 | 2 | 15 | 106 | 2 | 8 | 34300 | 2 | 8 | 57200 | 2 | 15 | 13200 | 2 | 8 | 1980 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 0 | 32 | A | 7 | 0.54 | A | 7 | 986 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27 | 6 | 0
2000-04-21 | 1900-04-20 | 9:00 | 9 | 738 | 1352 | 533 | 2 | 8 | 749 | 2 | 15 | 123 | 2 | 8 | 56100 | 2 | 8 | 74800 | 2 | 15 | 15300 | 2 | 8 | 2750 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.42 | A | 7 | 986 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 24.72 | 6 | 0
2000-04-21 | 1900-04-20 | 10:00 | 10 | 940 | 1352 | 696 | 2 | 8 | 826 | 2 | 15 | 121 | 2 | 8 | 73500 | 2 | 8 | 83100 | 2 | 15 | 15600 | 2 | 8 | 3220 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.49 | A | 7 | 986 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.86 | 6 | 0
2000-04-21 | 1900-04-20 | 11:00 | 11 | 1090 | 1352 | 821 | 2 | 8 | 821 | 2 | 15 | 158 | 2 | 8 | 86000 | 2 | 8 | 82500 | 2 | 15 | 19300 | 2 | 8 | 5310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 13.9 | 57.02 | A | 7 | 2.2 | 35.96 | A | 7 | 0.45 | A | 7 | 986 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.06 | 6 | 0
2000-04-21 | 1900-04-20 | 12:00 | 12 | 1179 | 1352 | 921 | 2 | 8 | 902 | 2 | 15 | 132 | 2 | 8 | 94500 | 2 | 8 | 90300 | 2 | 15 | 15600 | 2 | 8 | 4770 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 15.6 | 60.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.44 | A | 7 | 984 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.54 | 6 | 0
2000-04-21 | 1900-04-20 | 13:00 | 13 | 1199 | 1352 | 935 | 2 | 8 | 852 | 2 | 15 | 178 | 2 | 8 | 98100 | 2 | 8 | 85700 | 2 | 15 | 21900 | 2 | 8 | 8190 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.42 | A | 7 | 986 | A | 7 | 320 | B | 8 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.24 | 6 | 0
2000-04-21 | 1900-04-20 | 14:00 | 14 | 1150 | 1352 | 859 | 2 | 8 | 778 | 2 | 15 | 197 | 2 | 8 | 92100 | 2 | 8 | 79700 | 2 | 15 | 24100 | 2 | 8 | 8450 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 2.8 | 37.04 | A | 7 | 0.37 | A | 7 | 985 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.84 | 6 | 0
2000-04-21 | 1900-04-20 | 15:00 | 15 | 1035 | 1352 | 767 | 2 | 8 | 787 | 2 | 15 | 163 | 2 | 8 | 79400 | 2 | 8 | 78700 | 2 | 15 | 19100 | 2 | 8 | 4720 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.36 | A | 7 | 984 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.74 | 6 | 0
2000-04-21 | 1900-04-20 | 16:00 | 16 | 862 | 1352 | 628 | 2 | 8 | 805 | 2 | 15 | 114 | 2 | 8 | 65900 | 2 | 8 | 80500 | 2 | 15 | 14500 | 2 | 8 | 2740 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.9 | 66.02 | A | 7 | 3.3 | 37.94 | A | 7 | 0.35 | A | 7 | 983 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.24 | 6 | 0
2000-04-21 | 1900-04-20 | 17:00 | 17 | 642 | 1352 | 439 | 2 | 8 | 713 | 2 | 15 | 100 | 2 | 8 | 46400 | 2 | 8 | 70100 | 2 | 15 | 13000 | 2 | 8 | 2110 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.36 | A | 7 | 983 | A | 7 | 310 | B | 8 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.74 | 6 | 0
2000-04-21 | 1900-04-20 | 18:00 | 18 | 392 | 1352 | 232 | 2 | 8 | 535 | 2 | 15 | 77 | 2 | 8 | 23800 | 2 | 8 | 46500 | 2 | 15 | 10400 | 2 | 8 | 1410 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 17.8 | 64.04 | A | 7 | 2.2 | 35.96 | A | 7 | 0.35 | A | 7 | 980 | A | 7 | 320 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 27.76 | 6 | 0
2000-04-21 | 1900-04-20 | 19:00 | 19 | 130 | 1352 | 49 | 2 | 8 | 267 | 2 | 15 | 23 | 2 | 8 | 5000 | 2 | 8 | 14800 | 2 | 15 | 3600 | 2 | 8 | 420 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 2.2 | 35.96 | A | 7 | 0.38 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.16 | 6 | 0
2000-04-21 | 1900-04-20 | 20:00 | 20 | 0 | 34 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.47 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.36 | 6 | 0
2000-04-21 | 1900-04-20 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.9 | 57.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.44 | A | 7 | 982 | A | 7 | 180 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.26 | 6 | 0
2000-04-21 | 1900-04-20 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.26 | 6 | 0
2000-04-21 | 1900-04-20 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | 1.7 | 35.06 | A | 7 | 0.5 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.96 | 6 | 0
2000-04-21 | 1900-04-20 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.123 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.36 | 6 | 0
2000-04-22 | 1900-04-21 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 3 | E | 9 | 8.3 | 46.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.56 | 7 | 0
2000-04-22 | 1900-04-21 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 1 | E | 9 | 7.8 | 46.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.54 | 7 | 0
2000-04-22 | 1900-04-21 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 6.7 | 44.06 | A | 7 | 2.8 | 37.04 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.8 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.14 | 7 | 0
2000-04-22 | 1900-04-21 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | 2.2 | 35.96 | A | 7 | 0.73 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.8 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.76 | 7 | 0
2000-04-22 | 1900-04-21 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.46 | 7 | 0
2000-04-22 | 1900-04-21 | 6:00 | 6 | 24 | 619 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | B | 8 | 0 | B | 8 | 7.2 | 44.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.16 | 7 | 0
2000-04-22 | 1900-04-21 | 7:00 | 7 | 242 | 1352 | 130 | 2 | 8 | 297 | 2 | 15 | 76 | 2 | 8 | 13100 | 2 | 8 | 21000 | 2 | 15 | 9300 | 2 | 8 | 1430 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 5 | 41 | A | 7 | 0.66 | A | 7 | 978 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.4 | 7 | 0
2000-04-22 | 1900-04-21 | 8:00 | 8 | 503 | 1352 | 341 | 2 | 8 | 607 | 2 | 15 | 114 | 2 | 8 | 34700 | 2 | 8 | 55900 | 2 | 15 | 13900 | 2 | 8 | 2100 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 14.4 | 57.92 | A | 7 | 5 | 41 | A | 7 | 0.53 | A | 7 | 978 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.6 | 7 | 0
2000-04-22 | 1900-04-21 | 9:00 | 9 | 742 | 1352 | 512 | 2 | 8 | 651 | 2 | 15 | 154 | 2 | 8 | 53100 | 2 | 8 | 64300 | 2 | 15 | 17800 | 2 | 8 | 3340 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 5 | 41 | A | 7 | 0.43 | A | 7 | 978 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.2 | 7 | 0
2000-04-22 | 1900-04-21 | 10:00 | 10 | 944 | 1352 | 683 | 2 | 8 | 747 | 2 | 15 | 160 | 2 | 8 | 72500 | 2 | 8 | 76000 | 2 | 15 | 19300 | 2 | 8 | 4490 | 2 | 19 | 1 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 5.6 | 42.08 | A | 7 | 0.39 | A | 7 | 977 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.48 | 7 | 0
2000-04-22 | 1900-04-21 | 11:00 | 11 | 1094 | 1352 | 815 | 2 | 8 | 743 | 2 | 15 | 212 | 2 | 8 | 86200 | 2 | 8 | 75600 | 2 | 15 | 24900 | 2 | 8 | 7780 | 2 | 19 | 1 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.35 | A | 7 | 977 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.58 | 7 | 0
2000-04-22 | 1900-04-21 | 12:00 | 12 | 1182 | 1352 | 787 | 2 | 8 | 517 | 2 | 15 | 333 | 2 | 8 | 84100 | 2 | 8 | 54000 | 2 | 15 | 36800 | 2 | 8 | 15990 | 2 | 19 | 3 | E | 9 | 2 | E | 9 | 22.8 | 73.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.33 | A | 7 | 973 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.9 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.58 | 7 | 0
2000-04-22 | 1900-04-21 | 13:00 | 13 | 1202 | 1352 | 923 | 2 | 8 | 762 | 2 | 15 | 244 | 2 | 8 | 97800 | 2 | 8 | 77500 | 2 | 15 | 28800 | 2 | 8 | 12240 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 23.3 | 73.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.32 | A | 7 | 975 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.38 | 7 | 0
2000-04-22 | 1900-04-21 | 14:00 | 14 | 1153 | 1352 | 800 | 2 | 8 | 586 | 2 | 15 | 299 | 2 | 8 | 86200 | 2 | 8 | 61300 | 2 | 15 | 33800 | 2 | 8 | 13050 | 2 | 19 | 8 | E | 9 | 7 | E | 9 | 23.3 | 73.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.32 | A | 7 | 974 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.38 | 7 | 0
2000-04-22 | 1900-04-21 | 15:00 | 15 | 1038 | 1352 | 692 | 2 | 8 | 512 | 2 | 15 | 298 | 2 | 8 | 73400 | 2 | 8 | 53200 | 2 | 15 | 32400 | 2 | 8 | 9890 | 2 | 19 | 7 | E | 9 | 6 | E | 9 | 23.9 | 75.02 | A | 7 | 6.7 | 44.06 | A | 7 | 0.33 | A | 7 | 973 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.06 | 7 | 0
2000-04-22 | 1900-04-21 | 16:00 | 16 | 865 | 1352 | 320 | 2 | 8 | 77 | 2 | 15 | 270 | 2 | 8 | 35200 | 2 | 8 | 7800 | 2 | 15 | 30100 | 2 | 8 | 9110 | 2 | 19 | 9 | E | 9 | 4 | E | 9 | 23.3 | 73.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.33 | A | 7 | 972 | A | 7 | 150 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.1 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.28 | 7 | 0
2000-04-22 | 1900-04-21 | 17:00 | 17 | 646 | 1352 | 188 | 2 | 8 | 12 | 2 | 15 | 182 | 2 | 8 | 21400 | 2 | 8 | 1000 | 2 | 15 | 20900 | 2 | 8 | 7250 | 2 | 19 | 10 | E | 9 | 4 | E | 9 | 22.8 | 73.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.35 | A | 7 | 971 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.1 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.46 | 7 | 0
2000-04-22 | 1900-04-21 | 18:00 | 18 | 396 | 1352 | 82 | 2 | 8 | 0 | 2 | 15 | 82 | 2 | 8 | 9400 | 2 | 8 | 0 | 2 | 15 | 9400 | 2 | 8 | 3180 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.36 | A | 7 | 968 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.78 | 7 | 0
2000-04-22 | 1900-04-21 | 19:00 | 19 | 134 | 1352 | 25 | 2 | 8 | 0 | 2 | 15 | 25 | 2 | 8 | 2800 | 2 | 8 | 0 | 2 | 15 | 2800 | 2 | 8 | 880 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 20.6 | 69.08 | A | 7 | 5 | 41 | A | 7 | 0.36 | A | 7 | 970 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.2 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.7 | 7 | 0
2000-04-22 | 1900-04-21 | 20:00 | 20 | 0 | 56 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 9 | E | 9 | 4 | E | 9 | 19.4 | 66.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.4 | A | 7 | 970 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 2.3 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.68 | 7 | 0
2000-04-22 | 1900-04-21 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 19.4 | 66.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.42 | A | 7 | 970 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 2.3 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.68 | 7 | 0
2000-04-22 | 1900-04-21 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 18.9 | 66.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.43 | A | 7 | 970 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 2.3 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.78 | 7 | 0
2000-04-22 | 1900-04-21 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 6.7 | 44.06 | A | 7 | 0.52 | A | 7 | 969 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 2.4 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.06 | 7 | 0
2000-04-22 | 1900-04-21 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 4 | E | 9 | 17.8 | 64.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.46 | A | 7 | 969 | A | 7 | 250 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 2.4 | E | 8 | 0.124 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.28 | 7 | 0
2000-04-23 | 1900-04-22 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 16.1 | 60.98 | A | 7 | 7.2 | 44.96 | A | 7 | 0.56 | A | 7 | 971 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 2.4 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.46 | 1 | 0
2000-04-23 | 1900-04-22 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 15.6 | 60.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 80 | B | 8 | 1.5 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 2.5 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.04 | 1 | 0
2000-04-23 | 1900-04-22 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 14.4 | 57.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.65 | A | 7 | 970 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 2.5 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.84 | 1 | 0
2000-04-23 | 1900-04-22 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 14.4 | 57.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.65 | A | 7 | 971 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 2.5 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.84 | 1 | 0
2000-04-23 | 1900-04-22 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.77 | A | 7 | 971 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 2286 | A | 7 | 2.6 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.3 | 1 | 0
2000-04-23 | 1900-04-22 | 6:00 | 6 | 27 | 642 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 15 | 59 | A | 7 | 10 | 50 | A | 7 | 0.72 | A | 7 | 969 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2286 | A | 7 | 2.6 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.5 | 1 | 0
2000-04-23 | 1900-04-22 | 7:00 | 7 | 248 | 1351 | 49 | 2 | 8 | 0 | 2 | 15 | 49 | 2 | 8 | 5600 | 2 | 8 | 0 | 2 | 15 | 5600 | 2 | 8 | 1790 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 13 | 55.4 | A | 7 | 10 | 50 | A | 7 | 0.82 | A | 7 | 971 | A | 7 | 100 | A | 7 | 5.1 | A | 7 | 12900 | A | 7 | 750 | A | 7 | 2.6 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.1 | 1 | 0
2000-04-23 | 1900-04-22 | 8:00 | 8 | 508 | 1351 | 108 | 2 | 8 | 0 | 2 | 15 | 108 | 2 | 8 | 12500 | 2 | 8 | 0 | 2 | 15 | 12500 | 2 | 8 | 4380 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 14.4 | 57.92 | A | 7 | 10 | 50 | A | 7 | 0.75 | A | 7 | 970 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 2.6 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46 | 1 | 0
2000-04-23 | 1900-04-22 | 9:00 | 9 | 747 | 1351 | 86 | 2 | 8 | 0 | 2 | 15 | 86 | 2 | 8 | 10600 | 2 | 8 | 0 | 2 | 15 | 10600 | 2 | 8 | 4210 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 14.4 | 57.92 | A | 7 | 11.1 | 51.98 | A | 7 | 0.81 | A | 7 | 971 | A | 7 | 80 | B | 8 | 1.5 | A | 7 | 16000 | A | 7 | 1981 | A | 7 | 2.7 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.78 | 1 | 0
2000-04-23 | 1900-04-22 | 10:00 | 10 | 948 | 1351 | 115 | 2 | 8 | 0 | 2 | 15 | 115 | 2 | 8 | 14300 | 2 | 8 | 0 | 2 | 15 | 14300 | 2 | 8 | 5920 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 15 | 59 | A | 7 | 10 | 50 | A | 7 | 0.72 | A | 7 | 971 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 2.7 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.5 | 1 | 0
2000-04-23 | 1900-04-22 | 11:00 | 11 | 1097 | 1351 | 230 | 2 | 8 | 6 | 2 | 15 | 225 | 2 | 8 | 27700 | 2 | 8 | 500 | 2 | 15 | 27300 | 2 | 8 | 10980 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.1 | 60.98 | A | 7 | 10 | 50 | A | 7 | 0.67 | A | 7 | 971 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 2.7 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.6 | 1 | 0
2000-04-23 | 1900-04-22 | 12:00 | 12 | 1185 | 1351 | 146 | 2 | 8 | 0 | 2 | 15 | 146 | 2 | 8 | 18400 | 2 | 8 | 0 | 2 | 15 | 18400 | 2 | 8 | 7670 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 14.4 | 57.92 | A | 7 | 11.7 | 53.06 | A | 7 | 0.84 | A | 7 | 969 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 823 | A | 7 | 2.7 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.36 | 1 | 0
2000-04-23 | 1900-04-22 | 13:00 | 13 | 1205 | 1351 | 192 | 2 | 8 | 6 | 2 | 15 | 186 | 2 | 8 | 23800 | 2 | 8 | 400 | 2 | 15 | 23400 | 2 | 8 | 9510 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 15.6 | 60.08 | A | 7 | 11.7 | 53.06 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1494 | A | 7 | 2.7 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.36 | 1 | 0
2000-04-23 | 1900-04-22 | 14:00 | 14 | 1155 | 1351 | 547 | 2 | 8 | 167 | 2 | 15 | 404 | 2 | 8 | 60100 | 2 | 8 | 17800 | 2 | 15 | 44900 | 2 | 8 | 16630 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 17.2 | 62.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.72 | A | 7 | 971 | A | 7 | 60 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 2.6 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.06 | 1 | 0
2000-04-23 | 1900-04-22 | 15:00 | 15 | 1040 | 1351 | 433 | 2 | 8 | 89 | 2 | 15 | 364 | 2 | 8 | 47700 | 2 | 8 | 9200 | 2 | 15 | 40600 | 2 | 8 | 13850 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 16.7 | 62.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.72 | A | 7 | 971 | A | 7 | 70 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 2.5 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.26 | 1 | 0
2000-04-23 | 1900-04-22 | 16:00 | 16 | 868 | 1351 | 353 | 2 | 8 | 83 | 2 | 15 | 300 | 2 | 8 | 38900 | 2 | 8 | 8500 | 2 | 15 | 33400 | 2 | 8 | 9930 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 18.3 | 64.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 60 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.4 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.74 | 1 | 0
2000-04-23 | 1900-04-22 | 17:00 | 17 | 649 | 1351 | 236 | 2 | 8 | 58 | 2 | 15 | 208 | 2 | 8 | 25900 | 2 | 8 | 5800 | 2 | 15 | 23100 | 2 | 8 | 6100 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 972 | A | 7 | 70 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 4877 | A | 7 | 2.4 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.96 | 1 | 0
2000-04-23 | 1900-04-22 | 18:00 | 18 | 399 | 1351 | 228 | 2 | 8 | 389 | 2 | 15 | 113 | 2 | 8 | 23500 | 2 | 8 | 34100 | 2 | 15 | 13400 | 2 | 8 | 2150 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.67 | A | 7 | 970 | A | 7 | 80 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.38 | 1 | 0
2000-04-23 | 1900-04-22 | 19:00 | 19 | 138 | 1351 | 54 | 2 | 8 | 276 | 2 | 15 | 26 | 2 | 8 | 5500 | 2 | 8 | 15600 | 2 | 15 | 3900 | 2 | 8 | 470 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.7 | A | 7 | 972 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.08 | 1 | 0
2000-04-23 | 1900-04-22 | 20:00 | 20 | 0 | 79 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 10.6 | 51.08 | A | 7 | 0.75 | A | 7 | 972 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.98 | 1 | 0
2000-04-23 | 1900-04-22 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.48 | 1 | 0
2000-04-23 | 1900-04-22 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.48 | 1 | 0
2000-04-23 | 1900-04-22 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | A | 7 | 11.7 | 53.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.96 | A | 7 | 974 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2743 | A | 7 | 1.9 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 51.28 | 1 | 0
2000-04-23 | 1900-04-22 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 11.7 | 53.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 2896 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.88 | 1 | 0
2000-04-24 | 1900-04-23 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 11.1 | 51.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 30 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 3048 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.58 | 2 | 0
2000-04-24 | 1900-04-23 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 11.7 | 53.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 1829 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.88 | 2 | 0
2000-04-24 | 1900-04-23 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 11.7 | 53.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 9600 | A | 7 | 213 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.88 | 2 | 0
2000-04-24 | 1900-04-23 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 11.7 | 53.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 20 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 183 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.88 | 2 | 0
2000-04-24 | 1900-04-23 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 10.6 | 51.08 | A | 7 | 10 | 50 | A | 7 | 0.96 | A | 7 | 976 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 2800 | A | 7 | 183 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.3 | 2 | 0
2000-04-24 | 1900-04-23 | 6:00 | 6 | 29 | 664 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | B | 8 | 10 | B | 8 | 10.6 | 51.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.86 | A | 7 | 977 | A | 7 | 30 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 335 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.84 | 2 | 0
2000-04-24 | 1900-04-23 | 7:00 | 7 | 253 | 1350 | 39 | 2 | 8 | 0 | 2 | 15 | 39 | 2 | 8 | 4500 | 2 | 8 | 0 | 2 | 15 | 4500 | 2 | 8 | 1510 | 2 | 19 | 10 | B | 8 | 10 | B | 8 | 9.4 | 48.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 40 | A | 7 | 5.7 | A | 7 | 12800 | A | 7 | 305 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.54 | 2 | 0
2000-04-24 | 1900-04-23 | 8:00 | 8 | 512 | 1350 | 101 | 2 | 8 | 0 | 2 | 15 | 101 | 2 | 8 | 11700 | 2 | 8 | 0 | 2 | 15 | 11700 | 2 | 8 | 4180 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10.6 | 51.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.79 | A | 7 | 979 | A | 7 | 40 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 488 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.96 | 2 | 0
2000-04-24 | 1900-04-23 | 9:00 | 9 | 751 | 1350 | 199 | 2 | 8 | 6 | 2 | 15 | 196 | 2 | 8 | 23000 | 2 | 8 | 500 | 2 | 15 | 22700 | 2 | 8 | 8330 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 11.7 | 53.06 | A | 7 | 7.2 | 44.96 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 50 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 488 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.16 | 2 | 0
2000-04-24 | 1900-04-23 | 10:00 | 10 | 951 | 1350 | 568 | 2 | 8 | 328 | 2 | 15 | 336 | 2 | 8 | 61000 | 2 | 8 | 35300 | 2 | 15 | 36100 | 2 | 8 | 9910 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 12.8 | 55.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 50 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 671 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.84 | 2 | 0
2000-04-24 | 1900-04-23 | 11:00 | 11 | 1100 | 1350 | 696 | 2 | 8 | 471 | 2 | 15 | 312 | 2 | 8 | 74200 | 2 | 8 | 49100 | 2 | 15 | 34100 | 2 | 8 | 11920 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 16.1 | 60.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 60 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 914 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.84 | 2 | 0
2000-04-24 | 1900-04-23 | 12:00 | 12 | 1188 | 1350 | 835 | 2 | 8 | 571 | 2 | 15 | 331 | 2 | 8 | 89400 | 2 | 8 | 59700 | 2 | 15 | 36800 | 2 | 8 | 16280 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 15 | 59 | A | 7 | 7.2 | 44.96 | A | 7 | 0.6 | A | 7 | 979 | A | 7 | 60 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 975 | A | 7 | 1.8 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.06 | 2 | 0
2000-04-24 | 1900-04-23 | 13:00 | 13 | 1207 | 1350 | 671 | 2 | 8 | 300 | 2 | 15 | 402 | 2 | 8 | 73500 | 2 | 8 | 32600 | 2 | 15 | 44200 | 2 | 8 | 19540 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 15.6 | 60.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1158 | A | 7 | 1.7 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.66 | 2 | 0
2000-04-24 | 1900-04-23 | 14:00 | 14 | 1158 | 1350 | 359 | 2 | 8 | 24 | 2 | 15 | 338 | 2 | 8 | 42300 | 2 | 8 | 2200 | 2 | 15 | 40400 | 2 | 8 | 15190 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 16.1 | 60.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1311 | A | 7 | 1.7 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.74 | 2 | 0
2000-04-24 | 1900-04-23 | 15:00 | 15 | 1043 | 1350 | 323 | 2 | 8 | 18 | 2 | 15 | 309 | 2 | 8 | 37700 | 2 | 8 | 1600 | 2 | 15 | 36500 | 2 | 8 | 13740 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.1 | 60.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 1311 | A | 7 | 1.7 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.84 | 2 | 0
2000-04-24 | 1900-04-23 | 16:00 | 16 | 870 | 1350 | 292 | 2 | 8 | 24 | 2 | 15 | 277 | 2 | 8 | 33500 | 2 | 8 | 2200 | 2 | 15 | 32100 | 2 | 8 | 11540 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.1 | 60.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1311 | A | 7 | 1.6 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.74 | 2 | 0
2000-04-24 | 1900-04-23 | 17:00 | 17 | 652 | 1350 | 183 | 2 | 8 | 18 | 2 | 15 | 174 | 2 | 8 | 20900 | 2 | 8 | 1400 | 2 | 15 | 20200 | 2 | 8 | 7070 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.1 | 60.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 1341 | A | 7 | 1.6 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.74 | 2 | 0
2000-04-24 | 1900-04-23 | 18:00 | 18 | 403 | 1350 | 195 | 2 | 8 | 237 | 2 | 15 | 124 | 2 | 8 | 20500 | 2 | 8 | 21300 | 2 | 15 | 14100 | 2 | 8 | 2520 | 2 | 19 | 9 | E | 9 | 7 | A | 7 | 16.1 | 60.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1372 | A | 7 | 1.5 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.74 | 2 | 0
2000-04-24 | 1900-04-23 | 19:00 | 19 | 142 | 1350 | 55 | 2 | 8 | 207 | 2 | 15 | 33 | 2 | 8 | 5700 | 2 | 8 | 10900 | 2 | 15 | 4600 | 2 | 8 | 590 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 14.4 | 57.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.84 | 2 | 0
2000-04-24 | 1900-04-23 | 20:00 | 20 | 1 | 101 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 80 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.76 | 2 | 0
2000-04-24 | 1900-04-23 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 310 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.46 | 2 | 0
2000-04-24 | 1900-04-23 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.76 | 2 | 0
2000-04-24 | 1900-04-23 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 5 | A | 7 | 11.7 | 53.06 | A | 7 | 7.2 | 44.96 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.16 | 2 | 0
2000-04-24 | 1900-04-23 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 6.7 | 44.06 | A | 7 | 0.8 | A | 7 | 981 | A | 7 | 290 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.125 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.26 | 2 | 0
2000-04-25 | 1900-04-24 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 9.4 | 48.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.8 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.18 | 3 | 0
2000-04-25 | 1900-04-24 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | E | 9 | 9.4 | 48.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.83 | A | 7 | 982 | A | 7 | 60 | A | 7 | 1.5 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.66 | 3 | 0
2000-04-25 | 1900-04-24 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 2 | E | 9 | 10 | 50 | A | 7 | 7.2 | 44.96 | A | 7 | 0.83 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11200 | A | 7 | 6096 | A | 7 | 1.4 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.46 | 3 | 0
2000-04-25 | 1900-04-24 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | E | 9 | 6.7 | 44.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 9600 | A | 7 | 2896 | A | 7 | 1.5 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.38 | 3 | 0
2000-04-25 | 1900-04-24 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 4 | E | 9 | 6.7 | 44.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.08 | 3 | 0
2000-04-25 | 1900-04-24 | 6:00 | 6 | 32 | 708 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 8 | E | 9 | 7 | E | 9 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 9600 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.06 | 3 | 0
2000-04-25 | 1900-04-24 | 7:00 | 7 | 258 | 1349 | 29 | 2 | 8 | 0 | 2 | 15 | 29 | 2 | 8 | 3500 | 2 | 8 | 0 | 2 | 15 | 3500 | 2 | 8 | 1180 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9600 | A | 7 | 2896 | A | 7 | 1.6 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.34 | 3 | 0
2000-04-25 | 1900-04-24 | 8:00 | 8 | 517 | 1349 | 187 | 2 | 8 | 57 | 2 | 15 | 165 | 2 | 8 | 20500 | 2 | 8 | 5500 | 2 | 15 | 18400 | 2 | 8 | 4510 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.89 | A | 7 | 984 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 9600 | A | 7 | 2591 | A | 7 | 1.7 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.22 | 3 | 0
2000-04-25 | 1900-04-24 | 9:00 | 9 | 755 | 1349 | 232 | 2 | 8 | 12 | 2 | 15 | 225 | 2 | 8 | 26500 | 2 | 8 | 1000 | 2 | 15 | 25900 | 2 | 8 | 9200 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 11.7 | 53.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.83 | A | 7 | 985 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 9600 | A | 7 | 2438 | A | 7 | 1.7 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.42 | 3 | 0
2000-04-25 | 1900-04-24 | 10:00 | 10 | 955 | 1349 | 268 | 2 | 8 | 12 | 2 | 15 | 259 | 2 | 8 | 31300 | 2 | 8 | 1000 | 2 | 15 | 30500 | 2 | 8 | 11610 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 11.7 | 53.06 | A | 7 | 10 | 50 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 1829 | A | 7 | 1.8 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.2 | 3 | 0
2000-04-25 | 1900-04-24 | 11:00 | 11 | 1104 | 1349 | 137 | 2 | 8 | 0 | 2 | 15 | 137 | 2 | 8 | 17200 | 2 | 8 | 0 | 2 | 15 | 17200 | 2 | 8 | 7190 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.84 | A | 7 | 985 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 9600 | A | 7 | 1829 | A | 7 | 1.8 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.48 | 3 | 0
2000-04-25 | 1900-04-24 | 12:00 | 12 | 1191 | 1349 | 427 | 2 | 8 | 36 | 2 | 15 | 395 | 2 | 8 | 47100 | 2 | 8 | 3700 | 2 | 15 | 43900 | 2 | 8 | 18290 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 14.4 | 57.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.78 | A | 7 | 983 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 1829 | A | 7 | 1.9 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.48 | 3 | 0
2000-04-25 | 1900-04-24 | 13:00 | 13 | 1210 | 1349 | 431 | 2 | 8 | 30 | 2 | 15 | 404 | 2 | 8 | 47600 | 2 | 8 | 3100 | 2 | 15 | 44800 | 2 | 8 | 19330 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.1 | 60.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.64 | A | 7 | 985 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.8 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.22 | 3 | 0
2000-04-25 | 1900-04-24 | 14:00 | 14 | 1161 | 1349 | 306 | 2 | 8 | 24 | 2 | 15 | 285 | 2 | 8 | 33900 | 2 | 8 | 2400 | 2 | 15 | 31800 | 2 | 8 | 13120 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 17.8 | 64.04 | A | 7 | 9.4 | 48.92 | A | 7 | 0.58 | A | 7 | 984 | A | 7 | 80 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.8 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.22 | 3 | 0
2000-04-25 | 1900-04-24 | 15:00 | 15 | 1046 | 1349 | 756 | 2 | 8 | 554 | 2 | 15 | 325 | 2 | 8 | 79500 | 2 | 8 | 57600 | 2 | 15 | 34800 | 2 | 8 | 11060 | 2 | 19 | 7 | E | 9 | 7 | E | 9 | 18.3 | 64.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.54 | A | 7 | 983 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.72 | 3 | 0
2000-04-25 | 1900-04-24 | 16:00 | 16 | 873 | 1349 | 348 | 2 | 8 | 89 | 2 | 15 | 290 | 2 | 8 | 38300 | 2 | 8 | 9100 | 2 | 15 | 32400 | 2 | 8 | 9730 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 18.3 | 64.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.54 | 3 | 0
2000-04-25 | 1900-04-24 | 17:00 | 17 | 655 | 1349 | 419 | 2 | 8 | 486 | 2 | 15 | 183 | 2 | 8 | 43800 | 2 | 8 | 48400 | 2 | 15 | 20200 | 2 | 8 | 3860 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 18.3 | 64.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 110 | B | 8 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.54 | 3 | 0
2000-04-25 | 1900-04-24 | 18:00 | 18 | 406 | 1349 | 224 | 2 | 8 | 373 | 2 | 15 | 112 | 2 | 8 | 23200 | 2 | 8 | 32900 | 2 | 15 | 13200 | 2 | 8 | 2130 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.14 | 3 | 0
2000-04-25 | 1900-04-24 | 19:00 | 19 | 145 | 1349 | 36 | 2 | 8 | 43 | 2 | 15 | 31 | 2 | 8 | 3900 | 2 | 8 | 2500 | 2 | 15 | 3700 | 2 | 8 | 650 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 14.4 | 57.92 | A | 7 | 9.4 | 48.92 | A | 7 | 0.72 | A | 7 | 983 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.52 | 3 | 0
2000-04-25 | 1900-04-24 | 20:00 | 20 | 1 | 124 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 14.4 | 57.92 | A | 7 | 9.4 | 48.92 | A | 7 | 0.72 | A | 7 | 983 | A | 7 | 260 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.52 | 3 | 0
2000-04-25 | 1900-04-24 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 9.4 | 48.92 | A | 7 | 0.77 | A | 7 | 984 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.32 | 3 | 0
2000-04-25 | 1900-04-24 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.83 | A | 7 | 984 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.22 | 3 | 0
2000-04-25 | 1900-04-24 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.86 | A | 7 | 985 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.72 | 3 | 0
2000-04-25 | 1900-04-24 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.126 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.62 | 3 | 0
2000-04-26 | 1900-04-25 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.22 | 4 | 0
2000-04-26 | 1900-04-25 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.97 | A | 7 | 984 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.52 | 4 | 0
2000-04-26 | 1900-04-25 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 8.3 | 46.94 | A | 7 | 0.96 | A | 7 | 984 | A | 7 | 20 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.34 | 4 | 0
2000-04-26 | 1900-04-25 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 8.3 | 46.94 | A | 7 | 0.96 | A | 7 | 985 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.34 | 4 | 0
2000-04-26 | 1900-04-25 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.97 | A | 7 | 985 | A | 7 | 10 | B | 8 | 2.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.54 | 4 | 0
2000-04-26 | 1900-04-25 | 6:00 | 6 | 35 | 731 | 1 | 2 | 8 | 66 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.94 | 4 | 0
2000-04-26 | 1900-04-25 | 7:00 | 7 | 264 | 1349 | 151 | 2 | 8 | 368 | 2 | 15 | 79 | 2 | 8 | 15300 | 2 | 8 | 27100 | 2 | 15 | 10000 | 2 | 8 | 1480 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 8.9 | 48.02 | A | 7 | 0.86 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.82 | 4 | 0
2000-04-26 | 1900-04-25 | 8:00 | 8 | 522 | 1349 | 352 | 2 | 8 | 624 | 2 | 15 | 110 | 2 | 8 | 36100 | 2 | 8 | 58200 | 2 | 15 | 13600 | 2 | 8 | 2080 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 14.4 | 57.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.7 | A | 7 | 986 | A | 7 | 0 | A | 7 | 0 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.32 | 4 | 0
2000-04-26 | 1900-04-25 | 9:00 | 9 | 759 | 1349 | 543 | 2 | 8 | 736 | 2 | 15 | 128 | 2 | 8 | 57300 | 2 | 8 | 73700 | 2 | 15 | 15700 | 2 | 8 | 2920 | 2 | 19 | 1 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.48 | A | 7 | 986 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.46 | 4 | 0
2000-04-26 | 1900-04-25 | 10:00 | 10 | 959 | 1349 | 694 | 2 | 8 | 765 | 2 | 15 | 150 | 2 | 8 | 74300 | 2 | 8 | 78200 | 2 | 15 | 18600 | 2 | 8 | 4360 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 18.9 | 66.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.38 | A | 7 | 986 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 31.12 | 4 | 0
2000-04-26 | 1900-04-25 | 11:00 | 11 | 1107 | 1349 | 820 | 2 | 8 | 700 | 2 | 15 | 244 | 2 | 8 | 86100 | 2 | 8 | 70700 | 2 | 15 | 27900 | 2 | 8 | 9180 | 2 | 19 | 8 | E | 9 | 4 | E | 9 | 20 | 68 | A | 7 | 2.8 | 37.04 | A | 7 | 0.32 | A | 7 | 986 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 28.14 | 4 | 0
2000-04-26 | 1900-04-25 | 12:00 | 12 | 1193 | 1349 | 591 | 2 | 8 | 192 | 2 | 15 | 420 | 2 | 8 | 64900 | 2 | 8 | 20500 | 2 | 15 | 46800 | 2 | 8 | 18970 | 2 | 19 | 7 | E | 9 | 3 | E | 9 | 20 | 68 | A | 7 | 4.4 | 39.92 | A | 7 | 0.36 | A | 7 | 984 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.92 | 4 | 0
2000-04-26 | 1900-04-25 | 13:00 | 13 | 1213 | 1349 | 851 | 2 | 8 | 546 | 2 | 15 | 359 | 2 | 8 | 90800 | 2 | 8 | 57000 | 2 | 15 | 39400 | 2 | 8 | 19490 | 2 | 19 | 6 | E | 9 | 5 | E | 9 | 21.1 | 69.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.32 | A | 7 | 985 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.62 | 4 | 0
2000-04-26 | 1900-04-25 | 14:00 | 14 | 1163 | 1349 | 865 | 2 | 8 | 718 | 2 | 15 | 245 | 2 | 8 | 91400 | 2 | 8 | 72800 | 2 | 15 | 28400 | 2 | 8 | 10850 | 2 | 19 | 4 | E | 9 | 3 | E | 9 | 21.7 | 71.06 | A | 7 | 3.9 | 39.02 | A | 7 | 0.31 | A | 7 | 985 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 29.52 | 4 | 0
2000-04-26 | 1900-04-25 | 15:00 | 15 | 1048 | 1349 | 744 | 2 | 8 | 566 | 2 | 15 | 303 | 2 | 8 | 78900 | 2 | 8 | 58900 | 2 | 15 | 33000 | 2 | 8 | 10320 | 2 | 19 | 7 | E | 9 | 5 | E | 9 | 20.6 | 69.08 | A | 7 | 4.4 | 39.92 | A | 7 | 0.34 | A | 7 | 984 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 30.62 | 4 | 0
2000-04-26 | 1900-04-25 | 16:00 | 16 | 876 | 1349 | 275 | 2 | 8 | 59 | 2 | 15 | 237 | 2 | 8 | 30400 | 2 | 8 | 6000 | 2 | 15 | 26500 | 2 | 8 | 8280 | 2 | 19 | 5 | E | 9 | 3 | E | 9 | 21.7 | 71.06 | A | 7 | 6.7 | 44.06 | A | 7 | 0.38 | A | 7 | 983 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.86 | 4 | 0
2000-04-26 | 1900-04-25 | 17:00 | 17 | 658 | 1349 | 349 | 2 | 8 | 181 | 2 | 15 | 261 | 2 | 8 | 37500 | 2 | 8 | 18400 | 2 | 15 | 28600 | 2 | 8 | 6450 | 2 | 19 | 7 | E | 9 | 6 | E | 9 | 20 | 68 | A | 7 | 7.8 | 46.04 | A | 7 | 0.45 | A | 7 | 983 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.2 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.64 | 4 | 0
2000-04-26 | 1900-04-25 | 18:00 | 18 | 409 | 1349 | 39 | 2 | 8 | 0 | 2 | 15 | 39 | 2 | 8 | 4800 | 2 | 8 | 0 | 2 | 15 | 4800 | 2 | 8 | 1720 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.47 | A | 7 | 981 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.2 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.06 | 4 | 0
2000-04-26 | 1900-04-25 | 19:00 | 19 | 149 | 1349 | 10 | 2 | 8 | 0 | 2 | 15 | 10 | 2 | 8 | 1200 | 2 | 8 | 0 | 2 | 15 | 1200 | 2 | 8 | 410 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 17.2 | 62.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.56 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 1.2 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.14 | 4 | 0
2000-04-26 | 1900-04-25 | 20:00 | 20 | 1 | 146 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.1 | 60.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 1.1 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 40.84 | 4 | 0
2000-04-26 | 1900-04-25 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 16.1 | 60.98 | A | 7 | 8.9 | 48.02 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 1.1 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.02 | 4 | 0
2000-04-26 | 1900-04-25 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | E | 9 | 13 | 55.4 | A | 7 | 11 | 51.8 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 2700 | A | 7 | 1.1 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.8 | 4 | 0
2000-04-26 | 1900-04-25 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 14.4 | 57.92 | A | 7 | 10 | 50 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 2743 | A | 7 | 1.1 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46 | 4 | 0
2000-04-26 | 1900-04-25 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | E | 9 | 14.4 | 57.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 1 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.48 | 4 | 0
2000-04-27 | 1900-04-26 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 13.3 | 55.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.1 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.78 | 5 | 0
2000-04-27 | 1900-04-26 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 12.2 | 53.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 360 | A | 7 | 5.7 | A | 7 | 12800 | A | 7 | 1463 | A | 7 | 1.1 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.78 | 5 | 0
2000-04-27 | 1900-04-26 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 49.88 | 5 | 0
2000-04-27 | 1900-04-26 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 978 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.22 | 5 | 0
2000-04-27 | 1900-04-26 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 977 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.22 | 5 | 0
2000-04-27 | 1900-04-26 | 6:00 | 6 | 38 | 753 | 2 | 2 | 8 | 79 | 2 | 15 | 1 | 2 | 8 | 600 | 2 | 8 | 4500 | 2 | 15 | 400 | 2 | 8 | 40 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.83 | A | 7 | 976 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.54 | 5 | 0
2000-04-27 | 1900-04-26 | 7:00 | 7 | 269 | 1348 | 158 | 2 | 8 | 401 | 2 | 15 | 78 | 2 | 8 | 16100 | 2 | 8 | 29900 | 2 | 15 | 10200 | 2 | 8 | 1450 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.74 | A | 7 | 977 | A | 7 | 290 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.14 | 5 | 0
2000-04-27 | 1900-04-26 | 8:00 | 8 | 526 | 1348 | 358 | 2 | 8 | 642 | 2 | 15 | 107 | 2 | 8 | 36900 | 2 | 8 | 60100 | 2 | 15 | 13400 | 2 | 8 | 2040 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 14.4 | 57.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.62 | A | 7 | 977 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.36 | 5 | 0
2000-04-27 | 1900-04-26 | 9:00 | 9 | 763 | 1348 | 563 | 2 | 8 | 797 | 2 | 15 | 110 | 2 | 8 | 58300 | 2 | 8 | 78700 | 2 | 15 | 13600 | 2 | 8 | 2360 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 7.2 | 44.96 | A | 7 | 0.56 | A | 7 | 977 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.46 | 5 | 0
2000-04-27 | 1900-04-26 | 10:00 | 10 | 962 | 1348 | 726 | 2 | 8 | 837 | 2 | 15 | 127 | 2 | 8 | 76500 | 2 | 8 | 84200 | 2 | 15 | 16300 | 2 | 8 | 3480 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 17.2 | 62.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.5 | A | 7 | 977 | A | 7 | 310 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.76 | 5 | 0
2000-04-27 | 1900-04-26 | 11:00 | 11 | 1110 | 1348 | 845 | 2 | 8 | 742 | 2 | 15 | 232 | 2 | 8 | 89000 | 2 | 8 | 75200 | 2 | 15 | 26900 | 2 | 8 | 8860 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 17.8 | 64.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.48 | A | 7 | 977 | A | 7 | 300 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 1.4 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.46 | 5 | 0
2000-04-27 | 1900-04-26 | 12:00 | 12 | 1196 | 1348 | 579 | 2 | 8 | 283 | 2 | 15 | 327 | 2 | 8 | 64300 | 2 | 8 | 30800 | 2 | 15 | 36900 | 2 | 8 | 15130 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 15.6 | 60.08 | A | 7 | 6.7 | 44.06 | A | 7 | 0.55 | A | 7 | 975 | A | 7 | 310 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 1311 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.56 | 5 | 0
2000-04-27 | 1900-04-26 | 13:00 | 13 | 1215 | 1348 | 162 | 2 | 8 | 6 | 2 | 15 | 156 | 2 | 8 | 20300 | 2 | 8 | 400 | 2 | 15 | 19900 | 2 | 8 | 8160 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 14.4 | 57.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 1067 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.94 | 5 | 0
2000-04-27 | 1900-04-26 | 14:00 | 14 | 1166 | 1348 | 159 | 2 | 8 | 6 | 2 | 15 | 154 | 2 | 8 | 19900 | 2 | 8 | 400 | 2 | 15 | 19600 | 2 | 8 | 8030 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.1 | 60.98 | A | 7 | 10 | 50 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 320 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 792 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.6 | 5 | 0
2000-04-27 | 1900-04-26 | 15:00 | 15 | 1051 | 1348 | 542 | 2 | 8 | 244 | 2 | 15 | 352 | 2 | 8 | 58900 | 2 | 8 | 26400 | 2 | 15 | 38200 | 2 | 8 | 11910 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 17.8 | 64.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 320 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.88 | 5 | 0
2000-04-27 | 1900-04-26 | 16:00 | 16 | 879 | 1348 | 438 | 2 | 8 | 190 | 2 | 15 | 314 | 2 | 8 | 47700 | 2 | 8 | 20000 | 2 | 15 | 34700 | 2 | 8 | 8960 | 2 | 19 | 9 | B | 8 | 9 | B | 8 | 16.7 | 62.06 | A | 7 | 10 | 50 | A | 7 | 0.65 | A | 7 | 978 | A | 7 | 330 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 1036 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.3 | 5 | 0
2000-04-27 | 1900-04-26 | 17:00 | 17 | 661 | 1348 | 156 | 2 | 8 | 6 | 2 | 15 | 153 | 2 | 8 | 18100 | 2 | 8 | 500 | 2 | 15 | 17800 | 2 | 8 | 6490 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 914 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.86 | 5 | 0
2000-04-27 | 1900-04-26 | 18:00 | 18 | 413 | 1348 | 113 | 2 | 8 | 6 | 2 | 15 | 111 | 2 | 8 | 12700 | 2 | 8 | 400 | 2 | 15 | 12600 | 2 | 8 | 4040 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 340 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.48 | 5 | 0
2000-04-27 | 1900-04-26 | 19:00 | 19 | 153 | 1348 | 30 | 2 | 8 | 0 | 2 | 15 | 30 | 2 | 8 | 3400 | 2 | 8 | 0 | 2 | 15 | 3400 | 2 | 8 | 1060 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 14.4 | 57.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1433 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.48 | 5 | 0
2000-04-27 | 1900-04-26 | 20:00 | 20 | 2 | 168 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 2286 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.3 | 5 | 0
2000-04-27 | 1900-04-26 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 12.8 | 55.04 | A | 7 | 10 | 50 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.3 | 5 | 0
2000-04-27 | 1900-04-26 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 10 | 50 | A | 7 | 0.89 | A | 7 | 981 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.2 | 5 | 0
2000-04-27 | 1900-04-26 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 10 | 50 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.9 | 5 | 0
2000-04-27 | 1900-04-26 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.127 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.52 | 5 | 0
2000-04-28 | 1900-04-27 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 360 | A | 7 | 1.5 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.22 | 6 | 0
2000-04-28 | 1900-04-27 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 8.9 | 48.02 | A | 7 | 1 | A | 7 | 981 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.02 | 6 | 0
2000-04-28 | 1900-04-27 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8 | 46.4 | A | 7 | 8 | 46.4 | A | 7 | 1 | A | 7 | 981 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.3 | 6 | 0
2000-04-28 | 1900-04-27 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 981 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.84 | 6 | 0
2000-04-28 | 1900-04-27 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 981 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.84 | 6 | 0
2000-04-28 | 1900-04-27 | 6:00 | 6 | 40 | 797 | 2 | 2 | 8 | 58 | 2 | 15 | 1 | 2 | 8 | 500 | 2 | 8 | 3300 | 2 | 15 | 300 | 2 | 8 | 40 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 981 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 2400 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 46.84 | 6 | 0
2000-04-28 | 1900-04-27 | 7:00 | 7 | 273 | 1347 | 157 | 2 | 8 | 273 | 2 | 15 | 101 | 2 | 8 | 16100 | 2 | 8 | 20500 | 2 | 15 | 12000 | 2 | 8 | 2080 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 8.9 | 48.02 | A | 7 | 1 | A | 7 | 982 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 800 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.02 | 6 | 0
2000-04-28 | 1900-04-27 | 8:00 | 8 | 531 | 1347 | 314 | 2 | 8 | 365 | 2 | 15 | 170 | 2 | 8 | 33200 | 2 | 8 | 35900 | 2 | 15 | 19000 | 2 | 8 | 3630 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 11.7 | 53.06 | A | 7 | 11.7 | 53.06 | A | 7 | 1 | A | 7 | 983 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 2800 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 52.96 | 6 | 0
2000-04-28 | 1900-04-27 | 9:00 | 9 | 767 | 1347 | 377 | 2 | 8 | 178 | 2 | 15 | 276 | 2 | 8 | 41000 | 2 | 8 | 18500 | 2 | 15 | 30400 | 2 | 8 | 7260 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 983 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 50.86 | 6 | 0
2000-04-28 | 1900-04-27 | 10:00 | 10 | 966 | 1347 | 719 | 2 | 8 | 716 | 2 | 15 | 205 | 2 | 8 | 75300 | 2 | 8 | 72200 | 2 | 15 | 23400 | 2 | 8 | 5810 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.75 | A | 7 | 983 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 48.76 | 6 | 0
2000-04-28 | 1900-04-27 | 11:00 | 11 | 1113 | 1347 | 857 | 2 | 8 | 863 | 2 | 15 | 142 | 2 | 8 | 91100 | 2 | 8 | 87300 | 2 | 15 | 18800 | 2 | 8 | 5270 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 18.9 | 66.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.38 | 6 | 0
2000-04-28 | 1900-04-27 | 12:00 | 12 | 1199 | 1347 | 932 | 2 | 8 | 794 | 2 | 15 | 224 | 2 | 8 | 99400 | 2 | 8 | 81100 | 2 | 15 | 27100 | 2 | 8 | 11340 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 20.6 | 69.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.44 | A | 7 | 981 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.44 | 6 | 0
2000-04-28 | 1900-04-27 | 13:00 | 13 | 1218 | 1347 | 785 | 2 | 8 | 444 | 2 | 15 | 383 | 2 | 8 | 83200 | 2 | 8 | 46300 | 2 | 15 | 41300 | 2 | 8 | 21380 | 2 | 19 | 5 | E | 9 | 4 | E | 9 | 21.7 | 71.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.42 | A | 7 | 983 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.84 | 6 | 0
2000-04-28 | 1900-04-27 | 14:00 | 14 | 1168 | 1347 | 330 | 2 | 8 | 30 | 2 | 15 | 304 | 2 | 8 | 36500 | 2 | 8 | 3100 | 2 | 15 | 33900 | 2 | 8 | 14080 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 22.2 | 71.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.4 | A | 7 | 982 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 2.1 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.74 | 6 | 0
2000-04-28 | 1900-04-27 | 15:00 | 15 | 1053 | 1347 | 404 | 2 | 8 | 77 | 2 | 15 | 343 | 2 | 8 | 44500 | 2 | 8 | 7900 | 2 | 15 | 38300 | 2 | 8 | 13430 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 21.7 | 71.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.42 | A | 7 | 981 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 2 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.84 | 6 | 0
2000-04-28 | 1900-04-27 | 16:00 | 16 | 881 | 1347 | 629 | 2 | 8 | 628 | 2 | 15 | 218 | 2 | 8 | 67300 | 2 | 8 | 64900 | 2 | 15 | 24800 | 2 | 8 | 5590 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 21.1 | 69.98 | A | 7 | 7.2 | 44.96 | A | 7 | 0.41 | A | 7 | 981 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.06 | 6 | 0
2000-04-28 | 1900-04-27 | 17:00 | 17 | 664 | 1347 | 425 | 2 | 8 | 369 | 2 | 15 | 243 | 2 | 8 | 44800 | 2 | 8 | 38000 | 2 | 15 | 26000 | 2 | 8 | 5700 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 20 | 68 | A | 7 | 7.8 | 46.04 | A | 7 | 0.45 | A | 7 | 981 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.64 | 6 | 0
2000-04-28 | 1900-04-27 | 18:00 | 18 | 416 | 1347 | 39 | 2 | 8 | 0 | 2 | 15 | 39 | 2 | 8 | 4800 | 2 | 8 | 0 | 2 | 15 | 4800 | 2 | 8 | 1730 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 20 | 68 | A | 7 | 7.2 | 44.96 | A | 7 | 0.43 | A | 7 | 978 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.36 | 6 | 0
2000-04-28 | 1900-04-27 | 19:00 | 19 | 157 | 1347 | 10 | 2 | 8 | 0 | 2 | 15 | 10 | 2 | 8 | 1200 | 2 | 8 | 0 | 2 | 15 | 1200 | 2 | 8 | 410 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 17.8 | 64.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.74 | 6 | 0
2000-04-28 | 1900-04-27 | 20:00 | 20 | 2 | 191 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 17.2 | 62.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.5 | A | 7 | 981 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.76 | 6 | 0
2000-04-28 | 1900-04-27 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 16.7 | 62.06 | A | 7 | 6.7 | 44.06 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.06 | 6 | 0
2000-04-28 | 1900-04-27 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 350 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.98 | 6 | 0
2000-04-28 | 1900-04-27 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 6.1 | 42.98 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 360 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.58 | 6 | 0
2000-04-28 | 1900-04-27 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 6.7 | 44.06 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.128 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.96 | 6 | 0
2000-04-29 | 1900-04-28 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 14.4 | 57.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.88 | 7 | 0
2000-04-29 | 1900-04-28 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.48 | 7 | 0
2000-04-29 | 1900-04-28 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.08 | 7 | 0
2000-04-29 | 1900-04-28 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 9.4 | 48.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.98 | 7 | 0
2000-04-29 | 1900-04-28 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.9 | 7 | 0
2000-04-29 | 1900-04-28 | 6:00 | 6 | 43 | 819 | 3 | 2 | 8 | 93 | 2 | 15 | 2 | 2 | 8 | 800 | 2 | 8 | 5400 | 2 | 15 | 500 | 2 | 8 | 80 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 5 | 41 | A | 7 | 0.8 | A | 7 | 982 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.3 | 7 | 0
2000-04-29 | 1900-04-28 | 7:00 | 7 | 278 | 1347 | 164 | 2 | 8 | 404 | 2 | 15 | 80 | 2 | 8 | 16700 | 2 | 8 | 30600 | 2 | 15 | 10400 | 2 | 8 | 1490 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 984 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.08 | 7 | 0
2000-04-29 | 1900-04-28 | 8:00 | 8 | 535 | 1347 | 363 | 2 | 8 | 641 | 2 | 15 | 108 | 2 | 8 | 37400 | 2 | 8 | 60300 | 2 | 15 | 13400 | 2 | 8 | 2070 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.64 | A | 7 | 984 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.86 | 7 | 0
2000-04-29 | 1900-04-28 | 9:00 | 9 | 771 | 1347 | 562 | 2 | 8 | 766 | 2 | 15 | 122 | 2 | 8 | 59500 | 2 | 8 | 77000 | 2 | 15 | 15300 | 2 | 8 | 2840 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.56 | A | 7 | 984 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.34 | 7 | 0
2000-04-29 | 1900-04-28 | 10:00 | 10 | 969 | 1347 | 732 | 2 | 8 | 813 | 2 | 15 | 146 | 2 | 8 | 76100 | 2 | 8 | 81300 | 2 | 15 | 17500 | 2 | 8 | 3860 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 19.4 | 66.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.44 | A | 7 | 985 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.86 | 7 | 0
2000-04-29 | 1900-04-28 | 11:00 | 11 | 1116 | 1347 | 863 | 2 | 8 | 875 | 2 | 15 | 136 | 2 | 8 | 88500 | 2 | 8 | 87500 | 2 | 15 | 15900 | 2 | 8 | 3970 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 6.7 | 44.06 | A | 7 | 0.42 | A | 7 | 985 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.56 | 7 | 0
2000-04-29 | 1900-04-28 | 12:00 | 12 | 1201 | 1347 | 932 | 2 | 8 | 878 | 2 | 15 | 147 | 2 | 8 | 95400 | 2 | 8 | 87900 | 2 | 15 | 16800 | 2 | 8 | 5610 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 21.1 | 69.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.39 | A | 7 | 982 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.06 | 7 | 0
2000-04-29 | 1900-04-28 | 13:00 | 13 | 1220 | 1347 | 952 | 2 | 8 | 882 | 2 | 15 | 152 | 2 | 8 | 97400 | 2 | 8 | 88300 | 2 | 15 | 17200 | 2 | 8 | 6210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.37 | A | 7 | 984 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.76 | 7 | 0
2000-04-29 | 1900-04-28 | 14:00 | 14 | 1170 | 1347 | 913 | 2 | 8 | 879 | 2 | 15 | 147 | 2 | 8 | 93400 | 2 | 8 | 87900 | 2 | 15 | 16800 | 2 | 8 | 4940 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.35 | A | 7 | 984 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.46 | 7 | 0
2000-04-29 | 1900-04-28 | 15:00 | 15 | 1056 | 1347 | 802 | 2 | 8 | 817 | 2 | 15 | 161 | 2 | 8 | 83600 | 2 | 8 | 81900 | 2 | 15 | 19200 | 2 | 8 | 4980 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.35 | A | 7 | 983 | A | 7 | 110 | B | 8 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.16 | 7 | 0
2000-04-29 | 1900-04-28 | 16:00 | 16 | 884 | 1347 | 641 | 2 | 8 | 764 | 2 | 15 | 138 | 2 | 8 | 68300 | 2 | 8 | 77700 | 2 | 15 | 17100 | 2 | 8 | 3620 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.33 | A | 7 | 983 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.58 | 7 | 0
2000-04-29 | 1900-04-28 | 17:00 | 17 | 667 | 1347 | 447 | 2 | 8 | 662 | 2 | 15 | 119 | 2 | 8 | 46800 | 2 | 8 | 65100 | 2 | 15 | 14500 | 2 | 8 | 2510 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.33 | A | 7 | 982 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.58 | 7 | 0
2000-04-29 | 1900-04-28 | 18:00 | 18 | 420 | 1347 | 251 | 2 | 8 | 539 | 2 | 15 | 83 | 2 | 8 | 25800 | 2 | 8 | 47800 | 2 | 15 | 10900 | 2 | 8 | 1530 | 2 | 19 | 10 | E | 9 | 5 | A | 7 | 21.7 | 71.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.35 | A | 7 | 980 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 32.88 | 7 | 0
2000-04-29 | 1900-04-28 | 19:00 | 19 | 161 | 1347 | 66 | 2 | 8 | 302 | 2 | 15 | 30 | 2 | 8 | 6700 | 2 | 8 | 18400 | 2 | 15 | 4600 | 2 | 8 | 540 | 2 | 19 | 1 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 5.6 | 42.08 | A | 7 | 0.39 | A | 7 | 982 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 33.48 | 7 | 0
2000-04-29 | 1900-04-28 | 20:00 | 20 | 3 | 213 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 18.9 | 66.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.43 | A | 7 | 983 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.78 | 7 | 0
2000-04-29 | 1900-04-28 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 1 | E | 9 | 17.8 | 64.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.45 | A | 7 | 983 | A | 7 | 100 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 34.38 | 7 | 0
2000-04-29 | 1900-04-28 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 1 | E | 9 | 14.4 | 57.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.88 | 7 | 0
2000-04-29 | 1900-04-28 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 1 | E | 9 | 15.6 | 60.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.51 | A | 7 | 983 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.28 | 7 | 0
2000-04-29 | 1900-04-28 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 5.6 | 42.08 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.129 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 35.58 | 7 | 0
2000-04-30 | 1900-04-29 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.9 | 57.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.57 | A | 7 | 983 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.08 | 1 | 0
2000-04-30 | 1900-04-29 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.88 | 1 | 0
2000-04-30 | 1900-04-29 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 36.88 | 1 | 0
2000-04-30 | 1900-04-29 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 37.08 | 1 | 0
2000-04-30 | 1900-04-29 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 1 | E | 9 | 12.2 | 53.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 38.18 | 1 | 0
2000-04-30 | 1900-04-29 | 6:00 | 6 | 46 | 841 | 4 | 2 | 8 | 77 | 2 | 15 | 2 | 2 | 8 | 700 | 2 | 8 | 4500 | 2 | 15 | 500 | 2 | 8 | 80 | 2 | 19 | 2 | E | 9 | 1 | E | 9 | 12.2 | 53.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.69 | A | 7 | 981 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 39.66 | 1 | 0
2000-04-30 | 1900-04-29 | 7:00 | 7 | 283 | 1346 | 153 | 2 | 8 | 312 | 2 | 15 | 88 | 2 | 8 | 15600 | 2 | 8 | 23800 | 2 | 15 | 10600 | 2 | 8 | 1660 | 2 | 19 | 4 | E | 9 | 2 | E | 9 | 13.3 | 55.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.69 | A | 7 | 983 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 41.44 | 1 | 0
2000-04-30 | 1900-04-29 | 8:00 | 8 | 539 | 1346 | 292 | 2 | 8 | 314 | 2 | 15 | 165 | 2 | 8 | 30900 | 2 | 8 | 31000 | 2 | 15 | 18400 | 2 | 8 | 3500 | 2 | 19 | 3 | E | 9 | 2 | E | 9 | 15.6 | 60.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 42.42 | 1 | 0
2000-04-30 | 1900-04-29 | 9:00 | 9 | 774 | 1346 | 482 | 2 | 8 | 435 | 2 | 15 | 231 | 2 | 8 | 50200 | 2 | 8 | 44300 | 2 | 15 | 24700 | 2 | 8 | 5380 | 2 | 19 | 3 | E | 9 | 1 | E | 9 | 18.9 | 66.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.61 | A | 7 | 984 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.38 | 1 | 0
2000-04-30 | 1900-04-29 | 10:00 | 10 | 972 | 1346 | 662 | 2 | 8 | 607 | 2 | 15 | 222 | 2 | 8 | 68900 | 2 | 8 | 60900 | 2 | 15 | 24700 | 2 | 8 | 6310 | 2 | 19 | 5 | E | 9 | 4 | E | 9 | 21.7 | 71.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.53 | A | 7 | 984 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 44.76 | 1 | 0
2000-04-30 | 1900-04-29 | 11:00 | 11 | 1119 | 1346 | 807 | 2 | 8 | 658 | 2 | 15 | 259 | 2 | 8 | 84500 | 2 | 8 | 66300 | 2 | 15 | 29200 | 2 | 8 | 10050 | 2 | 19 | 4 | E | 9 | 3 | E | 9 | 24.4 | 75.92 | A | 7 | 11.7 | 53.06 | A | 7 | 0.45 | A | 7 | 984 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 43.26 | 1 | 0
2000-04-30 | 1900-04-29 | 12:00 | 12 | 1204 | 1346 | 920 | 2 | 8 | 758 | 2 | 15 | 240 | 2 | 8 | 97700 | 2 | 8 | 77200 | 2 | 15 | 28500 | 2 | 8 | 12380 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 24.4 | 75.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.48 | A | 7 | 981 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 45.44 | 1 | 0
2000-04-30 | 1900-04-29 | 13:00 | 13 | 1222 | 1346 | 647 | 2 | 8 | 288 | 2 | 15 | 385 | 2 | 8 | 71200 | 2 | 8 | 31300 | 2 | 15 | 42700 | 2 | 8 | 19830 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 23.3 | 73.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 47.24 | 1 | 0
2000-04-30 | 1900-04-29 | 14:00 | 14 | 1172 | 1346 | 306 | 2 | 8 | 24 | 2 | 15 | 285 | 2 | 8 | 33900 | 2 | 8 | 2400 | 2 | 15 | 31800 | 2 | 8 | 13420 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 11200 | A | 7 | 1097 | A | 7 | 2 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 57.58 | 1 | 0
2000-04-30 | 1900-04-29 | 15:00 | 15 | 1058 | 1346 | 127 | 2 | 8 | 0 | 2 | 15 | 127 | 2 | 8 | 15900 | 2 | 8 | 0 | 2 | 15 | 15900 | 2 | 8 | 6670 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 1372 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 3 | 1 | A | 7 | 60.66 | 1 | 0
2000-04-30 | 1900-04-29 | 16:00 | 16 | 886 | 1346 | 253 | 2 | 8 | 24 | 2 | 15 | 237 | 2 | 8 | 29400 | 2 | 8 | 2000 | 2 | 15 | 28100 | 2 | 8 | 10480 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 1463 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 58.36 | 1 | 0
2000-04-30 | 1900-04-29 | 17:00 | 17 | 670 | 1346 | 345 | 2 | 8 | 234 | 2 | 15 | 228 | 2 | 8 | 37400 | 2 | 8 | 23900 | 2 | 15 | 25500 | 2 | 8 | 5670 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 20.6 | 69.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 56.08 | 1 | 0
2000-04-30 | 1900-04-29 | 18:00 | 18 | 423 | 1346 | 94 | 2 | 8 | 0 | 2 | 15 | 94 | 2 | 8 | 10700 | 2 | 8 | 0 | 2 | 15 | 10700 | 2 | 8 | 3640 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 978 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 58.36 | 1 | 0
2000-04-30 | 1900-04-29 | 19:00 | 19 | 164 | 1346 | 11 | 2 | 8 | 0 | 2 | 15 | 11 | 2 | 8 | 1400 | 2 | 8 | 0 | 2 | 15 | 1400 | 2 | 8 | 450 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 2591 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 58.36 | 1 | 0
2000-04-30 | 1900-04-29 | 20:00 | 20 | 3 | 236 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 11200 | A | 7 | 1463 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 59.46 | 1 | 0
2000-04-30 | 1900-04-29 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 1402 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 57.88 | 1 | 0
2000-04-30 | 1900-04-29 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 17.6 | 63.68 | A | 7 | 14.6 | 58.28 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.5 | A | 7 | 11200 | A | 7 | 1372 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 57.68 | 1 | 0
2000-04-30 | 1900-04-29 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 16.4 | 61.52 | A | 7 | 13.1 | 55.58 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.3 | A | 7 | 9600 | A | 7 | 2286 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 54.88 | 1 | 0
2000-04-30 | 1900-04-29 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 15.1 | 59.18 | A | 7 | 11.6 | 52.88 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 190 | A | 7 | 4.2 | A | 7 | 8000 | A | 7 | 1158 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | 0.17 | F | 8 | 0 | 1 | A | 7 | 52.38 | 1 | 0
1986-05-01 | 1900-04-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 13.8 | 56.84 | A | 7 | 10.1 | 50.18 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 10 | A | 7 | 4 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.98 | 2 | 0
1986-05-01 | 1900-04-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.5 | 54.5 | A | 7 | 8.6 | 47.48 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 350 | A | 7 | 3.9 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.98 | 2 | 0
1986-05-01 | 1900-04-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.3 | 52.34 | A | 7 | 7.1 | 44.78 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 360 | A | 7 | 3.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.98 | 2 | 0
1986-05-01 | 1900-04-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 5.6 | 42.08 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.58 | 2 | 0
1986-05-01 | 1900-04-30 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 5 | 41 | A | 7 | 0.74 | A | 7 | 984 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.5 | 2 | 0
1986-05-01 | 1900-04-30 | 6:00 | 6 | 48 | 864 | 21 | 1 | 13 | 38 | 1 | 9 | 17 | 1 | 13 | 2100 | 1 | 13 | 1600 | 1 | 9 | 2000 | 1 | 13 | 350 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.74 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.52 | 2 | 0
1986-05-01 | 1900-04-30 | 7:00 | 7 | 285 | 1346 | 121 | 1 | 13 | 284 | 1 | 9 | 62 | 1 | 13 | 12900 | 1 | 13 | 21900 | 1 | 9 | 8200 | 1 | 13 | 1120 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 11.1 | 51.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.88 | 2 | 0
1986-05-01 | 1900-04-30 | 8:00 | 8 | 541 | 1346 | 317 | 1 | 9 | 567 | 1 | 9 | 90 | 1 | 13 | 33300 | 1 | 9 | 54000 | 1 | 9 | 11600 | 1 | 13 | 1790 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 14.4 | 57.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.49 | A | 7 | 987 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.42 | 2 | 0
1986-05-01 | 1900-04-30 | 9:00 | 9 | 776 | 1346 | 516 | 1 | 9 | 711 | 1 | 9 | 106 | 1 | 13 | 53900 | 1 | 9 | 70500 | 1 | 9 | 13200 | 1 | 13 | 2350 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.34 | A | 7 | 987 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.48 | 2 | 0
1986-05-01 | 1900-04-30 | 10:00 | 10 | 974 | 1346 | 723 | 1 | 9 | 816 | 1 | 9 | 133 | 1 | 13 | 76100 | 1 | 9 | 82000 | 1 | 9 | 16700 | 1 | 13 | 3670 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.29 | A | 7 | 988 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.22 | 2 | 0
1986-05-01 | 1900-04-30 | 11:00 | 11 | 1120 | 1346 | 864 | 1 | 9 | 862 | 1 | 9 | 147 | 1 | 13 | 91800 | 1 | 9 | 87100 | 1 | 9 | 19200 | 1 | 13 | 5540 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.26 | A | 7 | 988 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.22 | 2 | 0
1986-05-01 | 1900-04-30 | 12:00 | 12 | 1205 | 1346 | 940 | 1 | 9 | 878 | 1 | 9 | 154 | 1 | 13 | 100500 | 1 | 9 | 89000 | 1 | 9 | 20600 | 1 | 13 | 7630 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.23 | A | 7 | 988 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.34 | 2 | 0
1986-05-01 | 1900-04-30 | 13:00 | 13 | 1223 | 1346 | 955 | 1 | 9 | 881 | 1 | 9 | 155 | 1 | 13 | 97800 | 1 | 9 | 88200 | 1 | 9 | 17500 | 1 | 13 | 6390 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | -1.7 | 28.94 | A | 7 | 0.23 | A | 7 | 988 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.04 | 2 | 0
1986-05-01 | 1900-04-30 | 14:00 | 14 | 1174 | 1346 | 916 | 1 | 9 | 878 | 1 | 9 | 152 | 1 | 13 | 97800 | 1 | 9 | 88900 | 1 | 9 | 20100 | 1 | 13 | 6720 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.23 | A | 7 | 987 | A | 7 | 350 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.52 | 2 | 0
1986-05-01 | 1900-04-30 | 15:00 | 15 | 1059 | 1346 | 807 | 1 | 9 | 832 | 1 | 9 | 153 | 1 | 13 | 84700 | 1 | 9 | 83600 | 1 | 9 | 18800 | 1 | 13 | 4850 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 0 | 32 | A | 7 | 0.24 | A | 7 | 987 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.5 | 2 | 0
1986-05-01 | 1900-04-30 | 16:00 | 16 | 888 | 1346 | 650 | 1 | 9 | 799 | 1 | 9 | 125 | 1 | 13 | 68200 | 1 | 9 | 79800 | 1 | 9 | 15400 | 1 | 13 | 3040 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.21 | A | 7 | 987 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.84 | 2 | 0
1986-05-01 | 1900-04-30 | 17:00 | 17 | 671 | 1346 | 454 | 1 | 9 | 712 | 1 | 9 | 101 | 1 | 13 | 48400 | 1 | 9 | 70600 | 1 | 9 | 13100 | 1 | 13 | 2190 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.23 | A | 7 | 987 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.52 | 2 | 0
1986-05-01 | 1900-04-30 | 18:00 | 18 | 424 | 1346 | 242 | 1 | 9 | 547 | 1 | 9 | 71 | 1 | 13 | 25400 | 1 | 9 | 49100 | 1 | 9 | 9900 | 1 | 13 | 1350 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.24 | A | 7 | 987 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.62 | 2 | 0
1986-05-01 | 1900-04-30 | 19:00 | 19 | 166 | 1346 | 61 | 1 | 13 | 208 | 1 | 9 | 36 | 1 | 13 | 6500 | 1 | 13 | 12100 | 1 | 9 | 5000 | 1 | 13 | 640 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 0 | 32 | A | 7 | 0.3 | A | 7 | 987 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.2 | 2 | 0
1986-05-01 | 1900-04-30 | 20:00 | 20 | 3 | 236 | 1 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 0.6 | 33.08 | A | 7 | 0.36 | A | 7 | 988 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.68 | 2 | 0
1986-05-01 | 1900-04-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.42 | A | 7 | 989 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.18 | 2 | 0
1986-05-01 | 1900-04-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.47 | A | 7 | 989 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.78 | 2 | 0
1986-05-01 | 1900-04-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 1.7 | 35.06 | A | 7 | 0.51 | A | 7 | 989 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.16 | 2 | 0
1986-05-01 | 1900-04-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 2.2 | 35.96 | A | 7 | 0.59 | A | 7 | 989 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.86 | 2 | 0
1986-05-02 | 1900-05-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 2.2 | 35.96 | A | 7 | 0.59 | A | 7 | 990 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.86 | 3 | 0
1986-05-02 | 1900-05-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 8.9 | 48.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.66 | A | 7 | 990 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.94 | 3 | 0
1986-05-02 | 1900-05-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 8.3 | 46.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.68 | A | 7 | 990 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.14 | 3 | 0
1986-05-02 | 1900-05-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 9.4 | 48.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.66 | A | 7 | 991 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.74 | 3 | 0
1986-05-02 | 1900-05-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 8.9 | 48.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.74 | A | 7 | 991 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.52 | 3 | 0
1986-05-02 | 1900-05-01 | 6:00 | 6 | 51 | 886 | 16 | 1 | 13 | 7 | 1 | 13 | 15 | 1 | 13 | 1700 | 1 | 13 | 400 | 1 | 13 | 1700 | 1 | 13 | 370 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 9.4 | 48.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.66 | A | 7 | 992 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 1.3 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.74 | 3 | 0
1986-05-02 | 1900-05-01 | 7:00 | 7 | 289 | 1345 | 138 | 1 | 13 | 397 | 1 | 13 | 53 | 1 | 13 | 14200 | 1 | 13 | 31300 | 1 | 13 | 7500 | 1 | 13 | 960 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 10 | 50 | A | 7 | 3.9 | 39.02 | A | 7 | 0.66 | A | 7 | 992 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.72 | 3 | 0
1986-05-02 | 1900-05-01 | 8:00 | 8 | 545 | 1345 | 275 | 1 | 9 | 333 | 1 | 9 | 140 | 1 | 13 | 29600 | 1 | 9 | 33100 | 1 | 9 | 16200 | 1 | 13 | 2870 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.62 | A | 7 | 993 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.92 | 3 | 0
1986-05-02 | 1900-05-01 | 9:00 | 9 | 780 | 1345 | 548 | 1 | 9 | 785 | 1 | 9 | 94 | 1 | 13 | 58200 | 1 | 9 | 78300 | 1 | 9 | 12700 | 1 | 13 | 2190 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 12.8 | 55.04 | A | 7 | 3.9 | 39.02 | A | 7 | 0.55 | A | 7 | 993 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.22 | 3 | 0
1986-05-02 | 1900-05-01 | 10:00 | 10 | 977 | 1345 | 724 | 1 | 9 | 832 | 1 | 9 | 120 | 1 | 13 | 77100 | 1 | 9 | 84000 | 1 | 9 | 16000 | 1 | 13 | 3440 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 3.9 | 39.02 | A | 7 | 0.48 | A | 7 | 993 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.32 | 3 | 0
1986-05-02 | 1900-05-01 | 11:00 | 11 | 1123 | 1345 | 869 | 1 | 9 | 874 | 1 | 9 | 140 | 1 | 13 | 92900 | 1 | 9 | 88500 | 1 | 9 | 18800 | 1 | 13 | 5380 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 2.2 | 35.96 | A | 7 | 0.38 | A | 7 | 993 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.16 | 3 | 0
1986-05-02 | 1900-05-01 | 12:00 | 12 | 1207 | 1345 | 944 | 1 | 9 | 888 | 1 | 9 | 147 | 1 | 13 | 96800 | 1 | 9 | 88900 | 1 | 9 | 16800 | 1 | 13 | 5800 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 3.9 | 39.02 | A | 7 | 0.4 | A | 7 | 993 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 3 | 0
1986-05-02 | 1900-05-01 | 13:00 | 13 | 1226 | 1345 | 961 | 1 | 9 | 901 | 1 | 9 | 140 | 1 | 13 | 98700 | 1 | 9 | 90200 | 1 | 9 | 16200 | 1 | 13 | 6130 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.28 | A | 7 | 992 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.12 | 3 | 0
1986-05-02 | 1900-05-01 | 14:00 | 14 | 1176 | 1345 | 923 | 1 | 9 | 907 | 1 | 9 | 131 | 1 | 13 | 95100 | 1 | 9 | 90800 | 1 | 9 | 15500 | 1 | 13 | 4810 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.26 | A | 7 | 992 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.92 | 3 | 0
1986-05-02 | 1900-05-01 | 15:00 | 15 | 1061 | 1345 | 813 | 1 | 9 | 862 | 1 | 9 | 134 | 1 | 13 | 86700 | 1 | 9 | 87200 | 1 | 9 | 17800 | 1 | 13 | 4440 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.25 | A | 7 | 991 | A | 7 | 40 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.12 | 3 | 0
1986-05-02 | 1900-05-01 | 16:00 | 16 | 890 | 1345 | 660 | 1 | 9 | 835 | 1 | 9 | 109 | 1 | 13 | 70200 | 1 | 9 | 84000 | 1 | 9 | 14600 | 1 | 13 | 2790 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | -1.1 | 30.02 | A | 7 | 0.24 | A | 7 | 990 | A | 7 | 110 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.02 | 3 | 0
1986-05-02 | 1900-05-01 | 17:00 | 17 | 674 | 1345 | 466 | 1 | 9 | 757 | 1 | 9 | 88 | 1 | 13 | 48900 | 1 | 9 | 74200 | 1 | 9 | 11700 | 1 | 13 | 1870 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | -0.6 | 30.92 | A | 7 | 0.25 | A | 7 | 990 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.72 | 3 | 0
1986-05-02 | 1900-05-01 | 18:00 | 18 | 428 | 1345 | 252 | 1 | 9 | 601 | 1 | 9 | 63 | 1 | 13 | 26700 | 1 | 9 | 54400 | 1 | 9 | 9400 | 1 | 13 | 1230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 0 | 32 | A | 7 | 0.27 | A | 7 | 990 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.8 | 3 | 0
1986-05-02 | 1900-05-01 | 19:00 | 19 | 169 | 1345 | 67 | 1 | 13 | 270 | 1 | 9 | 34 | 1 | 13 | 6900 | 1 | 13 | 16800 | 1 | 9 | 4800 | 1 | 13 | 600 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.29 | A | 7 | 989 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.22 | 3 | 0
1986-05-02 | 1900-05-01 | 20:00 | 20 | 4 | 258 | 3 | 1 | 13 | 3 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 15.6 | 60.08 | A | 7 | 0 | 32 | A | 7 | 0.35 | A | 7 | 990 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.8 | 3 | 0
1986-05-02 | 1900-05-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 14.4 | 57.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.39 | A | 7 | 990 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.08 | 3 | 0
1986-05-02 | 1900-05-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 13.9 | 57.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.4 | A | 7 | 990 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 4570 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.18 | 3 | 0
1986-05-02 | 1900-05-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.4 | A | 7 | 991 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.18 | 3 | 0
1986-05-02 | 1900-05-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.45 | A | 7 | 991 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.36 | 3 | 0
1986-05-03 | 1900-05-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.45 | A | 7 | 991 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.36 | 4 | 0
1986-05-03 | 1900-05-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.8 | 55.04 | A | 7 | 2.8 | 37.04 | A | 7 | 0.51 | A | 7 | 991 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.74 | 4 | 0
1986-05-03 | 1900-05-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.62 | A | 7 | 991 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.92 | 4 | 0
1986-05-03 | 1900-05-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 6.7 | 44.06 | A | 7 | 0.8 | A | 7 | 991 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.26 | 4 | 0
1986-05-03 | 1900-05-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.83 | A | 7 | 991 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.66 | 4 | 0
1986-05-03 | 1900-05-02 | 6:00 | 6 | 54 | 908 | 9 | 1 | 13 | 0 | 1 | 9 | 9 | 1 | 13 | 1100 | 1 | 13 | 0 | 1 | 9 | 1100 | 1 | 13 | 340 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.86 | A | 7 | 991 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.96 | 4 | 0
1986-05-03 | 1900-05-02 | 7:00 | 7 | 294 | 1344 | 31 | 1 | 13 | 5 | 1 | 9 | 30 | 1 | 13 | 3700 | 1 | 13 | 100 | 1 | 9 | 3700 | 1 | 13 | 1250 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.86 | A | 7 | 991 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.96 | 4 | 0
1986-05-03 | 1900-05-02 | 8:00 | 8 | 549 | 1344 | 162 | 1 | 9 | 6 | 1 | 9 | 160 | 1 | 13 | 18300 | 1 | 9 | 500 | 1 | 9 | 18100 | 1 | 13 | 6060 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 7.8 | 46.04 | A | 7 | 0.86 | A | 7 | 991 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 3050 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 4 | 0
1986-05-03 | 1900-05-02 | 9:00 | 9 | 783 | 1344 | 230 | 1 | 9 | 22 | 1 | 9 | 217 | 1 | 13 | 26500 | 1 | 9 | 1900 | 1 | 9 | 25400 | 1 | 13 | 9190 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 11.1 | 51.98 | A | 7 | 7.2 | 44.96 | A | 7 | 0.77 | A | 7 | 991 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.66 | 4 | 0
1986-05-03 | 1900-05-02 | 10:00 | 10 | 980 | 1344 | 435 | 1 | 9 | 236 | 1 | 9 | 263 | 1 | 13 | 47900 | 1 | 9 | 25500 | 1 | 9 | 29200 | 1 | 13 | 7730 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 12.2 | 53.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.75 | A | 7 | 990 | A | 7 | 130 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.34 | 4 | 0
1986-05-03 | 1900-05-02 | 11:00 | 11 | 1125 | 1344 | 302 | 1 | 9 | 10 | 1 | 9 | 293 | 1 | 13 | 35800 | 1 | 9 | 900 | 1 | 9 | 35100 | 1 | 13 | 13590 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.75 | A | 7 | 990 | A | 7 | 130 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.12 | 4 | 0
1986-05-03 | 1900-05-02 | 12:00 | 12 | 1210 | 1344 | 458 | 1 | 9 | 102 | 1 | 9 | 366 | 1 | 13 | 50900 | 1 | 9 | 10900 | 1 | 9 | 41100 | 1 | 13 | 17450 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 14.4 | 57.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.7 | A | 7 | 989 | A | 7 | 130 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.32 | 4 | 0
1986-05-03 | 1900-05-02 | 13:00 | 13 | 1228 | 1344 | 635 | 1 | 9 | 197 | 1 | 9 | 454 | 1 | 13 | 69700 | 1 | 9 | 21000 | 1 | 9 | 50400 | 1 | 13 | 22870 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 14.4 | 57.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.6 | A | 7 | 988 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.26 | 4 | 0
1986-05-03 | 1900-05-02 | 14:00 | 14 | 1178 | 1344 | 522 | 1 | 9 | 231 | 1 | 9 | 319 | 1 | 13 | 58000 | 1 | 9 | 25200 | 1 | 9 | 35900 | 1 | 13 | 14070 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 17.2 | 62.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 140 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.86 | 4 | 0
1986-05-03 | 1900-05-02 | 15:00 | 15 | 1063 | 1344 | 428 | 1 | 9 | 164 | 1 | 9 | 298 | 1 | 13 | 47600 | 1 | 9 | 17500 | 1 | 9 | 33700 | 1 | 13 | 10500 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 17.2 | 62.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.56 | A | 7 | 986 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.14 | 4 | 0
1986-05-03 | 1900-05-02 | 16:00 | 16 | 892 | 1344 | 458 | 1 | 13 | 380 | 1 | 13 | 206 | 1 | 13 | 49400 | 1 | 13 | 39300 | 1 | 13 | 23300 | 1 | 13 | 5340 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 18.3 | 64.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.54 | A | 7 | 985 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 1.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.72 | 4 | 0
1986-05-03 | 1900-05-02 | 17:00 | 17 | 677 | 1344 | 457 | 1 | 9 | 748 | 1 | 9 | 82 | 1 | 13 | 48400 | 1 | 9 | 73600 | 1 | 9 | 11300 | 1 | 13 | 1800 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.53 | A | 7 | 985 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.52 | 4 | 0
1986-05-03 | 1900-05-02 | 18:00 | 18 | 431 | 1344 | 253 | 1 | 9 | 612 | 1 | 9 | 59 | 1 | 13 | 27000 | 1 | 9 | 55700 | 1 | 9 | 9100 | 1 | 13 | 1160 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.5 | A | 7 | 984 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.44 | 4 | 0
1986-05-03 | 1900-05-02 | 19:00 | 19 | 173 | 1344 | 70 | 1 | 13 | 300 | 1 | 9 | 33 | 1 | 13 | 7300 | 1 | 13 | 18900 | 1 | 9 | 4900 | 1 | 13 | 590 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.04 | 4 | 0
1986-05-03 | 1900-05-02 | 20:00 | 20 | 5 | 280 | 3 | 1 | 13 | 6 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.04 | 4 | 0
1986-05-03 | 1900-05-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.04 | 4 | 0
1986-05-03 | 1900-05-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 7.8 | 46.04 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.34 | 4 | 0
1986-05-03 | 1900-05-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.84 | 4 | 0
1986-05-03 | 1900-05-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.84 | 4 | 0
1986-05-04 | 1900-05-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.36 | 5 | 0
1986-05-04 | 1900-05-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.84 | 5 | 0
1986-05-04 | 1900-05-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 7.8 | 46.04 | A | 7 | 0.62 | A | 7 | 981 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.34 | 5 | 0
1986-05-04 | 1900-05-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 13.9 | 57.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 5 | 0
1986-05-04 | 1900-05-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 13.3 | 55.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.74 | 5 | 0
1986-05-04 | 1900-05-03 | 6:00 | 6 | 57 | 929 | 22 | 1 | 13 | 35 | 1 | 13 | 18 | 1 | 13 | 2300 | 1 | 13 | 1500 | 1 | 13 | 2200 | 1 | 13 | 370 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 13.3 | 55.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.74 | 5 | 0
1986-05-04 | 1900-05-03 | 7:00 | 7 | 298 | 1344 | 108 | 1 | 13 | 141 | 1 | 13 | 77 | 1 | 13 | 11500 | 1 | 13 | 11200 | 1 | 13 | 9000 | 1 | 13 | 1460 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 15 | 59 | A | 7 | 8.9 | 48.02 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.92 | 5 | 0
1986-05-04 | 1900-05-03 | 8:00 | 8 | 553 | 1344 | 258 | 1 | 13 | 238 | 1 | 13 | 161 | 1 | 13 | 27600 | 1 | 13 | 23700 | 1 | 13 | 17900 | 1 | 13 | 3400 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.72 | 5 | 0
1986-05-04 | 1900-05-03 | 9:00 | 9 | 786 | 1344 | 377 | 1 | 13 | 224 | 1 | 13 | 246 | 1 | 13 | 41300 | 1 | 13 | 23400 | 1 | 13 | 27600 | 1 | 13 | 6560 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 18.3 | 64.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.54 | A | 7 | 979 | A | 7 | 190 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.72 | 5 | 0
1986-05-04 | 1900-05-03 | 10:00 | 10 | 982 | 1344 | 600 | 1 | 13 | 584 | 1 | 13 | 174 | 1 | 13 | 63900 | 1 | 13 | 59500 | 1 | 13 | 20300 | 1 | 13 | 5210 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 20 | 68 | A | 7 | 8.9 | 48.02 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.92 | 5 | 0
1986-05-04 | 1900-05-03 | 11:00 | 11 | 1128 | 1344 | 761 | 1 | 13 | 682 | 1 | 13 | 188 | 1 | 13 | 81700 | 1 | 13 | 69900 | 1 | 13 | 22800 | 1 | 13 | 7750 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.44 | A | 7 | 978 | A | 7 | 190 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.72 | 5 | 0
1986-05-04 | 1900-05-03 | 12:00 | 12 | 1212 | 1344 | 871 | 1 | 9 | 749 | 1 | 9 | 195 | 1 | 13 | 90800 | 1 | 9 | 75100 | 1 | 9 | 22900 | 1 | 13 | 9560 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 10 | 50 | A | 7 | 0.43 | A | 7 | 977 | A | 7 | 200 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.5 | 5 | 0
1986-05-04 | 1900-05-03 | 13:00 | 13 | 1230 | 1344 | 910 | 1 | 9 | 894 | 1 | 9 | 92 | 1 | 13 | 94700 | 1 | 9 | 89800 | 1 | 9 | 12200 | 1 | 13 | 4710 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.42 | A | 7 | 976 | A | 7 | 190 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.08 | 5 | 0
1986-05-04 | 1900-05-03 | 14:00 | 14 | 1180 | 1344 | 890 | 1 | 9 | 921 | 1 | 9 | 83 | 1 | 13 | 93100 | 1 | 9 | 92500 | 1 | 9 | 11600 | 1 | 13 | 3650 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 25 | 77 | A | 7 | 10.6 | 51.08 | A | 7 | 0.4 | A | 7 | 974 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.78 | 5 | 0
1986-05-04 | 1900-05-03 | 15:00 | 15 | 1066 | 1344 | 779 | 1 | 9 | 870 | 1 | 9 | 90 | 1 | 13 | 81200 | 1 | 9 | 87200 | 1 | 9 | 12000 | 1 | 13 | 2900 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 10 | 50 | A | 7 | 0.42 | A | 7 | 973 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.3 | 5 | 0
1986-05-04 | 1900-05-03 | 16:00 | 16 | 895 | 1344 | 663 | 1 | 9 | 877 | 1 | 9 | 80 | 1 | 13 | 69400 | 1 | 9 | 87300 | 1 | 9 | 11200 | 1 | 13 | 2080 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 10 | 50 | A | 7 | 0.39 | A | 7 | 972 | A | 7 | 170 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.7 | 5 | 0
1986-05-04 | 1900-05-03 | 17:00 | 17 | 679 | 1344 | 468 | 1 | 9 | 817 | 1 | 9 | 57 | 1 | 13 | 49600 | 1 | 9 | 79800 | 1 | 9 | 9100 | 1 | 13 | 1440 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 9.4 | 48.92 | A | 7 | 0.39 | A | 7 | 972 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.92 | 5 | 0
1986-05-04 | 1900-05-03 | 18:00 | 18 | 434 | 1344 | 268 | 1 | 9 | 691 | 1 | 9 | 47 | 1 | 13 | 28600 | 1 | 9 | 63400 | 1 | 9 | 8100 | 1 | 13 | 1020 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.38 | A | 7 | 971 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.14 | 5 | 0
1986-05-04 | 1900-05-03 | 19:00 | 19 | 177 | 1344 | 77 | 1 | 13 | 394 | 1 | 9 | 28 | 1 | 13 | 8300 | 1 | 13 | 25400 | 1 | 9 | 4900 | 1 | 13 | 520 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.44 | A | 7 | 971 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.02 | 5 | 0
1986-05-04 | 1900-05-03 | 20:00 | 20 | 6 | 302 | 5 | 1 | 13 | 18 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 8.9 | 48.02 | A | 7 | 0.46 | A | 7 | 970 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.42 | 5 | 0
1986-05-04 | 1900-05-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 9.4 | 48.92 | A | 7 | 0.51 | A | 7 | 971 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.02 | 5 | 0
1986-05-04 | 1900-05-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 9.4 | 48.92 | A | 7 | 0.53 | A | 7 | 971 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.32 | 5 | 0
1986-05-04 | 1900-05-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 8.3 | 46.94 | A | 7 | 0.51 | A | 7 | 970 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.34 | 5 | 0
1986-05-04 | 1900-05-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.49 | A | 7 | 969 | A | 7 | 190 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.24 | 5 | 0
1986-05-05 | 1900-05-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.5 | A | 7 | 968 | A | 7 | 180 | A | 7 | 12.4 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.44 | 6 | 0
1986-05-05 | 1900-05-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.52 | A | 7 | 968 | A | 7 | 190 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.54 | 6 | 0
1986-05-05 | 1900-05-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.56 | A | 7 | 967 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.12 | 6 | 0
1986-05-05 | 1900-05-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 10 | 50 | A | 7 | 0.61 | A | 7 | 967 | A | 7 | 190 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.6 | 6 | 0
1986-05-05 | 1900-05-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 966 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.08 | 6 | 0
1986-05-05 | 1900-05-04 | 6:00 | 6 | 60 | 951 | 14 | 1 | 13 | 10 | 1 | 13 | 13 | 1 | 13 | 1500 | 1 | 13 | 600 | 1 | 13 | 1500 | 1 | 13 | 330 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 17.8 | 64.04 | A | 7 | 11.7 | 53.06 | A | 7 | 0.68 | A | 7 | 966 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 2.1 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.56 | 6 | 0
1986-05-05 | 1900-05-04 | 7:00 | 7 | 302 | 1343 | 127 | 1 | 13 | 216 | 1 | 13 | 78 | 1 | 13 | 13400 | 1 | 13 | 17200 | 1 | 13 | 9600 | 1 | 13 | 1480 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 18.3 | 64.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.68 | A | 7 | 967 | A | 7 | 200 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 2.2 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.36 | 6 | 0
1986-05-05 | 1900-05-04 | 8:00 | 8 | 557 | 1343 | 156 | 1 | 13 | 45 | 1 | 13 | 137 | 1 | 13 | 17100 | 1 | 13 | 4300 | 1 | 13 | 15300 | 1 | 13 | 4040 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 967 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 2.5 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 6 | 0
1986-05-05 | 1900-05-04 | 9:00 | 9 | 790 | 1343 | 420 | 1 | 13 | 281 | 1 | 13 | 255 | 1 | 13 | 45100 | 1 | 13 | 29800 | 1 | 13 | 27500 | 1 | 13 | 6320 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 967 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 2.5 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 6 | 0
1986-05-05 | 1900-05-04 | 10:00 | 10 | 985 | 1343 | 413 | 1 | 9 | 92 | 1 | 9 | 346 | 1 | 13 | 45600 | 1 | 9 | 9400 | 1 | 9 | 38600 | 1 | 13 | 12580 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 21.1 | 69.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.71 | A | 7 | 967 | A | 7 | 200 | A | 7 | 14.9 | A | 7 | 32200 | A | 7 | 820 | A | 7 | 2.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.48 | 6 | 0
1986-05-05 | 1900-05-04 | 11:00 | 11 | 1130 | 1343 | 468 | 1 | 9 | 168 | 1 | 9 | 327 | 1 | 13 | 52100 | 1 | 9 | 18000 | 1 | 9 | 37000 | 1 | 13 | 12940 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 22.8 | 73.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.66 | A | 7 | 967 | A | 7 | 200 | A | 7 | 12.4 | A | 7 | 24100 | A | 7 | 820 | A | 7 | 2.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.18 | 6 | 0
1986-05-05 | 1900-05-04 | 12:00 | 12 | 1214 | 1343 | 777 | 1 | 9 | 517 | 1 | 9 | 310 | 1 | 13 | 84300 | 1 | 9 | 54100 | 1 | 9 | 35300 | 1 | 13 | 17150 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 23.9 | 75.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.64 | A | 7 | 967 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 2.8 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.76 | 6 | 0
1986-05-05 | 1900-05-04 | 13:00 | 13 | 1232 | 1343 | 789 | 1 | 13 | 607 | 1 | 13 | 233 | 1 | 13 | 84400 | 1 | 13 | 62000 | 1 | 13 | 27400 | 1 | 13 | 13650 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | A | 7 | 967 | A | 7 | 210 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.66 | 6 | 0
1986-05-05 | 1900-05-04 | 14:00 | 14 | 1182 | 1343 | 795 | 1 | 13 | 662 | 1 | 13 | 213 | 1 | 13 | 85200 | 1 | 13 | 67700 | 1 | 13 | 25400 | 1 | 13 | 10320 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 27.2 | 80.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.54 | A | 7 | 967 | A | 7 | 210 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.26 | 6 | 0
1986-05-05 | 1900-05-04 | 15:00 | 15 | 1068 | 1343 | 840 | 1 | 13 | 795 | 1 | 13 | 209 | 1 | 13 | 89100 | 1 | 13 | 80800 | 1 | 13 | 24700 | 1 | 13 | 7330 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 27.2 | 80.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.54 | A | 7 | 967 | A | 7 | 200 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.26 | 6 | 0
1986-05-05 | 1900-05-04 | 16:00 | 16 | 897 | 1343 | 611 | 1 | 13 | 675 | 1 | 13 | 161 | 1 | 13 | 64700 | 1 | 13 | 68400 | 1 | 13 | 19000 | 1 | 13 | 4240 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 27.2 | 80.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.54 | A | 7 | 967 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.26 | 6 | 0
1986-05-05 | 1900-05-04 | 17:00 | 17 | 682 | 1343 | 297 | 1 | 13 | 248 | 1 | 13 | 171 | 1 | 13 | 32300 | 1 | 13 | 25800 | 1 | 13 | 19200 | 1 | 13 | 3750 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 25.6 | 78.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.58 | A | 7 | 967 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 2.8 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.46 | 6 | 0
1986-05-05 | 1900-05-04 | 18:00 | 18 | 437 | 1343 | 162 | 1 | 9 | 141 | 1 | 9 | 117 | 1 | 13 | 17800 | 1 | 9 | 13200 | 1 | 9 | 13500 | 1 | 13 | 2640 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 25 | 77 | A | 7 | 17.2 | 62.96 | A | 7 | 0.62 | A | 7 | 967 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 2.9 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.06 | 6 | 0
1986-05-05 | 1900-05-04 | 19:00 | 19 | 180 | 1343 | 23 | 1 | 13 | 0 | 1 | 9 | 23 | 1 | 13 | 2700 | 1 | 13 | 0 | 1 | 9 | 2700 | 1 | 13 | 890 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 968 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 3.2 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 6 | 0
1986-05-05 | 1900-05-04 | 20:00 | 20 | 6 | 325 | 2 | 1 | 13 | 3 | 1 | 13 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 968 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 6 | 0
1986-05-05 | 1900-05-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 969 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 6 | 0
1986-05-05 | 1900-05-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 6 | 0
1986-05-05 | 1900-05-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 6 | 0
1986-05-05 | 1900-05-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.93 | A | 7 | 970 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.58 | 6 | 0
1986-05-06 | 1900-05-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 16.7 | 62.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.97 | A | 7 | 970 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 940 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.38 | 7 | 0
1986-05-06 | 1900-05-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 16.1 | 60.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.97 | A | 7 | 969 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 7 | 0
1986-05-06 | 1900-05-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.97 | A | 7 | 969 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.46 | 7 | 0
1986-05-06 | 1900-05-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 17.2 | 62.96 | A | 7 | 1 | A | 7 | 969 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.86 | 7 | 0
1986-05-06 | 1900-05-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 16.7 | 62.06 | A | 7 | 1 | A | 7 | 970 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.96 | 7 | 0
1986-05-06 | 1900-05-05 | 6:00 | 6 | 63 | 973 | 29 | 1 | 13 | 33 | 1 | 13 | 26 | 1 | 13 | 3100 | 1 | 13 | 1500 | 1 | 13 | 3000 | 1 | 13 | 540 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.97 | A | 7 | 970 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.36 | 7 | 0
1986-05-06 | 1900-05-05 | 7:00 | 7 | 307 | 1342 | 61 | 1 | 13 | 0 | 1 | 9 | 61 | 1 | 13 | 7000 | 1 | 13 | 0 | 1 | 9 | 7000 | 1 | 13 | 2300 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.97 | A | 7 | 970 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 3200 | A | 7 | 850 | A | 7 | 3 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.44 | 7 | 0
1986-05-06 | 1900-05-05 | 8:00 | 8 | 560 | 1342 | 115 | 1 | 9 | 8 | 1 | 9 | 111 | 1 | 13 | 13300 | 1 | 9 | 500 | 1 | 9 | 13100 | 1 | 13 | 4690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 971 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 3200 | A | 7 | 850 | A | 7 | 3.1 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.54 | 7 | 0
1986-05-06 | 1900-05-05 | 9:00 | 9 | 793 | 1342 | 208 | 1 | 9 | 3 | 1 | 9 | 206 | 1 | 13 | 24100 | 1 | 9 | 200 | 1 | 9 | 24000 | 1 | 13 | 8920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 971 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 1220 | A | 7 | 3.2 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.92 | 7 | 0
1986-05-06 | 1900-05-05 | 10:00 | 10 | 988 | 1342 | 285 | 1 | 9 | 1 | 1 | 9 | 284 | 1 | 13 | 33200 | 1 | 9 | 100 | 1 | 9 | 33200 | 1 | 13 | 12650 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 971 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 430 | A | 7 | 3.3 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.52 | 7 | 0
1986-05-06 | 1900-05-05 | 11:00 | 11 | 1132 | 1342 | 328 | 1 | 9 | 3 | 1 | 9 | 325 | 1 | 13 | 38600 | 1 | 9 | 300 | 1 | 9 | 38400 | 1 | 13 | 14700 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 971 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 820 | A | 7 | 3.5 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.1 | 7 | 0
1986-05-06 | 1900-05-05 | 12:00 | 12 | 1216 | 1342 | 609 | 1 | 9 | 324 | 1 | 9 | 316 | 1 | 13 | 68200 | 1 | 9 | 35300 | 1 | 9 | 36100 | 1 | 13 | 15830 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 971 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 610 | A | 7 | 3.3 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 7 | 0
1986-05-06 | 1900-05-05 | 13:00 | 13 | 1234 | 1342 | 764 | 1 | 13 | 544 | 1 | 13 | 264 | 1 | 13 | 81000 | 1 | 13 | 55200 | 1 | 13 | 30100 | 1 | 13 | 15520 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 970 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 760 | A | 7 | 3.3 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.62 | 7 | 0
1986-05-06 | 1900-05-05 | 14:00 | 14 | 1184 | 1342 | 629 | 1 | 13 | 367 | 1 | 13 | 306 | 1 | 13 | 68100 | 1 | 13 | 38400 | 1 | 13 | 34200 | 1 | 13 | 15130 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.72 | A | 7 | 970 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 790 | A | 7 | 3.5 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.9 | 7 | 0
1986-05-06 | 1900-05-05 | 15:00 | 15 | 1070 | 1342 | 433 | 1 | 13 | 293 | 1 | 13 | 200 | 1 | 13 | 48200 | 1 | 13 | 30700 | 1 | 13 | 23600 | 1 | 13 | 7030 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 970 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 3.3 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.22 | 7 | 0
1986-05-06 | 1900-05-05 | 16:00 | 16 | 900 | 1342 | 576 | 1 | 13 | 609 | 1 | 13 | 169 | 1 | 13 | 60900 | 1 | 13 | 61500 | 1 | 13 | 19500 | 1 | 13 | 4440 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 970 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 7 | 0
1986-05-06 | 1900-05-05 | 17:00 | 17 | 685 | 1342 | 323 | 1 | 13 | 336 | 1 | 13 | 152 | 1 | 13 | 34700 | 1 | 13 | 33800 | 1 | 13 | 17400 | 1 | 13 | 3200 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 970 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.2 | 7 | 0
1986-05-06 | 1900-05-05 | 18:00 | 18 | 440 | 1342 | 239 | 1 | 13 | 426 | 1 | 13 | 100 | 1 | 13 | 25300 | 1 | 13 | 38800 | 1 | 13 | 12600 | 1 | 13 | 1870 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 970 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.62 | 7 | 0
1986-05-06 | 1900-05-05 | 19:00 | 19 | 184 | 1342 | 65 | 1 | 13 | 161 | 1 | 13 | 44 | 1 | 13 | 7000 | 1 | 13 | 9600 | 1 | 13 | 5700 | 1 | 13 | 800 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 970 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.82 | 7 | 0
1986-05-06 | 1900-05-05 | 20:00 | 20 | 7 | 347 | 4 | 1 | 13 | 2 | 1 | 13 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 971 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.62 | 7 | 0
1986-05-06 | 1900-05-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 971 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 9140 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.62 | 7 | 0
1986-05-06 | 1900-05-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 972 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1680 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 7 | 0
1986-05-06 | 1900-05-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.76 | A | 7 | 973 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.94 | 7 | 0
1986-05-06 | 1900-05-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 1220 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.72 | 7 | 0
1986-05-07 | 1900-05-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 975 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.9 | 1 | 0
1986-05-07 | 1900-05-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 15.6 | 60.08 | A | 7 | 1 | A | 7 | 973 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 1 | 0
1986-05-07 | 1900-05-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.97 | A | 7 | 973 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 1 | 0
1986-05-07 | 1900-05-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 210 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 1 | 0
1986-05-07 | 1900-05-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 1 | 0
1986-05-07 | 1900-05-06 | 6:00 | 6 | 66 | 995 | 19 | 1 | 13 | 3 | 1 | 9 | 19 | 1 | 13 | 2200 | 1 | 13 | 0 | 1 | 9 | 2200 | 1 | 13 | 660 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 15.6 | 60.08 | A | 7 | 15.6 | 60.08 | A | 7 | 1 | A | 7 | 975 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 2740 | A | 7 | 2.7 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 1 | 0
1986-05-07 | 1900-05-06 | 7:00 | 7 | 311 | 1342 | 109 | 1 | 13 | 130 | 1 | 13 | 79 | 1 | 13 | 11900 | 1 | 13 | 10800 | 1 | 13 | 9400 | 1 | 13 | 1720 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 16.1 | 60.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 1 | 0
1986-05-07 | 1900-05-06 | 8:00 | 8 | 564 | 1342 | 336 | 1 | 9 | 465 | 1 | 9 | 141 | 1 | 13 | 35400 | 1 | 9 | 45100 | 1 | 9 | 16400 | 1 | 13 | 2800 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 16.1 | 60.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.97 | A | 7 | 974 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 1 | 0
1986-05-07 | 1900-05-06 | 9:00 | 9 | 796 | 1342 | 536 | 1 | 9 | 674 | 1 | 9 | 137 | 1 | 13 | 56700 | 1 | 9 | 67800 | 1 | 9 | 16400 | 1 | 13 | 3230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.68 | A | 7 | 974 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.88 | 1 | 0
1986-05-07 | 1900-05-06 | 10:00 | 10 | 990 | 1342 | 715 | 1 | 9 | 751 | 1 | 9 | 161 | 1 | 13 | 76500 | 1 | 9 | 76800 | 1 | 9 | 19700 | 1 | 13 | 4950 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.56 | A | 7 | 974 | A | 7 | 120 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.52 | 1 | 0
1986-05-07 | 1900-05-06 | 11:00 | 11 | 1135 | 1342 | 844 | 1 | 9 | 790 | 1 | 9 | 176 | 1 | 13 | 88100 | 1 | 9 | 79300 | 1 | 9 | 21000 | 1 | 13 | 6680 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 974 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 1 | 0
1986-05-07 | 1900-05-06 | 12:00 | 12 | 1218 | 1342 | 918 | 1 | 9 | 808 | 1 | 9 | 185 | 1 | 13 | 96400 | 1 | 9 | 81200 | 1 | 9 | 22500 | 1 | 13 | 9500 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 974 | A | 7 | 150 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 1 | 0
1986-05-07 | 1900-05-06 | 13:00 | 13 | 1236 | 1342 | 890 | 1 | 9 | 724 | 1 | 9 | 223 | 1 | 13 | 95500 | 1 | 9 | 74100 | 1 | 9 | 27100 | 1 | 13 | 13400 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 27.2 | 80.96 | A | 7 | 20 | 68 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.2 | 1 | 0
1986-05-07 | 1900-05-06 | 14:00 | 14 | 1186 | 1342 | 835 | 1 | 9 | 689 | 1 | 9 | 227 | 1 | 13 | 89100 | 1 | 9 | 70300 | 1 | 9 | 26900 | 1 | 13 | 11140 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 27.8 | 82.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.61 | A | 7 | 972 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.32 | 1 | 0
1986-05-07 | 1900-05-06 | 15:00 | 15 | 1072 | 1342 | 740 | 1 | 9 | 729 | 1 | 9 | 158 | 1 | 13 | 77600 | 1 | 9 | 73200 | 1 | 9 | 18900 | 1 | 13 | 5170 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.55 | A | 7 | 972 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.24 | 1 | 0
1986-05-07 | 1900-05-06 | 16:00 | 16 | 902 | 1342 | 469 | 1 | 9 | 433 | 1 | 9 | 178 | 1 | 13 | 51400 | 1 | 9 | 44900 | 1 | 9 | 21200 | 1 | 13 | 4630 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 27.2 | 80.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.63 | A | 7 | 972 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.82 | 1 | 0
1986-05-07 | 1900-05-06 | 17:00 | 17 | 688 | 1342 | 428 | 1 | 9 | 601 | 1 | 9 | 121 | 1 | 13 | 45000 | 1 | 9 | 59400 | 1 | 9 | 14500 | 1 | 13 | 2600 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.61 | A | 7 | 971 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.32 | 1 | 0
1986-05-07 | 1900-05-06 | 18:00 | 18 | 443 | 1342 | 238 | 1 | 9 | 467 | 1 | 9 | 85 | 1 | 13 | 24700 | 1 | 9 | 42200 | 1 | 9 | 10700 | 1 | 13 | 1590 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.63 | A | 7 | 972 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.82 | 1 | 0
1986-05-07 | 1900-05-06 | 19:00 | 19 | 187 | 1342 | 62 | 1 | 13 | 140 | 1 | 9 | 43 | 1 | 13 | 6700 | 1 | 13 | 8500 | 1 | 9 | 5500 | 1 | 13 | 780 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 972 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.22 | 1 | 0
1986-05-07 | 1900-05-06 | 20:00 | 20 | 8 | 369 | 2 | 1 | 13 | 1 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 973 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.185 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.52 | 1 | 0
1986-05-07 | 1900-05-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 973 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 1 | 0
1986-05-07 | 1900-05-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 973 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.62 | 1 | 0
1986-05-07 | 1900-05-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 973 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 1 | 0
1986-05-07 | 1900-05-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 21.7 | 71.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.81 | A | 7 | 973 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.04 | 1 | 0
1986-05-08 | 1900-05-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 973 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 2 | 0
1986-05-08 | 1900-05-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 4 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 2 | 0
1986-05-08 | 1900-05-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 21.1 | 69.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 1520 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.64 | 2 | 0
1986-05-08 | 1900-05-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 3 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 2 | 0
1986-05-08 | 1900-05-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 20 | 68 | A | 7 | 18.3 | 64.94 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.94 | 2 | 0
1986-05-08 | 1900-05-07 | 6:00 | 6 | 69 | 1039 | 30 | 1 | 13 | 28 | 1 | 13 | 28 | 1 | 13 | 3300 | 1 | 13 | 1600 | 1 | 13 | 3200 | 1 | 13 | 640 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 20 | 68 | A | 7 | 17.8 | 64.04 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.44 | 2 | 0
1986-05-08 | 1900-05-07 | 7:00 | 7 | 314 | 1341 | 117 | 1 | 13 | 161 | 1 | 13 | 80 | 1 | 13 | 12500 | 1 | 13 | 13100 | 1 | 13 | 9500 | 1 | 13 | 1520 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.14 | 2 | 0
1986-05-08 | 1900-05-07 | 8:00 | 8 | 567 | 1341 | 275 | 1 | 13 | 322 | 1 | 13 | 140 | 1 | 13 | 29900 | 1 | 13 | 32300 | 1 | 13 | 16200 | 1 | 13 | 2880 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 22.8 | 73.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.76 | A | 7 | 974 | A | 7 | 150 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 2130 | A | 7 | 3.1 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.94 | 2 | 0
1986-05-08 | 1900-05-07 | 9:00 | 9 | 799 | 1341 | 535 | 1 | 9 | 723 | 1 | 9 | 105 | 1 | 13 | 56300 | 1 | 9 | 72000 | 1 | 9 | 13300 | 1 | 13 | 2410 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 974 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.82 | 2 | 0
1986-05-08 | 1900-05-07 | 10:00 | 10 | 993 | 1341 | 705 | 1 | 9 | 753 | 1 | 9 | 147 | 1 | 13 | 73600 | 1 | 9 | 75500 | 1 | 9 | 17600 | 1 | 13 | 4100 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 26.1 | 78.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.58 | A | 7 | 974 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.26 | 2 | 0
1986-05-08 | 1900-05-07 | 11:00 | 11 | 1137 | 1341 | 568 | 1 | 13 | 297 | 1 | 13 | 316 | 1 | 13 | 62900 | 1 | 13 | 32300 | 1 | 13 | 35400 | 1 | 13 | 12600 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 27.2 | 80.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.53 | A | 7 | 974 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 9140 | A | 7 | 2.9 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.36 | 2 | 0
1986-05-08 | 1900-05-07 | 12:00 | 12 | 1220 | 1341 | 337 | 1 | 9 | 15 | 1 | 9 | 324 | 1 | 13 | 40300 | 1 | 9 | 1300 | 1 | 9 | 39100 | 1 | 13 | 14970 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 25 | 77 | A | 7 | 16.1 | 60.98 | A | 7 | 0.58 | A | 7 | 974 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.48 | 2 | 0
1986-05-08 | 1900-05-07 | 13:00 | 13 | 1237 | 1341 | 307 | 1 | 9 | 3 | 1 | 9 | 304 | 1 | 13 | 36900 | 1 | 9 | 300 | 1 | 9 | 36700 | 1 | 13 | 14310 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.64 | A | 7 | 974 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.76 | 2 | 0
1986-05-08 | 1900-05-07 | 14:00 | 14 | 1188 | 1341 | 683 | 1 | 13 | 460 | 1 | 13 | 276 | 1 | 13 | 74700 | 1 | 13 | 48200 | 1 | 13 | 32000 | 1 | 13 | 13820 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 974 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 3.1 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.54 | 2 | 0
1986-05-08 | 1900-05-07 | 15:00 | 15 | 1074 | 1341 | 568 | 1 | 13 | 365 | 1 | 13 | 276 | 1 | 13 | 61200 | 1 | 13 | 38100 | 1 | 13 | 30600 | 1 | 13 | 9990 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 23.3 | 73.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.66 | A | 7 | 973 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.16 | 2 | 0
1986-05-08 | 1900-05-07 | 16:00 | 16 | 904 | 1341 | 498 | 1 | 13 | 393 | 1 | 13 | 233 | 1 | 13 | 53100 | 1 | 13 | 40700 | 1 | 13 | 25700 | 1 | 13 | 6210 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 972 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.24 | 2 | 0
1986-05-08 | 1900-05-07 | 17:00 | 17 | 690 | 1341 | 448 | 1 | 13 | 560 | 1 | 13 | 161 | 1 | 13 | 47900 | 1 | 13 | 56400 | 1 | 13 | 18900 | 1 | 13 | 3420 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 971 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.52 | 2 | 0
1986-05-08 | 1900-05-07 | 18:00 | 18 | 447 | 1341 | 195 | 1 | 13 | 288 | 1 | 13 | 100 | 1 | 13 | 20700 | 1 | 13 | 26300 | 1 | 13 | 12000 | 1 | 13 | 1870 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.54 | A | 7 | 971 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.88 | 2 | 0
1986-05-08 | 1900-05-07 | 19:00 | 19 | 191 | 1341 | 67 | 1 | 13 | 109 | 1 | 13 | 52 | 1 | 13 | 7100 | 1 | 13 | 6700 | 1 | 13 | 6200 | 1 | 13 | 980 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 971 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.38 | 2 | 0
1986-05-08 | 1900-05-07 | 20:00 | 20 | 9 | 391 | 4 | 1 | 13 | 2 | 1 | 13 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 972 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.38 | 2 | 0
1986-05-08 | 1900-05-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 23.3 | 73.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.66 | A | 7 | 973 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.16 | 2 | 0
1986-05-08 | 1900-05-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.69 | A | 7 | 973 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.86 | 2 | 0
1986-05-08 | 1900-05-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 973 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 2 | 0
1986-05-08 | 1900-05-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.69 | A | 7 | 973 | A | 7 | 140 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1400 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 2 | 0
1986-05-09 | 1900-05-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.76 | A | 7 | 974 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 2740 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.42 | 3 | 0
1986-05-09 | 1900-05-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 973 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 3 | 0
1986-05-09 | 1900-05-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 973 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 3960 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 3 | 0
1986-05-09 | 1900-05-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 3 | 0
1986-05-09 | 1900-05-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 974 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 3960 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 3 | 0
1986-05-09 | 1900-05-08 | 6:00 | 6 | 72 | 1061 | 17 | 1 | 13 | 13 | 1 | 9 | 15 | 1 | 13 | 1800 | 1 | 13 | 700 | 1 | 9 | 1700 | 1 | 13 | 380 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 974 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1040 | A | 7 | 2.6 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 3 | 0
1986-05-09 | 1900-05-08 | 7:00 | 7 | 318 | 1341 | 87 | 1 | 13 | 6 | 1 | 9 | 86 | 1 | 13 | 9800 | 1 | 13 | 300 | 1 | 9 | 9700 | 1 | 13 | 2990 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 975 | A | 7 | 30 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 2.7 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 3 | 0
1986-05-09 | 1900-05-08 | 8:00 | 8 | 570 | 1341 | 157 | 1 | 9 | 60 | 1 | 9 | 131 | 1 | 13 | 17200 | 1 | 9 | 5800 | 1 | 9 | 14800 | 1 | 13 | 3940 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 2.8 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 3 | 0
1986-05-09 | 1900-05-08 | 9:00 | 9 | 801 | 1341 | 514 | 1 | 13 | 597 | 1 | 13 | 157 | 1 | 13 | 53800 | 1 | 13 | 59700 | 1 | 13 | 18000 | 1 | 13 | 3660 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.76 | 3 | 0
1986-05-09 | 1900-05-08 | 10:00 | 10 | 995 | 1341 | 384 | 1 | 9 | 57 | 1 | 9 | 342 | 1 | 13 | 42400 | 1 | 9 | 5800 | 1 | 9 | 38000 | 1 | 13 | 12630 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 790 | A | 7 | 3.1 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.84 | 3 | 0
1986-05-09 | 1900-05-08 | 11:00 | 11 | 1139 | 1341 | 740 | 1 | 13 | 603 | 1 | 13 | 228 | 1 | 13 | 78500 | 1 | 13 | 61300 | 1 | 13 | 26300 | 1 | 13 | 9620 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 3.4 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.22 | 3 | 0
1986-05-09 | 1900-05-08 | 12:00 | 12 | 1222 | 1341 | 473 | 1 | 9 | 188 | 1 | 9 | 302 | 1 | 13 | 53100 | 1 | 9 | 20500 | 1 | 9 | 34400 | 1 | 13 | 15490 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 3.4 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 3 | 0
1986-05-09 | 1900-05-08 | 13:00 | 13 | 1239 | 1341 | 631 | 1 | 9 | 141 | 1 | 9 | 500 | 1 | 13 | 68900 | 1 | 9 | 15000 | 1 | 9 | 55000 | 1 | 13 | 26510 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 975 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 3.3 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.52 | 3 | 0
1986-05-09 | 1900-05-08 | 14:00 | 14 | 1189 | 1341 | 737 | 1 | 13 | 502 | 1 | 13 | 292 | 1 | 13 | 80200 | 1 | 13 | 52600 | 1 | 13 | 33500 | 1 | 13 | 14790 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 26.7 | 80.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.6 | A | 7 | 975 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 3.1 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.34 | 3 | 0
1986-05-09 | 1900-05-08 | 15:00 | 15 | 1076 | 1341 | 701 | 1 | 13 | 627 | 1 | 13 | 199 | 1 | 13 | 74700 | 1 | 13 | 63900 | 1 | 13 | 23300 | 1 | 13 | 7180 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 27.8 | 82.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.61 | A | 7 | 974 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.32 | 3 | 0
1986-05-09 | 1900-05-08 | 16:00 | 16 | 906 | 1341 | 619 | 1 | 9 | 666 | 1 | 9 | 170 | 1 | 13 | 65500 | 1 | 9 | 67400 | 1 | 9 | 19800 | 1 | 13 | 4520 | 1 | 18 | 10 | A | 7 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.57 | A | 7 | 974 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.62 | 3 | 0
1986-05-09 | 1900-05-08 | 17:00 | 17 | 693 | 1341 | 331 | 1 | 13 | 353 | 1 | 13 | 149 | 1 | 13 | 35700 | 1 | 13 | 35600 | 1 | 13 | 17200 | 1 | 13 | 3150 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 28.3 | 82.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.55 | A | 7 | 974 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.24 | 3 | 0
1986-05-09 | 1900-05-08 | 18:00 | 18 | 450 | 1341 | 210 | 1 | 13 | 322 | 1 | 13 | 103 | 1 | 13 | 22300 | 1 | 13 | 29500 | 1 | 13 | 12400 | 1 | 13 | 1940 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 27.2 | 80.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.56 | A | 7 | 974 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 3 | 0
1986-05-09 | 1900-05-08 | 19:00 | 19 | 195 | 1341 | 79 | 1 | 13 | 164 | 1 | 13 | 56 | 1 | 13 | 8400 | 1 | 13 | 10200 | 1 | 13 | 6900 | 1 | 13 | 1060 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 25 | 77 | A | 7 | 17.2 | 62.96 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.06 | 3 | 0
1986-05-09 | 1900-05-08 | 20:00 | 20 | 10 | 413 | 6 | 1 | 13 | 10 | 1 | 13 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.71 | A | 7 | 975 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.063 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.06 | 3 | 0
1986-05-09 | 1900-05-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.84 | 3 | 0
1986-05-09 | 1900-05-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.94 | 3 | 0
1986-05-09 | 1900-05-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.62 | 3 | 0
1986-05-09 | 1900-05-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 21.7 | 71.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.74 | 3 | 0
1986-05-10 | 1900-05-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 976 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 1520 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 4 | 0
1986-05-10 | 1900-05-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 4 | 0
1986-05-10 | 1900-05-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 4 | 0
1986-05-10 | 1900-05-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 4 | 0
1986-05-10 | 1900-05-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 17.2 | 62.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.58 | 4 | 0
1986-05-10 | 1900-05-09 | 6:00 | 6 | 75 | 1083 | 9 | 1 | 13 | 4 | 1 | 9 | 9 | 1 | 13 | 1000 | 1 | 13 | 200 | 1 | 9 | 1000 | 1 | 13 | 240 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 1220 | A | 7 | 2.8 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.66 | 4 | 0
1986-05-10 | 1900-05-09 | 7:00 | 7 | 322 | 1340 | 47 | 1 | 13 | 16 | 1 | 9 | 43 | 1 | 13 | 5200 | 1 | 13 | 1300 | 1 | 9 | 4800 | 1 | 13 | 1220 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.97 | A | 7 | 977 | A | 7 | 100 | A | 7 | 1.5 | A | 7 | 6400 | A | 7 | 1040 | A | 7 | 2.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.46 | 4 | 0
1986-05-10 | 1900-05-09 | 8:00 | 8 | 574 | 1340 | 207 | 1 | 9 | 63 | 1 | 9 | 181 | 1 | 13 | 22800 | 1 | 9 | 6100 | 1 | 9 | 20200 | 1 | 13 | 5130 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 490 | A | 7 | 2.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.56 | 4 | 0
1986-05-10 | 1900-05-09 | 9:00 | 9 | 804 | 1340 | 220 | 1 | 9 | 0 | 1 | 9 | 220 | 1 | 13 | 25400 | 1 | 9 | 0 | 1 | 9 | 25400 | 1 | 13 | 9440 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 760 | A | 7 | 2.8 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 4 | 0
1986-05-10 | 1900-05-09 | 10:00 | 10 | 998 | 1340 | 371 | 1 | 9 | 37 | 1 | 9 | 343 | 1 | 13 | 40800 | 1 | 9 | 3800 | 1 | 9 | 38000 | 1 | 13 | 12690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 977 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 760 | A | 7 | 2.8 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.48 | 4 | 0
1986-05-10 | 1900-05-09 | 11:00 | 11 | 1141 | 1340 | 363 | 1 | 9 | 133 | 1 | 9 | 250 | 1 | 13 | 41100 | 1 | 9 | 14300 | 1 | 9 | 28900 | 1 | 13 | 10160 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 2.8 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 4 | 0
1986-05-10 | 1900-05-09 | 12:00 | 12 | 1224 | 1340 | 544 | 1 | 9 | 173 | 1 | 9 | 386 | 1 | 13 | 60400 | 1 | 9 | 18500 | 1 | 9 | 43400 | 1 | 13 | 19450 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 20 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 910 | A | 7 | 2.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.16 | 4 | 0
1986-05-10 | 1900-05-09 | 13:00 | 13 | 1241 | 1340 | 350 | 1 | 9 | 8 | 1 | 9 | 343 | 1 | 13 | 41800 | 1 | 9 | 700 | 1 | 9 | 41100 | 1 | 13 | 15680 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 976 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 550 | A | 7 | 2.8 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 4 | 0
1986-05-10 | 1900-05-09 | 14:00 | 14 | 1191 | 1340 | 330 | 1 | 9 | 32 | 1 | 9 | 302 | 1 | 13 | 36600 | 1 | 9 | 3300 | 1 | 9 | 33700 | 1 | 13 | 14700 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 17.2 | 62.96 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 490 | A | 7 | 2.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.76 | 4 | 0
1986-05-10 | 1900-05-09 | 15:00 | 15 | 1078 | 1340 | 195 | 1 | 9 | 10 | 1 | 9 | 187 | 1 | 13 | 23800 | 1 | 9 | 800 | 1 | 9 | 23200 | 1 | 13 | 9400 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 310 | A | 7 | 2.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.56 | 4 | 0
1986-05-10 | 1900-05-09 | 16:00 | 16 | 909 | 1340 | 254 | 1 | 9 | 3 | 1 | 9 | 253 | 1 | 13 | 29700 | 1 | 9 | 300 | 1 | 9 | 29500 | 1 | 13 | 11160 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 340 | A | 7 | 2.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.36 | 4 | 0
1986-05-10 | 1900-05-09 | 17:00 | 17 | 695 | 1340 | 179 | 1 | 9 | 6 | 1 | 9 | 176 | 1 | 13 | 20700 | 1 | 9 | 500 | 1 | 9 | 20400 | 1 | 13 | 7410 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 910 | A | 7 | 2.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.36 | 4 | 0
1986-05-10 | 1900-05-09 | 18:00 | 18 | 453 | 1340 | 175 | 1 | 9 | 91 | 1 | 9 | 144 | 1 | 13 | 19100 | 1 | 9 | 8500 | 1 | 9 | 16300 | 1 | 13 | 3810 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 4 | 0
1986-05-10 | 1900-05-09 | 19:00 | 19 | 198 | 1340 | 60 | 1 | 13 | 63 | 1 | 13 | 51 | 1 | 13 | 6600 | 1 | 13 | 4300 | 1 | 13 | 6000 | 1 | 13 | 1080 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 4 | 0
1986-05-10 | 1900-05-09 | 20:00 | 20 | 11 | 435 | 2 | 1 | 13 | 1 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 3960 | A | 7 | 2.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.56 | 4 | 0
1986-05-10 | 1900-05-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 1340 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.36 | 4 | 0
1986-05-10 | 1900-05-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.46 | 4 | 0
1986-05-10 | 1900-05-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.38 | 4 | 0
1986-05-10 | 1900-05-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 300 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 4 | 0
1986-05-11 | 1900-05-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 15.6 | 60.08 | A | 7 | 1 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 5 | 0
1986-05-11 | 1900-05-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 15 | 59 | A | 7 | 14.4 | 57.92 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 5 | 0
1986-05-11 | 1900-05-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.9 | 5 | 0
1986-05-11 | 1900-05-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 13.9 | 57.02 | A | 7 | 1 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.02 | 5 | 0
1986-05-11 | 1900-05-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | 12.8 | 55.04 | A | 7 | 1 | A | 7 | 976 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 600 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.94 | 5 | 0
1986-05-11 | 1900-05-10 | 6:00 | 6 | 78 | 1105 | 25 | 1 | 13 | 41 | 1 | 9 | 21 | 1 | 13 | 2700 | 1 | 13 | 2000 | 1 | 9 | 2500 | 1 | 13 | 430 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | 12.8 | 55.04 | A | 7 | 1 | A | 7 | 976 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 2000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.94 | 5 | 0
1986-05-11 | 1900-05-10 | 7:00 | 7 | 325 | 1339 | 149 | 1 | 13 | 366 | 1 | 9 | 61 | 1 | 13 | 16100 | 1 | 13 | 30000 | 1 | 9 | 8800 | 1 | 13 | 1090 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 977 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.9 | 5 | 0
1986-05-11 | 1900-05-10 | 8:00 | 8 | 577 | 1339 | 365 | 1 | 9 | 645 | 1 | 9 | 87 | 1 | 13 | 38500 | 1 | 9 | 62500 | 1 | 9 | 11600 | 1 | 13 | 1790 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.98 | 5 | 0
1986-05-11 | 1900-05-10 | 9:00 | 9 | 807 | 1339 | 553 | 1 | 9 | 733 | 1 | 9 | 112 | 1 | 13 | 57800 | 1 | 9 | 72900 | 1 | 9 | 13900 | 1 | 13 | 2540 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.88 | 5 | 0
1986-05-11 | 1900-05-10 | 10:00 | 10 | 1000 | 1339 | 734 | 1 | 9 | 807 | 1 | 9 | 131 | 1 | 13 | 77700 | 1 | 9 | 81400 | 1 | 9 | 16800 | 1 | 13 | 3860 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.88 | 5 | 0
1986-05-11 | 1900-05-10 | 11:00 | 11 | 1143 | 1339 | 866 | 1 | 9 | 847 | 1 | 9 | 143 | 1 | 13 | 92600 | 1 | 9 | 85800 | 1 | 9 | 19200 | 1 | 13 | 5890 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.64 | A | 7 | 977 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.98 | 5 | 0
1986-05-11 | 1900-05-10 | 12:00 | 12 | 1225 | 1339 | 933 | 1 | 9 | 855 | 1 | 9 | 149 | 1 | 13 | 95400 | 1 | 9 | 85600 | 1 | 9 | 16900 | 1 | 13 | 6510 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.64 | A | 7 | 977 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.78 | 5 | 0
1986-05-11 | 1900-05-10 | 13:00 | 13 | 1243 | 1339 | 957 | 1 | 9 | 868 | 1 | 9 | 151 | 1 | 13 | 97900 | 1 | 9 | 86900 | 1 | 9 | 17100 | 1 | 13 | 7160 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.12 | 5 | 0
1986-05-11 | 1900-05-10 | 14:00 | 14 | 1193 | 1339 | 916 | 1 | 9 | 863 | 1 | 9 | 147 | 1 | 13 | 93900 | 1 | 9 | 86400 | 1 | 9 | 16800 | 1 | 13 | 5560 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 13.3 | 55.94 | A | 7 | 0.48 | A | 7 | 976 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.24 | 5 | 0
1986-05-11 | 1900-05-10 | 15:00 | 15 | 1080 | 1339 | 811 | 1 | 9 | 836 | 1 | 9 | 138 | 1 | 13 | 86400 | 1 | 9 | 84600 | 1 | 9 | 18100 | 1 | 13 | 4800 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.45 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.84 | 5 | 0
1986-05-11 | 1900-05-10 | 16:00 | 16 | 911 | 1339 | 661 | 1 | 9 | 793 | 1 | 9 | 122 | 1 | 13 | 69600 | 1 | 9 | 79600 | 1 | 9 | 15400 | 1 | 13 | 3130 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.42 | A | 7 | 975 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.36 | 5 | 0
1986-05-11 | 1900-05-10 | 17:00 | 17 | 698 | 1339 | 470 | 1 | 9 | 713 | 1 | 9 | 100 | 1 | 13 | 50300 | 1 | 9 | 71200 | 1 | 9 | 13100 | 1 | 13 | 2230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.45 | A | 7 | 974 | A | 7 | 40 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.54 | 5 | 0
1986-05-11 | 1900-05-10 | 18:00 | 18 | 456 | 1339 | 264 | 1 | 9 | 568 | 1 | 9 | 73 | 1 | 13 | 27900 | 1 | 9 | 52100 | 1 | 9 | 10100 | 1 | 13 | 1420 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.47 | A | 7 | 974 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.04 | 5 | 0
1986-05-11 | 1900-05-10 | 19:00 | 19 | 201 | 1339 | 81 | 1 | 13 | 273 | 1 | 9 | 41 | 1 | 13 | 8700 | 1 | 13 | 17800 | 1 | 9 | 6000 | 1 | 13 | 730 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.6 | A | 7 | 974 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.18 | 5 | 0
1986-05-11 | 1900-05-10 | 20:00 | 20 | 12 | 458 | 7 | 1 | 13 | 7 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.92 | 5 | 0
1986-05-11 | 1900-05-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 15 | 59 | A | 7 | 0.68 | A | 7 | 975 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.9 | 5 | 0
1986-05-11 | 1900-05-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 975 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 5 | 0
1986-05-11 | 1900-05-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 5 | 0
1986-05-11 | 1900-05-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 5 | 0
1986-05-12 | 1900-05-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.02 | 6 | 0
1986-05-12 | 1900-05-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.04 | 6 | 0
1986-05-12 | 1900-05-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.52 | 6 | 0
1986-05-12 | 1900-05-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 6 | 0
1986-05-12 | 1900-05-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 6 | 0
1986-05-12 | 1900-05-11 | 6:00 | 6 | 81 | 1127 | 35 | 1 | 13 | 132 | 1 | 9 | 22 | 1 | 13 | 3400 | 1 | 13 | 5800 | 1 | 9 | 2900 | 1 | 13 | 390 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.22 | 6 | 0
1986-05-12 | 1900-05-11 | 7:00 | 7 | 329 | 1339 | 176 | 1 | 13 | 517 | 1 | 9 | 50 | 1 | 13 | 18500 | 1 | 13 | 43100 | 1 | 9 | 7900 | 1 | 13 | 950 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 15 | 59 | A | 7 | 0.81 | A | 7 | 976 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.4 | 6 | 0
1986-05-12 | 1900-05-11 | 8:00 | 8 | 580 | 1339 | 377 | 1 | 9 | 702 | 1 | 9 | 74 | 1 | 13 | 39500 | 1 | 9 | 67500 | 1 | 9 | 10200 | 1 | 13 | 1540 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.26 | 6 | 0
1986-05-12 | 1900-05-11 | 9:00 | 9 | 809 | 1339 | 576 | 1 | 9 | 797 | 1 | 9 | 94 | 1 | 13 | 61400 | 1 | 9 | 79900 | 1 | 9 | 13000 | 1 | 13 | 2280 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.71 | A | 7 | 975 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.06 | 6 | 0
1986-05-12 | 1900-05-11 | 10:00 | 10 | 1002 | 1339 | 747 | 1 | 9 | 852 | 1 | 9 | 109 | 1 | 13 | 77300 | 1 | 9 | 85100 | 1 | 9 | 13500 | 1 | 13 | 2810 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.64 | A | 7 | 975 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.76 | 6 | 0
1986-05-12 | 1900-05-11 | 11:00 | 11 | 1144 | 1339 | 875 | 1 | 9 | 883 | 1 | 9 | 120 | 1 | 13 | 90300 | 1 | 9 | 88400 | 1 | 9 | 14500 | 1 | 13 | 4210 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.54 | A | 7 | 975 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.88 | 6 | 0
1986-05-12 | 1900-05-11 | 12:00 | 12 | 1227 | 1339 | 950 | 1 | 9 | 900 | 1 | 9 | 125 | 1 | 13 | 97900 | 1 | 9 | 90200 | 1 | 9 | 15000 | 1 | 13 | 5910 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 15 | 59 | A | 7 | 0.49 | A | 7 | 974 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.9 | 6 | 0
1986-05-12 | 1900-05-11 | 13:00 | 13 | 1244 | 1339 | 964 | 1 | 9 | 901 | 1 | 9 | 126 | 1 | 13 | 99200 | 1 | 9 | 90400 | 1 | 9 | 15000 | 1 | 13 | 6450 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 15 | 59 | A | 7 | 0.46 | A | 7 | 974 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.3 | 6 | 0
1986-05-12 | 1900-05-11 | 14:00 | 14 | 1194 | 1339 | 920 | 1 | 9 | 894 | 1 | 9 | 123 | 1 | 13 | 94900 | 1 | 9 | 89600 | 1 | 9 | 14800 | 1 | 13 | 5090 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 15 | 59 | A | 7 | 0.44 | A | 7 | 973 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.8 | 6 | 0
1986-05-12 | 1900-05-11 | 15:00 | 15 | 1081 | 1339 | 819 | 1 | 9 | 871 | 1 | 9 | 115 | 1 | 13 | 84600 | 1 | 9 | 87100 | 1 | 9 | 14100 | 1 | 13 | 3440 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.41 | A | 7 | 973 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.32 | 6 | 0
1986-05-12 | 1900-05-11 | 16:00 | 16 | 913 | 1339 | 667 | 1 | 9 | 829 | 1 | 9 | 102 | 1 | 13 | 71700 | 1 | 9 | 83800 | 1 | 9 | 14400 | 1 | 13 | 2780 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.44 | A | 7 | 972 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.68 | 6 | 0
1986-05-12 | 1900-05-11 | 17:00 | 17 | 700 | 1339 | 479 | 1 | 9 | 757 | 1 | 9 | 84 | 1 | 13 | 50800 | 1 | 9 | 74800 | 1 | 9 | 11600 | 1 | 13 | 1880 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.46 | A | 7 | 972 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.08 | 6 | 0
1986-05-12 | 1900-05-11 | 18:00 | 18 | 459 | 1339 | 275 | 1 | 9 | 629 | 1 | 9 | 62 | 1 | 13 | 28700 | 1 | 9 | 57900 | 1 | 9 | 8900 | 1 | 13 | 1230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 15 | 59 | A | 7 | 0.46 | A | 7 | 971 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.3 | 6 | 0
1986-05-12 | 1900-05-11 | 19:00 | 19 | 205 | 1339 | 84 | 1 | 13 | 310 | 1 | 9 | 38 | 1 | 13 | 8700 | 1 | 13 | 21200 | 1 | 9 | 5500 | 1 | 13 | 680 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 26.1 | 78.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.52 | A | 7 | 971 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.48 | 6 | 0
1986-05-12 | 1900-05-11 | 20:00 | 20 | 14 | 480 | 6 | 1 | 13 | 12 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 25 | 77 | A | 7 | 14.4 | 57.92 | A | 7 | 0.52 | A | 7 | 971 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.62 | 6 | 0
1986-05-12 | 1900-05-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.32 | 6 | 0
1986-05-12 | 1900-05-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.58 | A | 7 | 971 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.92 | 6 | 0
1986-05-12 | 1900-05-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 910 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.82 | 6 | 0
1986-05-12 | 1900-05-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 971 | A | 7 | 260 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.44 | 6 | 0
1986-05-13 | 1900-05-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.81 | A | 7 | 972 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.52 | 7 | 0
1986-05-13 | 1900-05-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.14 | 7 | 0
1986-05-13 | 1900-05-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 972 | A | 7 | 210 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.14 | 7 | 0
1986-05-13 | 1900-05-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 972 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.24 | 7 | 0
1986-05-13 | 1900-05-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 3 | A | 7 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 972 | A | 7 | 20 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.24 | 7 | 0
1986-05-13 | 1900-05-12 | 6:00 | 6 | 84 | 1148 | 21 | 1 | 13 | 7 | 1 | 13 | 20 | 1 | 13 | 2300 | 1 | 13 | 400 | 1 | 13 | 2200 | 1 | 13 | 500 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 973 | A | 7 | 350 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 2.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.14 | 7 | 0
1986-05-13 | 1900-05-12 | 7:00 | 7 | 332 | 1338 | 83 | 1 | 13 | 21 | 1 | 9 | 78 | 1 | 13 | 9100 | 1 | 13 | 1800 | 1 | 9 | 8700 | 1 | 13 | 2070 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 16.1 | 60.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.87 | A | 7 | 973 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 820 | A | 7 | 2.4 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.62 | 7 | 0
1986-05-13 | 1900-05-12 | 8:00 | 8 | 582 | 1338 | 92 | 1 | 9 | 20 | 1 | 9 | 83 | 1 | 13 | 10200 | 1 | 9 | 1900 | 1 | 9 | 9300 | 1 | 13 | 2660 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 820 | A | 7 | 2.5 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 7 | 0
1986-05-13 | 1900-05-12 | 9:00 | 9 | 812 | 1338 | 126 | 1 | 9 | 6 | 1 | 9 | 122 | 1 | 13 | 15200 | 1 | 9 | 400 | 1 | 9 | 15000 | 1 | 13 | 5920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 15 | 59 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 4000 | A | 7 | 730 | A | 7 | 2.6 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.4 | 7 | 0
1986-05-13 | 1900-05-12 | 10:00 | 10 | 1004 | 1338 | 498 | 1 | 9 | 255 | 1 | 9 | 306 | 1 | 13 | 54300 | 1 | 9 | 27600 | 1 | 9 | 33600 | 1 | 13 | 9560 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 15.6 | 60.08 | A | 7 | 15.6 | 60.08 | A | 7 | 1 | A | 7 | 973 | A | 7 | 0 | A | 7 | 0 | A | 7 | 3200 | A | 7 | 2440 | A | 7 | 2.7 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 7 | 0
1986-05-13 | 1900-05-12 | 11:00 | 11 | 1146 | 1338 | 469 | 1 | 9 | 95 | 1 | 9 | 388 | 1 | 13 | 51800 | 1 | 9 | 9800 | 1 | 9 | 43400 | 1 | 13 | 17010 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 240 | A | 7 | 2.7 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.48 | 7 | 0
1986-05-13 | 1900-05-12 | 12:00 | 12 | 1229 | 1338 | 543 | 1 | 9 | 155 | 1 | 9 | 400 | 1 | 13 | 60100 | 1 | 9 | 16600 | 1 | 9 | 44800 | 1 | 13 | 20590 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 370 | A | 7 | 2.7 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 7 | 0
1986-05-13 | 1900-05-12 | 13:00 | 13 | 1246 | 1338 | 690 | 1 | 9 | 226 | 1 | 9 | 480 | 1 | 13 | 75700 | 1 | 9 | 24100 | 1 | 9 | 53300 | 1 | 13 | 26270 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 19.4 | 66.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 460 | A | 7 | 2.7 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.28 | 7 | 0
1986-05-13 | 1900-05-12 | 14:00 | 14 | 1196 | 1338 | 926 | 1 | 13 | 767 | 1 | 13 | 240 | 1 | 13 | 98400 | 1 | 13 | 78100 | 1 | 13 | 28500 | 1 | 13 | 12330 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 20.6 | 69.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.73 | A | 7 | 974 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.88 | 7 | 0
1986-05-13 | 1900-05-12 | 15:00 | 15 | 1083 | 1338 | 721 | 1 | 13 | 596 | 1 | 13 | 239 | 1 | 13 | 75800 | 1 | 13 | 60200 | 1 | 13 | 27000 | 1 | 13 | 8660 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 21.7 | 71.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.64 | A | 7 | 973 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.12 | 7 | 0
1986-05-13 | 1900-05-12 | 16:00 | 16 | 915 | 1338 | 585 | 1 | 13 | 538 | 1 | 13 | 218 | 1 | 13 | 63100 | 1 | 13 | 55800 | 1 | 13 | 24900 | 1 | 13 | 5880 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.59 | A | 7 | 973 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.32 | 7 | 0
1986-05-13 | 1900-05-12 | 17:00 | 17 | 703 | 1338 | 443 | 1 | 13 | 473 | 1 | 13 | 195 | 1 | 13 | 46500 | 1 | 13 | 47600 | 1 | 13 | 21400 | 1 | 13 | 4260 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.57 | A | 7 | 973 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.04 | 7 | 0
1986-05-13 | 1900-05-12 | 18:00 | 18 | 462 | 1338 | 251 | 1 | 9 | 502 | 1 | 9 | 79 | 1 | 13 | 26300 | 1 | 9 | 46100 | 1 | 9 | 10300 | 1 | 13 | 1520 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.59 | A | 7 | 973 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.44 | 7 | 0
1986-05-13 | 1900-05-12 | 19:00 | 19 | 208 | 1338 | 81 | 1 | 13 | 237 | 1 | 9 | 45 | 1 | 13 | 8600 | 1 | 13 | 15700 | 1 | 9 | 6200 | 1 | 13 | 800 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 13.3 | 55.94 | A | 7 | 0.66 | A | 7 | 973 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.74 | 7 | 0
1986-05-13 | 1900-05-12 | 20:00 | 20 | 15 | 502 | 8 | 1 | 13 | 5 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 974 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.04 | 7 | 0
1986-05-13 | 1900-05-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.75 | A | 7 | 974 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.64 | 7 | 0
1986-05-13 | 1900-05-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.24 | 7 | 0
1986-05-13 | 1900-05-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.14 | 7 | 0
1986-05-13 | 1900-05-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 7 | 0
1986-05-14 | 1900-05-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.26 | 1 | 0
1986-05-14 | 1900-05-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.36 | 1 | 0
1986-05-14 | 1900-05-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.9 | A | 7 | 973 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.28 | 1 | 0
1986-05-14 | 1900-05-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 11.7 | 53.06 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.86 | 1 | 0
1986-05-14 | 1900-05-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.96 | A | 7 | 974 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.28 | 1 | 0
1986-05-14 | 1900-05-13 | 6:00 | 6 | 87 | 1170 | 39 | 1 | 13 | 185 | 1 | 9 | 21 | 1 | 13 | 3600 | 1 | 13 | 9300 | 1 | 9 | 2900 | 1 | 13 | 380 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.97 | A | 7 | 974 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 1 | 0
1986-05-14 | 1900-05-13 | 7:00 | 7 | 335 | 1337 | 187 | 1 | 13 | 575 | 1 | 9 | 44 | 1 | 13 | 19500 | 1 | 13 | 49000 | 1 | 9 | 7200 | 1 | 13 | 880 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.14 | 1 | 0
1986-05-14 | 1900-05-13 | 8:00 | 8 | 585 | 1337 | 363 | 1 | 9 | 669 | 1 | 9 | 71 | 1 | 13 | 38300 | 1 | 9 | 64600 | 1 | 9 | 10000 | 1 | 13 | 1510 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 974 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.04 | 1 | 0
1986-05-14 | 1900-05-13 | 9:00 | 9 | 814 | 1337 | 545 | 1 | 9 | 731 | 1 | 9 | 101 | 1 | 13 | 57800 | 1 | 9 | 73100 | 1 | 9 | 13200 | 1 | 13 | 2410 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 20.6 | 69.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.59 | A | 7 | 974 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.66 | 1 | 0
1986-05-14 | 1900-05-13 | 10:00 | 10 | 1006 | 1337 | 713 | 1 | 9 | 778 | 1 | 9 | 127 | 1 | 13 | 75700 | 1 | 9 | 78600 | 1 | 9 | 16500 | 1 | 13 | 3840 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.53 | A | 7 | 973 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.76 | 1 | 0
1986-05-14 | 1900-05-13 | 11:00 | 11 | 1148 | 1337 | 827 | 1 | 9 | 769 | 1 | 9 | 166 | 1 | 13 | 87000 | 1 | 9 | 77500 | 1 | 9 | 20400 | 1 | 13 | 6760 | 1 | 18 | 8 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.48 | A | 7 | 974 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.28 | 1 | 0
1986-05-14 | 1900-05-13 | 12:00 | 12 | 1230 | 1337 | 892 | 1 | 9 | 788 | 1 | 9 | 167 | 1 | 13 | 94800 | 1 | 9 | 79700 | 1 | 9 | 21400 | 1 | 13 | 9390 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.48 | A | 7 | 973 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.56 | 1 | 0
1986-05-14 | 1900-05-13 | 13:00 | 13 | 1247 | 1337 | 887 | 1 | 9 | 754 | 1 | 9 | 184 | 1 | 13 | 93500 | 1 | 9 | 76000 | 1 | 9 | 22600 | 1 | 13 | 11090 | 1 | 18 | 7 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.48 | A | 7 | 971 | A | 7 | 110 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.44 | 1 | 0
1986-05-14 | 1900-05-13 | 14:00 | 14 | 1198 | 1337 | 717 | 1 | 13 | 516 | 1 | 13 | 255 | 1 | 13 | 75900 | 1 | 13 | 52400 | 1 | 13 | 28900 | 1 | 13 | 13150 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 25 | 77 | A | 7 | 13.3 | 55.94 | A | 7 | 0.48 | A | 7 | 971 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.24 | 1 | 0
1986-05-14 | 1900-05-13 | 15:00 | 15 | 1085 | 1337 | 437 | 1 | 9 | 123 | 1 | 9 | 337 | 1 | 13 | 48300 | 1 | 9 | 13100 | 1 | 9 | 37700 | 1 | 13 | 12400 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 24.4 | 75.92 | A | 7 | 10 | 50 | A | 7 | 0.4 | A | 7 | 971 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 1.9 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.9 | 1 | 0
1986-05-14 | 1900-05-13 | 16:00 | 16 | 917 | 1337 | 269 | 1 | 9 | 7 | 1 | 9 | 264 | 1 | 13 | 31200 | 1 | 9 | 600 | 1 | 9 | 30800 | 1 | 13 | 11580 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.6 | A | 7 | 970 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.32 | 1 | 0
1986-05-14 | 1900-05-13 | 17:00 | 17 | 705 | 1337 | 169 | 1 | 9 | 6 | 1 | 9 | 166 | 1 | 13 | 19700 | 1 | 9 | 500 | 1 | 9 | 19400 | 1 | 13 | 7160 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 15 | 59 | A | 7 | 0.64 | A | 7 | 970 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 2.6 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.1 | 1 | 0
1986-05-14 | 1900-05-13 | 18:00 | 18 | 464 | 1337 | 146 | 1 | 9 | 4 | 1 | 9 | 145 | 1 | 13 | 16300 | 1 | 9 | 300 | 1 | 9 | 16200 | 1 | 13 | 5160 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.64 | A | 7 | 971 | A | 7 | 150 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 1280 | A | 7 | 2.5 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.12 | 1 | 0
1986-05-14 | 1900-05-13 | 19:00 | 19 | 212 | 1337 | 39 | 1 | 13 | 1 | 1 | 9 | 38 | 1 | 13 | 4400 | 1 | 13 | 0 | 1 | 9 | 4400 | 1 | 13 | 1400 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.68 | A | 7 | 970 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 2.3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.14 | 1 | 0
1986-05-14 | 1900-05-13 | 20:00 | 20 | 16 | 502 | 7 | 1 | 13 | 0 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.76 | A | 7 | 969 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 2.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.62 | 1 | 0
1986-05-14 | 1900-05-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 970 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 1 | 0
1986-05-14 | 1900-05-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 15.6 | 60.08 | A | 7 | 0.9 | A | 7 | 971 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.18 | 1 | 0
1986-05-14 | 1900-05-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.93 | A | 7 | 971 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.58 | 1 | 0
1986-05-14 | 1900-05-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 970 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 1 | 0
1986-05-15 | 1900-05-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 970 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 2 | 0
1986-05-15 | 1900-05-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.97 | A | 7 | 970 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 1680 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 2 | 0
1986-05-15 | 1900-05-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.97 | A | 7 | 970 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 1680 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 2 | 0
1986-05-15 | 1900-05-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 15.6 | 60.08 | A | 7 | 1 | A | 7 | 969 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 1830 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 2 | 0
1986-05-15 | 1900-05-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 15 | 59 | A | 7 | 0.97 | A | 7 | 969 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 1520 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.4 | 2 | 0
1986-05-15 | 1900-05-14 | 6:00 | 6 | 90 | 1170 | 12 | 1 | 13 | 0 | 1 | 9 | 12 | 1 | 13 | 1400 | 1 | 13 | 0 | 1 | 9 | 1400 | 1 | 13 | 460 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 15 | 59 | A | 7 | 0.97 | A | 7 | 969 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 1340 | A | 7 | 2.6 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.4 | 2 | 0
1986-05-15 | 1900-05-14 | 7:00 | 7 | 338 | 1337 | 46 | 1 | 13 | 2 | 1 | 9 | 45 | 1 | 13 | 5400 | 1 | 13 | 100 | 1 | 9 | 5400 | 1 | 13 | 1850 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 15.6 | 60.08 | A | 7 | 1 | A | 7 | 970 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 1040 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 2 | 0
1986-05-15 | 1900-05-14 | 8:00 | 8 | 588 | 1337 | 180 | 1 | 9 | 3 | 1 | 9 | 179 | 1 | 13 | 20300 | 1 | 9 | 200 | 1 | 9 | 20200 | 1 | 13 | 6810 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.97 | A | 7 | 970 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 120 | A | 7 | 2.8 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.38 | 2 | 0
1986-05-15 | 1900-05-14 | 9:00 | 9 | 816 | 1337 | 364 | 1 | 9 | 172 | 1 | 9 | 259 | 1 | 13 | 39900 | 1 | 9 | 18100 | 1 | 9 | 28900 | 1 | 13 | 7070 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 970 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 210 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 2 | 0
1986-05-15 | 1900-05-14 | 10:00 | 10 | 1008 | 1337 | 283 | 1 | 9 | 10 | 1 | 9 | 275 | 1 | 13 | 33200 | 1 | 9 | 900 | 1 | 9 | 32500 | 1 | 13 | 12500 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 971 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 2 | 0
1986-05-15 | 1900-05-14 | 11:00 | 11 | 1149 | 1337 | 559 | 1 | 9 | 215 | 1 | 9 | 375 | 1 | 13 | 61900 | 1 | 9 | 23000 | 1 | 9 | 42100 | 1 | 13 | 15620 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 971 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 2.8 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 2 | 0
1986-05-15 | 1900-05-14 | 12:00 | 12 | 1232 | 1337 | 417 | 1 | 9 | 107 | 1 | 9 | 318 | 1 | 13 | 46800 | 1 | 9 | 11500 | 1 | 9 | 36200 | 1 | 13 | 16590 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 20.6 | 69.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.73 | A | 7 | 971 | A | 7 | 260 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.88 | 2 | 0
1986-05-15 | 1900-05-14 | 13:00 | 13 | 1248 | 1337 | 694 | 1 | 9 | 382 | 1 | 9 | 337 | 1 | 13 | 75000 | 1 | 9 | 40000 | 1 | 9 | 37600 | 1 | 13 | 22420 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 22.8 | 73.04 | A | 7 | 15 | 59 | A | 7 | 0.62 | A | 7 | 971 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 2.6 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.7 | 2 | 0
1986-05-15 | 1900-05-14 | 14:00 | 14 | 1199 | 1337 | 651 | 1 | 9 | 345 | 1 | 9 | 342 | 1 | 13 | 72300 | 1 | 9 | 37600 | 1 | 9 | 38500 | 1 | 13 | 16540 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.62 | A | 7 | 972 | A | 7 | 260 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1070 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.58 | 2 | 0
1986-05-15 | 1900-05-14 | 15:00 | 15 | 1087 | 1337 | 763 | 1 | 13 | 610 | 1 | 13 | 268 | 1 | 13 | 79600 | 1 | 13 | 61200 | 1 | 13 | 29800 | 1 | 13 | 9690 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 23.9 | 75.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.6 | A | 7 | 972 | A | 7 | 250 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.18 | 2 | 0
1986-05-15 | 1900-05-14 | 16:00 | 16 | 919 | 1337 | 610 | 1 | 13 | 661 | 1 | 13 | 156 | 1 | 13 | 64900 | 1 | 13 | 67200 | 1 | 13 | 18600 | 1 | 13 | 4290 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 25 | 77 | A | 7 | 15.6 | 60.08 | A | 7 | 0.56 | A | 7 | 972 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.28 | 2 | 0
1986-05-15 | 1900-05-14 | 17:00 | 17 | 708 | 1337 | 447 | 1 | 13 | 609 | 1 | 13 | 126 | 1 | 13 | 47100 | 1 | 13 | 60400 | 1 | 13 | 15000 | 1 | 13 | 2750 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 24.4 | 75.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.6 | A | 7 | 973 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.98 | 2 | 0
1986-05-15 | 1900-05-14 | 18:00 | 18 | 467 | 1337 | 257 | 1 | 9 | 474 | 1 | 9 | 93 | 1 | 13 | 27800 | 1 | 9 | 44000 | 1 | 9 | 12300 | 1 | 13 | 1730 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.6 | A | 7 | 973 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.18 | 2 | 0
1986-05-15 | 1900-05-14 | 19:00 | 19 | 215 | 1337 | 91 | 1 | 13 | 321 | 1 | 9 | 41 | 1 | 13 | 9500 | 1 | 13 | 22400 | 1 | 9 | 5900 | 1 | 13 | 740 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.66 | A | 7 | 973 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.18 | 2 | 0
1986-05-15 | 1900-05-14 | 20:00 | 20 | 17 | 524 | 7 | 1 | 13 | 12 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 20.6 | 69.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.76 | A | 7 | 974 | A | 7 | 180 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.28 | 2 | 0
1986-05-15 | 1900-05-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 2 | 0
1986-05-15 | 1900-05-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 15 | 59 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.5 | 2 | 0
1986-05-15 | 1900-05-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 2 | 0
1986-05-15 | 1900-05-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 3 | A | 7 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.98 | 2 | 0
1986-05-16 | 1900-05-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 3 | 0
1986-05-16 | 1900-05-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 3 | 0
1986-05-16 | 1900-05-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 1340 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.38 | 3 | 0
1986-05-16 | 1900-05-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 6 | A | 7 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.66 | 3 | 0
1986-05-16 | 1900-05-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 850 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.46 | 3 | 0
1986-05-16 | 1900-05-15 | 6:00 | 6 | 93 | 1192 | 12 | 1 | 13 | 1 | 1 | 9 | 12 | 1 | 13 | 1400 | 1 | 13 | 0 | 1 | 9 | 1400 | 1 | 13 | 460 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.97 | A | 7 | 974 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 4800 | A | 7 | 460 | A | 7 | 2.9 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.36 | 3 | 0
1986-05-16 | 1900-05-15 | 7:00 | 7 | 341 | 1336 | 72 | 1 | 13 | 3 | 1 | 9 | 71 | 1 | 13 | 8200 | 1 | 13 | 100 | 1 | 9 | 8200 | 1 | 13 | 2700 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 4000 | A | 7 | 580 | A | 7 | 3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.36 | 3 | 0
1986-05-16 | 1900-05-15 | 8:00 | 8 | 590 | 1336 | 135 | 1 | 9 | 1 | 1 | 9 | 135 | 1 | 13 | 15600 | 1 | 9 | 100 | 1 | 9 | 15600 | 1 | 13 | 5600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 2400 | A | 7 | 610 | A | 7 | 3.1 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.34 | 3 | 0
1986-05-16 | 1900-05-15 | 9:00 | 9 | 818 | 1336 | 226 | 1 | 9 | 6 | 1 | 9 | 222 | 1 | 13 | 26100 | 1 | 9 | 500 | 1 | 9 | 25800 | 1 | 13 | 9610 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.97 | A | 7 | 976 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 1600 | A | 7 | 430 | A | 7 | 3.2 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.34 | 3 | 0
1986-05-16 | 1900-05-15 | 10:00 | 10 | 1009 | 1336 | 271 | 1 | 9 | 6 | 1 | 9 | 266 | 1 | 13 | 31900 | 1 | 9 | 500 | 1 | 9 | 31500 | 1 | 13 | 12210 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 20 | 68 | A | 7 | 0.97 | A | 7 | 976 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 4000 | A | 7 | 210 | A | 7 | 3.5 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.3 | 3 | 0
1986-05-16 | 1900-05-15 | 11:00 | 11 | 1151 | 1336 | 496 | 1 | 9 | 183 | 1 | 9 | 338 | 1 | 13 | 55200 | 1 | 9 | 19600 | 1 | 9 | 38200 | 1 | 13 | 14140 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 22.2 | 71.96 | A | 7 | 20 | 68 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 4800 | A | 7 | 270 | A | 7 | 3.4 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.2 | 3 | 0
1986-05-16 | 1900-05-15 | 12:00 | 12 | 1233 | 1336 | 694 | 1 | 13 | 410 | 1 | 13 | 315 | 1 | 13 | 75300 | 1 | 13 | 42900 | 1 | 13 | 35600 | 1 | 13 | 19420 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 8000 | A | 7 | 3050 | A | 7 | 3.3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 3 | 0
1986-05-16 | 1900-05-15 | 13:00 | 13 | 1250 | 1336 | 469 | 1 | 9 | 84 | 1 | 9 | 390 | 1 | 13 | 51900 | 1 | 9 | 8600 | 1 | 9 | 43800 | 1 | 13 | 21070 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 975 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 9700 | A | 7 | 3050 | A | 7 | 3.3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 3 | 0
1986-05-16 | 1900-05-15 | 14:00 | 14 | 1200 | 1336 | 512 | 1 | 9 | 140 | 1 | 9 | 386 | 1 | 13 | 56700 | 1 | 9 | 15000 | 1 | 9 | 43200 | 1 | 13 | 18300 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 975 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 3.2 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.82 | 3 | 0
1986-05-16 | 1900-05-15 | 15:00 | 15 | 1088 | 1336 | 322 | 1 | 9 | 2 | 1 | 9 | 321 | 1 | 13 | 37900 | 1 | 9 | 200 | 1 | 9 | 37700 | 1 | 13 | 14420 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 974 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 2440 | A | 7 | 3.3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 3 | 0
1986-05-16 | 1900-05-15 | 16:00 | 16 | 921 | 1336 | 511 | 1 | 9 | 276 | 1 | 9 | 321 | 1 | 13 | 55000 | 1 | 9 | 29600 | 1 | 9 | 34500 | 1 | 13 | 9190 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 974 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 3.3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 3 | 0
1986-05-16 | 1900-05-15 | 17:00 | 17 | 710 | 1336 | 187 | 1 | 9 | 1 | 1 | 9 | 187 | 1 | 13 | 21600 | 1 | 9 | 100 | 1 | 9 | 21600 | 1 | 13 | 7850 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 974 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 3.4 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 3 | 0
1986-05-16 | 1900-05-15 | 18:00 | 18 | 470 | 1336 | 153 | 1 | 9 | 60 | 1 | 9 | 132 | 1 | 13 | 16800 | 1 | 9 | 5600 | 1 | 9 | 14800 | 1 | 13 | 3630 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 973 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 3.3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 3 | 0
1986-05-16 | 1900-05-15 | 19:00 | 19 | 218 | 1336 | 39 | 1 | 13 | 66 | 1 | 9 | 28 | 1 | 13 | 4300 | 1 | 13 | 4400 | 1 | 9 | 3600 | 1 | 13 | 470 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 973 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 6100 | A | 7 | 3.3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 3 | 0
1986-05-16 | 1900-05-15 | 20:00 | 20 | 19 | 546 | 4 | 1 | 13 | 1 | 1 | 9 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.82 | A | 7 | 974 | A | 7 | 170 | A | 7 | 9.8 | A | 7 | 16100 | A | 7 | 4570 | A | 7 | 3.4 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.12 | 3 | 0
1986-05-16 | 1900-05-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 910 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 3 | 0
1986-05-16 | 1900-05-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 977 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.9 | 3 | 0
1986-05-16 | 1900-05-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 976 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 180 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.9 | 3 | 0
1986-05-16 | 1900-05-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 974 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 2440 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.9 | 3 | 0
1986-05-17 | 1900-05-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.9 | 4 | 0
1986-05-17 | 1900-05-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 975 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 150 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.9 | 4 | 0
1986-05-17 | 1900-05-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 974 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 90 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.84 | 4 | 0
1986-05-17 | 1900-05-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.8 | 55.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.97 | A | 7 | 974 | A | 7 | 10 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 90 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.46 | 4 | 0
1986-05-17 | 1900-05-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 12.2 | 53.96 | A | 7 | 1 | A | 7 | 975 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 90 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.86 | 4 | 0
1986-05-17 | 1900-05-16 | 6:00 | 6 | 96 | 1213 | 9 | 1 | 13 | 2 | 1 | 9 | 9 | 1 | 13 | 1100 | 1 | 13 | 0 | 1 | 9 | 1100 | 1 | 13 | 360 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.96 | A | 7 | 975 | A | 7 | 340 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 90 | A | 7 | 2 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.38 | 4 | 0
1986-05-17 | 1900-05-16 | 7:00 | 7 | 344 | 1336 | 38 | 1 | 13 | 1 | 1 | 9 | 37 | 1 | 13 | 4500 | 1 | 13 | 0 | 1 | 9 | 4500 | 1 | 13 | 1570 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 1.8 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.92 | 4 | 0
1986-05-17 | 1900-05-16 | 8:00 | 8 | 593 | 1336 | 82 | 1 | 9 | 1 | 1 | 9 | 81 | 1 | 13 | 9800 | 1 | 9 | 100 | 1 | 9 | 9800 | 1 | 13 | 3700 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 975 | A | 7 | 340 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 240 | A | 7 | 1.8 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 4 | 0
1986-05-17 | 1900-05-16 | 9:00 | 9 | 820 | 1336 | 156 | 1 | 9 | 3 | 1 | 9 | 154 | 1 | 13 | 18600 | 1 | 9 | 200 | 1 | 9 | 18400 | 1 | 13 | 7240 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 240 | A | 7 | 1.8 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.92 | 4 | 0
1986-05-17 | 1900-05-16 | 10:00 | 10 | 1011 | 1336 | 170 | 1 | 9 | 0 | 1 | 9 | 170 | 1 | 13 | 20700 | 1 | 9 | 0 | 1 | 9 | 20700 | 1 | 13 | 8530 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 975 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 240 | A | 7 | 1.8 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 4 | 0
1986-05-17 | 1900-05-16 | 11:00 | 11 | 1152 | 1336 | 264 | 1 | 9 | 5 | 1 | 9 | 260 | 1 | 13 | 31800 | 1 | 9 | 400 | 1 | 9 | 31500 | 1 | 13 | 12480 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 350 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 1.9 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.82 | 4 | 0
1986-05-17 | 1900-05-16 | 12:00 | 12 | 1234 | 1336 | 406 | 1 | 9 | 4 | 1 | 9 | 403 | 1 | 13 | 47900 | 1 | 9 | 400 | 1 | 9 | 47500 | 1 | 13 | 17540 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 340 | A | 7 | 1.9 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.32 | 4 | 0
1986-05-17 | 1900-05-16 | 13:00 | 13 | 1251 | 1336 | 398 | 1 | 9 | 0 | 1 | 9 | 398 | 1 | 13 | 47000 | 1 | 9 | 0 | 1 | 9 | 47000 | 1 | 13 | 17470 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 370 | A | 7 | 1.9 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.32 | 4 | 0
1986-05-17 | 1900-05-16 | 14:00 | 14 | 1202 | 1336 | 404 | 1 | 9 | 0 | 1 | 9 | 404 | 1 | 13 | 47400 | 1 | 9 | 0 | 1 | 9 | 47400 | 1 | 13 | 17410 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 350 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 460 | A | 7 | 1.8 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.72 | 4 | 0
1986-05-17 | 1900-05-16 | 15:00 | 15 | 1090 | 1336 | 379 | 1 | 9 | 0 | 1 | 9 | 379 | 1 | 13 | 43900 | 1 | 9 | 0 | 1 | 9 | 43900 | 1 | 13 | 16130 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 12.8 | 55.04 | A | 7 | 10 | 50 | A | 7 | 0.83 | A | 7 | 976 | A | 7 | 340 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 1.9 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.3 | 4 | 0
1986-05-17 | 1900-05-16 | 16:00 | 16 | 923 | 1336 | 329 | 1 | 9 | 1 | 1 | 9 | 328 | 1 | 13 | 37600 | 1 | 9 | 100 | 1 | 9 | 37500 | 1 | 13 | 13430 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 1.9 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.5 | 4 | 0
1986-05-17 | 1900-05-16 | 17:00 | 17 | 713 | 1336 | 219 | 1 | 9 | 56 | 1 | 9 | 189 | 1 | 13 | 24100 | 1 | 9 | 5600 | 1 | 9 | 21100 | 1 | 13 | 6010 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 13.9 | 57.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.72 | A | 7 | 977 | A | 7 | 340 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 1040 | A | 7 | 1.8 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.72 | 4 | 0
1986-05-17 | 1900-05-16 | 18:00 | 18 | 473 | 1336 | 104 | 1 | 9 | 14 | 1 | 9 | 100 | 1 | 13 | 12100 | 1 | 9 | 900 | 1 | 9 | 11800 | 1 | 13 | 4020 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.72 | A | 7 | 977 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 1400 | A | 7 | 1.8 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.72 | 4 | 0
1986-05-17 | 1900-05-16 | 19:00 | 19 | 221 | 1336 | 51 | 1 | 13 | 12 | 1 | 9 | 50 | 1 | 13 | 5900 | 1 | 13 | 200 | 1 | 9 | 5800 | 1 | 13 | 1750 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 13.9 | 57.02 | A | 7 | 9.4 | 48.92 | A | 7 | 0.75 | A | 7 | 978 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 1680 | A | 7 | 1.9 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.02 | 4 | 0
1986-05-17 | 1900-05-16 | 20:00 | 20 | 20 | 568 | 9 | 1 | 13 | 0 | 1 | 9 | 9 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 9.4 | 48.92 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 1.9 | E | 8 | 0.135 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.42 | 4 | 0
1986-05-17 | 1900-05-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 11.7 | 53.06 | A | 7 | 10 | 50 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.4 | 4 | 0
1986-05-17 | 1900-05-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 11.7 | 53.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.72 | 4 | 0
1986-05-17 | 1900-05-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 6 | A | 7 | 11.7 | 53.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.83 | A | 7 | 979 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.42 | 4 | 0
1986-05-17 | 1900-05-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 11.1 | 51.98 | A | 7 | 8.9 | 48.02 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.82 | 4 | 0
1986-05-18 | 1900-05-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 979 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.34 | 5 | 0
1986-05-18 | 1900-05-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 10.6 | 51.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.84 | 5 | 0
1986-05-18 | 1900-05-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 9.4 | 48.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.54 | 5 | 0
1986-05-18 | 1900-05-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 8.9 | 48.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.89 | A | 7 | 978 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.36 | 5 | 0
1986-05-18 | 1900-05-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 4 | A | 7 | 8.9 | 48.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.89 | A | 7 | 978 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.36 | 5 | 0
1986-05-18 | 1900-05-17 | 6:00 | 6 | 99 | 1235 | 29 | 1 | 13 | 12 | 1 | 13 | 28 | 1 | 13 | 3200 | 1 | 13 | 700 | 1 | 13 | 3100 | 1 | 13 | 670 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 9.4 | 48.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 1.6 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.96 | 5 | 0
1986-05-18 | 1900-05-17 | 7:00 | 7 | 347 | 1335 | 138 | 1 | 13 | 79 | 1 | 13 | 117 | 1 | 13 | 15000 | 1 | 13 | 7000 | 1 | 13 | 13200 | 1 | 13 | 2890 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 10 | 50 | A | 7 | 7.8 | 46.04 | A | 7 | 0.86 | A | 7 | 980 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 5 | 0
1986-05-18 | 1900-05-17 | 8:00 | 8 | 595 | 1335 | 234 | 1 | 9 | 75 | 1 | 9 | 201 | 1 | 13 | 25700 | 1 | 9 | 7400 | 1 | 9 | 22400 | 1 | 13 | 5690 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 11.7 | 53.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.64 | 5 | 0
1986-05-18 | 1900-05-17 | 9:00 | 9 | 822 | 1335 | 413 | 1 | 9 | 262 | 1 | 9 | 251 | 1 | 13 | 44500 | 1 | 9 | 27900 | 1 | 9 | 27300 | 1 | 13 | 6340 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 13.9 | 57.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 5 | 0
1986-05-18 | 1900-05-17 | 10:00 | 10 | 1013 | 1335 | 350 | 1 | 9 | 75 | 1 | 9 | 293 | 1 | 13 | 38600 | 1 | 9 | 7700 | 1 | 9 | 32800 | 1 | 13 | 11370 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 15 | 59 | A | 7 | 7.8 | 46.04 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 360 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.34 | 5 | 0
1986-05-18 | 1900-05-17 | 11:00 | 11 | 1154 | 1335 | 671 | 1 | 9 | 400 | 1 | 9 | 325 | 1 | 13 | 71900 | 1 | 9 | 41800 | 1 | 9 | 35700 | 1 | 13 | 14900 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 16.1 | 60.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 10 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.74 | 5 | 0
1986-05-18 | 1900-05-17 | 12:00 | 12 | 1235 | 1335 | 419 | 1 | 9 | 79 | 1 | 9 | 346 | 1 | 13 | 46400 | 1 | 9 | 8100 | 1 | 9 | 38900 | 1 | 13 | 18320 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 17.8 | 64.04 | A | 7 | 8.3 | 46.94 | A | 7 | 0.54 | A | 7 | 980 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.84 | 5 | 0
1986-05-18 | 1900-05-17 | 13:00 | 13 | 1252 | 1335 | 676 | 1 | 9 | 364 | 1 | 9 | 335 | 1 | 13 | 73200 | 1 | 9 | 38100 | 1 | 9 | 37400 | 1 | 13 | 22920 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 16.7 | 62.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.34 | 5 | 0
1986-05-18 | 1900-05-17 | 14:00 | 14 | 1203 | 1335 | 583 | 1 | 9 | 213 | 1 | 9 | 391 | 1 | 13 | 64600 | 1 | 9 | 22800 | 1 | 9 | 44000 | 1 | 13 | 18740 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 17.2 | 62.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.54 | A | 7 | 980 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.04 | 5 | 0
1986-05-18 | 1900-05-17 | 15:00 | 15 | 1092 | 1335 | 309 | 1 | 9 | 64 | 1 | 9 | 257 | 1 | 13 | 34300 | 1 | 9 | 6500 | 1 | 9 | 28900 | 1 | 13 | 11090 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 17.2 | 62.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.54 | A | 7 | 979 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.04 | 5 | 0
1986-05-18 | 1900-05-17 | 16:00 | 16 | 925 | 1335 | 490 | 1 | 13 | 354 | 1 | 13 | 245 | 1 | 13 | 53900 | 1 | 13 | 38200 | 1 | 13 | 27400 | 1 | 13 | 6740 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 18.3 | 64.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.52 | A | 7 | 979 | A | 7 | 10 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.54 | 5 | 0
1986-05-18 | 1900-05-17 | 17:00 | 17 | 715 | 1335 | 404 | 1 | 13 | 376 | 1 | 13 | 203 | 1 | 13 | 43700 | 1 | 13 | 39400 | 1 | 13 | 22500 | 1 | 13 | 4660 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.14 | 5 | 0
1986-05-18 | 1900-05-17 | 18:00 | 18 | 476 | 1335 | 212 | 1 | 13 | 286 | 1 | 13 | 111 | 1 | 13 | 23000 | 1 | 13 | 27400 | 1 | 13 | 13200 | 1 | 13 | 2180 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 17.8 | 64.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.52 | A | 7 | 979 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.74 | 5 | 0
1986-05-18 | 1900-05-17 | 19:00 | 19 | 224 | 1335 | 78 | 1 | 13 | 154 | 1 | 13 | 52 | 1 | 13 | 8300 | 1 | 13 | 10500 | 1 | 13 | 6500 | 1 | 13 | 950 | 1 | 23 | 7 | A | 7 | 4 | A | 7 | 15.6 | 60.08 | A | 7 | 6.7 | 44.06 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.66 | 5 | 0
1986-05-18 | 1900-05-17 | 20:00 | 20 | 21 | 590 | 10 | 1 | 13 | 5 | 1 | 13 | 9 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 13.9 | 57.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 5 | 0
1986-05-18 | 1900-05-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 13.9 | 57.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 5 | 0
1986-05-18 | 1900-05-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 12.8 | 55.04 | A | 7 | 9.4 | 48.92 | A | 7 | 0.8 | A | 7 | 981 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 1830 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.82 | 5 | 0
1986-05-18 | 1900-05-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 13.9 | 57.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 1830 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.72 | 5 | 0
1986-05-18 | 1900-05-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 12.8 | 55.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 1830 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.42 | 5 | 0
1986-05-19 | 1900-05-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.34 | 6 | 0
1986-05-19 | 1900-05-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.54 | 6 | 0
1986-05-19 | 1900-05-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.89 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.36 | 6 | 0
1986-05-19 | 1900-05-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.06 | 6 | 0
1986-05-19 | 1900-05-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 8.3 | 46.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.89 | A | 7 | 981 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.46 | 6 | 0
1986-05-19 | 1900-05-18 | 6:00 | 6 | 102 | 1257 | 27 | 1 | 13 | 39 | 1 | 9 | 24 | 1 | 13 | 3000 | 1 | 13 | 2000 | 1 | 9 | 2900 | 1 | 13 | 500 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 8.9 | 48.02 | A | 7 | 6.7 | 44.06 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.06 | 6 | 0
1986-05-19 | 1900-05-18 | 7:00 | 7 | 349 | 1335 | 167 | 1 | 9 | 351 | 1 | 9 | 76 | 1 | 13 | 17800 | 1 | 9 | 29600 | 1 | 9 | 10000 | 1 | 13 | 1390 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.8 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 6 | 0
1986-05-19 | 1900-05-18 | 8:00 | 8 | 597 | 1335 | 368 | 1 | 9 | 568 | 1 | 9 | 115 | 1 | 13 | 38400 | 1 | 9 | 54800 | 1 | 9 | 13800 | 1 | 13 | 2300 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.72 | A | 7 | 983 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.72 | 6 | 0
1986-05-19 | 1900-05-18 | 9:00 | 9 | 824 | 1335 | 572 | 1 | 9 | 687 | 1 | 9 | 148 | 1 | 13 | 60400 | 1 | 9 | 69200 | 1 | 9 | 17600 | 1 | 13 | 3590 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 6.7 | 44.06 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 360 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.06 | 6 | 0
1986-05-19 | 1900-05-18 | 10:00 | 10 | 1014 | 1335 | 749 | 1 | 9 | 759 | 1 | 9 | 172 | 1 | 13 | 80000 | 1 | 9 | 77600 | 1 | 9 | 20900 | 1 | 13 | 5550 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.5 | A | 7 | 983 | A | 7 | 20 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.76 | 6 | 0
1986-05-19 | 1900-05-18 | 11:00 | 11 | 1155 | 1335 | 836 | 1 | 13 | 696 | 1 | 13 | 233 | 1 | 13 | 88700 | 1 | 13 | 70800 | 1 | 13 | 27300 | 1 | 13 | 10490 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 18.3 | 64.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.43 | A | 7 | 983 | A | 7 | 20 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.08 | 6 | 0
1986-05-19 | 1900-05-18 | 12:00 | 12 | 1237 | 1335 | 869 | 1 | 13 | 587 | 1 | 13 | 324 | 1 | 13 | 94100 | 1 | 13 | 61500 | 1 | 13 | 37000 | 1 | 13 | 20500 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 18.3 | 64.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.45 | A | 7 | 983 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.08 | 6 | 0
1986-05-19 | 1900-05-18 | 13:00 | 13 | 1253 | 1335 | 786 | 1 | 13 | 543 | 1 | 13 | 276 | 1 | 13 | 83200 | 1 | 13 | 55100 | 1 | 13 | 31400 | 1 | 13 | 18510 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 19.4 | 66.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.44 | A | 7 | 983 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.86 | 6 | 0
1986-05-19 | 1900-05-18 | 14:00 | 14 | 1205 | 1335 | 892 | 1 | 13 | 672 | 1 | 13 | 285 | 1 | 13 | 93700 | 1 | 13 | 67800 | 1 | 13 | 32400 | 1 | 13 | 15130 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 18.3 | 64.94 | A | 7 | 4.4 | 39.92 | A | 7 | 0.4 | A | 7 | 983 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.42 | 6 | 0
1986-05-19 | 1900-05-18 | 15:00 | 15 | 1093 | 1335 | 792 | 1 | 13 | 642 | 1 | 13 | 267 | 1 | 13 | 82800 | 1 | 13 | 64500 | 1 | 13 | 29800 | 1 | 13 | 9870 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 19.4 | 66.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.4 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.68 | 6 | 0
1986-05-19 | 1900-05-18 | 16:00 | 16 | 927 | 1335 | 640 | 1 | 13 | 614 | 1 | 13 | 214 | 1 | 13 | 66600 | 1 | 13 | 61500 | 1 | 13 | 23800 | 1 | 13 | 5720 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 20 | 68 | A | 7 | 6.1 | 42.98 | A | 7 | 0.41 | A | 7 | 982 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.48 | 6 | 0
1986-05-19 | 1900-05-18 | 17:00 | 17 | 717 | 1335 | 390 | 1 | 13 | 414 | 1 | 13 | 169 | 1 | 13 | 41800 | 1 | 13 | 41900 | 1 | 13 | 19200 | 1 | 13 | 3670 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 20 | 68 | A | 7 | 5.6 | 42.08 | A | 7 | 0.39 | A | 7 | 982 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.48 | 6 | 0
1986-05-19 | 1900-05-18 | 18:00 | 18 | 478 | 1335 | 257 | 1 | 13 | 387 | 1 | 13 | 120 | 1 | 13 | 27100 | 1 | 13 | 36100 | 1 | 13 | 14200 | 1 | 13 | 2300 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 19.4 | 66.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.4 | A | 7 | 982 | A | 7 | 340 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.68 | 6 | 0
1986-05-19 | 1900-05-18 | 19:00 | 19 | 228 | 1335 | 88 | 1 | 13 | 212 | 1 | 9 | 53 | 1 | 13 | 9300 | 1 | 13 | 14700 | 1 | 9 | 6800 | 1 | 13 | 950 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.49 | A | 7 | 982 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.36 | 6 | 0
1986-05-19 | 1900-05-18 | 20:00 | 20 | 23 | 612 | 10 | 1 | 13 | 4 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.58 | A | 7 | 982 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.76 | 6 | 0
1986-05-19 | 1900-05-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.94 | 6 | 0
1986-05-19 | 1900-05-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.64 | A | 7 | 982 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.66 | 6 | 0
1986-05-19 | 1900-05-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 360 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.72 | 6 | 0
1986-05-19 | 1900-05-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 6.7 | 44.06 | A | 7 | 0.72 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.06 | 6 | 0
1986-05-20 | 1900-05-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.8 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.04 | 7 | 0
1986-05-20 | 1900-05-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 10 | 50 | A | 7 | 7.8 | 46.04 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 7 | 0
1986-05-20 | 1900-05-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 8.9 | 48.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.94 | 7 | 0
1986-05-20 | 1900-05-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 9.4 | 48.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.54 | 7 | 0
1986-05-20 | 1900-05-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.96 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.44 | 7 | 0
1986-05-20 | 1900-05-19 | 6:00 | 6 | 104 | 1278 | 36 | 1 | 13 | 133 | 1 | 9 | 23 | 1 | 13 | 3700 | 1 | 13 | 6300 | 1 | 9 | 3100 | 1 | 13 | 400 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 8.9 | 48.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.93 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.94 | 7 | 0
1986-05-20 | 1900-05-19 | 7:00 | 7 | 352 | 1334 | 191 | 1 | 9 | 511 | 1 | 9 | 56 | 1 | 13 | 19900 | 1 | 9 | 43600 | 1 | 9 | 8400 | 1 | 13 | 1060 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 10 | 50 | A | 7 | 0.83 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.3 | 7 | 0
1986-05-20 | 1900-05-19 | 8:00 | 8 | 599 | 1334 | 356 | 1 | 9 | 503 | 1 | 9 | 130 | 1 | 13 | 38100 | 1 | 9 | 49500 | 1 | 9 | 15800 | 1 | 13 | 2590 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.7 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.1 | 7 | 0
1986-05-20 | 1900-05-19 | 9:00 | 9 | 826 | 1334 | 555 | 1 | 9 | 647 | 1 | 9 | 154 | 1 | 13 | 58300 | 1 | 9 | 65100 | 1 | 9 | 18000 | 1 | 13 | 3730 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 17.8 | 64.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.56 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.12 | 7 | 0
1986-05-20 | 1900-05-19 | 10:00 | 10 | 1016 | 1334 | 709 | 1 | 9 | 776 | 1 | 9 | 117 | 1 | 13 | 76100 | 1 | 9 | 78700 | 1 | 9 | 16000 | 1 | 13 | 3700 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 18.9 | 66.02 | A | 7 | 6.7 | 44.06 | A | 7 | 0.45 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.96 | 7 | 0
1986-05-20 | 1900-05-19 | 11:00 | 11 | 1156 | 1334 | 841 | 1 | 13 | 755 | 1 | 13 | 187 | 1 | 13 | 87600 | 1 | 13 | 75600 | 1 | 13 | 21900 | 1 | 13 | 7680 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 20 | 68 | A | 7 | 7.2 | 44.96 | A | 7 | 0.44 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.56 | 7 | 0
1986-05-20 | 1900-05-19 | 12:00 | 12 | 1238 | 1334 | 800 | 1 | 13 | 588 | 1 | 13 | 254 | 1 | 13 | 85100 | 1 | 13 | 59800 | 1 | 13 | 29400 | 1 | 13 | 15810 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 21.1 | 69.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.42 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.14 | 7 | 0
1986-05-20 | 1900-05-19 | 13:00 | 13 | 1255 | 1334 | 946 | 1 | 13 | 828 | 1 | 13 | 166 | 1 | 13 | 100900 | 1 | 13 | 83800 | 1 | 13 | 21800 | 1 | 13 | 10780 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 21.7 | 71.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.37 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.88 | 7 | 0
1986-05-20 | 1900-05-19 | 14:00 | 14 | 1206 | 1334 | 890 | 1 | 13 | 765 | 1 | 13 | 198 | 1 | 13 | 92600 | 1 | 13 | 76600 | 1 | 13 | 23200 | 1 | 13 | 9780 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.35 | A | 7 | 982 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.58 | 7 | 0
1986-05-20 | 1900-05-19 | 15:00 | 15 | 1095 | 1334 | 791 | 1 | 13 | 740 | 1 | 13 | 184 | 1 | 13 | 84900 | 1 | 13 | 75800 | 1 | 13 | 22500 | 1 | 13 | 7100 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.37 | A | 7 | 981 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.76 | 7 | 0
1986-05-20 | 1900-05-19 | 16:00 | 16 | 929 | 1334 | 604 | 1 | 13 | 606 | 1 | 13 | 183 | 1 | 13 | 63700 | 1 | 13 | 61300 | 1 | 13 | 21000 | 1 | 13 | 5020 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.34 | A | 7 | 980 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.78 | 7 | 0
1986-05-20 | 1900-05-19 | 17:00 | 17 | 719 | 1334 | 440 | 1 | 13 | 540 | 1 | 13 | 150 | 1 | 13 | 47700 | 1 | 13 | 54800 | 1 | 13 | 18100 | 1 | 13 | 3230 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 21.1 | 69.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.38 | A | 7 | 980 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.08 | 7 | 0
1986-05-20 | 1900-05-19 | 18:00 | 18 | 481 | 1334 | 226 | 1 | 13 | 279 | 1 | 13 | 126 | 1 | 13 | 24300 | 1 | 13 | 26800 | 1 | 13 | 14600 | 1 | 13 | 2530 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 21.1 | 69.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.39 | A | 7 | 979 | A | 7 | 40 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.06 | 7 | 0
1986-05-20 | 1900-05-19 | 19:00 | 19 | 231 | 1334 | 75 | 1 | 13 | 98 | 1 | 13 | 59 | 1 | 13 | 8300 | 1 | 13 | 7200 | 1 | 13 | 7100 | 1 | 13 | 1260 | 1 | 23 | 7 | A | 7 | 4 | A | 7 | 20 | 68 | A | 7 | 7.2 | 44.96 | A | 7 | 0.44 | A | 7 | 979 | A | 7 | 40 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.56 | 7 | 0
1986-05-20 | 1900-05-19 | 20:00 | 20 | 24 | 634 | 10 | 1 | 13 | 5 | 1 | 13 | 9 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 18.3 | 64.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.54 | A | 7 | 980 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 3960 | A | 7 | 1.8 | E | 8 | 0.108 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.72 | 7 | 0
1986-05-20 | 1900-05-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 8.9 | 48.02 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 3960 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.42 | 7 | 0
1986-05-20 | 1900-05-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 4 | A | 7 | 15 | 59 | A | 7 | 8.9 | 48.02 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 3960 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.92 | 7 | 0
1986-05-20 | 1900-05-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 15.6 | 60.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 130 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 7 | 0
1986-05-20 | 1900-05-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 12.8 | 55.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.98 | 7 | 0
1986-05-21 | 1900-05-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 12.2 | 53.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.48 | 1 | 0
1986-05-21 | 1900-05-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.48 | 1 | 0
1986-05-21 | 1900-05-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 10 | 50 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.9 | 1 | 0
1986-05-21 | 1900-05-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 10 | 50 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 1 | 0
1986-05-21 | 1900-05-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 10.6 | 51.08 | A | 7 | 10 | 50 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 2740 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 1 | 0
1986-05-21 | 1900-05-20 | 6:00 | 6 | 107 | 1278 | 24 | 1 | 13 | 13 | 1 | 9 | 23 | 1 | 13 | 2600 | 1 | 13 | 800 | 1 | 9 | 2600 | 1 | 13 | 570 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 11.7 | 53.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 3050 | A | 7 | 2 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.88 | 1 | 0
1986-05-21 | 1900-05-20 | 7:00 | 7 | 354 | 1334 | 88 | 1 | 9 | 26 | 1 | 9 | 81 | 1 | 13 | 9700 | 1 | 9 | 2300 | 1 | 9 | 9000 | 1 | 13 | 2190 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 13.3 | 55.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12900 | A | 7 | 3050 | A | 7 | 2.1 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.36 | 1 | 0
1986-05-21 | 1900-05-20 | 8:00 | 8 | 601 | 1334 | 358 | 1 | 9 | 502 | 1 | 9 | 132 | 1 | 13 | 38300 | 1 | 9 | 49500 | 1 | 9 | 16000 | 1 | 13 | 2640 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.66 | 1 | 0
1986-05-21 | 1900-05-20 | 9:00 | 9 | 827 | 1334 | 569 | 1 | 9 | 670 | 1 | 9 | 153 | 1 | 13 | 59900 | 1 | 9 | 67400 | 1 | 9 | 18000 | 1 | 13 | 3720 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.66 | 1 | 0
1986-05-21 | 1900-05-20 | 10:00 | 10 | 1017 | 1334 | 713 | 1 | 9 | 693 | 1 | 9 | 184 | 1 | 13 | 75800 | 1 | 9 | 70600 | 1 | 9 | 21800 | 1 | 13 | 5940 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 21.1 | 69.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.47 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.32 | 1 | 0
1986-05-21 | 1900-05-20 | 11:00 | 11 | 1157 | 1334 | 741 | 1 | 13 | 502 | 1 | 13 | 305 | 1 | 13 | 79900 | 1 | 13 | 52500 | 1 | 13 | 34300 | 1 | 13 | 14160 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.48 | A | 7 | 980 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.28 | 1 | 0
1986-05-21 | 1900-05-20 | 12:00 | 12 | 1239 | 1334 | 892 | 1 | 13 | 638 | 1 | 13 | 299 | 1 | 13 | 93800 | 1 | 13 | 64300 | 1 | 13 | 33900 | 1 | 13 | 18550 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 8.9 | 48.02 | A | 7 | 0.43 | A | 7 | 979 | A | 7 | 70 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.82 | 1 | 0
1986-05-21 | 1900-05-20 | 13:00 | 13 | 1256 | 1334 | 927 | 1 | 13 | 678 | 1 | 13 | 288 | 1 | 13 | 97900 | 1 | 13 | 68600 | 1 | 13 | 33100 | 1 | 13 | 19610 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 8.9 | 48.02 | A | 7 | 0.43 | A | 7 | 978 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.82 | 1 | 0
1986-05-21 | 1900-05-20 | 14:00 | 14 | 1207 | 1334 | 842 | 1 | 13 | 643 | 1 | 13 | 260 | 1 | 13 | 89200 | 1 | 13 | 65200 | 1 | 13 | 30000 | 1 | 13 | 14100 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 8.9 | 48.02 | A | 7 | 0.43 | A | 7 | 977 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.82 | 1 | 0
1986-05-21 | 1900-05-20 | 15:00 | 15 | 1096 | 1334 | 779 | 1 | 13 | 659 | 1 | 13 | 238 | 1 | 13 | 82100 | 1 | 13 | 66700 | 1 | 13 | 27200 | 1 | 13 | 9010 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 10 | 50 | A | 7 | 0.43 | A | 7 | 977 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.5 | 1 | 0
1986-05-21 | 1900-05-20 | 16:00 | 16 | 931 | 1334 | 621 | 1 | 13 | 601 | 1 | 13 | 203 | 1 | 13 | 65100 | 1 | 13 | 60400 | 1 | 13 | 22800 | 1 | 13 | 5510 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 9.4 | 48.92 | A | 7 | 0.41 | A | 7 | 976 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.22 | 1 | 0
1986-05-21 | 1900-05-20 | 17:00 | 17 | 722 | 1334 | 345 | 1 | 13 | 231 | 1 | 13 | 220 | 1 | 13 | 37100 | 1 | 13 | 24200 | 1 | 13 | 23900 | 1 | 13 | 5140 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 22.8 | 73.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.46 | A | 7 | 976 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 2 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.88 | 1 | 0
1986-05-21 | 1900-05-20 | 18:00 | 18 | 484 | 1334 | 242 | 1 | 13 | 289 | 1 | 13 | 138 | 1 | 13 | 25900 | 1 | 13 | 27800 | 1 | 13 | 15800 | 1 | 13 | 2830 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 21.7 | 71.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.49 | A | 7 | 976 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 2 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.38 | 1 | 0
1986-05-21 | 1900-05-20 | 19:00 | 19 | 234 | 1334 | 88 | 1 | 13 | 88 | 1 | 13 | 73 | 1 | 13 | 9500 | 1 | 13 | 6400 | 1 | 13 | 8400 | 1 | 13 | 1560 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 20.6 | 69.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.53 | A | 7 | 976 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.18 | 1 | 0
1986-05-21 | 1900-05-20 | 20:00 | 20 | 26 | 656 | 8 | 1 | 13 | 2 | 1 | 13 | 8 | 1 | 13 | 1000 | 1 | 13 | 0 | 1 | 13 | 1000 | 1 | 13 | 300 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 18.3 | 64.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.63 | A | 7 | 976 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.211 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.68 | 1 | 0
1986-05-21 | 1900-05-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 976 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.08 | 1 | 0
1986-05-21 | 1900-05-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 17.2 | 62.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.65 | A | 7 | 976 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.28 | 1 | 0
1986-05-21 | 1900-05-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 16.7 | 62.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.58 | 1 | 0
1986-05-21 | 1900-05-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 16.1 | 60.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.7 | A | 7 | 976 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.08 | 1 | 0
1986-05-22 | 1900-05-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 976 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.48 | 2 | 0
1986-05-22 | 1900-05-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 15 | 59 | A | 7 | 10.6 | 51.08 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.98 | 2 | 0
1986-05-22 | 1900-05-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 14.4 | 57.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.48 | 2 | 0
1986-05-22 | 1900-05-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.78 | A | 7 | 974 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.5 | 2 | 0
1986-05-22 | 1900-05-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 13.9 | 57.02 | A | 7 | 9.4 | 48.92 | A | 7 | 0.75 | A | 7 | 974 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.02 | 2 | 0
1986-05-22 | 1900-05-21 | 6:00 | 6 | 109 | 1300 | 40 | 1 | 13 | 133 | 1 | 9 | 27 | 1 | 13 | 4000 | 1 | 13 | 6300 | 1 | 9 | 3500 | 1 | 13 | 480 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 9.4 | 48.92 | A | 7 | 0.75 | A | 7 | 974 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.02 | 2 | 0
1986-05-22 | 1900-05-21 | 7:00 | 7 | 357 | 1333 | 163 | 1 | 9 | 370 | 1 | 9 | 64 | 1 | 13 | 17600 | 1 | 9 | 31500 | 1 | 9 | 9100 | 1 | 13 | 1150 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 15 | 59 | A | 7 | 9.4 | 48.92 | A | 7 | 0.7 | A | 7 | 974 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.22 | 2 | 0
1986-05-22 | 1900-05-21 | 8:00 | 8 | 603 | 1333 | 306 | 1 | 13 | 345 | 1 | 13 | 150 | 1 | 13 | 32300 | 1 | 13 | 34000 | 1 | 13 | 16900 | 1 | 13 | 3040 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 16.7 | 62.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.67 | A | 7 | 974 | A | 7 | 90 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 1680 | A | 7 | 2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.58 | 2 | 0
1986-05-22 | 1900-05-21 | 9:00 | 9 | 829 | 1333 | 394 | 1 | 13 | 207 | 1 | 13 | 265 | 1 | 13 | 43200 | 1 | 13 | 21800 | 1 | 13 | 29600 | 1 | 13 | 7320 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 90 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 1680 | A | 7 | 2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.08 | 2 | 0
1986-05-22 | 1900-05-21 | 10:00 | 10 | 1018 | 1333 | 710 | 1 | 9 | 751 | 1 | 9 | 136 | 1 | 13 | 75100 | 1 | 9 | 75700 | 1 | 9 | 17100 | 1 | 13 | 4160 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 20 | 68 | A | 7 | 12.2 | 53.96 | A | 7 | 0.61 | A | 7 | 973 | A | 7 | 90 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.06 | 2 | 0
1986-05-22 | 1900-05-21 | 11:00 | 11 | 1158 | 1333 | 820 | 1 | 9 | 726 | 1 | 9 | 188 | 1 | 13 | 88300 | 1 | 9 | 74600 | 1 | 9 | 23300 | 1 | 13 | 8730 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 16.1 | 60.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.75 | A | 7 | 973 | A | 7 | 110 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.76 | 2 | 0
1986-05-22 | 1900-05-21 | 12:00 | 12 | 1240 | 1333 | 850 | 1 | 9 | 685 | 1 | 9 | 212 | 1 | 13 | 91500 | 1 | 9 | 70300 | 1 | 9 | 26000 | 1 | 13 | 13530 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.51 | A | 7 | 972 | A | 7 | 100 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.46 | 2 | 0
1986-05-22 | 1900-05-21 | 13:00 | 13 | 1257 | 1333 | 906 | 1 | 9 | 762 | 1 | 9 | 187 | 1 | 13 | 95500 | 1 | 9 | 76700 | 1 | 9 | 23000 | 1 | 13 | 12150 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.5 | A | 7 | 972 | A | 7 | 90 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.96 | 2 | 0
1986-05-22 | 1900-05-21 | 14:00 | 14 | 1208 | 1333 | 772 | 1 | 13 | 500 | 1 | 13 | 318 | 1 | 13 | 83500 | 1 | 13 | 52300 | 1 | 13 | 35900 | 1 | 13 | 17830 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 23.9 | 75.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.46 | A | 7 | 971 | A | 7 | 90 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 2.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.46 | 2 | 0
1986-05-22 | 1900-05-21 | 15:00 | 15 | 1098 | 1333 | 726 | 1 | 13 | 638 | 1 | 13 | 200 | 1 | 13 | 77400 | 1 | 13 | 65200 | 1 | 13 | 23600 | 1 | 13 | 7740 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.5 | A | 7 | 971 | A | 7 | 90 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.84 | 2 | 0
1986-05-22 | 1900-05-21 | 16:00 | 16 | 932 | 1333 | 621 | 1 | 13 | 654 | 1 | 13 | 164 | 1 | 13 | 66000 | 1 | 13 | 66500 | 1 | 13 | 19400 | 1 | 13 | 4600 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 24.4 | 75.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.47 | A | 7 | 971 | A | 7 | 110 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.36 | 2 | 0
1986-05-22 | 1900-05-21 | 17:00 | 17 | 724 | 1333 | 369 | 1 | 13 | 362 | 1 | 13 | 173 | 1 | 13 | 39400 | 1 | 13 | 36700 | 1 | 13 | 19500 | 1 | 13 | 3790 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 23.3 | 73.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.52 | A | 7 | 971 | A | 7 | 90 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 2.3 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.24 | 2 | 0
1986-05-22 | 1900-05-21 | 18:00 | 18 | 486 | 1333 | 154 | 1 | 9 | 48 | 1 | 9 | 137 | 1 | 13 | 17000 | 1 | 9 | 4500 | 1 | 9 | 15300 | 1 | 13 | 3810 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.53 | A | 7 | 971 | A | 7 | 80 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 2.2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.44 | 2 | 0
1986-05-22 | 1900-05-21 | 19:00 | 19 | 237 | 1333 | 71 | 1 | 13 | 6 | 1 | 9 | 70 | 1 | 13 | 7800 | 1 | 13 | 200 | 1 | 9 | 7800 | 1 | 13 | 2260 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.55 | A | 7 | 971 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 1400 | A | 7 | 2.2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.96 | 2 | 0
1986-05-22 | 1900-05-21 | 20:00 | 20 | 27 | 678 | 7 | 1 | 13 | 1 | 1 | 9 | 7 | 1 | 13 | 800 | 1 | 13 | 0 | 1 | 9 | 800 | 1 | 13 | 270 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.59 | A | 7 | 971 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 1160 | A | 7 | 2.2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.66 | 2 | 0
1986-05-22 | 1900-05-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.59 | A | 7 | 971 | A | 7 | 100 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 1100 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.66 | 2 | 0
1986-05-22 | 1900-05-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 12.2 | 53.96 | A | 7 | 0.61 | A | 7 | 972 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.06 | 2 | 0
1986-05-22 | 1900-05-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.63 | A | 7 | 972 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.46 | 2 | 0
1986-05-22 | 1900-05-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.63 | A | 7 | 972 | A | 7 | 80 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.66 | 2 | 0
1986-05-23 | 1900-05-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.61 | A | 7 | 972 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 790 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.58 | 3 | 0
1986-05-23 | 1900-05-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 10 | 50 | A | 7 | 0.61 | A | 7 | 972 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.6 | 3 | 0
1986-05-23 | 1900-05-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 8.9 | 48.02 | A | 7 | 0.58 | A | 7 | 972 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 730 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.42 | 3 | 0
1986-05-23 | 1900-05-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 15.6 | 60.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.62 | A | 7 | 972 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 730 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 3 | 0
1986-05-23 | 1900-05-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.65 | A | 7 | 972 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 460 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.52 | 3 | 0
1986-05-23 | 1900-05-22 | 6:00 | 6 | 112 | 1321 | 18 | 1 | 13 | 0 | 1 | 9 | 18 | 1 | 13 | 2100 | 1 | 13 | 0 | 1 | 9 | 2100 | 1 | 13 | 660 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 400 | A | 7 | 1.8 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.52 | 3 | 0
1986-05-23 | 1900-05-22 | 7:00 | 7 | 359 | 1332 | 74 | 1 | 9 | 1 | 1 | 9 | 74 | 1 | 13 | 8500 | 1 | 9 | 0 | 1 | 9 | 8500 | 1 | 13 | 2840 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.67 | A | 7 | 973 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 400 | A | 7 | 1.9 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.72 | 3 | 0
1986-05-23 | 1900-05-22 | 8:00 | 8 | 605 | 1332 | 167 | 1 | 9 | 2 | 1 | 9 | 166 | 1 | 13 | 19000 | 1 | 9 | 200 | 1 | 9 | 19000 | 1 | 13 | 6600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.7 | A | 7 | 974 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 370 | A | 7 | 1.9 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.1 | 3 | 0
1986-05-23 | 1900-05-22 | 9:00 | 9 | 830 | 1332 | 372 | 1 | 9 | 96 | 1 | 9 | 312 | 1 | 13 | 40900 | 1 | 9 | 9800 | 1 | 9 | 34700 | 1 | 13 | 9980 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 16.7 | 62.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.67 | A | 7 | 975 | A | 7 | 80 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 550 | A | 7 | 2 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.58 | 3 | 0
1986-05-23 | 1900-05-22 | 10:00 | 10 | 1019 | 1332 | 294 | 1 | 9 | 5 | 1 | 9 | 290 | 1 | 13 | 34400 | 1 | 9 | 400 | 1 | 9 | 34100 | 1 | 13 | 13080 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.73 | A | 7 | 975 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 430 | A | 7 | 2.1 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.46 | 3 | 0
1986-05-23 | 1900-05-22 | 11:00 | 11 | 1159 | 1332 | 287 | 1 | 9 | 10 | 1 | 9 | 278 | 1 | 13 | 34400 | 1 | 9 | 800 | 1 | 9 | 33700 | 1 | 13 | 13180 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.73 | A | 7 | 975 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 2.2 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.26 | 3 | 0
1986-05-23 | 1900-05-22 | 12:00 | 12 | 1241 | 1332 | 359 | 1 | 9 | 10 | 1 | 9 | 349 | 1 | 13 | 42700 | 1 | 9 | 900 | 1 | 9 | 41900 | 1 | 13 | 15900 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.73 | A | 7 | 976 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 490 | A | 7 | 2.2 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.26 | 3 | 0
1986-05-23 | 1900-05-22 | 13:00 | 13 | 1258 | 1332 | 347 | 1 | 9 | 6 | 1 | 9 | 341 | 1 | 13 | 41500 | 1 | 9 | 500 | 1 | 9 | 41000 | 1 | 13 | 15690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.75 | A | 7 | 976 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 580 | A | 7 | 2.3 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.64 | 3 | 0
1986-05-23 | 1900-05-22 | 14:00 | 14 | 1209 | 1332 | 332 | 1 | 9 | 1 | 1 | 9 | 331 | 1 | 13 | 39600 | 1 | 9 | 100 | 1 | 9 | 39500 | 1 | 13 | 15190 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 977 | A | 7 | 30 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 550 | A | 7 | 2.3 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.44 | 3 | 0
1986-05-23 | 1900-05-22 | 15:00 | 15 | 1099 | 1332 | 323 | 1 | 9 | 8 | 1 | 9 | 317 | 1 | 13 | 38100 | 1 | 9 | 700 | 1 | 9 | 37500 | 1 | 13 | 14340 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 976 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 2.3 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.44 | 3 | 0
1986-05-23 | 1900-05-22 | 16:00 | 16 | 934 | 1332 | 281 | 1 | 9 | 4 | 1 | 9 | 278 | 1 | 13 | 32600 | 1 | 9 | 400 | 1 | 9 | 32300 | 1 | 13 | 12150 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 2.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.62 | 3 | 0
1986-05-23 | 1900-05-22 | 17:00 | 17 | 726 | 1332 | 459 | 1 | 13 | 495 | 1 | 13 | 190 | 1 | 13 | 48600 | 1 | 13 | 50200 | 1 | 13 | 21200 | 1 | 13 | 4210 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 18.9 | 66.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.73 | A | 7 | 976 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.02 | 3 | 0
1986-05-23 | 1900-05-22 | 18:00 | 18 | 489 | 1332 | 234 | 1 | 13 | 234 | 1 | 13 | 149 | 1 | 13 | 24900 | 1 | 13 | 22600 | 1 | 13 | 16600 | 1 | 13 | 3100 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 18.3 | 64.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 1340 | A | 7 | 2.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.62 | 3 | 0
1986-05-23 | 1900-05-22 | 19:00 | 19 | 240 | 1332 | 15 | 1 | 13 | 0 | 1 | 9 | 15 | 1 | 13 | 1900 | 1 | 13 | 0 | 1 | 9 | 1900 | 1 | 13 | 640 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 610 | A | 7 | 2.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.62 | 3 | 0
1986-05-23 | 1900-05-22 | 20:00 | 20 | 29 | 677 | 9 | 1 | 13 | 0 | 1 | 9 | 9 | 1 | 13 | 1100 | 1 | 13 | 0 | 1 | 9 | 1100 | 1 | 13 | 330 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 977 | A | 7 | 60 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 610 | A | 7 | 2.5 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 3 | 0
1986-05-23 | 1900-05-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 978 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 640 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 3 | 0
1986-05-23 | 1900-05-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 978 | A | 7 | 360 | A | 7 | 1.5 | A | 7 | 12900 | A | 7 | 820 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 3 | 0
1986-05-23 | 1900-05-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 6 | A | 7 | 17.2 | 62.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.84 | A | 7 | 979 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 610 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.02 | 3 | 0
1986-05-23 | 1900-05-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 3 | 0
1986-05-24 | 1900-05-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.14 | 4 | 0
1986-05-24 | 1900-05-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 4 | 0
1986-05-24 | 1900-05-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 4 | 0
1986-05-24 | 1900-05-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.46 | 4 | 0
1986-05-24 | 1900-05-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 12.2 | 53.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.36 | 4 | 0
1986-05-24 | 1900-05-23 | 6:00 | 6 | 114 | 1321 | 41 | 1 | 13 | 104 | 1 | 9 | 32 | 1 | 13 | 4400 | 1 | 13 | 4600 | 1 | 9 | 3900 | 1 | 13 | 590 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | 11.7 | 53.06 | A | 7 | 1 | A | 7 | 980 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 4000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 4 | 0
1986-05-24 | 1900-05-23 | 7:00 | 7 | 361 | 1332 | 182 | 1 | 9 | 348 | 1 | 9 | 88 | 1 | 13 | 19000 | 1 | 9 | 29600 | 1 | 9 | 11000 | 1 | 13 | 1630 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 4000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 4 | 0
1986-05-24 | 1900-05-23 | 8:00 | 8 | 606 | 1332 | 149 | 1 | 9 | 46 | 1 | 9 | 128 | 1 | 13 | 16400 | 1 | 9 | 4500 | 1 | 9 | 14400 | 1 | 13 | 3980 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 7620 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 4 | 0
1986-05-24 | 1900-05-23 | 9:00 | 9 | 831 | 1332 | 268 | 1 | 9 | 24 | 1 | 9 | 254 | 1 | 13 | 30900 | 1 | 9 | 2100 | 1 | 9 | 29600 | 1 | 13 | 10670 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 18.3 | 64.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 7620 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.62 | 4 | 0
1986-05-24 | 1900-05-23 | 10:00 | 10 | 1020 | 1332 | 235 | 1 | 9 | 14 | 1 | 9 | 224 | 1 | 13 | 28100 | 1 | 9 | 1100 | 1 | 9 | 27200 | 1 | 13 | 10750 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.42 | 4 | 0
1986-05-24 | 1900-05-23 | 11:00 | 11 | 1160 | 1332 | 446 | 1 | 9 | 88 | 1 | 9 | 370 | 1 | 13 | 49400 | 1 | 9 | 9000 | 1 | 9 | 41500 | 1 | 13 | 16850 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 3660 | A | 7 | 2.5 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.42 | 4 | 0
1986-05-24 | 1900-05-23 | 12:00 | 12 | 1242 | 1332 | 579 | 1 | 9 | 136 | 1 | 9 | 452 | 1 | 13 | 63700 | 1 | 9 | 14500 | 1 | 9 | 50200 | 1 | 13 | 24880 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 20.6 | 69.08 | A | 7 | 15 | 59 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 3660 | A | 7 | 2.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.5 | 4 | 0
1986-05-24 | 1900-05-23 | 13:00 | 13 | 1259 | 1332 | 826 | 1 | 13 | 569 | 1 | 13 | 288 | 1 | 13 | 87300 | 1 | 13 | 57600 | 1 | 13 | 32700 | 1 | 13 | 20110 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 23.3 | 73.94 | A | 7 | 15 | 59 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.2 | 4 | 0
1986-05-24 | 1900-05-23 | 14:00 | 14 | 1211 | 1332 | 694 | 1 | 9 | 375 | 1 | 9 | 354 | 1 | 13 | 74400 | 1 | 9 | 39200 | 1 | 9 | 38700 | 1 | 13 | 20210 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 9140 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.72 | 4 | 0
1986-05-24 | 1900-05-23 | 15:00 | 15 | 1100 | 1332 | 626 | 1 | 13 | 372 | 1 | 13 | 319 | 1 | 13 | 66800 | 1 | 13 | 38800 | 1 | 13 | 34600 | 1 | 13 | 12650 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 24.4 | 75.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.48 | A | 7 | 980 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 2.3 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.44 | 4 | 0
1986-05-24 | 1900-05-23 | 16:00 | 16 | 936 | 1332 | 292 | 1 | 9 | 99 | 1 | 9 | 222 | 1 | 13 | 32700 | 1 | 9 | 10600 | 1 | 9 | 25200 | 1 | 13 | 6740 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 23.9 | 75.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.45 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 2.1 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.38 | 4 | 0
1986-05-24 | 1900-05-23 | 17:00 | 17 | 728 | 1332 | 288 | 1 | 9 | 91 | 1 | 9 | 239 | 1 | 13 | 31700 | 1 | 9 | 9200 | 1 | 9 | 26700 | 1 | 13 | 7380 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.5 | A | 7 | 979 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.96 | 4 | 0
1986-05-24 | 1900-05-23 | 18:00 | 18 | 491 | 1332 | 135 | 1 | 9 | 53 | 1 | 9 | 115 | 1 | 13 | 14800 | 1 | 9 | 5000 | 1 | 9 | 13000 | 1 | 13 | 3320 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 9140 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.32 | 4 | 0
1986-05-24 | 1900-05-23 | 19:00 | 19 | 242 | 1332 | 101 | 1 | 13 | 165 | 1 | 13 | 71 | 1 | 13 | 10600 | 1 | 13 | 11700 | 1 | 13 | 8500 | 1 | 13 | 1370 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 21.7 | 71.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.64 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 9140 | A | 7 | 2.5 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.12 | 4 | 0
1986-05-24 | 1900-05-23 | 20:00 | 20 | 30 | 699 | 14 | 1 | 13 | 7 | 1 | 13 | 14 | 1 | 13 | 1600 | 1 | 13 | 400 | 1 | 13 | 1600 | 1 | 13 | 340 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 19.4 | 66.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 4 | 0
1986-05-24 | 1900-05-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 20 | 68 | A | 7 | 12.2 | 53.96 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.06 | 4 | 0
1986-05-24 | 1900-05-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 18.9 | 66.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.86 | 4 | 0
1986-05-24 | 1900-05-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | 18.3 | 64.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 100 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.82 | 4 | 0
1986-05-24 | 1900-05-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.04 | 4 | 0
1986-05-25 | 1900-05-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.44 | 5 | 0
1986-05-25 | 1900-05-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 5 | 0
1986-05-25 | 1900-05-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 5 | 0
1986-05-25 | 1900-05-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.62 | 5 | 0
1986-05-25 | 1900-05-24 | 5:00 | 5 | 0 | 11 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 6 | A | 7 | 6 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.66 | 5 | 0
1986-05-25 | 1900-05-24 | 6:00 | 6 | 116 | 1331 | 18 | 1 | 13 | 2 | 1 | 9 | 18 | 1 | 13 | 2100 | 1 | 13 | 0 | 1 | 9 | 2100 | 1 | 13 | 660 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 15 | 59 | A | 7 | 11.1 | 51.98 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 2.1 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.28 | 5 | 0
1986-05-25 | 1900-05-24 | 7:00 | 7 | 363 | 1331 | 86 | 1 | 9 | 6 | 1 | 9 | 84 | 1 | 13 | 9700 | 1 | 9 | 300 | 1 | 9 | 9600 | 1 | 13 | 3140 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 2 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.28 | 5 | 0
1986-05-25 | 1900-05-24 | 8:00 | 8 | 608 | 1331 | 173 | 1 | 9 | 57 | 1 | 9 | 147 | 1 | 13 | 19100 | 1 | 9 | 5600 | 1 | 9 | 16500 | 1 | 13 | 4490 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.28 | 5 | 0
1986-05-25 | 1900-05-24 | 9:00 | 9 | 833 | 1331 | 487 | 1 | 9 | 313 | 1 | 9 | 292 | 1 | 13 | 52200 | 1 | 9 | 33400 | 1 | 9 | 31300 | 1 | 13 | 7660 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 18.9 | 66.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 350 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.18 | 5 | 0
1986-05-25 | 1900-05-24 | 10:00 | 10 | 1021 | 1331 | 444 | 1 | 9 | 162 | 1 | 9 | 319 | 1 | 13 | 49000 | 1 | 9 | 17300 | 1 | 9 | 35700 | 1 | 13 | 10730 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 18.3 | 64.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.61 | A | 7 | 981 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 2 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.58 | 5 | 0
1986-05-25 | 1900-05-24 | 11:00 | 11 | 1161 | 1331 | 716 | 1 | 13 | 441 | 1 | 13 | 331 | 1 | 13 | 76600 | 1 | 13 | 46100 | 1 | 13 | 36400 | 1 | 13 | 15710 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 18.3 | 64.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.72 | 5 | 0
1986-05-25 | 1900-05-24 | 12:00 | 12 | 1242 | 1331 | 810 | 1 | 13 | 488 | 1 | 13 | 354 | 1 | 13 | 87000 | 1 | 13 | 51000 | 1 | 13 | 39300 | 1 | 13 | 23450 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 20 | 68 | A | 7 | 9.4 | 48.92 | A | 7 | 0.51 | A | 7 | 982 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.02 | 5 | 0
1986-05-25 | 1900-05-24 | 13:00 | 13 | 1260 | 1331 | 937 | 1 | 9 | 750 | 1 | 9 | 227 | 1 | 13 | 100700 | 1 | 9 | 76800 | 1 | 9 | 27900 | 1 | 13 | 16180 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | 21.7 | 71.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.49 | A | 7 | 981 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.38 | 5 | 0
1986-05-25 | 1900-05-24 | 14:00 | 14 | 1212 | 1331 | 873 | 1 | 13 | 687 | 1 | 13 | 247 | 1 | 13 | 92800 | 1 | 13 | 69900 | 1 | 13 | 29000 | 1 | 13 | 13810 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.44 | A | 7 | 980 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.72 | 5 | 0
1986-05-25 | 1900-05-24 | 15:00 | 15 | 1102 | 1331 | 753 | 1 | 13 | 590 | 1 | 13 | 264 | 1 | 13 | 78700 | 1 | 13 | 59400 | 1 | 13 | 29400 | 1 | 13 | 10080 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 21.7 | 71.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.46 | A | 7 | 980 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.12 | 5 | 0
1986-05-25 | 1900-05-24 | 16:00 | 16 | 937 | 1331 | 630 | 1 | 13 | 605 | 1 | 13 | 205 | 1 | 13 | 66000 | 1 | 13 | 60900 | 1 | 13 | 23000 | 1 | 13 | 5640 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 8.3 | 46.94 | A | 7 | 0.4 | A | 7 | 979 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.54 | 5 | 0
1986-05-25 | 1900-05-24 | 17:00 | 17 | 730 | 1331 | 439 | 1 | 13 | 462 | 1 | 13 | 186 | 1 | 13 | 46600 | 1 | 13 | 46900 | 1 | 13 | 20800 | 1 | 13 | 4120 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.38 | A | 7 | 979 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.44 | 5 | 0
1986-05-25 | 1900-05-24 | 18:00 | 18 | 494 | 1331 | 236 | 1 | 13 | 319 | 1 | 13 | 118 | 1 | 13 | 24900 | 1 | 13 | 30000 | 1 | 13 | 13800 | 1 | 13 | 2260 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 21.7 | 71.06 | A | 7 | 7.2 | 44.96 | A | 7 | 0.4 | A | 7 | 979 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.96 | 5 | 0
1986-05-25 | 1900-05-24 | 19:00 | 19 | 245 | 1331 | 109 | 1 | 13 | 329 | 1 | 9 | 50 | 1 | 13 | 11700 | 1 | 13 | 23800 | 1 | 9 | 7300 | 1 | 13 | 890 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.42 | A | 7 | 979 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.26 | 5 | 0
1986-05-25 | 1900-05-24 | 20:00 | 20 | 32 | 721 | 14 | 1 | 13 | 24 | 1 | 9 | 12 | 1 | 13 | 1500 | 1 | 13 | 900 | 1 | 9 | 1400 | 1 | 13 | 250 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.52 | A | 7 | 979 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.86 | 5 | 0
1986-05-25 | 1900-05-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.74 | 5 | 0
1986-05-25 | 1900-05-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.74 | 5 | 0
1986-05-25 | 1900-05-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.42 | 5 | 0
1986-05-25 | 1900-05-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.42 | 5 | 0
1986-05-26 | 1900-05-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.8 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 6 | 0
1986-05-26 | 1900-05-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 979 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.34 | 6 | 0
1986-05-26 | 1900-05-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.84 | 6 | 0
1986-05-26 | 1900-05-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.44 | 6 | 0
1986-05-26 | 1900-05-25 | 5:00 | 5 | 0 | 33 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.84 | 6 | 0
1986-05-26 | 1900-05-25 | 6:00 | 6 | 118 | 1331 | 49 | 1 | 13 | 305 | 1 | 9 | 21 | 1 | 13 | 4900 | 1 | 13 | 16200 | 1 | 9 | 3500 | 1 | 13 | 380 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.32 | 6 | 0
1986-05-26 | 1900-05-25 | 7:00 | 7 | 364 | 1331 | 218 | 1 | 9 | 649 | 1 | 9 | 40 | 1 | 13 | 23000 | 1 | 9 | 57200 | 1 | 9 | 7300 | 1 | 13 | 860 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 10 | 50 | A | 7 | 0.8 | A | 7 | 978 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.8 | 6 | 0
1986-05-26 | 1900-05-25 | 8:00 | 8 | 609 | 1331 | 418 | 1 | 9 | 781 | 1 | 9 | 60 | 1 | 13 | 43900 | 1 | 9 | 75400 | 1 | 9 | 9300 | 1 | 13 | 1390 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.48 | 6 | 0
1986-05-26 | 1900-05-25 | 9:00 | 9 | 834 | 1331 | 570 | 1 | 9 | 790 | 1 | 9 | 74 | 1 | 13 | 59600 | 1 | 9 | 78400 | 1 | 9 | 10400 | 1 | 13 | 1890 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.96 | 6 | 0
1986-05-26 | 1900-05-25 | 10:00 | 10 | 1022 | 1331 | 727 | 1 | 9 | 822 | 1 | 9 | 95 | 1 | 13 | 75500 | 1 | 9 | 82200 | 1 | 9 | 12200 | 1 | 13 | 2790 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 18.9 | 66.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.18 | 6 | 0
1986-05-26 | 1900-05-25 | 11:00 | 11 | 1162 | 1331 | 818 | 1 | 13 | 743 | 1 | 13 | 169 | 1 | 13 | 86200 | 1 | 13 | 74900 | 1 | 13 | 20700 | 1 | 13 | 7330 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 20 | 68 | A | 7 | 10 | 50 | A | 7 | 0.53 | A | 7 | 978 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.2 | 6 | 0
1986-05-26 | 1900-05-25 | 12:00 | 12 | 1243 | 1331 | 865 | 1 | 13 | 712 | 1 | 13 | 199 | 1 | 13 | 93600 | 1 | 13 | 73300 | 1 | 13 | 25000 | 1 | 13 | 13070 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 21.1 | 69.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.47 | A | 7 | 978 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.32 | 6 | 0
1986-05-26 | 1900-05-25 | 13:00 | 13 | 1260 | 1331 | 911 | 1 | 13 | 789 | 1 | 13 | 163 | 1 | 13 | 97500 | 1 | 13 | 80000 | 1 | 13 | 21600 | 1 | 13 | 11160 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 20.6 | 69.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 1.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.62 | 6 | 0
1986-05-26 | 1900-05-25 | 14:00 | 14 | 1213 | 1331 | 671 | 1 | 13 | 469 | 1 | 13 | 243 | 1 | 13 | 74600 | 1 | 13 | 49300 | 1 | 13 | 29600 | 1 | 13 | 13850 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 22.2 | 71.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.44 | A | 7 | 978 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 1680 | A | 7 | 1.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.72 | 6 | 0
1986-05-26 | 1900-05-25 | 15:00 | 15 | 1103 | 1331 | 771 | 1 | 13 | 661 | 1 | 13 | 224 | 1 | 13 | 81700 | 1 | 13 | 67200 | 1 | 13 | 25900 | 1 | 13 | 8740 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 22.8 | 73.04 | A | 7 | 10 | 50 | A | 7 | 0.45 | A | 7 | 977 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.8 | 6 | 0
1986-05-26 | 1900-05-25 | 16:00 | 16 | 939 | 1331 | 640 | 1 | 13 | 659 | 1 | 13 | 176 | 1 | 13 | 67800 | 1 | 13 | 66800 | 1 | 13 | 20500 | 1 | 13 | 4960 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.41 | A | 7 | 977 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.52 | 6 | 0
1986-05-26 | 1900-05-25 | 17:00 | 17 | 732 | 1331 | 374 | 1 | 13 | 338 | 1 | 13 | 188 | 1 | 13 | 40700 | 1 | 13 | 35600 | 1 | 13 | 21100 | 1 | 13 | 4290 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 21.1 | 69.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.47 | A | 7 | 976 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.32 | 6 | 0
1986-05-26 | 1900-05-25 | 18:00 | 18 | 496 | 1331 | 272 | 1 | 13 | 353 | 1 | 13 | 142 | 1 | 13 | 29200 | 1 | 13 | 34200 | 1 | 13 | 16400 | 1 | 13 | 2920 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 21.1 | 69.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.53 | A | 7 | 977 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.88 | 6 | 0
1986-05-26 | 1900-05-25 | 19:00 | 19 | 248 | 1331 | 99 | 1 | 13 | 246 | 1 | 13 | 54 | 1 | 13 | 10500 | 1 | 13 | 17800 | 1 | 13 | 7200 | 1 | 13 | 970 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 20.6 | 69.08 | A | 7 | 11.1 | 51.98 | A | 7 | 0.55 | A | 7 | 977 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.28 | 6 | 0
1986-05-26 | 1900-05-25 | 20:00 | 20 | 34 | 743 | 14 | 1 | 13 | 9 | 1 | 13 | 13 | 1 | 13 | 1500 | 1 | 13 | 500 | 1 | 13 | 1500 | 1 | 13 | 320 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 18.3 | 64.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.06 | 6 | 0
1986-05-26 | 1900-05-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 4 | A | 7 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.08 | 6 | 0
1986-05-26 | 1900-05-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | 17.2 | 62.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.58 | 6 | 0
1986-05-26 | 1900-05-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 16.1 | 60.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.75 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.76 | 6 | 0
1986-05-26 | 1900-05-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 15 | 59 | A | 7 | 11.1 | 51.98 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.28 | 6 | 0
1986-05-27 | 1900-05-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 20 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.28 | 7 | 0
1986-05-27 | 1900-05-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | 12.2 | 53.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.78 | 7 | 0
1986-05-27 | 1900-05-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.76 | 7 | 0
1986-05-27 | 1900-05-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.76 | 7 | 0
1986-05-27 | 1900-05-26 | 5:00 | 5 | 0 | 33 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.97 | A | 7 | 977 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 4270 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 7 | 0
1986-05-27 | 1900-05-26 | 6:00 | 6 | 120 | 1331 | 24 | 1 | 13 | 13 | 1 | 9 | 23 | 1 | 13 | 2700 | 1 | 13 | 800 | 1 | 9 | 2600 | 1 | 13 | 570 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.97 | A | 7 | 977 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 2400 | A | 7 | 4270 | A | 7 | 2.3 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 7 | 0
1986-05-27 | 1900-05-26 | 7:00 | 7 | 366 | 1331 | 109 | 1 | 9 | 11 | 1 | 9 | 106 | 1 | 13 | 12200 | 1 | 9 | 600 | 1 | 9 | 12000 | 1 | 13 | 3700 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 2400 | A | 7 | 4270 | A | 7 | 2.3 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.14 | 7 | 0
1986-05-27 | 1900-05-26 | 8:00 | 8 | 611 | 1331 | 306 | 1 | 9 | 252 | 1 | 9 | 190 | 1 | 13 | 32600 | 1 | 9 | 25700 | 1 | 9 | 20800 | 1 | 13 | 4180 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 6400 | A | 7 | 9140 | A | 7 | 2.4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 7 | 0
1986-05-27 | 1900-05-26 | 9:00 | 9 | 835 | 1331 | 496 | 1 | 13 | 456 | 1 | 13 | 210 | 1 | 13 | 53000 | 1 | 13 | 46900 | 1 | 13 | 23500 | 1 | 13 | 5150 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 18.9 | 66.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 9140 | A | 7 | 2.5 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.42 | 7 | 0
1986-05-27 | 1900-05-26 | 10:00 | 10 | 1023 | 1331 | 509 | 1 | 13 | 225 | 1 | 13 | 336 | 1 | 13 | 56100 | 1 | 13 | 23900 | 1 | 13 | 37600 | 1 | 13 | 11350 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 18.9 | 66.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.73 | A | 7 | 978 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 9140 | A | 7 | 2.4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.02 | 7 | 0
1986-05-27 | 1900-05-26 | 11:00 | 11 | 1163 | 1331 | 746 | 1 | 13 | 552 | 1 | 13 | 263 | 1 | 13 | 78500 | 1 | 13 | 55800 | 1 | 13 | 29600 | 1 | 13 | 12160 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 20.6 | 69.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.04 | 7 | 0
1986-05-27 | 1900-05-26 | 12:00 | 12 | 1244 | 1331 | 670 | 1 | 13 | 308 | 1 | 13 | 382 | 1 | 13 | 74200 | 1 | 13 | 33500 | 1 | 13 | 42700 | 1 | 13 | 22660 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 21.7 | 71.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.59 | A | 7 | 977 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.44 | 7 | 0
1986-05-27 | 1900-05-26 | 13:00 | 13 | 1261 | 1331 | 741 | 1 | 13 | 358 | 1 | 13 | 401 | 1 | 13 | 81800 | 1 | 13 | 39000 | 1 | 13 | 44800 | 1 | 13 | 26010 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 21.1 | 69.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 2.3 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.84 | 7 | 0
1986-05-27 | 1900-05-26 | 14:00 | 14 | 1214 | 1331 | 572 | 1 | 9 | 150 | 1 | 9 | 435 | 1 | 13 | 63000 | 1 | 9 | 16000 | 1 | 9 | 48400 | 1 | 13 | 21800 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 22.2 | 71.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.55 | A | 7 | 976 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 2.3 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.84 | 7 | 0
1986-05-27 | 1900-05-26 | 15:00 | 15 | 1104 | 1331 | 475 | 1 | 9 | 91 | 1 | 9 | 400 | 1 | 13 | 52500 | 1 | 9 | 9400 | 1 | 9 | 44700 | 1 | 13 | 16550 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.66 | A | 7 | 976 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.3 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.94 | 7 | 0
1986-05-27 | 1900-05-26 | 16:00 | 16 | 941 | 1331 | 523 | 1 | 9 | 260 | 1 | 9 | 339 | 1 | 13 | 56200 | 1 | 9 | 28000 | 1 | 9 | 36400 | 1 | 13 | 10040 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 22.2 | 71.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.04 | 7 | 0
1986-05-27 | 1900-05-26 | 17:00 | 17 | 734 | 1331 | 183 | 1 | 9 | 2 | 1 | 9 | 182 | 1 | 13 | 21200 | 1 | 9 | 200 | 1 | 9 | 21200 | 1 | 13 | 7850 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 3 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.84 | 7 | 0
1986-05-27 | 1900-05-26 | 18:00 | 18 | 499 | 1331 | 147 | 1 | 9 | 25 | 1 | 9 | 138 | 1 | 13 | 16200 | 1 | 9 | 2400 | 1 | 9 | 15300 | 1 | 13 | 3880 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 11.7 | 53.06 | A | 7 | 0.68 | A | 7 | 976 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.1 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.56 | 7 | 0
1986-05-27 | 1900-05-26 | 19:00 | 19 | 251 | 1331 | 90 | 1 | 13 | 44 | 1 | 9 | 82 | 1 | 13 | 9900 | 1 | 13 | 3500 | 1 | 9 | 9200 | 1 | 13 | 1940 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 190 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.16 | 7 | 0
1986-05-27 | 1900-05-26 | 20:00 | 20 | 35 | 765 | 14 | 1 | 13 | 5 | 1 | 13 | 14 | 1 | 13 | 1600 | 1 | 13 | 300 | 1 | 13 | 1600 | 1 | 13 | 340 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 14.4 | 57.92 | A | 7 | 11.7 | 53.06 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 180 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.36 | 7 | 0
1986-05-27 | 1900-05-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.26 | 7 | 0
1986-05-27 | 1900-05-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 12.8 | 55.04 | A | 7 | 11.7 | 53.06 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.86 | 7 | 0
1986-05-27 | 1900-05-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 12.2 | 53.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 200 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.78 | 7 | 0
1986-05-27 | 1900-05-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 12.8 | 55.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.97 | A | 7 | 977 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.46 | 7 | 0
1986-05-28 | 1900-05-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.96 | A | 7 | 977 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.36 | 1 | 0
1986-05-28 | 1900-05-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.96 | A | 7 | 977 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.36 | 1 | 0
1986-05-28 | 1900-05-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.96 | A | 7 | 977 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.36 | 1 | 0
1986-05-28 | 1900-05-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | 11.7 | 53.06 | A | 7 | 1 | A | 7 | 977 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 1 | 0
1986-05-28 | 1900-05-27 | 5:00 | 5 | 0 | 55 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 8 | A | 7 | 6 | A | 7 | 11.7 | 53.06 | A | 7 | 11.7 | 53.06 | A | 7 | 1 | A | 7 | 977 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 3660 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 1 | 0
1986-05-28 | 1900-05-27 | 6:00 | 6 | 122 | 1330 | 30 | 1 | 13 | 13 | 1 | 9 | 29 | 1 | 13 | 3300 | 1 | 13 | 800 | 1 | 9 | 3200 | 1 | 13 | 700 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 12.8 | 55.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 9140 | A | 7 | 2.2 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.46 | 1 | 0
1986-05-28 | 1900-05-27 | 7:00 | 7 | 368 | 1330 | 143 | 1 | 13 | 213 | 1 | 13 | 84 | 1 | 13 | 15400 | 1 | 13 | 18600 | 1 | 13 | 10200 | 1 | 13 | 1590 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 15 | 59 | A | 7 | 12.8 | 55.04 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 9140 | A | 7 | 2.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.74 | 1 | 0
1986-05-28 | 1900-05-27 | 8:00 | 8 | 612 | 1330 | 173 | 1 | 9 | 91 | 1 | 9 | 131 | 1 | 13 | 19300 | 1 | 9 | 9300 | 1 | 9 | 15000 | 1 | 13 | 3170 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 2.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 1 | 0
1986-05-28 | 1900-05-27 | 9:00 | 9 | 836 | 1330 | 572 | 1 | 13 | 605 | 1 | 13 | 191 | 1 | 13 | 59300 | 1 | 13 | 60300 | 1 | 13 | 21300 | 1 | 13 | 4540 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 19.4 | 66.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 1 | 0
1986-05-28 | 1900-05-27 | 10:00 | 10 | 1024 | 1330 | 637 | 1 | 13 | 551 | 1 | 13 | 213 | 1 | 13 | 67100 | 1 | 13 | 55800 | 1 | 13 | 24100 | 1 | 13 | 6900 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 20 | 68 | A | 7 | 13.3 | 55.94 | A | 7 | 0.66 | A | 7 | 979 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.74 | 1 | 0
1986-05-28 | 1900-05-27 | 11:00 | 11 | 1163 | 1330 | 743 | 1 | 13 | 536 | 1 | 13 | 274 | 1 | 13 | 81100 | 1 | 13 | 56100 | 1 | 13 | 31900 | 1 | 13 | 13030 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 21.7 | 71.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.64 | A | 7 | 979 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.12 | 1 | 0
1986-05-28 | 1900-05-27 | 12:00 | 12 | 1244 | 1330 | 844 | 1 | 13 | 580 | 1 | 13 | 300 | 1 | 13 | 88700 | 1 | 13 | 58500 | 1 | 13 | 33800 | 1 | 13 | 19480 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 22.2 | 71.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.62 | A | 7 | 979 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 910 | A | 7 | 2.5 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.72 | 1 | 0
1986-05-28 | 1900-05-27 | 13:00 | 13 | 1262 | 1330 | 479 | 1 | 9 | 109 | 1 | 9 | 375 | 1 | 13 | 53400 | 1 | 9 | 11700 | 1 | 9 | 42300 | 1 | 13 | 22690 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 2.6 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.9 | 1 | 0
1986-05-28 | 1900-05-27 | 14:00 | 14 | 1215 | 1330 | 591 | 1 | 9 | 259 | 1 | 9 | 355 | 1 | 13 | 65600 | 1 | 9 | 28200 | 1 | 9 | 39800 | 1 | 13 | 18580 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 2.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.72 | 1 | 0
1986-05-28 | 1900-05-27 | 15:00 | 15 | 1106 | 1330 | 426 | 1 | 9 | 148 | 1 | 9 | 302 | 1 | 13 | 47500 | 1 | 9 | 15900 | 1 | 9 | 34300 | 1 | 13 | 11640 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 22.8 | 73.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 2.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.92 | 1 | 0
1986-05-28 | 1900-05-27 | 16:00 | 16 | 942 | 1330 | 567 | 1 | 13 | 553 | 1 | 13 | 175 | 1 | 13 | 60000 | 1 | 13 | 56100 | 1 | 13 | 20100 | 1 | 13 | 4970 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 25 | 77 | A | 7 | 13.9 | 57.02 | A | 7 | 0.5 | A | 7 | 978 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.52 | 1 | 0
1986-05-28 | 1900-05-27 | 17:00 | 17 | 736 | 1330 | 393 | 1 | 13 | 410 | 1 | 13 | 167 | 1 | 13 | 42300 | 1 | 13 | 41700 | 1 | 13 | 19200 | 1 | 13 | 3680 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 22.2 | 71.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.5 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.72 | 1 | 0
1986-05-28 | 1900-05-27 | 18:00 | 18 | 501 | 1330 | 165 | 1 | 13 | 47 | 1 | 13 | 148 | 1 | 13 | 18200 | 1 | 13 | 4500 | 1 | 13 | 16500 | 1 | 13 | 4110 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 22.8 | 73.04 | A | 7 | 15 | 59 | A | 7 | 0.62 | A | 7 | 977 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.6 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.7 | 1 | 0
1986-05-28 | 1900-05-27 | 19:00 | 19 | 253 | 1330 | 78 | 1 | 13 | 34 | 1 | 9 | 72 | 1 | 13 | 8600 | 1 | 13 | 2700 | 1 | 9 | 8100 | 1 | 13 | 1770 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 21.1 | 69.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.66 | A | 7 | 978 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.5 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 1 | 0
1986-05-28 | 1900-05-27 | 20:00 | 20 | 37 | 765 | 8 | 1 | 13 | 2 | 1 | 9 | 8 | 1 | 13 | 1000 | 1 | 13 | 0 | 1 | 9 | 1000 | 1 | 13 | 300 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 40 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 2.5 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 1 | 0
1986-05-28 | 1900-05-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 18.9 | 66.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.76 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.42 | 1 | 0
1986-05-28 | 1900-05-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 17.2 | 62.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.84 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.02 | 1 | 0
1986-05-28 | 1900-05-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 1 | 0
1986-05-28 | 1900-05-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 1 | 0
1986-05-29 | 1900-05-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.62 | 2 | 0
1986-05-29 | 1900-05-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 15.6 | 60.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.22 | 2 | 0
1986-05-29 | 1900-05-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.42 | 2 | 0
1986-05-29 | 1900-05-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.34 | 2 | 0
1986-05-29 | 1900-05-28 | 5:00 | 5 | 0 | 55 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 3 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 13.9 | 57.02 | A | 7 | 1 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 2400 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.02 | 2 | 0
1986-05-29 | 1900-05-28 | 6:00 | 6 | 124 | 1330 | 43 | 1 | 13 | 108 | 1 | 9 | 32 | 1 | 13 | 4400 | 1 | 13 | 4900 | 1 | 9 | 4000 | 1 | 13 | 580 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 400 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.84 | 2 | 0
1986-05-29 | 1900-05-28 | 7:00 | 7 | 369 | 1330 | 132 | 1 | 13 | 45 | 1 | 13 | 119 | 1 | 13 | 14400 | 1 | 13 | 4000 | 1 | 13 | 13300 | 1 | 13 | 3010 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 14.4 | 57.92 | A | 7 | 14.4 | 57.92 | A | 7 | 1 | A | 7 | 981 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 100 | A | 7 | 9140 | A | 7 | 2.5 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.82 | 2 | 0
1986-05-29 | 1900-05-28 | 8:00 | 8 | 613 | 1330 | 192 | 1 | 9 | 4 | 1 | 9 | 190 | 1 | 13 | 21700 | 1 | 9 | 300 | 1 | 9 | 21500 | 1 | 13 | 7290 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 16.7 | 62.06 | A | 7 | 1 | A | 7 | 981 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 100 | A | 7 | 0 | A | 7 | 2.9 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.96 | 2 | 0
1986-05-29 | 1900-05-28 | 9:00 | 9 | 837 | 1330 | 501 | 1 | 13 | 459 | 1 | 13 | 212 | 1 | 13 | 53400 | 1 | 13 | 47300 | 1 | 13 | 23600 | 1 | 13 | 5220 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 1600 | A | 7 | 9140 | A | 7 | 3 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.96 | 2 | 0
1986-05-29 | 1900-05-28 | 10:00 | 10 | 1024 | 1330 | 666 | 1 | 13 | 609 | 1 | 13 | 196 | 1 | 13 | 70500 | 1 | 13 | 61900 | 1 | 13 | 22700 | 1 | 13 | 6430 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.16 | 2 | 0
1986-05-29 | 1900-05-28 | 11:00 | 11 | 1164 | 1330 | 785 | 1 | 13 | 621 | 1 | 13 | 241 | 1 | 13 | 83200 | 1 | 13 | 63100 | 1 | 13 | 27800 | 1 | 13 | 11310 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.74 | 2 | 0
1986-05-29 | 1900-05-28 | 12:00 | 12 | 1245 | 1330 | 970 | 1 | 13 | 783 | 1 | 13 | 236 | 1 | 13 | 103800 | 1 | 13 | 80000 | 1 | 13 | 28700 | 1 | 13 | 15640 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.38 | 2 | 0
1986-05-29 | 1900-05-28 | 13:00 | 13 | 1263 | 1330 | 567 | 1 | 9 | 281 | 1 | 9 | 300 | 1 | 13 | 64000 | 1 | 9 | 30700 | 1 | 9 | 34800 | 1 | 13 | 19340 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.66 | A | 7 | 981 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 2290 | A | 7 | 2.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.16 | 2 | 0
1986-05-29 | 1900-05-28 | 14:00 | 14 | 1215 | 1330 | 721 | 1 | 13 | 428 | 1 | 13 | 329 | 1 | 13 | 77800 | 1 | 13 | 44800 | 1 | 13 | 36800 | 1 | 13 | 19300 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 25 | 77 | A | 7 | 15.6 | 60.08 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 2.7 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.28 | 2 | 0
1986-05-29 | 1900-05-28 | 15:00 | 15 | 1107 | 1330 | 477 | 1 | 13 | 193 | 1 | 13 | 316 | 1 | 13 | 52600 | 1 | 13 | 21000 | 1 | 13 | 35100 | 1 | 13 | 12020 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 24.4 | 75.92 | A | 7 | 15 | 59 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 2.6 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.4 | 2 | 0
1986-05-29 | 1900-05-28 | 16:00 | 16 | 944 | 1330 | 673 | 1 | 13 | 603 | 1 | 13 | 245 | 1 | 13 | 72000 | 1 | 13 | 62600 | 1 | 13 | 27500 | 1 | 13 | 7000 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 24.4 | 75.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.54 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 2.5 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.12 | 2 | 0
1986-05-29 | 1900-05-28 | 17:00 | 17 | 738 | 1330 | 486 | 1 | 13 | 591 | 1 | 13 | 159 | 1 | 13 | 50500 | 1 | 13 | 58400 | 1 | 13 | 18100 | 1 | 13 | 3460 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 25 | 77 | A | 7 | 14.4 | 57.92 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.62 | 2 | 0
1986-05-29 | 1900-05-28 | 18:00 | 18 | 503 | 1330 | 226 | 1 | 13 | 289 | 1 | 13 | 118 | 1 | 13 | 24600 | 1 | 13 | 28200 | 1 | 13 | 13900 | 1 | 13 | 2340 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 24.4 | 75.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.5 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.64 | 2 | 0
1986-05-29 | 1900-05-28 | 19:00 | 19 | 256 | 1330 | 95 | 1 | 13 | 222 | 1 | 13 | 53 | 1 | 13 | 10100 | 1 | 13 | 16400 | 1 | 13 | 7000 | 1 | 13 | 950 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.92 | 2 | 0
1986-05-29 | 1900-05-28 | 20:00 | 20 | 38 | 787 | 18 | 1 | 13 | 48 | 1 | 9 | 13 | 1 | 13 | 1700 | 1 | 13 | 1400 | 1 | 9 | 1600 | 1 | 13 | 220 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 70 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.72 | 2 | 0
1986-05-29 | 1900-05-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.64 | A | 7 | 980 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.12 | 2 | 0
1986-05-29 | 1900-05-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 2 | 0
1986-05-29 | 1900-05-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 2 | 0
1986-05-29 | 1900-05-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 15 | 59 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.4 | 2 | 0
1986-05-30 | 1900-05-29 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 16.7 | 62.06 | A | 7 | 15 | 59 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 3050 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.1 | 3 | 0
1986-05-30 | 1900-05-29 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 15 | 59 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 2130 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.1 | 3 | 0
1986-05-30 | 1900-05-29 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 15 | 59 | A | 7 | 14.4 | 57.92 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 3 | 0
1986-05-30 | 1900-05-29 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 15.6 | 60.08 | A | 7 | 15 | 59 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 2440 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.4 | 3 | 0
1986-05-30 | 1900-05-29 | 5:00 | 5 | 0 | 78 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 9 | A | 7 | 16.1 | 60.98 | A | 7 | 15 | 59 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 70 | A | 7 | 1.5 | A | 7 | 8000 | A | 7 | 1980 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.7 | 3 | 0
1986-05-30 | 1900-05-29 | 6:00 | 6 | 125 | 1329 | 29 | 1 | 13 | 16 | 1 | 9 | 28 | 1 | 13 | 3200 | 1 | 13 | 1000 | 1 | 9 | 3100 | 1 | 13 | 680 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 16.1 | 60.98 | A | 7 | 15 | 59 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 3050 | A | 7 | 2.6 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.7 | 3 | 0
1986-05-30 | 1900-05-29 | 7:00 | 7 | 370 | 1329 | 149 | 1 | 9 | 137 | 1 | 9 | 111 | 1 | 13 | 16200 | 1 | 9 | 12200 | 1 | 9 | 12800 | 1 | 13 | 2460 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 2740 | A | 7 | 2.7 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.58 | 3 | 0
1986-05-30 | 1900-05-29 | 8:00 | 8 | 614 | 1329 | 276 | 1 | 13 | 253 | 1 | 13 | 159 | 1 | 13 | 29800 | 1 | 13 | 25900 | 1 | 13 | 17900 | 1 | 13 | 3380 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 22.2 | 71.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 6400 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.26 | 3 | 0
1986-05-30 | 1900-05-29 | 9:00 | 9 | 837 | 1329 | 563 | 1 | 13 | 621 | 1 | 13 | 171 | 1 | 13 | 58800 | 1 | 13 | 62300 | 1 | 13 | 19500 | 1 | 13 | 4150 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.38 | 3 | 0
1986-05-30 | 1900-05-29 | 10:00 | 10 | 1025 | 1329 | 570 | 1 | 13 | 470 | 1 | 13 | 207 | 1 | 13 | 62800 | 1 | 13 | 49100 | 1 | 13 | 24800 | 1 | 13 | 6760 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.08 | 3 | 0
1986-05-30 | 1900-05-29 | 11:00 | 11 | 1164 | 1329 | 511 | 1 | 9 | 242 | 1 | 9 | 299 | 1 | 13 | 57100 | 1 | 9 | 26400 | 1 | 9 | 33900 | 1 | 13 | 13100 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 350 | A | 7 | 1.5 | A | 7 | 8000 | A | 7 | 1400 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.38 | 3 | 0
1986-05-30 | 1900-05-29 | 12:00 | 12 | 1246 | 1329 | 650 | 1 | 9 | 333 | 1 | 9 | 338 | 1 | 13 | 72700 | 1 | 9 | 36300 | 1 | 9 | 38600 | 1 | 13 | 20160 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 1220 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.38 | 3 | 0
1986-05-30 | 1900-05-29 | 13:00 | 13 | 1263 | 1329 | 827 | 1 | 13 | 566 | 1 | 13 | 288 | 1 | 13 | 87300 | 1 | 13 | 57300 | 1 | 13 | 32800 | 1 | 13 | 21010 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 26.1 | 78.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 1370 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 3 | 0
1986-05-30 | 1900-05-29 | 14:00 | 14 | 1216 | 1329 | 710 | 1 | 13 | 480 | 1 | 13 | 270 | 1 | 13 | 78200 | 1 | 13 | 50400 | 1 | 13 | 32000 | 1 | 13 | 15810 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 26.7 | 80.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.51 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.18 | 3 | 0
1986-05-30 | 1900-05-29 | 15:00 | 15 | 1108 | 1329 | 503 | 1 | 9 | 116 | 1 | 9 | 406 | 1 | 13 | 55100 | 1 | 9 | 12300 | 1 | 9 | 44800 | 1 | 13 | 15750 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 25.6 | 78.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 1400 | A | 7 | 2.8 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.08 | 3 | 0
1986-05-30 | 1900-05-29 | 16:00 | 16 | 945 | 1329 | 659 | 1 | 9 | 723 | 1 | 9 | 145 | 1 | 13 | 70700 | 1 | 9 | 74000 | 1 | 9 | 18000 | 1 | 13 | 4230 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.88 | 3 | 0
1986-05-30 | 1900-05-29 | 17:00 | 17 | 740 | 1329 | 435 | 1 | 9 | 618 | 1 | 9 | 91 | 1 | 13 | 47000 | 1 | 9 | 62600 | 1 | 9 | 12100 | 1 | 13 | 2140 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 26.1 | 78.98 | A | 7 | 15 | 59 | A | 7 | 0.51 | A | 7 | 978 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 3 | 0
1986-05-30 | 1900-05-29 | 18:00 | 18 | 505 | 1329 | 291 | 1 | 9 | 582 | 1 | 9 | 72 | 1 | 13 | 31000 | 1 | 9 | 55100 | 1 | 9 | 10100 | 1 | 13 | 1450 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 26.1 | 78.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.48 | 3 | 0
1986-05-30 | 1900-05-29 | 19:00 | 19 | 259 | 1329 | 129 | 1 | 13 | 421 | 1 | 9 | 49 | 1 | 13 | 13400 | 1 | 13 | 31800 | 1 | 9 | 7200 | 1 | 13 | 880 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 25 | 77 | A | 7 | 15 | 59 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50 | 3 | 0
1986-05-30 | 1900-05-29 | 20:00 | 20 | 40 | 809 | 19 | 1 | 13 | 58 | 1 | 9 | 14 | 1 | 13 | 1900 | 1 | 13 | 1700 | 1 | 9 | 1800 | 1 | 13 | 240 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.083 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.58 | 3 | 0
1986-05-30 | 1900-05-29 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.73 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.68 | 3 | 0
1986-05-30 | 1900-05-29 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 170 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.68 | 3 | 0
1986-05-30 | 1900-05-29 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 20 | 68 | A | 7 | 15.6 | 60.08 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.48 | 3 | 0
1986-05-30 | 1900-05-29 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 210 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.68 | 3 | 0
1986-05-31 | 1900-05-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.88 | 4 | 0
1986-05-31 | 1900-05-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 4 | 0
1986-05-31 | 1900-05-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 180 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 4 | 0
1986-05-31 | 1900-05-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 4 | 0
1986-05-31 | 1900-05-30 | 5:00 | 5 | 0 | 78 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 15 | 59 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.4 | 4 | 0
1986-05-31 | 1900-05-30 | 6:00 | 6 | 127 | 1329 | 44 | 1 | 13 | 125 | 1 | 9 | 32 | 1 | 13 | 4600 | 1 | 13 | 5800 | 1 | 9 | 4100 | 1 | 13 | 580 | 1 | 21 | 4 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 4 | 0
1986-05-31 | 1900-05-30 | 7:00 | 7 | 372 | 1329 | 196 | 1 | 9 | 471 | 1 | 9 | 64 | 1 | 13 | 20300 | 1 | 9 | 40800 | 1 | 9 | 8900 | 1 | 13 | 1200 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.26 | 4 | 0
1986-05-31 | 1900-05-30 | 8:00 | 8 | 615 | 1329 | 395 | 1 | 9 | 651 | 1 | 9 | 94 | 1 | 13 | 41800 | 1 | 9 | 63800 | 1 | 9 | 12200 | 1 | 13 | 1980 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 4 | 0
1986-05-31 | 1900-05-30 | 9:00 | 9 | 838 | 1329 | 593 | 1 | 9 | 719 | 1 | 9 | 140 | 1 | 13 | 63000 | 1 | 9 | 72800 | 1 | 9 | 17000 | 1 | 13 | 3500 | 1 | 18 | 4 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.66 | 4 | 0
1986-05-31 | 1900-05-30 | 10:00 | 10 | 1026 | 1329 | 653 | 1 | 9 | 535 | 1 | 9 | 239 | 1 | 13 | 70800 | 1 | 9 | 55800 | 1 | 9 | 27600 | 1 | 13 | 7890 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 26.1 | 78.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.68 | 4 | 0
1986-05-31 | 1900-05-30 | 11:00 | 11 | 1165 | 1329 | 761 | 1 | 13 | 569 | 1 | 13 | 262 | 1 | 13 | 80200 | 1 | 13 | 57600 | 1 | 13 | 29600 | 1 | 13 | 12280 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 4 | 0
1986-05-31 | 1900-05-30 | 12:00 | 12 | 1246 | 1329 | 860 | 1 | 13 | 603 | 1 | 13 | 294 | 1 | 13 | 90600 | 1 | 13 | 60900 | 1 | 13 | 33400 | 1 | 13 | 19420 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 27.2 | 80.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.51 | A | 7 | 977 | A | 7 | 200 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.98 | 4 | 0
1986-05-31 | 1900-05-30 | 13:00 | 13 | 1264 | 1329 | 864 | 1 | 13 | 613 | 1 | 13 | 280 | 1 | 13 | 91500 | 1 | 13 | 62100 | 1 | 13 | 32200 | 1 | 13 | 20590 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 28.3 | 82.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.46 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.08 | 4 | 0
1986-05-31 | 1900-05-30 | 14:00 | 14 | 1217 | 1329 | 780 | 1 | 13 | 539 | 1 | 13 | 286 | 1 | 13 | 85400 | 1 | 13 | 56500 | 1 | 13 | 33600 | 1 | 13 | 16870 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 29.4 | 84.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.45 | A | 7 | 976 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.58 | 4 | 0
1986-05-31 | 1900-05-30 | 15:00 | 15 | 1109 | 1329 | 777 | 1 | 9 | 710 | 1 | 9 | 185 | 1 | 13 | 83500 | 1 | 9 | 72800 | 1 | 9 | 22600 | 1 | 13 | 7500 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 29.4 | 84.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.43 | A | 7 | 976 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.48 | 4 | 0
1986-05-31 | 1900-05-30 | 16:00 | 16 | 947 | 1329 | 651 | 1 | 13 | 634 | 1 | 13 | 200 | 1 | 13 | 68400 | 1 | 13 | 63900 | 1 | 13 | 22700 | 1 | 13 | 5630 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 28.9 | 84.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.46 | A | 7 | 975 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.88 | 4 | 0
1986-05-31 | 1900-05-30 | 17:00 | 17 | 742 | 1329 | 460 | 1 | 13 | 474 | 1 | 13 | 197 | 1 | 13 | 48800 | 1 | 13 | 48200 | 1 | 13 | 21800 | 1 | 13 | 4430 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 28.3 | 82.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.48 | A | 7 | 975 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.28 | 4 | 0
1986-05-31 | 1900-05-30 | 18:00 | 18 | 508 | 1329 | 290 | 1 | 13 | 451 | 1 | 13 | 119 | 1 | 13 | 30800 | 1 | 13 | 42800 | 1 | 13 | 14400 | 1 | 13 | 2290 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 28.3 | 82.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.48 | A | 7 | 975 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.28 | 4 | 0
1986-05-31 | 1900-05-30 | 19:00 | 19 | 261 | 1329 | 89 | 1 | 13 | 105 | 1 | 9 | 69 | 1 | 13 | 9800 | 1 | 13 | 8100 | 1 | 9 | 8200 | 1 | 13 | 1480 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.52 | A | 7 | 975 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.18 | 4 | 0
1986-05-31 | 1900-05-30 | 20:00 | 20 | 41 | 830 | 14 | 1 | 13 | 10 | 1 | 9 | 13 | 1 | 13 | 1500 | 1 | 13 | 500 | 1 | 9 | 1500 | 1 | 13 | 330 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | 26.1 | 78.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.56 | A | 7 | 975 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 4 | 0
1986-05-31 | 1900-05-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.71 | A | 7 | 975 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.06 | 4 | 0
1986-05-31 | 1900-05-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 22 | 71.6 | A | 7 | 17 | 62.6 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.4 | 4 | 0
1986-05-31 | 1900-05-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.2 | 70.16 | A | 7 | 16.9 | 62.42 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.62 | 4 | 0
1986-05-31 | 1900-05-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20.4 | 68.72 | A | 7 | 16.7 | 62.06 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.86 | 4 | 0
2005-06-01 | 1900-05-31 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 19.6 | 67.28 | A | 7 | 16.6 | 61.88 | A | 7 | 0.94 | A | 7 | 978 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 3000 | A | 7 | 3.4 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.68 | 5 | 0
2005-06-01 | 1900-05-31 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 18.8 | 65.84 | A | 7 | 16.4 | 61.52 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 3.5 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.02 | 5 | 0
2005-06-01 | 1900-05-31 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 18 | 64.4 | A | 7 | 16.3 | 61.34 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 12800 | A | 7 | 1829 | A | 7 | 3.6 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 59.94 | 5 | 0
2005-06-01 | 1900-05-31 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 17.2 | 62.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 14400 | A | 7 | 2591 | A | 7 | 3.5 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 59.58 | 5 | 0
2005-06-01 | 1900-05-31 | 5:00 | 5 | 1 | 100 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 17.2 | 62.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 1524 | A | 7 | 3.4 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 59.58 | 5 | 0
2005-06-01 | 1900-05-31 | 6:00 | 6 | 129 | 1328 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 17.2 | 62.96 | A | 7 | 15.6 | 60.08 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 1372 | A | 7 | 3.3 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 58.18 | 5 | 0
2005-06-01 | 1900-05-31 | 7:00 | 7 | 373 | 1328 | 39 | 2 | 8 | 0 | 2 | 15 | 39 | 2 | 8 | 4700 | 2 | 8 | 0 | 2 | 15 | 4700 | 2 | 8 | 1680 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 975 | A | 7 | 3.3 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 58.78 | 5 | 0
2005-06-01 | 1900-05-31 | 8:00 | 8 | 616 | 1328 | 69 | 2 | 8 | 0 | 2 | 15 | 69 | 2 | 8 | 8400 | 2 | 8 | 0 | 2 | 15 | 8400 | 2 | 8 | 3260 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 4800 | A | 7 | 762 | A | 7 | 3.3 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 58.78 | 5 | 0
2005-06-01 | 1900-05-31 | 9:00 | 9 | 839 | 1328 | 98 | 2 | 8 | 0 | 2 | 15 | 98 | 2 | 8 | 12100 | 2 | 8 | 0 | 2 | 15 | 12100 | 2 | 8 | 4950 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 17.2 | 62.96 | A | 7 | 15.6 | 60.08 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 3962 | A | 7 | 3.2 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 58.18 | 5 | 0
2005-06-01 | 1900-05-31 | 10:00 | 10 | 1026 | 1328 | 133 | 2 | 8 | 0 | 2 | 15 | 133 | 2 | 8 | 16600 | 2 | 8 | 0 | 2 | 15 | 16600 | 2 | 8 | 6920 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 70 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 488 | A | 7 | 3.2 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 57.58 | 5 | 0
2005-06-01 | 1900-05-31 | 11:00 | 11 | 1165 | 1328 | 297 | 2 | 8 | 12 | 2 | 15 | 286 | 2 | 8 | 35600 | 2 | 8 | 1000 | 2 | 15 | 34700 | 2 | 8 | 13500 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 3962 | A | 7 | 3.2 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.88 | 5 | 0
2005-06-01 | 1900-05-31 | 12:00 | 12 | 1247 | 1328 | 487 | 2 | 8 | 84 | 2 | 15 | 408 | 2 | 8 | 53900 | 2 | 8 | 8600 | 2 | 15 | 45700 | 2 | 8 | 22190 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 976 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 4572 | A | 7 | 3.2 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.66 | 5 | 0
2005-06-01 | 1900-05-31 | 13:00 | 13 | 1265 | 1328 | 401 | 2 | 8 | 42 | 2 | 15 | 361 | 2 | 8 | 44400 | 2 | 8 | 4300 | 2 | 15 | 40300 | 2 | 8 | 21050 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 21.7 | 71.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 3.2 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.08 | 5 | 0
2005-06-01 | 1900-05-31 | 14:00 | 14 | 1219 | 1328 | 484 | 2 | 8 | 60 | 2 | 15 | 429 | 2 | 8 | 53500 | 2 | 8 | 6200 | 2 | 15 | 47800 | 2 | 8 | 21560 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 22.8 | 73.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.64 | A | 7 | 978 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 3.1 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.98 | 5 | 0
2005-06-01 | 1900-05-31 | 15:00 | 15 | 1111 | 1328 | 388 | 2 | 8 | 36 | 2 | 15 | 358 | 2 | 8 | 42900 | 2 | 8 | 3700 | 2 | 15 | 39800 | 2 | 8 | 15260 | 2 | 19 | 8 | E | 9 | 7 | E | 9 | 23.9 | 75.02 | A | 7 | 15 | 59 | A | 7 | 0.57 | A | 7 | 976 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.6 | 5 | 0
2005-06-01 | 1900-05-31 | 16:00 | 16 | 949 | 1328 | 448 | 2 | 8 | 160 | 2 | 15 | 333 | 2 | 8 | 49000 | 2 | 8 | 16900 | 2 | 15 | 36800 | 2 | 8 | 10290 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 24.4 | 75.92 | A | 7 | 15 | 59 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 50.4 | 5 | 0
2005-06-01 | 1900-05-31 | 17:00 | 17 | 744 | 1328 | 422 | 2 | 8 | 400 | 2 | 15 | 198 | 2 | 8 | 44600 | 2 | 8 | 40700 | 2 | 15 | 21800 | 2 | 8 | 4470 | 2 | 19 | 6 | E | 9 | 5 | E | 9 | 24.4 | 75.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.54 | A | 7 | 977 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.12 | 5 | 0
2005-06-01 | 1900-05-31 | 18:00 | 18 | 511 | 1328 | 279 | 2 | 8 | 340 | 2 | 15 | 148 | 2 | 8 | 29700 | 2 | 8 | 33200 | 2 | 15 | 16900 | 2 | 8 | 3070 | 2 | 19 | 8 | E | 9 | 8 | A | 7 | 23.9 | 75.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.55 | A | 7 | 975 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.7 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.32 | 5 | 0
2005-06-01 | 1900-05-31 | 19:00 | 19 | 265 | 1328 | 57 | 2 | 8 | 0 | 2 | 15 | 57 | 2 | 8 | 6500 | 2 | 8 | 0 | 2 | 15 | 6500 | 2 | 8 | 2070 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.53 | A | 7 | 977 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.24 | 5 | 0
2005-06-01 | 1900-05-31 | 20:00 | 20 | 44 | 852 | 2 | 2 | 8 | 0 | 2 | 15 | 2 | 2 | 8 | 300 | 2 | 8 | 0 | 2 | 15 | 300 | 2 | 8 | 80 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.04 | 5 | 0
2005-06-01 | 1900-05-31 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 20.6 | 69.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.65 | A | 7 | 975 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.52 | 5 | 0
2005-06-01 | 1900-05-31 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 20.6 | 69.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.52 | 5 | 0
2005-06-01 | 1900-05-31 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.04 | 5 | 0
2005-06-01 | 1900-05-31 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.145 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.44 | 5 | 0
2005-06-02 | 1900-06-01 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.04 | 6 | 0
2005-06-02 | 1900-06-01 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.64 | 6 | 0
2005-06-02 | 1900-06-01 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | E | 9 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 974 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.16 | 6 | 0
2005-06-02 | 1900-06-01 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | E | 9 | 16.1 | 60.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.76 | 6 | 0
2005-06-02 | 1900-06-01 | 5:00 | 5 | 1 | 100 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9600 | A | 7 | 4572 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.86 | 6 | 0
2005-06-02 | 1900-06-01 | 6:00 | 6 | 130 | 1328 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 2 | E | 9 | 2 | E | 9 | 17.2 | 62.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.72 | A | 7 | 975 | A | 7 | 130 | A | 7 | 1.5 | A | 7 | 8000 | A | 7 | 6096 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.06 | 6 | 0
2005-06-02 | 1900-06-01 | 7:00 | 7 | 374 | 1328 | 219 | 2 | 8 | 431 | 2 | 15 | 98 | 2 | 8 | 22800 | 2 | 8 | 37200 | 2 | 15 | 12300 | 2 | 8 | 1830 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 13.9 | 57.02 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 130 | B | 8 | 1.5 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.12 | 6 | 0
2005-06-02 | 1900-06-01 | 8:00 | 8 | 617 | 1328 | 391 | 2 | 8 | 614 | 2 | 15 | 106 | 2 | 8 | 41000 | 2 | 8 | 59900 | 2 | 15 | 13200 | 2 | 8 | 2190 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.63 | A | 7 | 977 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.12 | 6 | 0
2005-06-02 | 1900-06-01 | 9:00 | 9 | 839 | 1328 | 573 | 2 | 8 | 702 | 2 | 15 | 129 | 2 | 8 | 61200 | 2 | 8 | 71300 | 2 | 15 | 16000 | 2 | 8 | 3270 | 2 | 19 | 2 | E | 9 | 2 | E | 9 | 23.9 | 75.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.55 | A | 7 | 974 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.32 | 6 | 0
2005-06-02 | 1900-06-01 | 10:00 | 10 | 1027 | 1328 | 701 | 2 | 8 | 636 | 2 | 15 | 209 | 2 | 8 | 73900 | 2 | 8 | 64500 | 2 | 15 | 24000 | 2 | 8 | 6850 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 25 | 77 | A | 7 | 15 | 59 | A | 7 | 0.54 | A | 7 | 977 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50 | 6 | 0
2005-06-02 | 1900-06-01 | 11:00 | 11 | 1166 | 1328 | 798 | 2 | 8 | 615 | 2 | 15 | 257 | 2 | 8 | 84100 | 2 | 8 | 62300 | 2 | 15 | 29300 | 2 | 8 | 12130 | 2 | 19 | 10 | E | 9 | 5 | E | 9 | 26.1 | 78.98 | A | 7 | 15 | 59 | A | 7 | 0.5 | A | 7 | 977 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.1 | 6 | 0
2005-06-02 | 1900-06-01 | 12:00 | 12 | 1247 | 1328 | 754 | 2 | 8 | 361 | 2 | 15 | 415 | 2 | 8 | 83000 | 2 | 8 | 39300 | 2 | 15 | 46100 | 2 | 8 | 25470 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 26.1 | 78.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.47 | A | 7 | 975 | A | 7 | 80 | B | 8 | 3.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.92 | 6 | 0
2005-06-02 | 1900-06-01 | 13:00 | 13 | 1265 | 1328 | 461 | 2 | 8 | 60 | 2 | 15 | 404 | 2 | 8 | 51000 | 2 | 8 | 6200 | 2 | 15 | 45200 | 2 | 8 | 23340 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 26.1 | 78.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.48 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12800 | A | 7 | 6096 | A | 7 | 2.8 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.82 | 6 | 0
2005-06-02 | 1900-06-01 | 14:00 | 14 | 1219 | 1328 | 442 | 2 | 8 | 54 | 2 | 15 | 393 | 2 | 8 | 48900 | 2 | 8 | 5500 | 2 | 15 | 43800 | 2 | 8 | 20040 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 26.7 | 80.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.47 | A | 7 | 976 | A | 7 | 210 | A | 7 | 1.5 | A | 7 | 14400 | A | 7 | 5486 | A | 7 | 2.9 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.62 | 6 | 0
2005-06-02 | 1900-06-01 | 15:00 | 15 | 1112 | 1328 | 371 | 2 | 8 | 24 | 2 | 15 | 351 | 2 | 8 | 43500 | 2 | 8 | 2200 | 2 | 15 | 41600 | 2 | 8 | 15470 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 25.6 | 78.08 | A | 7 | 15 | 59 | A | 7 | 0.52 | A | 7 | 973 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 12800 | A | 7 | 4572 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.6 | 6 | 0
2005-06-02 | 1900-06-01 | 16:00 | 16 | 950 | 1328 | 278 | 2 | 8 | 12 | 2 | 15 | 269 | 2 | 8 | 32400 | 2 | 8 | 1100 | 2 | 15 | 31600 | 2 | 8 | 12000 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 25.6 | 78.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.56 | A | 7 | 973 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 12800 | A | 7 | 6096 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.08 | 6 | 0
2005-06-02 | 1900-06-01 | 17:00 | 17 | 746 | 1328 | 159 | 2 | 8 | 6 | 2 | 15 | 156 | 2 | 8 | 18800 | 2 | 8 | 500 | 2 | 15 | 18500 | 2 | 8 | 7030 | 2 | 19 | 9 | E | 9 | 7 | E | 9 | 26.1 | 78.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.52 | A | 7 | 973 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 6096 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.48 | 6 | 0
2005-06-02 | 1900-06-01 | 18:00 | 18 | 513 | 1328 | 222 | 2 | 8 | 167 | 2 | 15 | 157 | 2 | 8 | 24100 | 2 | 8 | 16300 | 2 | 15 | 17800 | 2 | 8 | 3650 | 2 | 19 | 7 | E | 9 | 7 | A | 7 | 25.6 | 78.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.5 | A | 7 | 971 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.22 | 6 | 0
2005-06-02 | 1900-06-01 | 19:00 | 19 | 267 | 1328 | 57 | 2 | 8 | 0 | 2 | 15 | 57 | 2 | 8 | 6500 | 2 | 8 | 0 | 2 | 15 | 6500 | 2 | 8 | 2080 | 2 | 19 | 4 | E | 9 | 3 | E | 9 | 24.4 | 75.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.36 | 6 | 0
2005-06-02 | 1900-06-01 | 20:00 | 20 | 45 | 852 | 2 | 2 | 8 | 0 | 2 | 15 | 2 | 2 | 8 | 300 | 2 | 8 | 0 | 2 | 15 | 300 | 2 | 8 | 80 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 15 | 59 | A | 7 | 0.66 | A | 7 | 974 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.5 | 6 | 0
2005-06-02 | 1900-06-01 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 972 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.92 | 6 | 0
2005-06-02 | 1900-06-01 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 974 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.92 | 6 | 0
2005-06-02 | 1900-06-01 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 974 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.92 | 6 | 0
2005-06-02 | 1900-06-01 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 5 | E | 9 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.7 | A | 7 | 972 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.32 | 6 | 0
2005-06-03 | 1900-06-02 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 973 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 14400 | A | 7 | 3048 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.92 | 7 | 0
2005-06-03 | 1900-06-02 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.7 | A | 7 | 973 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.32 | 7 | 0
2005-06-03 | 1900-06-02 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 7 | E | 9 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 971 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.9 | 7 | 0
2005-06-03 | 1900-06-02 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 7 | E | 9 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 972 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 12800 | A | 7 | 6096 | A | 7 | 3.4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.9 | 7 | 0
2005-06-03 | 1900-06-02 | 5:00 | 5 | 1 | 122 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 19.4 | 66.92 | A | 7 | 15 | 59 | A | 7 | 0.76 | A | 7 | 972 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 4267 | A | 7 | 3.7 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.5 | 7 | 0
2005-06-03 | 1900-06-02 | 6:00 | 6 | 131 | 1328 | 16 | 2 | 8 | 0 | 2 | 15 | 16 | 2 | 8 | 1900 | 2 | 8 | 0 | 2 | 15 | 1900 | 2 | 8 | 610 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.79 | A | 7 | 971 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 3048 | A | 7 | 4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.08 | 7 | 0
2005-06-03 | 1900-06-02 | 7:00 | 7 | 375 | 1328 | 39 | 2 | 8 | 0 | 2 | 15 | 39 | 2 | 8 | 4700 | 2 | 8 | 0 | 2 | 15 | 4700 | 2 | 8 | 1690 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 18 | 64.4 | A | 7 | 17 | 62.6 | A | 7 | 0.94 | A | 7 | 974 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 1020 | A | 7 | 4.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 3 | 1 | A | 7 | 61.4 | 7 | 0
2005-06-03 | 1900-06-02 | 8:00 | 8 | 617 | 1328 | 62 | 2 | 8 | 0 | 2 | 15 | 62 | 2 | 8 | 7600 | 2 | 8 | 0 | 2 | 15 | 7600 | 2 | 8 | 2960 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 1676 | A | 7 | 4.4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 10 | 1 | A | 7 | 60.66 | 7 | 0
2005-06-03 | 1900-06-02 | 9:00 | 9 | 840 | 1328 | 91 | 2 | 8 | 0 | 2 | 15 | 91 | 2 | 8 | 11300 | 2 | 8 | 0 | 2 | 15 | 11300 | 2 | 8 | 4640 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.96 | A | 7 | 974 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 2400 | A | 7 | 1219 | A | 7 | 4.6 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 4 | 1 | A | 7 | 62.16 | 7 | 0
2005-06-03 | 1900-06-02 | 10:00 | 10 | 1027 | 1328 | 120 | 2 | 8 | 0 | 2 | 15 | 120 | 2 | 8 | 15100 | 2 | 8 | 0 | 2 | 15 | 15100 | 2 | 8 | 6320 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 2400 | A | 7 | 732 | A | 7 | 4.4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 5 | 1 | A | 7 | 61.56 | 7 | 0
2005-06-03 | 1900-06-02 | 11:00 | 11 | 1166 | 1328 | 136 | 2 | 8 | 0 | 2 | 15 | 136 | 2 | 8 | 17200 | 2 | 8 | 0 | 2 | 15 | 17200 | 2 | 8 | 7200 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 3962 | A | 7 | 4.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 3 | 1 | A | 7 | 61.56 | 7 | 0
2005-06-03 | 1900-06-02 | 12:00 | 12 | 1248 | 1328 | 146 | 2 | 8 | 0 | 2 | 15 | 146 | 2 | 8 | 18600 | 2 | 8 | 0 | 2 | 15 | 18600 | 2 | 8 | 7720 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 971 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 9600 | A | 7 | 3048 | A | 7 | 4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.06 | 7 | 0
2005-06-03 | 1900-06-02 | 13:00 | 13 | 1266 | 1328 | 150 | 2 | 8 | 0 | 2 | 15 | 150 | 2 | 8 | 19100 | 2 | 8 | 0 | 2 | 15 | 19100 | 2 | 8 | 7920 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 972 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 3962 | A | 7 | 4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.56 | 7 | 0
2005-06-03 | 1900-06-02 | 14:00 | 14 | 1220 | 1328 | 183 | 2 | 8 | 6 | 2 | 15 | 177 | 2 | 8 | 22800 | 2 | 8 | 400 | 2 | 15 | 22400 | 2 | 8 | 9140 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 970 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 4267 | A | 7 | 4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.96 | 7 | 0
2005-06-03 | 1900-06-02 | 15:00 | 15 | 1113 | 1328 | 168 | 2 | 8 | 0 | 2 | 15 | 168 | 2 | 8 | 20800 | 2 | 8 | 0 | 2 | 15 | 20800 | 2 | 8 | 8630 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 20 | 68 | A | 7 | 17.8 | 64.04 | A | 7 | 0.87 | A | 7 | 969 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 3962 | A | 7 | 4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.44 | 7 | 0
2005-06-03 | 1900-06-02 | 16:00 | 16 | 952 | 1328 | 108 | 2 | 8 | 0 | 2 | 15 | 108 | 2 | 8 | 13500 | 2 | 8 | 0 | 2 | 15 | 13500 | 2 | 8 | 5630 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 972 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 11200 | A | 7 | 3048 | A | 7 | 3.9 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.36 | 7 | 0
2005-06-03 | 1900-06-02 | 17:00 | 17 | 748 | 1328 | 77 | 2 | 8 | 0 | 2 | 15 | 77 | 2 | 8 | 9600 | 2 | 8 | 0 | 2 | 15 | 9600 | 2 | 8 | 3840 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 972 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 975 | A | 7 | 3.7 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 60.66 | 7 | 0
2005-06-03 | 1900-06-02 | 18:00 | 18 | 515 | 1328 | 52 | 2 | 8 | 0 | 2 | 15 | 52 | 2 | 8 | 6400 | 2 | 8 | 0 | 2 | 15 | 6400 | 2 | 8 | 2390 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 967 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 3.6 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.88 | 7 | 0
2005-06-03 | 1900-06-02 | 19:00 | 19 | 269 | 1328 | 22 | 2 | 8 | 0 | 2 | 15 | 22 | 2 | 8 | 2700 | 2 | 8 | 0 | 2 | 15 | 2700 | 2 | 8 | 930 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 969 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 3.7 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.06 | 7 | 0
2005-06-03 | 1900-06-02 | 20:00 | 20 | 47 | 874 | 2 | 2 | 8 | 0 | 2 | 15 | 2 | 2 | 8 | 300 | 2 | 8 | 0 | 2 | 15 | 300 | 2 | 8 | 80 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 3.9 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.46 | 7 | 0
2005-06-03 | 1900-06-02 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 969 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.06 | 7 | 0
2005-06-03 | 1900-06-02 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 971 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 12800 | A | 7 | 1829 | A | 7 | 4.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 3 | 1 | A | 7 | 61.56 | 7 | 0
2005-06-03 | 1900-06-02 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 17.2 | 62.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.97 | A | 7 | 971 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 1433 | A | 7 | 4.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.46 | 7 | 0
2005-06-03 | 1900-06-02 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.96 | A | 7 | 969 | A | 7 | 50 | A | 7 | 1.5 | A | 7 | 8000 | A | 7 | 945 | A | 7 | 4.5 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 3 | 1 | A | 7 | 62.16 | 7 | 0
2005-06-04 | 1900-06-03 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.96 | A | 7 | 971 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 579 | A | 7 | 4.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 11 | 1 | A | 7 | 62.16 | 1 | 0
2005-06-04 | 1900-06-03 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.96 | A | 7 | 969 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 1097 | A | 7 | 4.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 4 | 1 | A | 7 | 62.16 | 1 | 0
2005-06-04 | 1900-06-03 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 967 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 2134 | A | 7 | 4.1 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 60.66 | 1 | 0
2005-06-04 | 1900-06-03 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 7 | E | 9 | 17.2 | 62.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.97 | A | 7 | 968 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 3.9 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.46 | 1 | 0
2005-06-04 | 1900-06-03 | 5:00 | 5 | 1 | 122 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.96 | A | 7 | 969 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 914 | A | 7 | 3.7 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.16 | 1 | 0
2005-06-04 | 1900-06-03 | 6:00 | 6 | 132 | 1327 | 16 | 2 | 8 | 0 | 2 | 15 | 16 | 2 | 8 | 1900 | 2 | 8 | 0 | 2 | 15 | 1900 | 2 | 8 | 610 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 18.9 | 66.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.93 | A | 7 | 967 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 9600 | A | 7 | 488 | A | 7 | 3.5 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.64 | 1 | 0
2005-06-04 | 1900-06-03 | 7:00 | 7 | 375 | 1327 | 47 | 2 | 8 | 0 | 2 | 15 | 47 | 2 | 8 | 5600 | 2 | 8 | 0 | 2 | 15 | 5600 | 2 | 8 | 1990 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 969 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 1372 | A | 7 | 3.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.54 | 1 | 0
2005-06-04 | 1900-06-03 | 8:00 | 8 | 618 | 1327 | 96 | 2 | 8 | 0 | 2 | 15 | 96 | 2 | 8 | 11500 | 2 | 8 | 0 | 2 | 15 | 11500 | 2 | 8 | 4350 | 2 | 19 | 9 | E | 9 | 6 | E | 9 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 970 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.04 | 1 | 0
2005-06-04 | 1900-06-03 | 9:00 | 9 | 840 | 1327 | 488 | 2 | 8 | 342 | 2 | 15 | 272 | 2 | 8 | 52600 | 2 | 8 | 36500 | 2 | 15 | 29500 | 2 | 8 | 7090 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 969 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.72 | 1 | 0
2005-06-04 | 1900-06-03 | 10:00 | 10 | 1027 | 1327 | 714 | 2 | 8 | 636 | 2 | 15 | 221 | 2 | 8 | 75000 | 2 | 8 | 64300 | 2 | 15 | 25100 | 2 | 8 | 7220 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 971 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 762 | A | 7 | 3.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.62 | 1 | 0
2005-06-04 | 1900-06-03 | 11:00 | 11 | 1166 | 1327 | 823 | 2 | 8 | 573 | 2 | 15 | 319 | 2 | 8 | 88500 | 2 | 8 | 59900 | 2 | 15 | 35800 | 2 | 8 | 15570 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.76 | A | 7 | 971 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.58 | 1 | 0
2005-06-04 | 1900-06-03 | 12:00 | 12 | 1248 | 1327 | 286 | 2 | 8 | 30 | 2 | 15 | 258 | 2 | 8 | 31800 | 2 | 8 | 3000 | 2 | 15 | 28900 | 2 | 8 | 14760 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 968 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.66 | 1 | 0
2005-06-04 | 1900-06-03 | 13:00 | 13 | 1266 | 1327 | 473 | 2 | 8 | 102 | 2 | 15 | 376 | 2 | 8 | 52800 | 2 | 8 | 10900 | 2 | 15 | 42400 | 2 | 8 | 23560 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 27.8 | 82.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.72 | A | 7 | 971 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.46 | 1 | 0
2005-06-04 | 1900-06-03 | 14:00 | 14 | 1221 | 1327 | 767 | 2 | 8 | 497 | 2 | 15 | 309 | 2 | 8 | 83300 | 2 | 8 | 52100 | 2 | 15 | 35400 | 2 | 8 | 18690 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 28.3 | 82.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.67 | A | 7 | 970 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 12800 | A | 7 | 1524 | A | 7 | 3.6 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.46 | 1 | 0
2005-06-04 | 1900-06-03 | 15:00 | 15 | 1114 | 1327 | 731 | 2 | 8 | 549 | 2 | 15 | 269 | 2 | 8 | 79300 | 2 | 8 | 57400 | 2 | 15 | 31000 | 2 | 8 | 11060 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 29.4 | 84.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.63 | A | 7 | 968 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.46 | 1 | 0
2005-06-04 | 1900-06-03 | 16:00 | 16 | 953 | 1327 | 522 | 2 | 8 | 273 | 2 | 15 | 325 | 2 | 8 | 56300 | 2 | 8 | 29400 | 2 | 15 | 35100 | 2 | 8 | 9710 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 969 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 62.96 | 1 | 0
2005-06-04 | 1900-06-03 | 17:00 | 17 | 749 | 1327 | 329 | 2 | 8 | 147 | 2 | 15 | 246 | 2 | 8 | 35900 | 2 | 8 | 15300 | 2 | 15 | 27300 | 2 | 8 | 6440 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 969 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 1250 | A | 7 | 3.8 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.48 | 1 | 0
2005-06-04 | 1900-06-03 | 18:00 | 18 | 517 | 1327 | 279 | 2 | 8 | 352 | 2 | 15 | 142 | 2 | 8 | 29900 | 2 | 8 | 34600 | 2 | 15 | 16400 | 2 | 8 | 2920 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 27.2 | 80.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.67 | A | 7 | 966 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 1250 | A | 7 | 3.9 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.68 | 1 | 0
2005-06-04 | 1900-06-03 | 19:00 | 19 | 271 | 1327 | 132 | 2 | 8 | 417 | 2 | 15 | 47 | 2 | 8 | 13700 | 2 | 8 | 32300 | 2 | 15 | 7100 | 2 | 8 | 860 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 26.1 | 78.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.72 | A | 7 | 969 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 1676 | A | 7 | 4.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.88 | 1 | 0
2005-06-04 | 1900-06-03 | 20:00 | 20 | 48 | 896 | 4 | 2 | 8 | 0 | 2 | 15 | 4 | 2 | 8 | 500 | 2 | 8 | 0 | 2 | 15 | 500 | 2 | 8 | 160 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.79 | A | 7 | 969 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 975 | A | 7 | 4.4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.08 | 1 | 0
2005-06-04 | 1900-06-03 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 969 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 671 | A | 7 | 4.7 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 20 | 1 | A | 7 | 59.08 | 1 | 0
2005-06-04 | 1900-06-03 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 972 | A | 7 | 220 | A | 7 | 10.3 | A | 7 | 6400 | A | 7 | 549 | A | 7 | 4.5 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 13 | 1 | A | 7 | 60.06 | 1 | 0
2005-06-04 | 1900-06-03 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 20 | 68 | A | 7 | 18.3 | 64.94 | A | 7 | 0.9 | A | 7 | 969 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 4.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 62.94 | 1 | 0
2005-06-04 | 1900-06-03 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 5 | E | 9 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 968 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 9144 | A | 7 | 4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.46 | 1 | 0
2005-06-05 | 1900-06-04 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 4 | E | 9 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 9144 | A | 7 | 3.9 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.46 | 2 | 0
2005-06-05 | 1900-06-04 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | E | 9 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 970 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 9144 | A | 7 | 3.8 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.08 | 2 | 0
2005-06-05 | 1900-06-04 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 969 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 9144 | A | 7 | 3.8 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.08 | 2 | 0
2005-06-05 | 1900-06-04 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | E | 9 | 18 | 64.4 | A | 7 | 17 | 62.6 | A | 7 | 0.94 | A | 7 | 970 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 600 | A | 7 | 3.5 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.4 | 2 | 0
2005-06-05 | 1900-06-04 | 5:00 | 5 | 1 | 122 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 971 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 3.1 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.96 | 2 | 0
2005-06-05 | 1900-06-04 | 6:00 | 6 | 133 | 1327 | 48 | 2 | 8 | 0 | 2 | 15 | 48 | 2 | 8 | 5200 | 2 | 8 | 0 | 2 | 15 | 5200 | 2 | 8 | 1360 | 2 | 19 | 6 | E | 9 | 4 | E | 9 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 971 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 9144 | A | 7 | 2.8 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.96 | 2 | 0
2005-06-05 | 1900-06-04 | 7:00 | 7 | 376 | 1327 | 219 | 2 | 8 | 418 | 2 | 15 | 100 | 2 | 8 | 22700 | 2 | 8 | 36100 | 2 | 15 | 12400 | 2 | 8 | 1880 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 19.4 | 66.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.73 | A | 7 | 973 | A | 7 | 220 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.92 | 2 | 0
2005-06-05 | 1900-06-04 | 8:00 | 8 | 618 | 1327 | 398 | 2 | 8 | 639 | 2 | 15 | 100 | 2 | 8 | 41900 | 2 | 8 | 62600 | 2 | 15 | 12700 | 2 | 8 | 2090 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.7 | A | 7 | 973 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.32 | 2 | 0
2005-06-05 | 1900-06-04 | 9:00 | 9 | 840 | 1327 | 579 | 2 | 8 | 726 | 2 | 15 | 119 | 2 | 8 | 60500 | 2 | 8 | 72400 | 2 | 15 | 14600 | 2 | 8 | 2790 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 15 | 59 | A | 7 | 0.68 | A | 7 | 972 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.9 | 2 | 0
2005-06-05 | 1900-06-04 | 10:00 | 10 | 1027 | 1327 | 739 | 2 | 8 | 751 | 2 | 15 | 157 | 2 | 8 | 77100 | 2 | 8 | 75300 | 2 | 15 | 18700 | 2 | 8 | 4740 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 22.2 | 71.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.68 | A | 7 | 974 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.68 | 2 | 0
2005-06-05 | 1900-06-04 | 11:00 | 11 | 1166 | 1327 | 866 | 2 | 8 | 826 | 2 | 15 | 139 | 2 | 8 | 88800 | 2 | 8 | 82700 | 2 | 15 | 16000 | 2 | 8 | 5080 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 22.8 | 73.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.64 | A | 7 | 975 | A | 7 | 230 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.98 | 2 | 0
2005-06-05 | 1900-06-04 | 12:00 | 12 | 1248 | 1327 | 925 | 2 | 8 | 788 | 2 | 15 | 182 | 2 | 8 | 97600 | 2 | 8 | 79500 | 2 | 15 | 22700 | 2 | 8 | 11670 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 23.9 | 75.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.6 | A | 7 | 973 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.18 | 2 | 0
2005-06-05 | 1900-06-04 | 13:00 | 13 | 1267 | 1327 | 965 | 2 | 8 | 870 | 2 | 15 | 132 | 2 | 8 | 99000 | 2 | 8 | 87300 | 2 | 15 | 15500 | 2 | 8 | 8130 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 25 | 77 | A | 7 | 15.6 | 60.08 | A | 7 | 0.56 | A | 7 | 976 | A | 7 | 240 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.28 | 2 | 0
2005-06-05 | 1900-06-04 | 14:00 | 14 | 1221 | 1327 | 921 | 2 | 8 | 856 | 2 | 15 | 131 | 2 | 8 | 94500 | 2 | 8 | 85800 | 2 | 15 | 15400 | 2 | 8 | 6240 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 25.6 | 78.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.56 | A | 7 | 976 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.08 | 2 | 0
2005-06-05 | 1900-06-04 | 15:00 | 15 | 1115 | 1327 | 818 | 2 | 8 | 805 | 2 | 15 | 140 | 2 | 8 | 87300 | 2 | 8 | 81600 | 2 | 15 | 18600 | 2 | 8 | 5490 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 25.6 | 78.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.54 | A | 7 | 974 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.88 | 2 | 0
2005-06-05 | 1900-06-04 | 16:00 | 16 | 954 | 1327 | 681 | 2 | 8 | 766 | 2 | 15 | 129 | 2 | 8 | 71700 | 2 | 8 | 77000 | 2 | 15 | 16200 | 2 | 8 | 3560 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 26.1 | 78.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.52 | A | 7 | 976 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.48 | 2 | 0
2005-06-05 | 1900-06-04 | 17:00 | 17 | 751 | 1327 | 500 | 2 | 8 | 689 | 2 | 15 | 109 | 2 | 8 | 53300 | 2 | 8 | 69500 | 2 | 15 | 13900 | 2 | 8 | 2540 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 26.1 | 78.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.52 | A | 7 | 976 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.48 | 2 | 0
2005-06-05 | 1900-06-04 | 18:00 | 18 | 519 | 1327 | 316 | 2 | 8 | 601 | 2 | 15 | 81 | 2 | 8 | 33200 | 2 | 8 | 57100 | 2 | 15 | 10900 | 2 | 8 | 1620 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 15 | 59 | A | 7 | 0.52 | A | 7 | 974 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.6 | 2 | 0
2005-06-05 | 1900-06-04 | 19:00 | 19 | 274 | 1327 | 133 | 2 | 8 | 396 | 2 | 15 | 51 | 2 | 8 | 13600 | 2 | 8 | 30700 | 2 | 15 | 7300 | 2 | 8 | 930 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 977 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.38 | 2 | 0
2005-06-05 | 1900-06-04 | 20:00 | 20 | 50 | 896 | 4 | 2 | 8 | 0 | 2 | 15 | 4 | 2 | 8 | 500 | 2 | 8 | 0 | 2 | 15 | 500 | 2 | 8 | 160 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.73 | A | 7 | 976 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.68 | 2 | 0
2005-06-05 | 1900-06-04 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.88 | 2 | 0
2005-06-05 | 1900-06-04 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.98 | 2 | 0
2005-06-05 | 1900-06-04 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 977 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.58 | 2 | 0
2005-06-05 | 1900-06-04 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 15 | 59 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.146 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.6 | 2 | 0
2005-06-06 | 1900-06-05 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.98 | 3 | 0
2005-06-06 | 1900-06-05 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.02 | 3 | 0
2005-06-06 | 1900-06-05 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.32 | 3 | 0
2005-06-06 | 1900-06-05 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.86 | A | 7 | 977 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.32 | 3 | 0
2005-06-06 | 1900-06-05 | 5:00 | 5 | 1 | 122 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.86 | A | 7 | 977 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.32 | 3 | 0
2005-06-06 | 1900-06-05 | 6:00 | 6 | 134 | 1326 | 32 | 2 | 8 | 0 | 2 | 15 | 32 | 2 | 8 | 3600 | 2 | 8 | 0 | 2 | 15 | 3600 | 2 | 8 | 1070 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.96 | 3 | 0
2005-06-06 | 1900-06-05 | 7:00 | 7 | 377 | 1326 | 187 | 2 | 8 | 248 | 2 | 15 | 117 | 2 | 8 | 19700 | 2 | 8 | 21900 | 2 | 15 | 13500 | 2 | 8 | 2360 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.72 | 3 | 0
2005-06-06 | 1900-06-05 | 8:00 | 8 | 618 | 1326 | 398 | 2 | 8 | 614 | 2 | 15 | 111 | 2 | 8 | 41600 | 2 | 8 | 59800 | 2 | 15 | 13600 | 2 | 8 | 2290 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 20.6 | 69.08 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.98 | 3 | 0
2005-06-06 | 1900-06-05 | 9:00 | 9 | 840 | 1326 | 579 | 2 | 8 | 726 | 2 | 15 | 119 | 2 | 8 | 60500 | 2 | 8 | 72400 | 2 | 15 | 14600 | 2 | 8 | 2790 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.74 | A | 7 | 977 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.18 | 3 | 0
2005-06-06 | 1900-06-05 | 10:00 | 10 | 1027 | 1326 | 733 | 2 | 8 | 733 | 2 | 15 | 164 | 2 | 8 | 78600 | 2 | 8 | 75200 | 2 | 15 | 20300 | 2 | 8 | 5530 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.98 | 3 | 0
2005-06-06 | 1900-06-05 | 11:00 | 11 | 1166 | 1326 | 866 | 2 | 8 | 802 | 2 | 15 | 160 | 2 | 8 | 91800 | 2 | 8 | 81000 | 2 | 15 | 20400 | 2 | 8 | 7250 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.98 | 3 | 0
2005-06-06 | 1900-06-05 | 12:00 | 12 | 1248 | 1326 | 943 | 2 | 8 | 806 | 2 | 15 | 183 | 2 | 8 | 99500 | 2 | 8 | 81300 | 2 | 15 | 22900 | 2 | 8 | 11760 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 28.3 | 82.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.63 | A | 7 | 976 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.68 | 3 | 0
2005-06-06 | 1900-06-05 | 13:00 | 13 | 1267 | 1326 | 839 | 2 | 8 | 552 | 2 | 15 | 311 | 2 | 8 | 91700 | 2 | 8 | 57900 | 2 | 15 | 36300 | 2 | 8 | 24340 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.98 | 3 | 0
2005-06-06 | 1900-06-05 | 14:00 | 14 | 1222 | 1326 | 826 | 2 | 8 | 598 | 2 | 15 | 274 | 2 | 8 | 87200 | 2 | 8 | 60600 | 2 | 15 | 31300 | 2 | 8 | 16260 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.98 | 3 | 0
2005-06-06 | 1900-06-05 | 15:00 | 15 | 1116 | 1326 | 800 | 2 | 8 | 722 | 2 | 15 | 192 | 2 | 8 | 85700 | 2 | 8 | 74000 | 2 | 15 | 23400 | 2 | 8 | 7950 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 27.8 | 82.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.65 | A | 7 | 974 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.18 | 3 | 0
2005-06-06 | 1900-06-05 | 16:00 | 16 | 955 | 1326 | 664 | 2 | 8 | 719 | 2 | 15 | 145 | 2 | 8 | 71200 | 2 | 8 | 73700 | 2 | 15 | 18100 | 2 | 8 | 4310 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.96 | 3 | 0
2005-06-06 | 1900-06-05 | 17:00 | 17 | 752 | 1326 | 500 | 2 | 8 | 613 | 2 | 15 | 152 | 2 | 8 | 52100 | 2 | 8 | 60900 | 2 | 15 | 17500 | 2 | 8 | 3390 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 976 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.48 | 3 | 0
2005-06-06 | 1900-06-05 | 18:00 | 18 | 520 | 1326 | 264 | 2 | 8 | 277 | 2 | 15 | 155 | 2 | 8 | 28100 | 2 | 8 | 27200 | 2 | 15 | 17400 | 2 | 8 | 3250 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.98 | 3 | 0
2005-06-06 | 1900-06-05 | 19:00 | 19 | 276 | 1326 | 133 | 2 | 8 | 358 | 2 | 15 | 59 | 2 | 8 | 14100 | 2 | 8 | 27400 | 2 | 15 | 8400 | 2 | 8 | 1060 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.98 | 3 | 0
2005-06-06 | 1900-06-05 | 20:00 | 20 | 51 | 917 | 4 | 2 | 8 | 0 | 2 | 15 | 4 | 2 | 8 | 500 | 2 | 8 | 0 | 2 | 15 | 500 | 2 | 8 | 160 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.58 | 3 | 0
2005-06-06 | 1900-06-05 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 20.6 | 69.08 | A | 7 | 0.77 | A | 7 | 973 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.98 | 3 | 0
2005-06-06 | 1900-06-05 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.42 | 3 | 0
2005-06-06 | 1900-06-05 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.62 | 3 | 0
2005-06-06 | 1900-06-05 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.04 | 3 | 0
2005-06-07 | 1900-06-06 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.62 | 4 | 0
2005-06-07 | 1900-06-06 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.81 | A | 7 | 975 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.92 | 4 | 0
2005-06-07 | 1900-06-06 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 972 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.52 | 4 | 0
2005-06-07 | 1900-06-06 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.22 | 4 | 0
2005-06-07 | 1900-06-06 | 5:00 | 5 | 1 | 144 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.52 | 4 | 0
2005-06-07 | 1900-06-06 | 6:00 | 6 | 134 | 1326 | 47 | 2 | 8 | 0 | 2 | 15 | 47 | 2 | 8 | 5100 | 2 | 8 | 0 | 2 | 15 | 5100 | 2 | 8 | 1350 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 972 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.52 | 4 | 0
2005-06-07 | 1900-06-06 | 7:00 | 7 | 377 | 1326 | 218 | 2 | 8 | 417 | 2 | 15 | 100 | 2 | 8 | 22700 | 2 | 8 | 36100 | 2 | 15 | 12400 | 2 | 8 | 1880 | 2 | 19 | 8 | E | 9 | 7 | E | 9 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.5 | 4 | 0
2005-06-07 | 1900-06-06 | 8:00 | 8 | 619 | 1326 | 336 | 2 | 8 | 316 | 2 | 15 | 188 | 2 | 8 | 35800 | 2 | 8 | 32300 | 2 | 15 | 20700 | 2 | 8 | 4140 | 2 | 19 | 7 | E | 9 | 5 | E | 9 | 25.6 | 78.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.74 | A | 7 | 974 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.28 | 4 | 0
2005-06-07 | 1900-06-06 | 9:00 | 9 | 840 | 1326 | 566 | 2 | 8 | 641 | 2 | 15 | 160 | 2 | 8 | 59600 | 2 | 8 | 64500 | 2 | 15 | 18600 | 2 | 8 | 3950 | 2 | 19 | 2 | E | 9 | 2 | E | 9 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 972 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.18 | 4 | 0
2005-06-07 | 1900-06-06 | 10:00 | 10 | 1027 | 1326 | 588 | 2 | 8 | 303 | 2 | 15 | 353 | 2 | 8 | 63700 | 2 | 8 | 32800 | 2 | 15 | 38300 | 2 | 8 | 11820 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 974 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.98 | 4 | 0
2005-06-07 | 1900-06-06 | 11:00 | 11 | 1167 | 1326 | 848 | 2 | 8 | 687 | 2 | 15 | 242 | 2 | 8 | 89800 | 2 | 8 | 69800 | 2 | 15 | 28200 | 2 | 8 | 11580 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 28.3 | 82.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.67 | A | 7 | 975 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.46 | 4 | 0
2005-06-07 | 1900-06-06 | 12:00 | 12 | 1248 | 1326 | 925 | 2 | 8 | 746 | 2 | 15 | 221 | 2 | 8 | 99400 | 2 | 8 | 76500 | 2 | 15 | 27200 | 2 | 8 | 15230 | 2 | 19 | 7 | E | 9 | 7 | E | 9 | 30 | 86 | A | 7 | 21.7 | 71.06 | A | 7 | 0.61 | A | 7 | 972 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.96 | 4 | 0
2005-06-07 | 1900-06-06 | 13:00 | 13 | 1268 | 1326 | 779 | 2 | 8 | 438 | 2 | 15 | 360 | 2 | 8 | 83900 | 2 | 8 | 45800 | 2 | 15 | 40000 | 2 | 8 | 28420 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 29.4 | 84.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.63 | A | 7 | 974 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.46 | 4 | 0
2005-06-07 | 1900-06-06 | 14:00 | 14 | 1223 | 1326 | 750 | 2 | 8 | 443 | 2 | 15 | 340 | 2 | 8 | 80700 | 2 | 8 | 46300 | 2 | 15 | 37800 | 2 | 8 | 20910 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 31.1 | 87.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.57 | A | 7 | 974 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.86 | 4 | 0
2005-06-07 | 1900-06-06 | 15:00 | 15 | 1116 | 1326 | 435 | 2 | 8 | 90 | 2 | 15 | 360 | 2 | 8 | 48100 | 2 | 8 | 9200 | 2 | 15 | 40300 | 2 | 8 | 15500 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 31.1 | 87.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.57 | A | 7 | 971 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.86 | 4 | 0
2005-06-07 | 1900-06-06 | 16:00 | 16 | 957 | 1326 | 579 | 2 | 8 | 380 | 2 | 15 | 304 | 2 | 8 | 62800 | 2 | 8 | 41000 | 2 | 15 | 33200 | 2 | 8 | 9030 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 972 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.98 | 4 | 0
2005-06-07 | 1900-06-06 | 17:00 | 17 | 754 | 1326 | 93 | 2 | 8 | 0 | 2 | 15 | 93 | 2 | 8 | 11400 | 2 | 8 | 0 | 2 | 15 | 11400 | 2 | 8 | 4560 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 30 | 86 | A | 7 | 20 | 68 | A | 7 | 0.55 | A | 7 | 972 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.5 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.8 | 4 | 0
2005-06-07 | 1900-06-06 | 18:00 | 18 | 522 | 1326 | 285 | 2 | 8 | 341 | 2 | 15 | 151 | 2 | 8 | 30400 | 2 | 8 | 33600 | 2 | 15 | 17200 | 2 | 8 | 3150 | 2 | 19 | 8 | E | 9 | 5 | A | 7 | 28.3 | 82.94 | A | 7 | 20 | 68 | A | 7 | 0.61 | A | 7 | 970 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.3 | 4 | 0
2005-06-07 | 1900-06-06 | 19:00 | 19 | 278 | 1326 | 133 | 2 | 8 | 391 | 2 | 15 | 52 | 2 | 8 | 13700 | 2 | 8 | 30400 | 2 | 15 | 7400 | 2 | 8 | 940 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 973 | A | 7 | 130 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.96 | 4 | 0
2005-06-07 | 1900-06-06 | 20:00 | 20 | 53 | 917 | 4 | 2 | 8 | 0 | 2 | 15 | 4 | 2 | 8 | 500 | 2 | 8 | 0 | 2 | 15 | 500 | 2 | 8 | 160 | 2 | 19 | 8 | E | 9 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 973 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.6 | 4 | 0
2005-06-07 | 1900-06-06 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 971 | A | 7 | 140 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.3 | 4 | 0
2005-06-07 | 1900-06-06 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 973 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.82 | 4 | 0
2005-06-07 | 1900-06-06 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 973 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.42 | 4 | 0
2005-06-07 | 1900-06-06 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 971 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.1 | 4 | 0
2005-06-08 | 1900-06-07 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 972 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.1 | 5 | 0
2005-06-08 | 1900-06-07 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.85 | A | 7 | 971 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.78 | 5 | 0
2005-06-08 | 1900-06-07 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 22.8 | 73.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.87 | A | 7 | 969 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 66.28 | 5 | 0
2005-06-08 | 1900-06-07 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 970 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 67.78 | 5 | 0
2005-06-08 | 1900-06-07 | 5:00 | 5 | 1 | 144 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 22.2 | 71.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.93 | A | 7 | 970 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 68.48 | 5 | 0
2005-06-08 | 1900-06-07 | 6:00 | 6 | 135 | 1326 | 31 | 2 | 8 | 0 | 2 | 15 | 31 | 2 | 8 | 3500 | 2 | 8 | 0 | 2 | 15 | 3500 | 2 | 8 | 1050 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 969 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 67.78 | 5 | 0
2005-06-08 | 1900-06-07 | 7:00 | 7 | 377 | 1326 | 218 | 2 | 8 | 450 | 2 | 15 | 90 | 2 | 8 | 22900 | 2 | 8 | 39000 | 2 | 15 | 11800 | 2 | 8 | 1670 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 971 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 67.76 | 5 | 0
2005-06-08 | 1900-06-07 | 8:00 | 8 | 619 | 1326 | 377 | 2 | 8 | 515 | 2 | 15 | 137 | 2 | 8 | 40400 | 2 | 8 | 51100 | 2 | 15 | 16500 | 2 | 8 | 2770 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 26.7 | 80.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.76 | A | 7 | 971 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 66.46 | 5 | 0
2005-06-08 | 1900-06-07 | 9:00 | 9 | 840 | 1326 | 579 | 2 | 8 | 647 | 2 | 15 | 169 | 2 | 8 | 60700 | 2 | 8 | 65000 | 2 | 15 | 19400 | 2 | 8 | 4140 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 27.8 | 82.04 | A | 7 | 22.8 | 73.04 | A | 7 | 0.74 | A | 7 | 968 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 4.6 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 66.94 | 5 | 0
2005-06-08 | 1900-06-07 | 10:00 | 10 | 1027 | 1326 | 550 | 2 | 8 | 260 | 2 | 15 | 348 | 2 | 8 | 59700 | 2 | 8 | 28100 | 2 | 15 | 37800 | 2 | 8 | 11630 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 29.4 | 84.92 | A | 7 | 23.3 | 73.94 | A | 7 | 0.7 | A | 7 | 972 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 12800 | A | 7 | 1676 | A | 7 | 4.4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 66.74 | 5 | 0
2005-06-08 | 1900-06-07 | 11:00 | 11 | 1167 | 1326 | 272 | 2 | 8 | 30 | 2 | 15 | 246 | 2 | 8 | 30200 | 2 | 8 | 3000 | 2 | 15 | 27600 | 2 | 8 | 11960 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 31.1 | 87.98 | A | 7 | 23.9 | 75.02 | A | 7 | 0.66 | A | 7 | 971 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 66.72 | 5 | 0
2005-06-08 | 1900-06-07 | 12:00 | 12 | 1249 | 1326 | 888 | 2 | 8 | 589 | 2 | 15 | 332 | 2 | 8 | 96100 | 2 | 8 | 61700 | 2 | 15 | 37900 | 2 | 8 | 23340 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 30.6 | 87.08 | A | 7 | 22.8 | 73.04 | A | 7 | 0.63 | A | 7 | 969 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 1463 | A | 7 | 3.9 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.14 | 5 | 0
2005-06-08 | 1900-06-07 | 13:00 | 13 | 1268 | 1326 | 917 | 2 | 8 | 702 | 2 | 15 | 244 | 2 | 8 | 98000 | 2 | 8 | 71700 | 2 | 15 | 29300 | 2 | 8 | 18870 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 32.2 | 89.96 | A | 7 | 23.3 | 73.94 | A | 7 | 0.59 | A | 7 | 972 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.84 | 5 | 0
2005-06-08 | 1900-06-07 | 14:00 | 14 | 1223 | 1326 | 862 | 2 | 8 | 575 | 2 | 15 | 331 | 2 | 8 | 93100 | 2 | 8 | 60200 | 2 | 15 | 37500 | 2 | 8 | 20420 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 32.8 | 91.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.57 | A | 7 | 972 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.34 | 5 | 0
2005-06-08 | 1900-06-07 | 15:00 | 15 | 1117 | 1326 | 348 | 2 | 8 | 72 | 2 | 15 | 288 | 2 | 8 | 38600 | 2 | 8 | 7300 | 2 | 15 | 32400 | 2 | 8 | 12800 | 2 | 19 | 7 | E | 9 | 6 | E | 9 | 33.3 | 91.94 | A | 7 | 23.9 | 75.02 | A | 7 | 0.58 | A | 7 | 969 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.52 | 5 | 0
2005-06-08 | 1900-06-07 | 16:00 | 16 | 958 | 1326 | 658 | 2 | 8 | 576 | 2 | 15 | 241 | 2 | 8 | 70600 | 2 | 8 | 59900 | 2 | 15 | 27300 | 2 | 8 | 7060 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 32.8 | 91.04 | A | 7 | 23.9 | 75.02 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.12 | 5 | 0
2005-06-08 | 1900-06-07 | 17:00 | 17 | 755 | 1326 | 506 | 2 | 8 | 583 | 2 | 15 | 173 | 2 | 8 | 54200 | 2 | 8 | 59500 | 2 | 15 | 20300 | 2 | 8 | 3890 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 30.6 | 87.08 | A | 7 | 23.9 | 75.02 | A | 7 | 0.68 | A | 7 | 971 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 1524 | A | 7 | 4.1 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 67.22 | 5 | 0
2005-06-08 | 1900-06-07 | 18:00 | 18 | 524 | 1326 | 182 | 2 | 8 | 64 | 2 | 15 | 156 | 2 | 8 | 19900 | 2 | 8 | 6200 | 2 | 15 | 17500 | 2 | 8 | 4380 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 29.4 | 84.92 | A | 7 | 23.9 | 75.02 | A | 7 | 0.72 | A | 7 | 969 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 12800 | A | 7 | 4572 | A | 7 | 4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 68.22 | 5 | 0
2005-06-08 | 1900-06-07 | 19:00 | 19 | 280 | 1326 | 31 | 2 | 8 | 0 | 2 | 15 | 31 | 2 | 8 | 3700 | 2 | 8 | 0 | 2 | 15 | 3700 | 2 | 8 | 1280 | 2 | 19 | 10 | E | 9 | 8 | E | 9 | 27.8 | 82.04 | A | 7 | 24.4 | 75.92 | A | 7 | 0.82 | A | 7 | 972 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 2743 | A | 7 | 4.2 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 71.62 | 5 | 0
2005-06-08 | 1900-06-07 | 20:00 | 20 | 54 | 939 | 8 | 2 | 8 | 67 | 2 | 15 | 5 | 2 | 8 | 1000 | 2 | 8 | 3200 | 2 | 15 | 800 | 2 | 8 | 100 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 23.3 | 73.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.53 | A | 7 | 972 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 1524 | A | 7 | 4.3 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 47.24 | 5 | 0
2005-06-08 | 1900-06-07 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2134 | A | 7 | 4.5 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 56.08 | 5 | 0
2005-06-08 | 1900-06-07 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 12800 | A | 7 | 1250 | A | 7 | 4.4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 3 | 1 | A | 7 | 60.36 | 5 | 0
2005-06-08 | 1900-06-07 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 20 | 68 | A | 7 | 15.6 | 60.08 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 1981 | A | 7 | 4.4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 55.48 | 5 | 0
2005-06-08 | 1900-06-07 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 19.4 | 66.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 1829 | A | 7 | 4.4 | E | 8 | 0.147 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.28 | 5 | 0
2005-06-09 | 1900-06-08 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 7 | E | 9 | 19.4 | 66.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 4.2 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.28 | 6 | 0
2005-06-09 | 1900-06-08 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 7 | E | 9 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 973 | A | 7 | 140 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 4.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.68 | 6 | 0
2005-06-09 | 1900-06-08 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 20 | 68 | A | 7 | 15.6 | 60.08 | A | 7 | 0.76 | A | 7 | 972 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 3.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.48 | 6 | 0
2005-06-09 | 1900-06-08 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 3.5 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.08 | 6 | 0
2005-06-09 | 1900-06-08 | 5:00 | 5 | 1 | 144 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 21.1 | 69.98 | A | 7 | 15 | 59 | A | 7 | 0.68 | A | 7 | 975 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 3.2 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.9 | 6 | 0
2005-06-09 | 1900-06-08 | 6:00 | 6 | 135 | 1325 | 16 | 2 | 8 | 0 | 2 | 15 | 16 | 2 | 8 | 1900 | 2 | 8 | 0 | 2 | 15 | 1900 | 2 | 8 | 610 | 2 | 19 | 10 | E | 9 | 4 | E | 9 | 20.6 | 69.08 | A | 7 | 15 | 59 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 2.8 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.3 | 6 | 0
2005-06-09 | 1900-06-08 | 7:00 | 7 | 378 | 1325 | 55 | 2 | 8 | 0 | 2 | 15 | 55 | 2 | 8 | 6500 | 2 | 8 | 0 | 2 | 15 | 6500 | 2 | 8 | 2280 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 22.2 | 71.96 | A | 7 | 15 | 59 | A | 7 | 0.64 | A | 7 | 974 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 2.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.1 | 6 | 0
2005-06-09 | 1900-06-08 | 8:00 | 8 | 619 | 1325 | 199 | 2 | 8 | 19 | 2 | 15 | 190 | 2 | 8 | 22500 | 2 | 8 | 1600 | 2 | 15 | 21800 | 2 | 8 | 7350 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.38 | 6 | 0
2005-06-09 | 1900-06-08 | 9:00 | 9 | 840 | 1325 | 182 | 2 | 8 | 0 | 2 | 15 | 182 | 2 | 8 | 21500 | 2 | 8 | 0 | 2 | 15 | 21500 | 2 | 8 | 8410 | 2 | 19 | 9 | E | 9 | 6 | E | 9 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 973 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 3.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.38 | 6 | 0
2005-06-09 | 1900-06-08 | 10:00 | 10 | 1027 | 1325 | 385 | 2 | 8 | 73 | 2 | 15 | 329 | 2 | 8 | 42500 | 2 | 8 | 7500 | 2 | 15 | 36700 | 2 | 8 | 12830 | 2 | 19 | 7 | E | 9 | 6 | E | 9 | 25.6 | 78.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | A | 7 | 976 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 9144 | A | 7 | 3.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.66 | 6 | 0
2005-06-09 | 1900-06-08 | 11:00 | 11 | 1166 | 1325 | 848 | 2 | 8 | 645 | 2 | 15 | 279 | 2 | 8 | 88900 | 2 | 8 | 65000 | 2 | 15 | 31500 | 2 | 8 | 13210 | 2 | 19 | 9 | E | 9 | 6 | E | 9 | 26.7 | 80.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.58 | A | 7 | 976 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 9144 | A | 7 | 3.8 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.14 | 6 | 0
2005-06-09 | 1900-06-08 | 12:00 | 12 | 1249 | 1325 | 815 | 2 | 8 | 493 | 2 | 15 | 350 | 2 | 8 | 87800 | 2 | 8 | 51600 | 2 | 15 | 39100 | 2 | 8 | 24700 | 2 | 19 | 10 | E | 9 | 4 | E | 9 | 26.1 | 78.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.58 | A | 7 | 974 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 4.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.26 | 6 | 0
2005-06-09 | 1900-06-08 | 13:00 | 13 | 1268 | 1325 | 473 | 2 | 8 | 66 | 2 | 15 | 410 | 2 | 8 | 52400 | 2 | 8 | 6800 | 2 | 15 | 45900 | 2 | 8 | 24070 | 2 | 19 | 9 | E | 9 | 4 | E | 9 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 4.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.64 | 6 | 0
2005-06-09 | 1900-06-08 | 14:00 | 14 | 1224 | 1325 | 437 | 2 | 8 | 54 | 2 | 15 | 387 | 2 | 8 | 48300 | 2 | 8 | 5500 | 2 | 15 | 43200 | 2 | 8 | 20080 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 25.6 | 78.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.62 | A | 7 | 977 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 9144 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.04 | 6 | 0
2005-06-09 | 1900-06-08 | 15:00 | 15 | 1118 | 1325 | 395 | 2 | 8 | 36 | 2 | 15 | 364 | 2 | 8 | 43600 | 2 | 8 | 3700 | 2 | 15 | 40400 | 2 | 8 | 15700 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 975 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.84 | 6 | 0
2005-06-09 | 1900-06-08 | 16:00 | 16 | 959 | 1325 | 477 | 2 | 8 | 208 | 2 | 15 | 326 | 2 | 8 | 52300 | 2 | 8 | 22100 | 2 | 15 | 36300 | 2 | 8 | 10210 | 2 | 19 | 9 | E | 9 | 7 | E | 9 | 27.2 | 80.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.26 | 6 | 0
2005-06-09 | 1900-06-08 | 17:00 | 17 | 757 | 1325 | 506 | 2 | 8 | 624 | 2 | 15 | 149 | 2 | 8 | 52800 | 2 | 8 | 62100 | 2 | 15 | 17300 | 2 | 8 | 3360 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 27.8 | 82.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.49 | A | 7 | 975 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.48 | 6 | 0
2005-06-09 | 1900-06-08 | 18:00 | 18 | 525 | 1325 | 322 | 2 | 8 | 613 | 2 | 15 | 79 | 2 | 8 | 34000 | 2 | 8 | 58500 | 2 | 15 | 10800 | 2 | 8 | 1590 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 972 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.64 | 6 | 0
2005-06-09 | 1900-06-08 | 19:00 | 19 | 281 | 1325 | 138 | 2 | 8 | 408 | 2 | 15 | 52 | 2 | 8 | 14300 | 2 | 8 | 32000 | 2 | 15 | 7500 | 2 | 8 | 950 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.04 | 6 | 0
2005-06-09 | 1900-06-08 | 20:00 | 20 | 55 | 939 | 6 | 2 | 8 | 0 | 2 | 15 | 6 | 2 | 8 | 700 | 2 | 8 | 0 | 2 | 15 | 700 | 2 | 8 | 240 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.71 | A | 7 | 974 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.04 | 6 | 0
2005-06-09 | 1900-06-08 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 973 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.62 | 6 | 0
2005-06-09 | 1900-06-08 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 975 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.62 | 6 | 0
2005-06-09 | 1900-06-08 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 25 | 77 | A | 7 | 16.7 | 62.06 | A | 7 | 0.6 | A | 7 | 975 | A | 7 | 150 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.86 | 6 | 0
2005-06-09 | 1900-06-08 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 4 | E | 9 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 973 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.38 | 6 | 0
2005-06-10 | 1900-06-09 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | E | 9 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.84 | 7 | 0
2005-06-10 | 1900-06-09 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 20.6 | 69.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.75 | A | 7 | 977 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 823 | A | 7 | 3.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.08 | 7 | 0
2005-06-10 | 1900-06-09 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1097 | A | 7 | 3.6 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 60.96 | 7 | 0
2005-06-10 | 1900-06-09 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 975 | A | 7 | 3.8 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.36 | 7 | 0
2005-06-10 | 1900-06-09 | 5:00 | 5 | 1 | 144 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 914 | A | 7 | 3.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.66 | 7 | 0
2005-06-10 | 1900-06-09 | 6:00 | 6 | 136 | 1325 | 31 | 2 | 8 | 0 | 2 | 15 | 31 | 2 | 8 | 3500 | 2 | 8 | 0 | 2 | 15 | 3500 | 2 | 8 | 1050 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 975 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.36 | 7 | 0
2005-06-10 | 1900-06-09 | 7:00 | 7 | 378 | 1325 | 210 | 2 | 8 | 313 | 2 | 15 | 121 | 2 | 8 | 22100 | 2 | 8 | 27600 | 2 | 15 | 14200 | 2 | 8 | 2460 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 21.1 | 69.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.26 | 7 | 0
2005-06-10 | 1900-06-09 | 8:00 | 8 | 619 | 1325 | 213 | 2 | 8 | 50 | 2 | 15 | 189 | 2 | 8 | 23300 | 2 | 8 | 4900 | 2 | 15 | 21000 | 2 | 8 | 5570 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 21.7 | 71.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 110 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 3.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.74 | 7 | 0
2005-06-10 | 1900-06-09 | 9:00 | 9 | 840 | 1325 | 202 | 2 | 8 | 6 | 2 | 15 | 198 | 2 | 8 | 23700 | 2 | 8 | 500 | 2 | 15 | 23400 | 2 | 8 | 8980 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.62 | 7 | 0
2005-06-10 | 1900-06-09 | 10:00 | 10 | 1027 | 1325 | 581 | 2 | 8 | 279 | 2 | 15 | 365 | 2 | 8 | 62900 | 2 | 8 | 30200 | 2 | 15 | 39400 | 2 | 8 | 12290 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 25 | 77 | A | 7 | 20.6 | 69.08 | A | 7 | 0.77 | A | 7 | 975 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.98 | 7 | 0
2005-06-10 | 1900-06-09 | 11:00 | 11 | 1166 | 1325 | 606 | 2 | 8 | 253 | 2 | 15 | 383 | 2 | 8 | 66500 | 2 | 8 | 27500 | 2 | 15 | 42200 | 2 | 8 | 17470 | 2 | 19 | 10 | E | 9 | 8 | E | 9 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 4572 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.48 | 7 | 0
2005-06-10 | 1900-06-09 | 12:00 | 12 | 1249 | 1325 | 201 | 2 | 8 | 6 | 2 | 15 | 195 | 2 | 8 | 25000 | 2 | 8 | 400 | 2 | 15 | 24600 | 2 | 8 | 9980 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 25.6 | 78.08 | A | 7 | 21.7 | 71.06 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 12800 | A | 7 | 3962 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 66.36 | 7 | 0
2005-06-10 | 1900-06-09 | 13:00 | 13 | 1268 | 1325 | 480 | 2 | 8 | 102 | 2 | 15 | 382 | 2 | 8 | 53500 | 2 | 8 | 10900 | 2 | 15 | 43000 | 2 | 8 | 24430 | 2 | 19 | 3 | E | 9 | 2 | E | 9 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 974 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.98 | 7 | 0
2005-06-10 | 1900-06-09 | 14:00 | 14 | 1224 | 1325 | 590 | 2 | 8 | 209 | 2 | 15 | 396 | 2 | 8 | 65400 | 2 | 8 | 22400 | 2 | 15 | 44700 | 2 | 8 | 20900 | 2 | 19 | 9 | E | 9 | 6 | E | 9 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 975 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.52 | 7 | 0
2005-06-10 | 1900-06-09 | 15:00 | 15 | 1119 | 1325 | 174 | 2 | 8 | 6 | 2 | 15 | 169 | 2 | 8 | 21600 | 2 | 8 | 400 | 2 | 15 | 21200 | 2 | 8 | 8690 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 27.2 | 80.96 | A | 7 | 20 | 68 | A | 7 | 0.65 | A | 7 | 971 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.2 | 7 | 0
2005-06-10 | 1900-06-09 | 16:00 | 16 | 960 | 1325 | 403 | 2 | 8 | 107 | 2 | 15 | 326 | 2 | 8 | 44500 | 2 | 8 | 11000 | 2 | 15 | 36500 | 2 | 8 | 11830 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.8 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.18 | 7 | 0
2005-06-10 | 1900-06-09 | 17:00 | 17 | 758 | 1325 | 380 | 2 | 8 | 247 | 2 | 15 | 238 | 2 | 8 | 40800 | 2 | 8 | 26100 | 2 | 15 | 25800 | 2 | 8 | 5750 | 2 | 19 | 6 | E | 9 | 5 | E | 9 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.84 | 7 | 0
2005-06-10 | 1900-06-09 | 18:00 | 18 | 527 | 1325 | 213 | 2 | 8 | 116 | 2 | 15 | 167 | 2 | 8 | 23200 | 2 | 8 | 11400 | 2 | 15 | 18600 | 2 | 8 | 3910 | 2 | 19 | 10 | E | 9 | 7 | A | 7 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.64 | A | 7 | 972 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.6 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.02 | 7 | 0
2005-06-10 | 1900-06-09 | 19:00 | 19 | 283 | 1325 | 139 | 2 | 8 | 327 | 2 | 15 | 69 | 2 | 8 | 14500 | 2 | 8 | 25200 | 2 | 15 | 9100 | 2 | 8 | 1260 | 2 | 19 | 9 | E | 9 | 6 | E | 9 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 975 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.62 | 7 | 0
2005-06-10 | 1900-06-09 | 20:00 | 20 | 57 | 961 | 6 | 2 | 8 | 0 | 2 | 15 | 6 | 2 | 8 | 700 | 2 | 8 | 0 | 2 | 15 | 700 | 2 | 8 | 240 | 2 | 19 | 6 | E | 9 | 4 | E | 9 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 975 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.8 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.32 | 7 | 0
2005-06-10 | 1900-06-09 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 23.9 | 75.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 66.48 | 7 | 0
2005-06-10 | 1900-06-09 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 6 | E | 9 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.85 | A | 7 | 975 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 4.2 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.78 | 7 | 0
2005-06-10 | 1900-06-09 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 20 | 68 | A | 7 | 18.3 | 64.94 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 14400 | A | 7 | 1250 | A | 7 | 4.3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 62.94 | 7 | 0
2005-06-10 | 1900-06-09 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 6 | E | 9 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 972 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 4.5 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.96 | 7 | 0
2005-06-11 | 1900-06-10 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | E | 9 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 4.5 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.54 | 1 | 0
2005-06-11 | 1900-06-10 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | E | 9 | 20 | 68 | A | 7 | 17.8 | 64.04 | A | 7 | 0.87 | A | 7 | 972 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 4.5 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.44 | 1 | 0
2005-06-11 | 1900-06-10 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 970 | A | 7 | 110 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 2286 | A | 7 | 4.5 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.92 | 1 | 0
2005-06-11 | 1900-06-10 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 973 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 4.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 60.36 | 1 | 0
2005-06-11 | 1900-06-10 | 5:00 | 5 | 1 | 144 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 14400 | A | 7 | 2286 | A | 7 | 3.8 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.46 | 1 | 0
2005-06-11 | 1900-06-10 | 6:00 | 6 | 136 | 1325 | 15 | 2 | 8 | 0 | 2 | 15 | 15 | 2 | 8 | 1800 | 2 | 8 | 0 | 2 | 15 | 1800 | 2 | 8 | 580 | 2 | 19 | 10 | E | 9 | 5 | E | 9 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 970 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 3962 | A | 7 | 3.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.48 | 1 | 0
2005-06-11 | 1900-06-10 | 7:00 | 7 | 378 | 1325 | 78 | 2 | 8 | 0 | 2 | 15 | 78 | 2 | 8 | 8900 | 2 | 8 | 0 | 2 | 15 | 8900 | 2 | 8 | 3030 | 2 | 19 | 8 | E | 9 | 7 | E | 9 | 19.4 | 66.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.81 | A | 7 | 973 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.28 | 1 | 0
2005-06-11 | 1900-06-10 | 8:00 | 8 | 618 | 1325 | 185 | 2 | 8 | 12 | 2 | 15 | 179 | 2 | 8 | 21000 | 2 | 8 | 1000 | 2 | 15 | 20500 | 2 | 8 | 7070 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 974 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 2743 | A | 7 | 4.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.68 | 1 | 0
2005-06-11 | 1900-06-10 | 9:00 | 9 | 840 | 1325 | 143 | 2 | 8 | 0 | 2 | 15 | 143 | 2 | 8 | 17200 | 2 | 8 | 0 | 2 | 15 | 17200 | 2 | 8 | 6900 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 973 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 762 | A | 7 | 4.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 60.96 | 1 | 0
2005-06-11 | 1900-06-10 | 10:00 | 10 | 1027 | 1325 | 120 | 2 | 8 | 0 | 2 | 15 | 120 | 2 | 8 | 15100 | 2 | 8 | 0 | 2 | 15 | 15100 | 2 | 8 | 6320 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 4000 | A | 7 | 671 | A | 7 | 4.2 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 4 | 1 | A | 7 | 61.56 | 1 | 0
2005-06-11 | 1900-06-10 | 11:00 | 11 | 1166 | 1325 | 142 | 2 | 8 | 0 | 2 | 15 | 142 | 2 | 8 | 17900 | 2 | 8 | 0 | 2 | 15 | 17900 | 2 | 8 | 7480 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 3.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 62.04 | 1 | 0
2005-06-11 | 1900-06-10 | 12:00 | 12 | 1249 | 1325 | 481 | 2 | 8 | 108 | 2 | 15 | 379 | 2 | 8 | 53600 | 2 | 8 | 11600 | 2 | 15 | 42700 | 2 | 8 | 22070 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 972 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.22 | 1 | 0
2005-06-11 | 1900-06-10 | 13:00 | 13 | 1269 | 1325 | 869 | 2 | 8 | 546 | 2 | 15 | 345 | 2 | 8 | 94000 | 2 | 8 | 57200 | 2 | 15 | 39100 | 2 | 8 | 27610 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25 | 77 | A | 7 | 18.3 | 64.94 | A | 7 | 0.66 | A | 7 | 974 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.74 | 1 | 0
2005-06-11 | 1900-06-10 | 14:00 | 14 | 1225 | 1325 | 921 | 2 | 8 | 796 | 2 | 15 | 184 | 2 | 8 | 96900 | 2 | 8 | 80100 | 2 | 15 | 22600 | 2 | 8 | 10470 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.24 | 1 | 0
2005-06-11 | 1900-06-10 | 15:00 | 15 | 1120 | 1325 | 778 | 2 | 8 | 633 | 2 | 15 | 242 | 2 | 8 | 82000 | 2 | 8 | 64200 | 2 | 15 | 27700 | 2 | 8 | 9970 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 972 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.6 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.84 | 1 | 0
2005-06-11 | 1900-06-10 | 16:00 | 16 | 961 | 1325 | 659 | 2 | 8 | 677 | 2 | 15 | 167 | 2 | 8 | 70100 | 2 | 8 | 69000 | 2 | 15 | 19900 | 2 | 8 | 4950 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 26.7 | 80.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.82 | 1 | 0
2005-06-11 | 1900-06-10 | 17:00 | 17 | 759 | 1325 | 506 | 2 | 8 | 701 | 2 | 15 | 104 | 2 | 8 | 52900 | 2 | 8 | 69500 | 2 | 15 | 13000 | 2 | 8 | 2310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 974 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.84 | 1 | 0
2005-06-11 | 1900-06-10 | 18:00 | 18 | 528 | 1325 | 317 | 2 | 8 | 567 | 2 | 15 | 91 | 2 | 8 | 33100 | 2 | 8 | 53800 | 2 | 15 | 11700 | 2 | 8 | 1800 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 972 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.52 | 1 | 0
2005-06-11 | 1900-06-10 | 19:00 | 19 | 285 | 1325 | 139 | 2 | 8 | 398 | 2 | 15 | 54 | 2 | 8 | 14300 | 2 | 8 | 31300 | 2 | 15 | 7600 | 2 | 8 | 980 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 974 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.3 | 1 | 0
2005-06-11 | 1900-06-10 | 20:00 | 20 | 58 | 960 | 7 | 2 | 8 | 0 | 2 | 15 | 7 | 2 | 8 | 900 | 2 | 8 | 0 | 2 | 15 | 900 | 2 | 8 | 270 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.52 | 1 | 0
2005-06-11 | 1900-06-10 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 3.3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.52 | 1 | 0
2005-06-11 | 1900-06-10 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 3.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.52 | 1 | 0
2005-06-11 | 1900-06-10 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.32 | 1 | 0
2005-06-11 | 1900-06-10 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 21.7 | 71.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.87 | A | 7 | 973 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 2286 | A | 7 | 3.5 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.22 | 1 | 0
2005-06-12 | 1900-06-11 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.32 | 2 | 0
2005-06-12 | 1900-06-11 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 21.7 | 71.06 | A | 7 | 20 | 68 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 1676 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.9 | 2 | 0
2005-06-12 | 1900-06-11 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 22.2 | 71.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.91 | A | 7 | 972 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 12800 | A | 7 | 1372 | A | 7 | 3.8 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 67.08 | 2 | 0
2005-06-12 | 1900-06-11 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 22.2 | 71.96 | A | 7 | 20 | 68 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.2 | 2 | 0
2005-06-12 | 1900-06-11 | 5:00 | 5 | 1 | 143 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 22.2 | 71.96 | A | 7 | 20 | 68 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 3.7 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.2 | 2 | 0
2005-06-12 | 1900-06-11 | 6:00 | 6 | 136 | 1325 | 46 | 2 | 8 | 0 | 2 | 15 | 46 | 2 | 8 | 5000 | 2 | 8 | 0 | 2 | 15 | 5000 | 2 | 8 | 1350 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 21.7 | 71.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 3.6 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.04 | 2 | 0
2005-06-12 | 1900-06-11 | 7:00 | 7 | 378 | 1325 | 195 | 2 | 8 | 313 | 2 | 15 | 105 | 2 | 8 | 20600 | 2 | 8 | 27700 | 2 | 15 | 12700 | 2 | 8 | 2070 | 2 | 19 | 7 | E | 9 | 6 | E | 9 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.81 | A | 7 | 976 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.92 | 2 | 0
2005-06-12 | 1900-06-11 | 8:00 | 8 | 618 | 1325 | 384 | 2 | 8 | 354 | 2 | 15 | 219 | 2 | 8 | 40600 | 2 | 8 | 36100 | 2 | 15 | 23700 | 2 | 8 | 4980 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.81 | A | 7 | 977 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 975 | A | 7 | 4.2 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.92 | 2 | 0
2005-06-12 | 1900-06-11 | 9:00 | 9 | 840 | 1325 | 91 | 2 | 8 | 0 | 2 | 15 | 91 | 2 | 8 | 11300 | 2 | 8 | 0 | 2 | 15 | 11300 | 2 | 8 | 4640 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 762 | A | 7 | 4.5 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 62.72 | 2 | 0
2005-06-12 | 1900-06-11 | 10:00 | 10 | 1027 | 1325 | 505 | 2 | 8 | 194 | 2 | 15 | 355 | 2 | 8 | 55500 | 2 | 8 | 20600 | 2 | 15 | 39500 | 2 | 8 | 12120 | 2 | 19 | 8 | E | 9 | 7 | E | 9 | 23.9 | 75.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.82 | A | 7 | 974 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 4.3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 65.18 | 2 | 0
2005-06-12 | 1900-06-11 | 11:00 | 11 | 1166 | 1325 | 866 | 2 | 8 | 748 | 2 | 15 | 207 | 2 | 8 | 92800 | 2 | 8 | 76600 | 2 | 15 | 25200 | 2 | 8 | 10050 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.2 | 2 | 0
2005-06-12 | 1900-06-11 | 12:00 | 12 | 1249 | 1325 | 943 | 2 | 8 | 848 | 2 | 15 | 142 | 2 | 8 | 96600 | 2 | 8 | 85000 | 2 | 15 | 16300 | 2 | 8 | 7720 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 973 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.7 | 2 | 0
2005-06-12 | 1900-06-11 | 13:00 | 13 | 1269 | 1325 | 965 | 2 | 8 | 870 | 2 | 15 | 130 | 2 | 8 | 99100 | 2 | 8 | 87300 | 2 | 15 | 15300 | 2 | 8 | 8270 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 28.3 | 82.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.63 | A | 7 | 974 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.68 | 2 | 0
2005-06-12 | 1900-06-11 | 14:00 | 14 | 1225 | 1325 | 903 | 2 | 8 | 700 | 2 | 15 | 254 | 2 | 8 | 95900 | 2 | 8 | 71200 | 2 | 15 | 29900 | 2 | 8 | 15500 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 974 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.98 | 2 | 0
2005-06-12 | 1900-06-11 | 15:00 | 15 | 1120 | 1325 | 447 | 2 | 8 | 90 | 2 | 15 | 371 | 2 | 8 | 49400 | 2 | 8 | 9200 | 2 | 15 | 41500 | 2 | 8 | 16020 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 971 | A | 7 | 210 | A | 7 | 1.5 | A | 7 | 12800 | A | 7 | 1158 | A | 7 | 4.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 6 | 1 | A | 7 | 64.66 | 2 | 0
2005-06-12 | 1900-06-11 | 16:00 | 16 | 962 | 1325 | 148 | 2 | 8 | 0 | 2 | 15 | 148 | 2 | 8 | 18100 | 2 | 8 | 0 | 2 | 15 | 18100 | 2 | 8 | 7470 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21 | 69.8 | A | 7 | 19 | 66.2 | A | 7 | 0.88 | A | 7 | 973 | A | 7 | 260 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 1500 | A | 7 | 4.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 6 | 1 | A | 7 | 63.7 | 2 | 0
2005-06-12 | 1900-06-11 | 17:00 | 17 | 760 | 1325 | 83 | 2 | 8 | 0 | 2 | 15 | 83 | 2 | 8 | 10300 | 2 | 8 | 0 | 2 | 15 | 10300 | 2 | 8 | 4130 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 20 | 68 | A | 7 | 19.4 | 66.92 | A | 7 | 0.96 | A | 7 | 974 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 914 | A | 7 | 4.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 16 | 1 | A | 7 | 66.02 | 2 | 0
2005-06-12 | 1900-06-11 | 18:00 | 18 | 530 | 1325 | 78 | 2 | 8 | 0 | 2 | 15 | 78 | 2 | 8 | 9300 | 2 | 8 | 0 | 2 | 15 | 9300 | 2 | 8 | 3450 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 20 | 68 | A | 7 | 19.4 | 66.92 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 12800 | A | 7 | 3048 | A | 7 | 4.4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 66.02 | 2 | 0
2005-06-12 | 1900-06-11 | 19:00 | 19 | 286 | 1325 | 22 | 2 | 8 | 0 | 2 | 15 | 22 | 2 | 8 | 2700 | 2 | 8 | 0 | 2 | 15 | 2700 | 2 | 8 | 940 | 2 | 19 | 10 | E | 9 | 8 | E | 9 | 20.6 | 69.08 | A | 7 | 20.6 | 69.08 | A | 7 | 1 | A | 7 | 973 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 4.3 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 68.98 | 2 | 0
2005-06-12 | 1900-06-11 | 20:00 | 20 | 59 | 982 | 7 | 2 | 8 | 0 | 2 | 15 | 7 | 2 | 8 | 900 | 2 | 8 | 0 | 2 | 15 | 900 | 2 | 8 | 270 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 20 | 68 | A | 7 | 19.4 | 66.92 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 4572 | A | 7 | 4.2 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 66.02 | 2 | 0
2005-06-12 | 1900-06-11 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 6 | E | 9 | 20 | 68 | A | 7 | 19.4 | 66.92 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 4572 | A | 7 | 4.1 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 66.02 | 2 | 0
2005-06-12 | 1900-06-11 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 8 | E | 9 | 20 | 68 | A | 7 | 18.9 | 66.02 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 12800 | A | 7 | 1524 | A | 7 | 4 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 64.52 | 2 | 0
2005-06-12 | 1900-06-11 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 7 | E | 9 | 19.4 | 66.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.97 | A | 7 | 973 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.42 | 2 | 0
2005-06-12 | 1900-06-11 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 4 | E | 9 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 971 | A | 7 | 140 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.148 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.36 | 2 | 0
2005-06-13 | 1900-06-12 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 4 | E | 9 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 971 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.46 | 3 | 0
2005-06-13 | 1900-06-12 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | E | 9 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 972 | A | 7 | 260 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.06 | 3 | 0
2005-06-13 | 1900-06-12 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 7 | E | 9 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 971 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.48 | 3 | 0
2005-06-13 | 1900-06-12 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 971 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 3.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.48 | 3 | 0
2005-06-13 | 1900-06-12 | 5:00 | 5 | 1 | 143 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 971 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.98 | 3 | 0
2005-06-13 | 1900-06-12 | 6:00 | 6 | 136 | 1324 | 46 | 2 | 8 | 0 | 2 | 15 | 46 | 2 | 8 | 5000 | 2 | 8 | 0 | 2 | 15 | 5000 | 2 | 8 | 1350 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.48 | 3 | 0
2005-06-13 | 1900-06-12 | 7:00 | 7 | 377 | 1324 | 202 | 2 | 8 | 235 | 2 | 15 | 135 | 2 | 8 | 21000 | 2 | 8 | 20700 | 2 | 15 | 15100 | 2 | 8 | 2820 | 2 | 19 | 5 | E | 9 | 4 | E | 9 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.78 | A | 7 | 972 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.66 | 3 | 0
2005-06-13 | 1900-06-12 | 8:00 | 8 | 618 | 1324 | 69 | 2 | 8 | 0 | 2 | 15 | 69 | 2 | 8 | 8400 | 2 | 8 | 0 | 2 | 15 | 8400 | 2 | 8 | 3260 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 972 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.36 | 3 | 0
2005-06-13 | 1900-06-12 | 9:00 | 9 | 839 | 1324 | 273 | 2 | 8 | 49 | 2 | 15 | 242 | 2 | 8 | 30100 | 2 | 8 | 5000 | 2 | 15 | 26900 | 2 | 8 | 8270 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 20.6 | 69.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.81 | A | 7 | 971 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.16 | 3 | 0
2005-06-13 | 1900-06-12 | 10:00 | 10 | 1026 | 1324 | 714 | 2 | 8 | 569 | 2 | 15 | 272 | 2 | 8 | 76500 | 2 | 8 | 59300 | 2 | 15 | 30400 | 2 | 8 | 9130 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.73 | A | 7 | 973 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.44 | 3 | 0
2005-06-13 | 1900-06-12 | 11:00 | 11 | 1166 | 1324 | 836 | 2 | 8 | 718 | 2 | 15 | 202 | 2 | 8 | 89600 | 2 | 8 | 73600 | 2 | 15 | 24700 | 2 | 8 | 9830 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 973 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.54 | 3 | 0
2005-06-13 | 1900-06-12 | 12:00 | 12 | 1249 | 1324 | 889 | 2 | 8 | 661 | 2 | 15 | 264 | 2 | 8 | 94300 | 2 | 8 | 67200 | 2 | 15 | 30800 | 2 | 8 | 18220 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 970 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 762 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.82 | 3 | 0
2005-06-13 | 1900-06-12 | 13:00 | 13 | 1269 | 1324 | 881 | 2 | 8 | 618 | 2 | 15 | 288 | 2 | 8 | 93200 | 2 | 8 | 62600 | 2 | 15 | 33100 | 2 | 8 | 22460 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 25 | 77 | A | 7 | 17.8 | 64.04 | A | 7 | 0.64 | A | 7 | 972 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.54 | 3 | 0
2005-06-13 | 1900-06-12 | 14:00 | 14 | 1225 | 1324 | 927 | 2 | 8 | 814 | 2 | 15 | 172 | 2 | 8 | 98200 | 2 | 8 | 82200 | 2 | 15 | 21900 | 2 | 8 | 9970 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 971 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.24 | 3 | 0
2005-06-13 | 1900-06-12 | 15:00 | 15 | 1121 | 1324 | 824 | 2 | 8 | 794 | 2 | 15 | 151 | 2 | 8 | 87400 | 2 | 8 | 80200 | 2 | 15 | 19300 | 2 | 8 | 5970 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 969 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.52 | 3 | 0
2005-06-13 | 1900-06-12 | 16:00 | 16 | 963 | 1324 | 682 | 2 | 8 | 743 | 2 | 15 | 141 | 2 | 8 | 71300 | 2 | 8 | 74500 | 2 | 15 | 17000 | 2 | 8 | 3850 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 26.7 | 80.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.34 | 3 | 0
2005-06-13 | 1900-06-12 | 17:00 | 17 | 762 | 1324 | 490 | 2 | 8 | 636 | 2 | 15 | 123 | 2 | 8 | 51900 | 2 | 8 | 64000 | 2 | 15 | 15000 | 2 | 8 | 2870 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 26.7 | 80.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.58 | A | 7 | 971 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.14 | 3 | 0
2005-06-13 | 1900-06-12 | 18:00 | 18 | 531 | 1324 | 323 | 2 | 8 | 556 | 2 | 15 | 99 | 2 | 8 | 33500 | 2 | 8 | 52600 | 2 | 15 | 12300 | 2 | 8 | 1940 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 967 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.64 | 3 | 0
2005-06-13 | 1900-06-12 | 19:00 | 19 | 288 | 1324 | 144 | 2 | 8 | 393 | 2 | 15 | 59 | 2 | 8 | 14700 | 2 | 8 | 30900 | 2 | 15 | 8000 | 2 | 8 | 1050 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 25 | 77 | A | 7 | 18.3 | 64.94 | A | 7 | 0.66 | A | 7 | 969 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.74 | 3 | 0
2005-06-13 | 1900-06-12 | 20:00 | 20 | 60 | 982 | 2 | 2 | 8 | 0 | 2 | 15 | 2 | 2 | 8 | 300 | 2 | 8 | 0 | 2 | 15 | 300 | 2 | 8 | 80 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 23.9 | 75.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.5 | A | 7 | 970 | A | 7 | 250 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45.84 | 3 | 0
2005-06-13 | 1900-06-12 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 21.7 | 71.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.59 | A | 7 | 970 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.44 | 3 | 0
2005-06-13 | 1900-06-12 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.63 | A | 7 | 972 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.12 | 3 | 0
2005-06-13 | 1900-06-12 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 972 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1676 | A | 7 | 2.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.92 | 3 | 0
2005-06-13 | 1900-06-12 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.32 | 3 | 0
2005-06-14 | 1900-06-13 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 19.4 | 66.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.73 | A | 7 | 973 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.92 | 4 | 0
2005-06-14 | 1900-06-13 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 973 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.04 | 4 | 0
2005-06-14 | 1900-06-13 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 972 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.44 | 4 | 0
2005-06-14 | 1900-06-13 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.75 | A | 7 | 974 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.64 | 4 | 0
2005-06-14 | 1900-06-13 | 5:00 | 5 | 1 | 143 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.14 | 4 | 0
2005-06-14 | 1900-06-13 | 6:00 | 6 | 136 | 1324 | 62 | 2 | 8 | 123 | 2 | 15 | 49 | 2 | 8 | 6300 | 2 | 8 | 5900 | 2 | 15 | 5700 | 2 | 8 | 970 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.75 | A | 7 | 974 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.64 | 4 | 0
2005-06-14 | 1900-06-13 | 7:00 | 7 | 377 | 1324 | 218 | 2 | 8 | 450 | 2 | 15 | 90 | 2 | 8 | 22900 | 2 | 8 | 39100 | 2 | 15 | 11800 | 2 | 8 | 1670 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 976 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.04 | 4 | 0
2005-06-14 | 1900-06-13 | 8:00 | 8 | 618 | 1324 | 398 | 2 | 8 | 633 | 2 | 15 | 102 | 2 | 8 | 41800 | 2 | 8 | 61900 | 2 | 15 | 12900 | 2 | 8 | 2130 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 19.4 | 66.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 270 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.52 | 4 | 0
2005-06-14 | 1900-06-13 | 9:00 | 9 | 839 | 1324 | 579 | 2 | 8 | 726 | 2 | 15 | 119 | 2 | 8 | 60500 | 2 | 8 | 72400 | 2 | 15 | 14600 | 2 | 8 | 2790 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.63 | A | 7 | 976 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.12 | 4 | 0
2005-06-14 | 1900-06-13 | 10:00 | 10 | 1026 | 1324 | 739 | 2 | 8 | 775 | 2 | 15 | 138 | 2 | 8 | 78200 | 2 | 8 | 78200 | 2 | 15 | 17500 | 2 | 8 | 4340 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 22.8 | 73.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.92 | 4 | 0
2005-06-14 | 1900-06-13 | 11:00 | 11 | 1166 | 1324 | 854 | 2 | 8 | 784 | 2 | 15 | 163 | 2 | 8 | 90400 | 2 | 8 | 79200 | 2 | 15 | 20500 | 2 | 8 | 7390 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 23.9 | 75.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 260 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.32 | 4 | 0
2005-06-14 | 1900-06-13 | 12:00 | 12 | 1248 | 1324 | 937 | 2 | 8 | 830 | 2 | 15 | 153 | 2 | 8 | 95700 | 2 | 8 | 83100 | 2 | 15 | 17200 | 2 | 8 | 8120 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 24.4 | 75.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.12 | 4 | 0
2005-06-14 | 1900-06-13 | 13:00 | 13 | 1269 | 1324 | 965 | 2 | 8 | 798 | 2 | 15 | 199 | 2 | 8 | 101200 | 2 | 8 | 80200 | 2 | 15 | 24200 | 2 | 8 | 14650 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 26.1 | 78.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.48 | A | 7 | 978 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.82 | 4 | 0
2005-06-14 | 1900-06-13 | 14:00 | 14 | 1226 | 1324 | 661 | 2 | 8 | 287 | 2 | 15 | 395 | 2 | 8 | 72800 | 2 | 8 | 31200 | 2 | 15 | 43900 | 2 | 8 | 22280 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 26.7 | 80.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.45 | A | 7 | 978 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.42 | 4 | 0
2005-06-14 | 1900-06-13 | 15:00 | 15 | 1121 | 1324 | 598 | 2 | 8 | 221 | 2 | 15 | 410 | 2 | 8 | 65600 | 2 | 8 | 23500 | 2 | 15 | 45600 | 2 | 8 | 16470 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 26.7 | 80.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.47 | A | 7 | 976 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.62 | 4 | 0
2005-06-14 | 1900-06-13 | 16:00 | 16 | 964 | 1324 | 511 | 2 | 8 | 208 | 2 | 15 | 360 | 2 | 8 | 55800 | 2 | 8 | 22000 | 2 | 15 | 39700 | 2 | 8 | 11350 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 27.2 | 80.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.44 | A | 7 | 978 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.22 | 4 | 0
2005-06-14 | 1900-06-13 | 17:00 | 17 | 763 | 1324 | 391 | 2 | 8 | 218 | 2 | 15 | 265 | 2 | 8 | 42500 | 2 | 8 | 22700 | 2 | 15 | 29400 | 2 | 8 | 7010 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 27.2 | 80.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.42 | A | 7 | 978 | A | 7 | 280 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.94 | 4 | 0
2005-06-14 | 1900-06-13 | 18:00 | 18 | 533 | 1324 | 260 | 2 | 8 | 174 | 2 | 15 | 190 | 2 | 8 | 28100 | 2 | 8 | 17100 | 2 | 15 | 21200 | 2 | 8 | 4460 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.45 | A | 7 | 976 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.42 | 4 | 0
2005-06-14 | 1900-06-13 | 19:00 | 19 | 289 | 1324 | 117 | 2 | 8 | 115 | 2 | 15 | 92 | 2 | 8 | 12700 | 2 | 8 | 9300 | 2 | 15 | 10600 | 2 | 8 | 1990 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25 | 77 | A | 7 | 14.4 | 57.92 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.62 | 4 | 0
2005-06-14 | 1900-06-13 | 20:00 | 20 | 61 | 1004 | 9 | 2 | 8 | 19 | 2 | 15 | 8 | 2 | 8 | 1100 | 2 | 8 | 700 | 2 | 15 | 1000 | 2 | 8 | 130 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 22.8 | 73.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.12 | 4 | 0
2005-06-14 | 1900-06-13 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.52 | 4 | 0
2005-06-14 | 1900-06-13 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 21.1 | 69.98 | A | 7 | 15 | 59 | A | 7 | 0.68 | A | 7 | 979 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.9 | 4 | 0
2005-06-14 | 1900-06-13 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.9 | 4 | 0
2005-06-14 | 1900-06-13 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 19.4 | 66.92 | A | 7 | 15 | 59 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.5 | 4 | 0
2005-06-15 | 1900-06-14 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 18.3 | 64.94 | A | 7 | 15 | 59 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2134 | A | 7 | 1.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.4 | 5 | 0
2005-06-15 | 1900-06-14 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.8 | A | 7 | 979 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.22 | 5 | 0
2005-06-15 | 1900-06-14 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.02 | 5 | 0
2005-06-15 | 1900-06-14 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.04 | 5 | 0
2005-06-15 | 1900-06-14 | 5:00 | 5 | 1 | 143 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.14 | 5 | 0
2005-06-15 | 1900-06-14 | 6:00 | 6 | 135 | 1324 | 62 | 2 | 8 | 114 | 2 | 15 | 50 | 2 | 8 | 6300 | 2 | 8 | 5500 | 2 | 15 | 5800 | 2 | 8 | 990 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 978 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.44 | 5 | 0
2005-06-15 | 1900-06-14 | 7:00 | 7 | 377 | 1324 | 226 | 2 | 8 | 463 | 2 | 15 | 94 | 2 | 8 | 23600 | 2 | 8 | 40100 | 2 | 15 | 12200 | 2 | 8 | 1750 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 13.9 | 57.02 | A | 7 | 0.68 | A | 7 | 980 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.12 | 5 | 0
2005-06-15 | 1900-06-14 | 8:00 | 8 | 617 | 1324 | 398 | 2 | 8 | 602 | 2 | 15 | 117 | 2 | 8 | 41400 | 2 | 8 | 58500 | 2 | 15 | 14100 | 2 | 8 | 2390 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22 | 71.6 | A | 7 | 14 | 57.2 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.7 | 5 | 0
2005-06-15 | 1900-06-14 | 9:00 | 9 | 838 | 1324 | 573 | 2 | 8 | 702 | 2 | 15 | 128 | 2 | 8 | 61200 | 2 | 8 | 71400 | 2 | 15 | 15900 | 2 | 8 | 3250 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.52 | A | 7 | 979 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.24 | 5 | 0
2005-06-15 | 1900-06-14 | 10:00 | 10 | 1025 | 1324 | 752 | 2 | 8 | 799 | 2 | 15 | 132 | 2 | 8 | 79900 | 2 | 8 | 80700 | 2 | 15 | 17200 | 2 | 8 | 4200 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 12.8 | 55.04 | A | 7 | 0.47 | A | 7 | 981 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45.24 | 5 | 0
2005-06-15 | 1900-06-14 | 11:00 | 11 | 1165 | 1324 | 860 | 2 | 8 | 802 | 2 | 15 | 153 | 2 | 8 | 91600 | 2 | 8 | 81200 | 2 | 15 | 20000 | 2 | 8 | 7020 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.48 | A | 7 | 981 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.12 | 5 | 0
2005-06-15 | 1900-06-14 | 12:00 | 12 | 1248 | 1324 | 943 | 2 | 8 | 854 | 2 | 15 | 137 | 2 | 8 | 96800 | 2 | 8 | 85600 | 2 | 15 | 15900 | 2 | 8 | 7550 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.44 | A | 7 | 979 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.64 | 5 | 0
2005-06-15 | 1900-06-14 | 13:00 | 13 | 1269 | 1324 | 959 | 2 | 8 | 846 | 2 | 15 | 147 | 2 | 8 | 98100 | 2 | 8 | 84800 | 2 | 15 | 16700 | 2 | 8 | 9110 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.35 | A | 7 | 981 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 40.48 | 5 | 0
2005-06-15 | 1900-06-14 | 14:00 | 14 | 1226 | 1324 | 921 | 2 | 8 | 838 | 2 | 15 | 144 | 2 | 8 | 94300 | 2 | 8 | 83900 | 2 | 15 | 16400 | 2 | 8 | 6870 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.37 | A | 7 | 980 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 42.36 | 5 | 0
2005-06-15 | 1900-06-14 | 15:00 | 15 | 1122 | 1324 | 824 | 2 | 8 | 806 | 2 | 15 | 140 | 2 | 8 | 88100 | 2 | 8 | 81700 | 2 | 15 | 18700 | 2 | 8 | 5660 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.9 | 84.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.38 | A | 7 | 978 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.14 | 5 | 0
2005-06-15 | 1900-06-14 | 16:00 | 16 | 964 | 1324 | 682 | 2 | 8 | 743 | 2 | 15 | 140 | 2 | 8 | 71300 | 2 | 8 | 74500 | 2 | 15 | 17000 | 2 | 8 | 3850 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.9 | 84.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.38 | A | 7 | 980 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.14 | 5 | 0
2005-06-15 | 1900-06-14 | 17:00 | 17 | 764 | 1324 | 507 | 2 | 8 | 695 | 2 | 15 | 105 | 2 | 8 | 54300 | 2 | 8 | 70400 | 2 | 15 | 13700 | 2 | 8 | 2500 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.41 | A | 7 | 979 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45.62 | 5 | 0
2005-06-15 | 1900-06-14 | 18:00 | 18 | 534 | 1324 | 323 | 2 | 8 | 579 | 2 | 15 | 89 | 2 | 8 | 33800 | 2 | 8 | 55200 | 2 | 15 | 11500 | 2 | 8 | 1780 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 27.8 | 82.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.41 | A | 7 | 977 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.74 | 5 | 0
2005-06-15 | 1900-06-14 | 19:00 | 19 | 291 | 1324 | 145 | 2 | 8 | 377 | 2 | 15 | 62 | 2 | 8 | 15300 | 2 | 8 | 29500 | 2 | 15 | 8800 | 2 | 8 | 1120 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.51 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.18 | 5 | 0
2005-06-15 | 1900-06-14 | 20:00 | 20 | 62 | 1004 | 9 | 2 | 8 | 19 | 2 | 15 | 8 | 2 | 8 | 1100 | 2 | 8 | 700 | 2 | 15 | 1000 | 2 | 8 | 130 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.48 | A | 7 | 978 | B | 8 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.12 | 5 | 0
2005-06-15 | 1900-06-14 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 23.3 | 73.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.72 | 5 | 0
2005-06-15 | 1900-06-14 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | E | 9 | 23.9 | 75.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.54 | A | 7 | 977 | B | 8 | 80 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.32 | 5 | 0
2005-06-15 | 1900-06-14 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 21.7 | 71.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.63 | A | 7 | 977 | B | 8 | 130 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.7 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.92 | 5 | 0
2005-06-15 | 1900-06-14 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 22.2 | 71.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 170 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.8 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.04 | 5 | 0
2005-06-16 | 1900-06-15 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 21.1 | 69.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.9 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.48 | 6 | 0
2005-06-16 | 1900-06-15 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 4 | E | 9 | 21.1 | 69.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.66 | A | 7 | 978 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.52 | 6 | 0
2005-06-16 | 1900-06-15 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 20.6 | 69.08 | A | 7 | 15 | 59 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.3 | 6 | 0
2005-06-16 | 1900-06-15 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 6 | E | 9 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3.1 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.9 | 6 | 0
2005-06-16 | 1900-06-15 | 5:00 | 5 | 1 | 143 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 5486 | A | 7 | 3.1 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.9 | 6 | 0
2005-06-16 | 1900-06-15 | 6:00 | 6 | 135 | 1324 | 31 | 2 | 8 | 0 | 2 | 15 | 31 | 2 | 8 | 3500 | 2 | 8 | 0 | 2 | 15 | 3500 | 2 | 8 | 1050 | 2 | 19 | 8 | E | 9 | 7 | E | 9 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.9 | 6 | 0
2005-06-16 | 1900-06-15 | 7:00 | 7 | 376 | 1324 | 210 | 2 | 8 | 404 | 2 | 15 | 95 | 2 | 8 | 21900 | 2 | 8 | 35000 | 2 | 15 | 11900 | 2 | 8 | 1770 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 15.6 | 60.08 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 100 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.48 | 6 | 0
2005-06-16 | 1900-06-15 | 8:00 | 8 | 617 | 1324 | 391 | 2 | 8 | 602 | 2 | 15 | 110 | 2 | 8 | 40900 | 2 | 8 | 58700 | 2 | 15 | 13500 | 2 | 8 | 2270 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 21.7 | 71.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 100 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.08 | 6 | 0
2005-06-16 | 1900-06-15 | 9:00 | 9 | 838 | 1324 | 560 | 2 | 8 | 677 | 2 | 15 | 130 | 2 | 8 | 59600 | 2 | 8 | 68800 | 2 | 15 | 16000 | 2 | 8 | 3290 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.68 | A | 7 | 979 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.66 | 6 | 0
2005-06-16 | 1900-06-15 | 10:00 | 10 | 1025 | 1324 | 720 | 2 | 8 | 690 | 2 | 15 | 185 | 2 | 8 | 76600 | 2 | 8 | 70400 | 2 | 15 | 22000 | 2 | 8 | 6170 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 24.4 | 75.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.62 | A | 7 | 981 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.36 | 6 | 0
2005-06-16 | 1900-06-15 | 11:00 | 11 | 1165 | 1324 | 867 | 2 | 8 | 808 | 2 | 15 | 154 | 2 | 8 | 92200 | 2 | 8 | 81800 | 2 | 15 | 20100 | 2 | 8 | 7050 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 25 | 77 | A | 7 | 17.2 | 62.96 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.06 | 6 | 0
2005-06-16 | 1900-06-15 | 12:00 | 12 | 1248 | 1324 | 943 | 2 | 8 | 854 | 2 | 15 | 137 | 2 | 8 | 96800 | 2 | 8 | 85600 | 2 | 15 | 15900 | 2 | 8 | 7560 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.58 | A | 7 | 977 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.14 | 6 | 0
2005-06-16 | 1900-06-15 | 13:00 | 13 | 1269 | 1324 | 965 | 2 | 8 | 864 | 2 | 15 | 135 | 2 | 8 | 99000 | 2 | 8 | 86600 | 2 | 15 | 15700 | 2 | 8 | 8590 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 27.2 | 80.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.64 | 6 | 0
2005-06-16 | 1900-06-15 | 14:00 | 14 | 1226 | 1324 | 915 | 2 | 8 | 820 | 2 | 15 | 154 | 2 | 8 | 98100 | 2 | 8 | 83200 | 2 | 15 | 20800 | 2 | 8 | 9150 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 28.3 | 82.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 160 | B | 8 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.24 | 6 | 0
2005-06-16 | 1900-06-15 | 15:00 | 15 | 1123 | 1324 | 813 | 2 | 8 | 746 | 2 | 15 | 179 | 2 | 8 | 84600 | 2 | 8 | 74800 | 2 | 15 | 21100 | 2 | 8 | 6830 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 27.2 | 80.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.56 | A | 7 | 976 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.64 | 6 | 0
2005-06-16 | 1900-06-15 | 16:00 | 16 | 965 | 1324 | 671 | 2 | 8 | 689 | 2 | 15 | 167 | 2 | 8 | 71300 | 2 | 8 | 70300 | 2 | 15 | 20000 | 2 | 8 | 5000 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 28.3 | 82.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.53 | A | 7 | 978 | A | 7 | 130 | B | 8 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.94 | 6 | 0
2005-06-16 | 1900-06-15 | 17:00 | 17 | 765 | 1324 | 496 | 2 | 8 | 631 | 2 | 15 | 131 | 2 | 8 | 52400 | 2 | 8 | 63300 | 2 | 15 | 15700 | 2 | 8 | 3040 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 27.2 | 80.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.64 | 6 | 0
2005-06-16 | 1900-06-15 | 18:00 | 18 | 535 | 1324 | 281 | 2 | 8 | 347 | 2 | 15 | 141 | 2 | 8 | 30300 | 2 | 8 | 34400 | 2 | 15 | 16300 | 2 | 8 | 2900 | 2 | 19 | 7 | E | 9 | 7 | A | 7 | 27.2 | 80.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.58 | A | 7 | 975 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.94 | 6 | 0
2005-06-16 | 1900-06-15 | 19:00 | 19 | 292 | 1324 | 127 | 2 | 8 | 241 | 2 | 15 | 74 | 2 | 8 | 13500 | 2 | 8 | 19000 | 2 | 15 | 9300 | 2 | 8 | 1400 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 26.7 | 80.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 50 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.34 | 6 | 0
2005-06-16 | 1900-06-15 | 20:00 | 20 | 63 | 1004 | 11 | 2 | 8 | 56 | 2 | 15 | 9 | 2 | 8 | 1500 | 2 | 8 | 2300 | 2 | 15 | 1300 | 2 | 8 | 150 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25 | 77 | A | 7 | 18.3 | 64.94 | A | 7 | 0.66 | A | 7 | 978 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.74 | 6 | 0
2005-06-16 | 1900-06-15 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | E | 9 | 25 | 77 | A | 7 | 18.3 | 64.94 | A | 7 | 0.66 | A | 7 | 975 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 3.4 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.74 | 6 | 0
2005-06-16 | 1900-06-15 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 7 | E | 9 | 23.9 | 75.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 3.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.64 | 6 | 0
2005-06-16 | 1900-06-15 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | E | 9 | 23.3 | 73.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 3.3 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.04 | 6 | 0
2005-06-16 | 1900-06-15 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | E | 9 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.73 | A | 7 | 975 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3.2 | E | 8 | 0.149 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.44 | 6 | 0
2005-06-17 | 1900-06-16 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | E | 9 | 22.2 | 71.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 3.2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.26 | 7 | 0
2005-06-17 | 1900-06-16 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 8 | E | 9 | 21.7 | 71.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 3.3 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.08 | 7 | 0
2005-06-17 | 1900-06-16 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 8 | E | 9 | 20.6 | 69.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 3.3 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.08 | 7 | 0
2005-06-17 | 1900-06-16 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 20.6 | 69.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 3.3 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.88 | 7 | 0
2005-06-17 | 1900-06-16 | 5:00 | 5 | 1 | 143 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 20 | 68 | A | 7 | 13.9 | 57.02 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 3.2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.12 | 7 | 0
2005-06-17 | 1900-06-16 | 6:00 | 6 | 135 | 1323 | 31 | 2 | 8 | 0 | 2 | 15 | 31 | 2 | 8 | 3500 | 2 | 8 | 0 | 2 | 15 | 3500 | 2 | 8 | 1050 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 20.6 | 69.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.63 | A | 7 | 977 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1372 | A | 7 | 3.2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.14 | 7 | 0
2005-06-17 | 1900-06-16 | 7:00 | 7 | 376 | 1323 | 210 | 2 | 8 | 372 | 2 | 15 | 105 | 2 | 8 | 21700 | 2 | 8 | 32200 | 2 | 15 | 12600 | 2 | 8 | 1980 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 21.1 | 69.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.64 | 7 | 0
2005-06-17 | 1900-06-16 | 8:00 | 8 | 616 | 1323 | 384 | 2 | 8 | 546 | 2 | 15 | 130 | 2 | 8 | 39700 | 2 | 8 | 52800 | 2 | 15 | 15100 | 2 | 8 | 2600 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.84 | 7 | 0
2005-06-17 | 1900-06-16 | 9:00 | 9 | 837 | 1323 | 540 | 2 | 8 | 592 | 2 | 15 | 165 | 2 | 8 | 56600 | 2 | 8 | 59500 | 2 | 15 | 18900 | 2 | 8 | 4050 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 23.9 | 75.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.5 | A | 7 | 977 | A | 7 | 70 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45.84 | 7 | 0
2005-06-17 | 1900-06-16 | 10:00 | 10 | 1024 | 1323 | 721 | 2 | 8 | 660 | 2 | 15 | 209 | 2 | 8 | 76000 | 2 | 8 | 66900 | 2 | 15 | 24100 | 2 | 8 | 6880 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 13.9 | 57.02 | A | 7 | 0.5 | A | 7 | 979 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.52 | 7 | 0
2005-06-17 | 1900-06-16 | 11:00 | 11 | 1164 | 1323 | 848 | 2 | 8 | 748 | 2 | 15 | 189 | 2 | 8 | 88300 | 2 | 8 | 75000 | 2 | 15 | 22200 | 2 | 8 | 8270 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.48 | A | 7 | 979 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.12 | 7 | 0
2005-06-17 | 1900-06-16 | 12:00 | 12 | 1248 | 1323 | 937 | 2 | 8 | 830 | 2 | 15 | 153 | 2 | 8 | 95800 | 2 | 8 | 83100 | 2 | 15 | 17200 | 2 | 8 | 8130 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.47 | A | 7 | 977 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.92 | 7 | 0
2005-06-17 | 1900-06-16 | 13:00 | 13 | 1269 | 1323 | 953 | 2 | 8 | 828 | 2 | 15 | 158 | 2 | 8 | 102500 | 2 | 8 | 84100 | 2 | 15 | 21700 | 2 | 8 | 12040 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.47 | A | 7 | 979 | A | 7 | 90 | B | 8 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.62 | 7 | 0
2005-06-17 | 1900-06-16 | 14:00 | 14 | 1226 | 1323 | 915 | 2 | 8 | 820 | 2 | 15 | 154 | 2 | 8 | 98200 | 2 | 8 | 83200 | 2 | 15 | 20800 | 2 | 8 | 9170 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.42 | A | 7 | 979 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.24 | 7 | 0
2005-06-17 | 1900-06-16 | 15:00 | 15 | 1123 | 1323 | 813 | 2 | 8 | 758 | 2 | 15 | 168 | 2 | 8 | 85200 | 2 | 8 | 76200 | 2 | 15 | 20300 | 2 | 8 | 6540 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.41 | A | 7 | 977 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.04 | 7 | 0
2005-06-17 | 1900-06-16 | 16:00 | 16 | 966 | 1323 | 676 | 2 | 8 | 731 | 2 | 15 | 142 | 2 | 8 | 70700 | 2 | 8 | 73300 | 2 | 15 | 17100 | 2 | 8 | 3900 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.41 | A | 7 | 979 | A | 7 | 60 | B | 8 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.04 | 7 | 0
2005-06-17 | 1900-06-16 | 17:00 | 17 | 766 | 1323 | 512 | 2 | 8 | 696 | 2 | 15 | 109 | 2 | 8 | 54800 | 2 | 8 | 70400 | 2 | 15 | 14000 | 2 | 8 | 2590 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.39 | A | 7 | 978 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 42.06 | 7 | 0
2005-06-17 | 1900-06-16 | 18:00 | 18 | 536 | 1323 | 328 | 2 | 8 | 608 | 2 | 15 | 82 | 2 | 8 | 34600 | 2 | 8 | 58200 | 2 | 15 | 11000 | 2 | 8 | 1660 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.39 | A | 7 | 976 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 41.28 | 7 | 0
2005-06-17 | 1900-06-16 | 19:00 | 19 | 293 | 1323 | 145 | 2 | 8 | 411 | 2 | 15 | 54 | 2 | 8 | 14900 | 2 | 8 | 32700 | 2 | 15 | 7700 | 2 | 8 | 990 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 10 | 50 | A | 7 | 0.39 | A | 7 | 978 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 39.7 | 7 | 0
2005-06-17 | 1900-06-16 | 20:00 | 20 | 64 | 1026 | 9 | 2 | 8 | 19 | 2 | 15 | 9 | 2 | 8 | 1200 | 2 | 8 | 900 | 2 | 15 | 1100 | 2 | 8 | 190 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.46 | A | 7 | 978 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 42.58 | 7 | 0
2005-06-17 | 1900-06-16 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.55 | A | 7 | 977 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45.96 | 7 | 0
2005-06-17 | 1900-06-16 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.76 | 7 | 0
2005-06-17 | 1900-06-16 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 19.4 | 66.92 | A | 7 | 11.7 | 53.06 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.26 | 7 | 0
2005-06-17 | 1900-06-16 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.9 | 66.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.63 | A | 7 | 977 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 46.66 | 7 | 0
2005-06-18 | 1900-06-17 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.06 | 1 | 0
2005-06-18 | 1900-06-17 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.76 | 1 | 0
2005-06-18 | 1900-06-17 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.96 | 1 | 0
2005-06-18 | 1900-06-17 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.76 | 1 | 0
2005-06-18 | 1900-06-17 | 5:00 | 5 | 1 | 143 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.26 | 1 | 0
2005-06-18 | 1900-06-17 | 6:00 | 6 | 134 | 1323 | 47 | 2 | 8 | 0 | 2 | 15 | 47 | 2 | 8 | 5100 | 2 | 8 | 0 | 2 | 15 | 5100 | 2 | 8 | 1350 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.76 | 1 | 0
2005-06-18 | 1900-06-17 | 7:00 | 7 | 375 | 1323 | 218 | 2 | 8 | 417 | 2 | 15 | 100 | 2 | 8 | 22600 | 2 | 8 | 36100 | 2 | 15 | 12400 | 2 | 8 | 1880 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 12.8 | 55.04 | A | 7 | 0.63 | A | 7 | 981 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.34 | 1 | 0
2005-06-18 | 1900-06-17 | 8:00 | 8 | 615 | 1323 | 398 | 2 | 8 | 614 | 2 | 15 | 112 | 2 | 8 | 41500 | 2 | 8 | 59800 | 2 | 15 | 13700 | 2 | 8 | 2300 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.53 | A | 7 | 981 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45.56 | 1 | 0
2005-06-18 | 1900-06-17 | 9:00 | 9 | 837 | 1323 | 573 | 2 | 8 | 702 | 2 | 15 | 129 | 2 | 8 | 61200 | 2 | 8 | 71300 | 2 | 15 | 16000 | 2 | 8 | 3270 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.54 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.32 | 1 | 0
2005-06-18 | 1900-06-17 | 10:00 | 10 | 1024 | 1323 | 733 | 2 | 8 | 739 | 2 | 15 | 160 | 2 | 8 | 78700 | 2 | 8 | 75900 | 2 | 15 | 19900 | 2 | 8 | 5400 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 12.2 | 53.96 | A | 7 | 0.45 | A | 7 | 983 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 43.96 | 1 | 0
2005-06-18 | 1900-06-17 | 11:00 | 11 | 1164 | 1323 | 860 | 2 | 8 | 808 | 2 | 15 | 148 | 2 | 8 | 91900 | 2 | 8 | 81900 | 2 | 15 | 19700 | 2 | 8 | 6820 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.42 | A | 7 | 982 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 43.36 | 1 | 0
2005-06-18 | 1900-06-17 | 12:00 | 12 | 1248 | 1323 | 931 | 2 | 8 | 812 | 2 | 15 | 164 | 2 | 8 | 99400 | 2 | 8 | 82300 | 2 | 15 | 21700 | 2 | 8 | 10870 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.42 | A | 7 | 980 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 43.36 | 1 | 0
2005-06-18 | 1900-06-17 | 13:00 | 13 | 1269 | 1323 | 965 | 2 | 8 | 864 | 2 | 15 | 135 | 2 | 8 | 99000 | 2 | 8 | 86600 | 2 | 15 | 15700 | 2 | 8 | 8610 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.39 | A | 7 | 982 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 42.76 | 1 | 0
2005-06-18 | 1900-06-17 | 14:00 | 14 | 1227 | 1323 | 921 | 2 | 8 | 838 | 2 | 15 | 143 | 2 | 8 | 94400 | 2 | 8 | 83900 | 2 | 15 | 16400 | 2 | 8 | 6890 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.38 | A | 7 | 981 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 42.56 | 1 | 0
2005-06-18 | 1900-06-17 | 15:00 | 15 | 1123 | 1323 | 830 | 2 | 8 | 824 | 2 | 15 | 130 | 2 | 8 | 85400 | 2 | 8 | 82500 | 2 | 15 | 15200 | 2 | 8 | 4260 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.39 | A | 7 | 979 | A | 7 | 110 | B | 8 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 42.76 | 1 | 0
2005-06-18 | 1900-06-17 | 16:00 | 16 | 966 | 1323 | 682 | 2 | 8 | 737 | 2 | 15 | 143 | 2 | 8 | 71200 | 2 | 8 | 73900 | 2 | 15 | 17200 | 2 | 8 | 3920 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.38 | A | 7 | 981 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 42.56 | 1 | 0
2005-06-18 | 1900-06-17 | 17:00 | 17 | 766 | 1323 | 518 | 2 | 8 | 719 | 2 | 15 | 101 | 2 | 8 | 54400 | 2 | 8 | 71500 | 2 | 15 | 12900 | 2 | 8 | 2290 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.38 | A | 7 | 981 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 41.86 | 1 | 0
2005-06-18 | 1900-06-17 | 18:00 | 18 | 537 | 1323 | 329 | 2 | 8 | 602 | 2 | 15 | 84 | 2 | 8 | 34600 | 2 | 8 | 57600 | 2 | 15 | 11200 | 2 | 8 | 1690 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.41 | A | 7 | 978 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 43.16 | 1 | 0
2005-06-18 | 1900-06-17 | 19:00 | 19 | 294 | 1323 | 150 | 2 | 8 | 405 | 2 | 15 | 60 | 2 | 8 | 15300 | 2 | 8 | 32100 | 2 | 15 | 8200 | 2 | 8 | 1070 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.43 | A | 7 | 981 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 43.56 | 1 | 0
2005-06-18 | 1900-06-17 | 20:00 | 20 | 65 | 1025 | 8 | 2 | 8 | 0 | 2 | 15 | 8 | 2 | 8 | 1000 | 2 | 8 | 0 | 2 | 15 | 1000 | 2 | 8 | 310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.46 | A | 7 | 981 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 44.16 | 1 | 0
2005-06-18 | 1900-06-17 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.51 | A | 7 | 979 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45.16 | 1 | 0
2005-06-18 | 1900-06-17 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.44 | 1 | 0
2005-06-18 | 1900-06-17 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 982 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.04 | 1 | 0
2005-06-18 | 1900-06-17 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 19.4 | 66.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.14 | 1 | 0
2005-06-19 | 1900-06-18 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 982 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.04 | 2 | 0
2005-06-19 | 1900-06-18 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.9 | 66.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.7 | A | 7 | 982 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.54 | 2 | 0
2005-06-19 | 1900-06-18 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.44 | 2 | 0
2005-06-19 | 1900-06-18 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.04 | 2 | 0
2005-06-19 | 1900-06-18 | 5:00 | 5 | 1 | 143 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.8 | A | 7 | 983 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.34 | 2 | 0
2005-06-19 | 1900-06-18 | 6:00 | 6 | 134 | 1323 | 47 | 2 | 8 | 0 | 2 | 15 | 47 | 2 | 8 | 5100 | 2 | 8 | 0 | 2 | 15 | 5100 | 2 | 8 | 1350 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 982 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.04 | 2 | 0
2005-06-19 | 1900-06-18 | 7:00 | 7 | 374 | 1323 | 218 | 2 | 8 | 463 | 2 | 15 | 87 | 2 | 8 | 22900 | 2 | 8 | 40100 | 2 | 15 | 11600 | 2 | 8 | 1610 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20.6 | 69.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.65 | A | 7 | 984 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.52 | 2 | 0
2005-06-19 | 1900-06-18 | 8:00 | 8 | 614 | 1323 | 377 | 2 | 8 | 527 | 2 | 15 | 132 | 2 | 8 | 40500 | 2 | 8 | 52200 | 2 | 15 | 16200 | 2 | 8 | 2660 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.61 | A | 7 | 985 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.52 | 2 | 0
2005-06-19 | 1900-06-18 | 9:00 | 9 | 836 | 1323 | 573 | 2 | 8 | 665 | 2 | 15 | 152 | 2 | 8 | 60400 | 2 | 8 | 67100 | 2 | 15 | 17900 | 2 | 8 | 3770 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 15 | 59 | A | 7 | 0.57 | A | 7 | 983 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.6 | 2 | 0
2005-06-19 | 1900-06-18 | 10:00 | 10 | 1023 | 1323 | 733 | 2 | 8 | 739 | 2 | 15 | 161 | 2 | 8 | 78800 | 2 | 8 | 75800 | 2 | 15 | 20000 | 2 | 8 | 5430 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 15.6 | 60.08 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.28 | 2 | 0
2005-06-19 | 1900-06-18 | 11:00 | 11 | 1164 | 1323 | 854 | 2 | 8 | 784 | 2 | 15 | 163 | 2 | 8 | 90300 | 2 | 8 | 79200 | 2 | 15 | 20500 | 2 | 8 | 7360 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.52 | A | 7 | 985 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.48 | 2 | 0
2005-06-19 | 1900-06-18 | 12:00 | 12 | 1247 | 1323 | 925 | 2 | 8 | 788 | 2 | 15 | 181 | 2 | 8 | 97800 | 2 | 8 | 79500 | 2 | 15 | 22700 | 2 | 8 | 11820 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.51 | A | 7 | 983 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.98 | 2 | 0
2005-06-19 | 1900-06-18 | 13:00 | 13 | 1269 | 1323 | 947 | 2 | 8 | 804 | 2 | 15 | 175 | 2 | 8 | 100800 | 2 | 8 | 81300 | 2 | 15 | 22600 | 2 | 8 | 13210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.51 | A | 7 | 985 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.86 | 2 | 0
2005-06-19 | 1900-06-18 | 14:00 | 14 | 1227 | 1323 | 927 | 2 | 8 | 838 | 2 | 15 | 149 | 2 | 8 | 94900 | 2 | 8 | 83900 | 2 | 15 | 16900 | 2 | 8 | 7080 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 15 | 59 | A | 7 | 0.44 | A | 7 | 985 | A | 7 | 120 | B | 8 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.8 | 2 | 0
2005-06-19 | 1900-06-18 | 15:00 | 15 | 1124 | 1323 | 819 | 2 | 8 | 776 | 2 | 15 | 158 | 2 | 8 | 86400 | 2 | 8 | 78300 | 2 | 15 | 19700 | 2 | 8 | 6270 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 15 | 59 | A | 7 | 0.44 | A | 7 | 982 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.8 | 2 | 0
2005-06-19 | 1900-06-18 | 16:00 | 16 | 967 | 1323 | 688 | 2 | 8 | 772 | 2 | 15 | 122 | 2 | 8 | 73000 | 2 | 8 | 77900 | 2 | 15 | 15900 | 2 | 8 | 3530 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.48 | A | 7 | 984 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.28 | 2 | 0
2005-06-19 | 1900-06-18 | 17:00 | 17 | 767 | 1323 | 518 | 2 | 8 | 707 | 2 | 15 | 107 | 2 | 8 | 55500 | 2 | 8 | 71600 | 2 | 15 | 13900 | 2 | 8 | 2550 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.48 | A | 7 | 984 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.28 | 2 | 0
2005-06-19 | 1900-06-18 | 18:00 | 18 | 538 | 1323 | 329 | 2 | 8 | 602 | 2 | 15 | 83 | 2 | 8 | 34600 | 2 | 8 | 57700 | 2 | 15 | 11100 | 2 | 8 | 1680 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 27.2 | 80.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.51 | A | 7 | 982 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 50.98 | 2 | 0
2005-06-19 | 1900-06-18 | 19:00 | 19 | 295 | 1323 | 150 | 2 | 8 | 405 | 2 | 15 | 59 | 2 | 8 | 15300 | 2 | 8 | 32200 | 2 | 15 | 8100 | 2 | 8 | 1060 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 110 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.68 | 2 | 0
2005-06-19 | 1900-06-18 | 20:00 | 20 | 66 | 1025 | 8 | 2 | 8 | 0 | 2 | 15 | 8 | 2 | 8 | 1000 | 2 | 8 | 0 | 2 | 15 | 1000 | 2 | 8 | 310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 15.6 | 60.08 | A | 7 | 0.56 | A | 7 | 984 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.28 | 2 | 0
2005-06-19 | 1900-06-18 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.18 | 2 | 0
2005-06-19 | 1900-06-18 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.64 | A | 7 | 985 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.98 | 2 | 0
2005-06-19 | 1900-06-18 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 15.6 | 60.08 | A | 7 | 0.66 | A | 7 | 985 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.48 | 2 | 0
2005-06-19 | 1900-06-18 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 984 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.9 | 2 | 0
2005-06-20 | 1900-06-19 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 985 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.9 | 3 | 0
2005-06-20 | 1900-06-19 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.78 | A | 7 | 985 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.82 | 3 | 0
2005-06-20 | 1900-06-19 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.78 | A | 7 | 984 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.02 | 3 | 0
2005-06-20 | 1900-06-19 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.81 | A | 7 | 985 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.52 | 3 | 0
2005-06-20 | 1900-06-19 | 5:00 | 5 | 1 | 143 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.78 | A | 7 | 986 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.02 | 3 | 0
2005-06-20 | 1900-06-19 | 6:00 | 6 | 133 | 1323 | 47 | 2 | 8 | 0 | 2 | 15 | 47 | 2 | 8 | 5100 | 2 | 8 | 0 | 2 | 15 | 5100 | 2 | 8 | 1350 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.78 | A | 7 | 985 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.82 | 3 | 0
2005-06-20 | 1900-06-19 | 7:00 | 7 | 373 | 1323 | 211 | 2 | 8 | 418 | 2 | 15 | 93 | 2 | 8 | 22000 | 2 | 8 | 36100 | 2 | 15 | 11800 | 2 | 8 | 1730 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.71 | A | 7 | 987 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.48 | 3 | 0
2005-06-20 | 1900-06-19 | 8:00 | 8 | 614 | 1323 | 391 | 2 | 8 | 620 | 2 | 15 | 103 | 2 | 8 | 41100 | 2 | 8 | 60600 | 2 | 15 | 12900 | 2 | 8 | 2140 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.78 | 3 | 0
2005-06-20 | 1900-06-19 | 9:00 | 9 | 835 | 1323 | 567 | 2 | 8 | 708 | 2 | 15 | 119 | 2 | 8 | 60800 | 2 | 8 | 72100 | 2 | 15 | 15200 | 2 | 8 | 3040 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 15.6 | 60.08 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.28 | 3 | 0
2005-06-20 | 1900-06-19 | 10:00 | 10 | 1022 | 1323 | 727 | 2 | 8 | 721 | 2 | 15 | 169 | 2 | 8 | 77800 | 2 | 8 | 73800 | 2 | 15 | 20600 | 2 | 8 | 5660 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.18 | 3 | 0
2005-06-20 | 1900-06-19 | 11:00 | 11 | 1163 | 1323 | 854 | 2 | 8 | 772 | 2 | 15 | 174 | 2 | 8 | 89700 | 2 | 8 | 77700 | 2 | 15 | 21200 | 2 | 8 | 7730 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.54 | A | 7 | 987 | A | 7 | 10 | B | 8 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.26 | 3 | 0
2005-06-20 | 1900-06-19 | 12:00 | 12 | 1247 | 1323 | 938 | 2 | 8 | 836 | 2 | 15 | 148 | 2 | 8 | 95900 | 2 | 8 | 83700 | 2 | 15 | 16800 | 2 | 8 | 7940 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.51 | A | 7 | 985 | A | 7 | 30 | B | 8 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.56 | 3 | 0
2005-06-20 | 1900-06-19 | 13:00 | 13 | 1269 | 1323 | 954 | 2 | 8 | 828 | 2 | 15 | 158 | 2 | 8 | 102500 | 2 | 8 | 84100 | 2 | 15 | 21700 | 2 | 8 | 12080 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 29.4 | 84.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.51 | A | 7 | 987 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.24 | 3 | 0
2005-06-20 | 1900-06-19 | 14:00 | 14 | 1227 | 1323 | 910 | 2 | 8 | 796 | 2 | 15 | 170 | 2 | 8 | 96500 | 2 | 8 | 80500 | 2 | 15 | 21700 | 2 | 8 | 10030 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 29.4 | 84.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.51 | A | 7 | 987 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.24 | 3 | 0
2005-06-20 | 1900-06-19 | 15:00 | 15 | 1124 | 1323 | 825 | 2 | 8 | 800 | 2 | 15 | 144 | 2 | 8 | 88000 | 2 | 8 | 81000 | 2 | 15 | 19000 | 2 | 8 | 5840 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 29.4 | 84.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.48 | A | 7 | 983 | A | 7 | 120 | B | 8 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.86 | 3 | 0
2005-06-20 | 1900-06-19 | 16:00 | 16 | 968 | 1323 | 682 | 2 | 8 | 731 | 2 | 15 | 147 | 2 | 8 | 73300 | 2 | 8 | 74900 | 2 | 15 | 18400 | 2 | 8 | 4480 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 29.4 | 84.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.86 | 3 | 0
2005-06-20 | 1900-06-19 | 17:00 | 17 | 768 | 1323 | 513 | 2 | 8 | 690 | 2 | 15 | 112 | 2 | 8 | 54800 | 2 | 8 | 69700 | 2 | 15 | 14300 | 2 | 8 | 2660 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 29.4 | 84.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.45 | A | 7 | 985 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.58 | 3 | 0
2005-06-20 | 1900-06-19 | 18:00 | 18 | 539 | 1323 | 329 | 2 | 8 | 573 | 2 | 15 | 95 | 2 | 8 | 34300 | 2 | 8 | 54600 | 2 | 15 | 12000 | 2 | 8 | 1880 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.4 | A | 7 | 982 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 45.42 | 3 | 0
2005-06-20 | 1900-06-19 | 19:00 | 19 | 296 | 1323 | 136 | 2 | 8 | 296 | 2 | 15 | 70 | 2 | 8 | 14300 | 2 | 8 | 23400 | 2 | 15 | 9000 | 2 | 8 | 1270 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.4 | A | 7 | 985 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 43.84 | 3 | 0
2005-06-20 | 1900-06-19 | 20:00 | 20 | 66 | 1047 | 10 | 2 | 8 | 11 | 2 | 15 | 9 | 2 | 8 | 1100 | 2 | 8 | 500 | 2 | 15 | 1100 | 2 | 8 | 190 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 26.7 | 80.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.47 | A | 7 | 986 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 47.62 | 3 | 0
2005-06-20 | 1900-06-19 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 25.6 | 78.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.5 | A | 7 | 984 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 48.22 | 3 | 0
2005-06-20 | 1900-06-19 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 4 | E | 9 | 25.6 | 78.08 | A | 7 | 15 | 59 | A | 7 | 0.52 | A | 7 | 986 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 49.6 | 3 | 0
2005-06-20 | 1900-06-19 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 23.3 | 73.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.62 | A | 7 | 987 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.58 | 3 | 0
2005-06-20 | 1900-06-19 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 22.8 | 73.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.64 | A | 7 | 984 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.98 | 3 | 0
2005-06-21 | 1900-06-20 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 6 | E | 9 | 21.1 | 69.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 130 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.48 | 4 | 0
2005-06-21 | 1900-06-20 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | B | 8 | 6 | B | 8 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.79 | A | 7 | 984 | A | 7 | 160 | B | 8 | 2.1 | B | 8 | 16000 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.08 | 4 | 0
2005-06-21 | 1900-06-20 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | E | 9 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 983 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.48 | 4 | 0
2005-06-21 | 1900-06-20 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.98 | 4 | 0
2005-06-21 | 1900-06-20 | 5:00 | 5 | 1 | 121 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.79 | A | 7 | 984 | A | 7 | 240 | A | 7 | 1.5 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.08 | 4 | 0
2005-06-21 | 1900-06-20 | 6:00 | 6 | 132 | 1322 | 16 | 2 | 8 | 0 | 2 | 15 | 16 | 2 | 8 | 1900 | 2 | 8 | 0 | 2 | 15 | 1900 | 2 | 8 | 610 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 12800 | A | 7 | 3658 | A | 7 | 3.7 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.36 | 4 | 0
2005-06-21 | 1900-06-20 | 7:00 | 7 | 373 | 1322 | 187 | 2 | 8 | 222 | 2 | 15 | 125 | 2 | 8 | 19600 | 2 | 8 | 19500 | 2 | 15 | 14100 | 2 | 8 | 2560 | 2 | 19 | 10 | E | 9 | 8 | E | 9 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 986 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 12800 | A | 7 | 7620 | A | 7 | 3.7 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.16 | 4 | 0
2005-06-21 | 1900-06-20 | 8:00 | 8 | 613 | 1322 | 227 | 2 | 8 | 50 | 2 | 15 | 204 | 2 | 8 | 24900 | 2 | 8 | 4900 | 2 | 15 | 22600 | 2 | 8 | 5880 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 24.4 | 75.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.56 | 4 | 0
2005-06-21 | 1900-06-20 | 9:00 | 9 | 834 | 1322 | 326 | 2 | 8 | 79 | 2 | 15 | 276 | 2 | 8 | 35900 | 2 | 8 | 8000 | 2 | 15 | 30800 | 2 | 8 | 9160 | 2 | 19 | 10 | E | 9 | 8 | E | 9 | 25 | 77 | A | 7 | 18.3 | 64.94 | A | 7 | 0.66 | A | 7 | 985 | A | 7 | 310 | B | 8 | 2.1 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 3.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.74 | 4 | 0
2005-06-21 | 1900-06-20 | 10:00 | 10 | 1022 | 1322 | 620 | 2 | 8 | 382 | 2 | 15 | 324 | 2 | 8 | 67600 | 2 | 8 | 41400 | 2 | 15 | 35600 | 2 | 8 | 10660 | 2 | 19 | 7 | E | 9 | 5 | E | 9 | 27.2 | 80.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.61 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.52 | 4 | 0
2005-06-21 | 1900-06-20 | 11:00 | 11 | 1162 | 1322 | 632 | 2 | 8 | 271 | 2 | 15 | 393 | 2 | 8 | 69100 | 2 | 8 | 29400 | 2 | 15 | 43200 | 2 | 8 | 17890 | 2 | 19 | 6 | E | 9 | 4 | E | 9 | 29.4 | 84.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.55 | A | 7 | 986 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.82 | 4 | 0
2005-06-21 | 1900-06-20 | 12:00 | 12 | 1247 | 1322 | 925 | 2 | 8 | 704 | 2 | 15 | 261 | 2 | 8 | 98400 | 2 | 8 | 71600 | 2 | 15 | 30700 | 2 | 8 | 18000 | 2 | 19 | 5 | E | 9 | 4 | E | 9 | 30 | 86 | A | 7 | 18.9 | 66.02 | A | 7 | 0.51 | A | 7 | 983 | A | 7 | 30 | B | 8 | 2.1 | A | 7 | 14400 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.12 | 4 | 0
2005-06-21 | 1900-06-20 | 13:00 | 13 | 1269 | 1322 | 792 | 2 | 8 | 474 | 2 | 15 | 336 | 2 | 8 | 85900 | 2 | 8 | 49600 | 2 | 15 | 38200 | 2 | 8 | 27310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 30 | 86 | A | 7 | 20 | 68 | A | 7 | 0.55 | A | 7 | 985 | A | 7 | 70 | B | 8 | 3.1 | A | 7 | 14400 | A | 7 | 7620 | A | 7 | 4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.8 | 4 | 0
2005-06-21 | 1900-06-20 | 14:00 | 14 | 1227 | 1322 | 916 | 2 | 8 | 754 | 2 | 15 | 214 | 2 | 8 | 98400 | 2 | 8 | 77400 | 2 | 15 | 26500 | 2 | 8 | 13450 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 31.1 | 87.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.5 | A | 7 | 985 | A | 7 | 100 | B | 8 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.62 | 4 | 0
2005-06-21 | 1900-06-20 | 15:00 | 15 | 1125 | 1322 | 813 | 2 | 8 | 740 | 2 | 15 | 183 | 2 | 8 | 87500 | 2 | 8 | 76000 | 2 | 15 | 22700 | 2 | 8 | 7880 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 31.1 | 87.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.5 | A | 7 | 983 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.62 | 4 | 0
2005-06-21 | 1900-06-20 | 16:00 | 16 | 968 | 1322 | 665 | 2 | 8 | 666 | 2 | 15 | 177 | 2 | 8 | 70500 | 2 | 8 | 67800 | 2 | 15 | 20800 | 2 | 8 | 5300 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.54 | A | 7 | 985 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.38 | 4 | 0
2005-06-21 | 1900-06-20 | 17:00 | 17 | 769 | 1322 | 502 | 2 | 8 | 660 | 2 | 15 | 117 | 2 | 8 | 53400 | 2 | 8 | 66600 | 2 | 15 | 14600 | 2 | 8 | 2770 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 31.1 | 87.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.42 | 4 | 0
2005-06-21 | 1900-06-20 | 18:00 | 18 | 540 | 1322 | 308 | 2 | 8 | 458 | 2 | 15 | 121 | 2 | 8 | 32800 | 2 | 8 | 44200 | 2 | 15 | 14700 | 2 | 8 | 2350 | 2 | 19 | 9 | E | 9 | 5 | A | 7 | 30 | 86 | A | 7 | 20 | 68 | A | 7 | 0.55 | A | 7 | 982 | A | 7 | 210 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.8 | 4 | 0
2005-06-21 | 1900-06-20 | 19:00 | 19 | 297 | 1322 | 150 | 2 | 8 | 345 | 2 | 15 | 72 | 2 | 8 | 15600 | 2 | 8 | 27200 | 2 | 15 | 9500 | 2 | 8 | 1320 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.9 | 84.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.61 | A | 7 | 984 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.18 | 4 | 0
2005-06-21 | 1900-06-20 | 20:00 | 20 | 67 | 1047 | 8 | 2 | 8 | 0 | 2 | 15 | 8 | 2 | 8 | 1000 | 2 | 8 | 0 | 2 | 15 | 1000 | 2 | 8 | 310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 20 | 68 | A | 7 | 0.63 | A | 7 | 984 | A | 7 | 230 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.7 | 4 | 0
2005-06-21 | 1900-06-20 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 210 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.6 | 4 | 0
2005-06-21 | 1900-06-20 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 984 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.62 | 4 | 0
2005-06-21 | 1900-06-20 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 984 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.82 | 4 | 0
2005-06-21 | 1900-06-20 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.15 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.82 | 4 | 0
2005-06-22 | 1900-06-21 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.82 | 5 | 0
2005-06-22 | 1900-06-21 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 984 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.62 | 5 | 0
2005-06-22 | 1900-06-21 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 983 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.72 | 5 | 0
2005-06-22 | 1900-06-21 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.22 | 5 | 0
2005-06-22 | 1900-06-21 | 5:00 | 5 | 1 | 121 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 985 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 3.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.72 | 5 | 0
2005-06-22 | 1900-06-21 | 6:00 | 6 | 131 | 1322 | 48 | 2 | 8 | 0 | 2 | 15 | 48 | 2 | 8 | 5200 | 2 | 8 | 0 | 2 | 15 | 5200 | 2 | 8 | 1350 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 983 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 7620 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.52 | 5 | 0
2005-06-22 | 1900-06-21 | 7:00 | 7 | 372 | 1322 | 211 | 2 | 8 | 431 | 2 | 15 | 90 | 2 | 8 | 22100 | 2 | 8 | 37200 | 2 | 15 | 11700 | 2 | 8 | 1670 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.48 | 5 | 0
2005-06-22 | 1900-06-21 | 8:00 | 8 | 612 | 1322 | 343 | 2 | 8 | 397 | 2 | 15 | 159 | 2 | 8 | 36100 | 2 | 8 | 39200 | 2 | 15 | 17900 | 2 | 8 | 3260 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 986 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.18 | 5 | 0
2005-06-22 | 1900-06-21 | 9:00 | 9 | 833 | 1322 | 489 | 2 | 8 | 397 | 2 | 15 | 238 | 2 | 8 | 51500 | 2 | 8 | 40800 | 2 | 15 | 25700 | 2 | 8 | 5930 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.59 | A | 7 | 984 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.82 | 5 | 0
2005-06-22 | 1900-06-21 | 10:00 | 10 | 1021 | 1322 | 727 | 2 | 8 | 690 | 2 | 15 | 193 | 2 | 8 | 77000 | 2 | 8 | 70200 | 2 | 15 | 22700 | 2 | 8 | 6370 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.9 | 84.02 | A | 7 | 20 | 68 | A | 7 | 0.59 | A | 7 | 986 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.8 | 5 | 0
2005-06-22 | 1900-06-21 | 11:00 | 11 | 1162 | 1322 | 848 | 2 | 8 | 772 | 2 | 15 | 169 | 2 | 8 | 89400 | 2 | 8 | 77800 | 2 | 15 | 20900 | 2 | 8 | 7540 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 30 | 86 | A | 7 | 20.6 | 69.08 | A | 7 | 0.57 | A | 7 | 986 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.18 | 5 | 0
2005-06-22 | 1900-06-21 | 12:00 | 12 | 1246 | 1322 | 926 | 2 | 8 | 794 | 2 | 15 | 176 | 2 | 8 | 98100 | 2 | 8 | 80200 | 2 | 15 | 22400 | 2 | 8 | 11500 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 30.6 | 87.08 | A | 7 | 20 | 68 | A | 7 | 0.53 | A | 7 | 983 | A | 7 | 210 | B | 8 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.3 | 5 | 0
2005-06-22 | 1900-06-21 | 13:00 | 13 | 1269 | 1322 | 948 | 2 | 8 | 804 | 2 | 15 | 175 | 2 | 8 | 100800 | 2 | 8 | 81300 | 2 | 15 | 22600 | 2 | 8 | 13220 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.54 | A | 7 | 985 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.38 | 5 | 0
2005-06-22 | 1900-06-21 | 14:00 | 14 | 1227 | 1322 | 910 | 2 | 8 | 796 | 2 | 15 | 169 | 2 | 8 | 96500 | 2 | 8 | 80500 | 2 | 15 | 21700 | 2 | 8 | 10000 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 31.7 | 89.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.12 | 5 | 0
2005-06-22 | 1900-06-21 | 15:00 | 15 | 1125 | 1322 | 807 | 2 | 8 | 716 | 2 | 15 | 197 | 2 | 8 | 86400 | 2 | 8 | 73300 | 2 | 15 | 23900 | 2 | 8 | 8450 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 31.1 | 87.98 | A | 7 | 20 | 68 | A | 7 | 0.52 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57 | 5 | 0
2005-06-22 | 1900-06-21 | 16:00 | 16 | 969 | 1322 | 671 | 2 | 8 | 683 | 2 | 15 | 169 | 2 | 8 | 71300 | 2 | 8 | 69600 | 2 | 15 | 20200 | 2 | 8 | 5090 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 31.7 | 89.06 | A | 7 | 20 | 68 | A | 7 | 0.5 | A | 7 | 984 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.5 | 5 | 0
2005-06-22 | 1900-06-21 | 17:00 | 17 | 769 | 1322 | 502 | 2 | 8 | 660 | 2 | 15 | 117 | 2 | 8 | 53400 | 2 | 8 | 66600 | 2 | 15 | 14600 | 2 | 8 | 2770 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 31.1 | 87.98 | A | 7 | 20 | 68 | A | 7 | 0.52 | A | 7 | 984 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57 | 5 | 0
2005-06-22 | 1900-06-21 | 18:00 | 18 | 540 | 1322 | 313 | 2 | 8 | 498 | 2 | 15 | 109 | 2 | 8 | 33600 | 2 | 8 | 48100 | 2 | 15 | 13900 | 2 | 8 | 2100 | 2 | 19 | 6 | E | 9 | 2 | A | 7 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.98 | 5 | 0
2005-06-22 | 1900-06-21 | 19:00 | 19 | 298 | 1322 | 141 | 2 | 8 | 329 | 2 | 15 | 67 | 2 | 8 | 14800 | 2 | 8 | 26000 | 2 | 15 | 9000 | 2 | 8 | 1210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.98 | 5 | 0
2005-06-22 | 1900-06-21 | 20:00 | 20 | 67 | 1047 | 8 | 2 | 8 | 0 | 2 | 15 | 8 | 2 | 8 | 1000 | 2 | 8 | 0 | 2 | 15 | 1000 | 2 | 8 | 310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 983 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.2 | 5 | 0
2005-06-22 | 1900-06-21 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.42 | 5 | 0
2005-06-22 | 1900-06-21 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.62 | 5 | 0
2005-06-22 | 1900-06-21 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.62 | 5 | 0
2005-06-22 | 1900-06-21 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.22 | 5 | 0
2005-06-23 | 1900-06-22 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.84 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.64 | 6 | 0
2005-06-23 | 1900-06-22 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.14 | 6 | 0
2005-06-23 | 1900-06-22 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 17.8 | 64.04 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.44 | 6 | 0
2005-06-23 | 1900-06-22 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.96 | 6 | 0
2005-06-23 | 1900-06-22 | 5:00 | 5 | 1 | 121 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.36 | 6 | 0
2005-06-23 | 1900-06-22 | 6:00 | 6 | 130 | 1322 | 48 | 2 | 8 | 0 | 2 | 15 | 48 | 2 | 8 | 5200 | 2 | 8 | 0 | 2 | 15 | 5200 | 2 | 8 | 1340 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.64 | 6 | 0
2005-06-23 | 1900-06-22 | 7:00 | 7 | 370 | 1322 | 211 | 2 | 8 | 392 | 2 | 15 | 101 | 2 | 8 | 21800 | 2 | 8 | 33700 | 2 | 15 | 12400 | 2 | 8 | 1900 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.84 | 6 | 0
2005-06-23 | 1900-06-22 | 8:00 | 8 | 611 | 1322 | 385 | 2 | 8 | 596 | 2 | 15 | 109 | 2 | 8 | 40200 | 2 | 8 | 58000 | 2 | 15 | 13400 | 2 | 8 | 2240 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 984 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.72 | 6 | 0
2005-06-23 | 1900-06-22 | 9:00 | 9 | 832 | 1322 | 567 | 2 | 8 | 714 | 2 | 15 | 117 | 2 | 8 | 59300 | 2 | 8 | 71200 | 2 | 15 | 14400 | 2 | 8 | 2740 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.82 | 6 | 0
2005-06-23 | 1900-06-22 | 10:00 | 10 | 1020 | 1322 | 721 | 2 | 8 | 709 | 2 | 15 | 173 | 2 | 8 | 77000 | 2 | 8 | 72500 | 2 | 15 | 20900 | 2 | 8 | 5760 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.9 | 84.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.12 | 6 | 0
2005-06-23 | 1900-06-22 | 11:00 | 11 | 1161 | 1322 | 842 | 2 | 8 | 748 | 2 | 15 | 184 | 2 | 8 | 87900 | 2 | 8 | 75100 | 2 | 15 | 21800 | 2 | 8 | 8030 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 30 | 86 | A | 7 | 19.4 | 66.92 | A | 7 | 0.53 | A | 7 | 983 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.32 | 6 | 0
2005-06-23 | 1900-06-22 | 12:00 | 12 | 1246 | 1322 | 913 | 2 | 8 | 752 | 2 | 15 | 204 | 2 | 8 | 95300 | 2 | 8 | 75400 | 2 | 15 | 24100 | 2 | 8 | 13000 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 30.6 | 87.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.5 | A | 7 | 980 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.92 | 6 | 0
2005-06-23 | 1900-06-22 | 13:00 | 13 | 1268 | 1322 | 948 | 2 | 8 | 810 | 2 | 15 | 169 | 2 | 8 | 101100 | 2 | 8 | 82000 | 2 | 15 | 22200 | 2 | 8 | 12820 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 31.1 | 87.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.48 | A | 7 | 982 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.42 | 6 | 0
2005-06-23 | 1900-06-22 | 14:00 | 14 | 1227 | 1322 | 904 | 2 | 8 | 772 | 2 | 15 | 186 | 2 | 8 | 95000 | 2 | 8 | 77700 | 2 | 15 | 22700 | 2 | 8 | 10850 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 31.7 | 89.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.45 | A | 7 | 982 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.74 | 6 | 0
2005-06-23 | 1900-06-22 | 15:00 | 15 | 1125 | 1322 | 813 | 2 | 8 | 734 | 2 | 15 | 187 | 2 | 8 | 87300 | 2 | 8 | 75400 | 2 | 15 | 23100 | 2 | 8 | 8060 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 31.7 | 89.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.45 | A | 7 | 979 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.74 | 6 | 0
2005-06-23 | 1900-06-22 | 16:00 | 16 | 969 | 1322 | 665 | 2 | 8 | 666 | 2 | 15 | 177 | 2 | 8 | 70600 | 2 | 8 | 67800 | 2 | 15 | 20800 | 2 | 8 | 5310 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 31.7 | 89.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.47 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.12 | 6 | 0
2005-06-23 | 1900-06-22 | 17:00 | 17 | 770 | 1322 | 496 | 2 | 8 | 607 | 2 | 15 | 142 | 2 | 8 | 52100 | 2 | 8 | 60800 | 2 | 15 | 16600 | 2 | 8 | 3280 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 30.6 | 87.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.48 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.54 | 6 | 0
2005-06-23 | 1900-06-22 | 18:00 | 18 | 541 | 1322 | 292 | 2 | 8 | 377 | 2 | 15 | 138 | 2 | 8 | 30700 | 2 | 8 | 36300 | 2 | 15 | 15800 | 2 | 8 | 2720 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.51 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.24 | 6 | 0
2005-06-23 | 1900-06-22 | 19:00 | 19 | 298 | 1322 | 123 | 2 | 8 | 176 | 2 | 15 | 83 | 2 | 8 | 13000 | 2 | 8 | 14000 | 2 | 15 | 9800 | 2 | 8 | 1600 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.82 | 6 | 0
2005-06-23 | 1900-06-22 | 20:00 | 20 | 68 | 1047 | 10 | 2 | 8 | 4 | 2 | 15 | 10 | 2 | 8 | 1100 | 2 | 8 | 200 | 2 | 15 | 1100 | 2 | 8 | 260 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.64 | 6 | 0
2005-06-23 | 1900-06-22 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.94 | 6 | 0
2005-06-23 | 1900-06-22 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.84 | 6 | 0
2005-06-23 | 1900-06-22 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.54 | 6 | 0
2005-06-23 | 1900-06-22 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.84 | 6 | 0
2005-06-24 | 1900-06-23 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.44 | 7 | 0
2005-06-24 | 1900-06-23 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.64 | 7 | 0
2005-06-24 | 1900-06-23 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.44 | 7 | 0
2005-06-24 | 1900-06-23 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.64 | 7 | 0
2005-06-24 | 1900-06-23 | 5:00 | 5 | 1 | 121 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.44 | 7 | 0
2005-06-24 | 1900-06-23 | 6:00 | 6 | 129 | 1322 | 33 | 2 | 8 | 0 | 2 | 15 | 33 | 2 | 8 | 3700 | 2 | 8 | 0 | 2 | 15 | 3700 | 2 | 8 | 1080 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.84 | 7 | 0
2005-06-24 | 1900-06-23 | 7:00 | 7 | 369 | 1322 | 196 | 2 | 8 | 340 | 2 | 15 | 101 | 2 | 8 | 20300 | 2 | 8 | 29200 | 2 | 15 | 12100 | 2 | 8 | 1900 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.92 | 7 | 0
2005-06-24 | 1900-06-23 | 8:00 | 8 | 610 | 1322 | 364 | 2 | 8 | 497 | 2 | 15 | 135 | 2 | 8 | 39000 | 2 | 8 | 49200 | 2 | 15 | 16300 | 2 | 8 | 2720 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.64 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.02 | 7 | 0
2005-06-24 | 1900-06-23 | 9:00 | 9 | 831 | 1322 | 534 | 2 | 8 | 555 | 2 | 15 | 185 | 2 | 8 | 57800 | 2 | 8 | 57200 | 2 | 15 | 21700 | 2 | 8 | 4500 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.3 | 82.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.82 | 7 | 0
2005-06-24 | 1900-06-23 | 10:00 | 10 | 1019 | 1322 | 715 | 2 | 8 | 654 | 2 | 15 | 209 | 2 | 8 | 75200 | 2 | 8 | 66300 | 2 | 15 | 24000 | 2 | 8 | 6810 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 30 | 86 | A | 7 | 20 | 68 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.8 | 7 | 0
2005-06-24 | 1900-06-23 | 11:00 | 11 | 1161 | 1322 | 848 | 2 | 8 | 754 | 2 | 15 | 185 | 2 | 8 | 88400 | 2 | 8 | 75600 | 2 | 15 | 21900 | 2 | 8 | 8050 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.38 | 7 | 0
2005-06-24 | 1900-06-23 | 12:00 | 12 | 1245 | 1322 | 926 | 2 | 8 | 794 | 2 | 15 | 176 | 2 | 8 | 98100 | 2 | 8 | 80200 | 2 | 15 | 22300 | 2 | 8 | 11460 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 32.8 | 91.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.49 | A | 7 | 979 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.08 | 7 | 0
2005-06-24 | 1900-06-23 | 13:00 | 13 | 1268 | 1322 | 960 | 2 | 8 | 852 | 2 | 15 | 141 | 2 | 8 | 98300 | 2 | 8 | 85400 | 2 | 15 | 16200 | 2 | 8 | 8890 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 32.8 | 91.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.45 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.32 | 7 | 0
2005-06-24 | 1900-06-23 | 14:00 | 14 | 1227 | 1322 | 916 | 2 | 8 | 814 | 2 | 15 | 159 | 2 | 8 | 97900 | 2 | 8 | 82500 | 2 | 15 | 21100 | 2 | 8 | 9510 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 33.3 | 91.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.44 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.12 | 7 | 0
2005-06-24 | 1900-06-23 | 15:00 | 15 | 1125 | 1322 | 807 | 2 | 8 | 716 | 2 | 15 | 197 | 2 | 8 | 86500 | 2 | 8 | 73300 | 2 | 15 | 23900 | 2 | 8 | 8470 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 33.9 | 93.02 | A | 7 | 20 | 68 | A | 7 | 0.44 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.9 | 7 | 0
2005-06-24 | 1900-06-23 | 16:00 | 16 | 969 | 1322 | 665 | 2 | 8 | 660 | 2 | 15 | 181 | 2 | 8 | 70500 | 2 | 8 | 67100 | 2 | 15 | 21200 | 2 | 8 | 5420 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 33.3 | 91.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.43 | A | 7 | 980 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.12 | 7 | 0
2005-06-24 | 1900-06-23 | 17:00 | 17 | 770 | 1322 | 491 | 2 | 8 | 590 | 2 | 15 | 147 | 2 | 8 | 51500 | 2 | 8 | 59000 | 2 | 15 | 17100 | 2 | 8 | 3380 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 32.2 | 89.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.47 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.82 | 7 | 0
2005-06-24 | 1900-06-23 | 18:00 | 18 | 541 | 1322 | 298 | 2 | 8 | 406 | 2 | 15 | 131 | 2 | 8 | 31400 | 2 | 8 | 39200 | 2 | 15 | 15400 | 2 | 8 | 2570 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 20 | 68 | A | 7 | 0.52 | A | 7 | 977 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57 | 7 | 0
2005-06-24 | 1900-06-23 | 19:00 | 19 | 299 | 1322 | 123 | 2 | 8 | 176 | 2 | 15 | 83 | 2 | 8 | 13000 | 2 | 8 | 14000 | 2 | 15 | 9800 | 2 | 8 | 1600 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 29.4 | 84.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.55 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.82 | 7 | 0
2005-06-24 | 1900-06-23 | 20:00 | 20 | 68 | 1047 | 8 | 2 | 8 | 0 | 2 | 15 | 8 | 2 | 8 | 1000 | 2 | 8 | 0 | 2 | 15 | 1000 | 2 | 8 | 310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.92 | 7 | 0
2005-06-24 | 1900-06-23 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.92 | 7 | 0
2005-06-24 | 1900-06-23 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.82 | 7 | 0
2005-06-24 | 1900-06-23 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.32 | 7 | 0
2005-06-24 | 1900-06-23 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | E | 9 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.8 | 7 | 0
2005-06-25 | 1900-06-24 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | E | 9 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.32 | 1 | 0
2005-06-25 | 1900-06-24 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.52 | 1 | 0
2005-06-25 | 1900-06-24 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.52 | 1 | 0
2005-06-25 | 1900-06-24 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.82 | 1 | 0
2005-06-25 | 1900-06-24 | 5:00 | 5 | 1 | 99 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.62 | 1 | 0
2005-06-25 | 1900-06-24 | 6:00 | 6 | 128 | 1322 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 2 | E | 9 | 2 | E | 9 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.52 | 1 | 0
2005-06-25 | 1900-06-24 | 7:00 | 7 | 368 | 1322 | 204 | 2 | 8 | 353 | 2 | 15 | 106 | 2 | 8 | 21000 | 2 | 8 | 30300 | 2 | 15 | 12600 | 2 | 8 | 2010 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 6096 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.22 | 1 | 0
2005-06-25 | 1900-06-24 | 8:00 | 8 | 608 | 1322 | 364 | 2 | 8 | 497 | 2 | 15 | 136 | 2 | 8 | 39000 | 2 | 8 | 49200 | 2 | 15 | 16300 | 2 | 8 | 2740 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 6096 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.7 | 1 | 0
2005-06-25 | 1900-06-24 | 9:00 | 9 | 830 | 1322 | 548 | 2 | 8 | 616 | 2 | 15 | 160 | 2 | 8 | 57500 | 2 | 8 | 61900 | 2 | 15 | 18500 | 2 | 8 | 3910 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 28.9 | 84.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 6096 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.18 | 1 | 0
2005-06-25 | 1900-06-24 | 10:00 | 10 | 1018 | 1322 | 708 | 2 | 8 | 666 | 2 | 15 | 194 | 2 | 8 | 75000 | 2 | 8 | 67800 | 2 | 15 | 22700 | 2 | 8 | 6370 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 6096 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.98 | 1 | 0
2005-06-25 | 1900-06-24 | 11:00 | 11 | 1160 | 1322 | 830 | 2 | 8 | 712 | 2 | 15 | 204 | 2 | 8 | 88900 | 2 | 8 | 73000 | 2 | 15 | 24800 | 2 | 8 | 9780 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 31.7 | 89.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.52 | A | 7 | 983 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.88 | 1 | 0
2005-06-25 | 1900-06-24 | 12:00 | 12 | 1245 | 1322 | 914 | 2 | 8 | 752 | 2 | 15 | 204 | 2 | 8 | 95300 | 2 | 8 | 75400 | 2 | 15 | 24100 | 2 | 8 | 12950 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 32.2 | 89.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.5 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.38 | 1 | 0
2005-06-25 | 1900-06-24 | 13:00 | 13 | 1268 | 1322 | 936 | 2 | 8 | 750 | 2 | 15 | 215 | 2 | 8 | 101000 | 2 | 8 | 77100 | 2 | 15 | 26900 | 2 | 8 | 17140 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 33.3 | 91.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.47 | A | 7 | 982 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.58 | 1 | 0
2005-06-25 | 1900-06-24 | 14:00 | 14 | 1227 | 1322 | 851 | 2 | 8 | 640 | 2 | 15 | 255 | 2 | 8 | 90300 | 2 | 8 | 65100 | 2 | 15 | 29700 | 2 | 8 | 15910 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 33.3 | 91.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.44 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.12 | 1 | 0
2005-06-25 | 1900-06-24 | 15:00 | 15 | 1125 | 1322 | 778 | 2 | 8 | 633 | 2 | 15 | 239 | 2 | 8 | 82200 | 2 | 8 | 64200 | 2 | 15 | 27400 | 2 | 8 | 10110 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 33.9 | 93.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.41 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 52.62 | 1 | 0
2005-06-25 | 1900-06-24 | 16:00 | 16 | 970 | 1322 | 671 | 2 | 8 | 677 | 2 | 15 | 173 | 2 | 8 | 71200 | 2 | 8 | 69000 | 2 | 15 | 20500 | 2 | 8 | 5220 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 33.3 | 91.94 | A | 7 | 20 | 68 | A | 7 | 0.46 | A | 7 | 981 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.5 | 1 | 0
2005-06-25 | 1900-06-24 | 17:00 | 17 | 771 | 1322 | 480 | 2 | 8 | 537 | 2 | 15 | 167 | 2 | 8 | 51900 | 2 | 8 | 55000 | 2 | 15 | 19800 | 2 | 8 | 3800 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 32.2 | 89.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.5 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.38 | 1 | 0
2005-06-25 | 1900-06-24 | 18:00 | 18 | 542 | 1322 | 282 | 2 | 8 | 324 | 2 | 15 | 149 | 2 | 8 | 30200 | 2 | 8 | 32200 | 2 | 15 | 17000 | 2 | 8 | 3100 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.48 | 1 | 0
2005-06-25 | 1900-06-24 | 19:00 | 19 | 299 | 1322 | 118 | 2 | 8 | 170 | 2 | 15 | 80 | 2 | 8 | 12600 | 2 | 8 | 13600 | 2 | 15 | 9500 | 2 | 8 | 1530 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.48 | 1 | 0
2005-06-25 | 1900-06-24 | 20:00 | 20 | 69 | 1047 | 6 | 2 | 8 | 0 | 2 | 15 | 6 | 2 | 8 | 700 | 2 | 8 | 0 | 2 | 15 | 700 | 2 | 8 | 240 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.7 | 1 | 0
2005-06-25 | 1900-06-24 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.6 | 1 | 0
2005-06-25 | 1900-06-24 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.8 | 1 | 0
2005-06-25 | 1900-06-24 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.1 | 1 | 0
2005-06-25 | 1900-06-24 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.1 | 1 | 0
2005-06-26 | 1900-06-25 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.42 | 2 | 0
2005-06-26 | 1900-06-25 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.62 | 2 | 0
2005-06-26 | 1900-06-25 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.52 | 2 | 0
2005-06-26 | 1900-06-25 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.32 | 2 | 0
2005-06-26 | 1900-06-25 | 5:00 | 5 | 1 | 99 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.64 | 2 | 0
2005-06-26 | 1900-06-25 | 6:00 | 6 | 126 | 1322 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 20 | 68 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.2 | 2 | 0
2005-06-26 | 1900-06-25 | 7:00 | 7 | 367 | 1322 | 212 | 2 | 8 | 445 | 2 | 15 | 89 | 2 | 8 | 22200 | 2 | 8 | 38200 | 2 | 15 | 11600 | 2 | 8 | 1650 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 20.6 | 69.08 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.98 | 2 | 0
2005-06-26 | 1900-06-25 | 8:00 | 8 | 607 | 1322 | 371 | 2 | 8 | 534 | 2 | 15 | 126 | 2 | 8 | 40000 | 2 | 8 | 52900 | 2 | 15 | 15700 | 2 | 8 | 2520 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 983 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.18 | 2 | 0
2005-06-26 | 1900-06-25 | 9:00 | 9 | 829 | 1322 | 554 | 2 | 8 | 678 | 2 | 15 | 128 | 2 | 8 | 59100 | 2 | 8 | 68800 | 2 | 15 | 15800 | 2 | 8 | 3220 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 29.4 | 84.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.59 | A | 7 | 980 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.68 | 2 | 0
2005-06-26 | 1900-06-25 | 10:00 | 10 | 1017 | 1322 | 715 | 2 | 8 | 690 | 2 | 15 | 182 | 2 | 8 | 76000 | 2 | 8 | 70400 | 2 | 15 | 21700 | 2 | 8 | 6000 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 30.6 | 87.08 | A | 7 | 20 | 68 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.3 | 2 | 0
2005-06-26 | 1900-06-25 | 11:00 | 11 | 1159 | 1322 | 842 | 2 | 8 | 754 | 2 | 15 | 180 | 2 | 8 | 88100 | 2 | 8 | 75700 | 2 | 15 | 21500 | 2 | 8 | 7840 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 31.7 | 89.06 | A | 7 | 20 | 68 | A | 7 | 0.5 | A | 7 | 982 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.5 | 2 | 0
2005-06-26 | 1900-06-25 | 12:00 | 12 | 1244 | 1322 | 914 | 2 | 8 | 740 | 2 | 15 | 216 | 2 | 8 | 98400 | 2 | 8 | 76000 | 2 | 15 | 26800 | 2 | 8 | 14900 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 32.2 | 89.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.47 | A | 7 | 980 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.82 | 2 | 0
2005-06-26 | 1900-06-25 | 13:00 | 13 | 1268 | 1322 | 870 | 2 | 8 | 594 | 2 | 15 | 299 | 2 | 8 | 91700 | 2 | 8 | 60000 | 2 | 15 | 34000 | 2 | 8 | 23440 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 32.8 | 91.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.45 | A | 7 | 982 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.32 | 2 | 0
2005-06-26 | 1900-06-25 | 14:00 | 14 | 1227 | 1322 | 904 | 2 | 8 | 730 | 2 | 15 | 225 | 2 | 8 | 96900 | 2 | 8 | 74700 | 2 | 15 | 27400 | 2 | 8 | 14140 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 33.3 | 91.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.41 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.74 | 2 | 0
2005-06-26 | 1900-06-25 | 15:00 | 15 | 1125 | 1322 | 802 | 2 | 8 | 692 | 2 | 15 | 211 | 2 | 8 | 85400 | 2 | 8 | 70700 | 2 | 15 | 25100 | 2 | 8 | 9030 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 33.9 | 93.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.4 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.54 | 2 | 0
2005-06-26 | 1900-06-25 | 16:00 | 16 | 970 | 1322 | 648 | 2 | 8 | 630 | 2 | 15 | 185 | 2 | 8 | 68500 | 2 | 8 | 64000 | 2 | 15 | 21500 | 2 | 8 | 5540 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 33.9 | 93.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.4 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.54 | 2 | 0
2005-06-26 | 1900-06-25 | 17:00 | 17 | 771 | 1322 | 485 | 2 | 8 | 560 | 2 | 15 | 158 | 2 | 8 | 50600 | 2 | 8 | 55800 | 2 | 15 | 18000 | 2 | 8 | 3590 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 33.3 | 91.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.43 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.12 | 2 | 0
2005-06-26 | 1900-06-25 | 18:00 | 18 | 542 | 1322 | 272 | 2 | 8 | 238 | 2 | 15 | 174 | 2 | 8 | 28800 | 2 | 8 | 23600 | 2 | 15 | 19100 | 2 | 8 | 3740 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 31.7 | 89.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.48 | A | 7 | 977 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.12 | 2 | 0
2005-06-26 | 1900-06-25 | 19:00 | 19 | 300 | 1322 | 114 | 2 | 8 | 143 | 2 | 15 | 82 | 2 | 8 | 12500 | 2 | 8 | 11800 | 2 | 15 | 9800 | 2 | 8 | 1780 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 29.4 | 84.92 | A | 7 | 20 | 68 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.3 | 2 | 0
2005-06-26 | 1900-06-25 | 20:00 | 20 | 69 | 1046 | 6 | 2 | 8 | 0 | 2 | 15 | 6 | 2 | 8 | 700 | 2 | 8 | 0 | 2 | 15 | 700 | 2 | 8 | 240 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.12 | 2 | 0
2005-06-26 | 1900-06-25 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.52 | 2 | 0
2005-06-26 | 1900-06-25 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 27.8 | 82.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.82 | 2 | 0
2005-06-26 | 1900-06-25 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 26.7 | 80.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.82 | 2 | 0
2005-06-26 | 1900-06-25 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.151 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.62 | 2 | 0
2005-06-27 | 1900-06-26 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.5 | 3 | 0
2005-06-27 | 1900-06-26 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.5 | 3 | 0
2005-06-27 | 1900-06-26 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.92 | 3 | 0
2005-06-27 | 1900-06-26 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.92 | 3 | 0
2005-06-27 | 1900-06-26 | 5:00 | 5 | 0 | 99 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.72 | 3 | 0
2005-06-27 | 1900-06-26 | 6:00 | 6 | 125 | 1322 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 979 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.82 | 3 | 0
2005-06-27 | 1900-06-26 | 7:00 | 7 | 365 | 1322 | 204 | 2 | 8 | 399 | 2 | 15 | 94 | 2 | 8 | 21300 | 2 | 8 | 34200 | 2 | 15 | 11800 | 2 | 8 | 1750 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.6 | 3 | 0
2005-06-27 | 1900-06-26 | 8:00 | 8 | 606 | 1322 | 358 | 2 | 8 | 478 | 2 | 15 | 138 | 2 | 8 | 38100 | 2 | 8 | 47200 | 2 | 15 | 16400 | 2 | 8 | 2780 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.68 | 3 | 0
2005-06-27 | 1900-06-26 | 9:00 | 9 | 828 | 1322 | 541 | 2 | 8 | 598 | 2 | 15 | 166 | 2 | 8 | 56600 | 2 | 8 | 60000 | 2 | 15 | 19000 | 2 | 8 | 4030 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 29.4 | 84.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.68 | 3 | 0
2005-06-27 | 1900-06-26 | 10:00 | 10 | 1016 | 1322 | 709 | 2 | 8 | 672 | 2 | 15 | 190 | 2 | 8 | 75100 | 2 | 8 | 68400 | 2 | 15 | 22300 | 2 | 8 | 6220 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.38 | 3 | 0
2005-06-27 | 1900-06-26 | 11:00 | 11 | 1158 | 1322 | 842 | 2 | 8 | 742 | 2 | 15 | 191 | 2 | 8 | 90700 | 2 | 8 | 76200 | 2 | 15 | 23700 | 2 | 8 | 9160 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 32.2 | 89.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.5 | A | 7 | 981 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.38 | 3 | 0
2005-06-27 | 1900-06-26 | 12:00 | 12 | 1244 | 1322 | 926 | 2 | 8 | 800 | 2 | 15 | 172 | 2 | 8 | 98400 | 2 | 8 | 80900 | 2 | 15 | 22100 | 2 | 8 | 11160 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 33.9 | 93.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.46 | A | 7 | 979 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.28 | 3 | 0
2005-06-27 | 1900-06-26 | 13:00 | 13 | 1267 | 1322 | 948 | 2 | 8 | 810 | 2 | 15 | 170 | 2 | 8 | 101100 | 2 | 8 | 82000 | 2 | 15 | 22300 | 2 | 8 | 12820 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 33.9 | 93.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.43 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.82 | 3 | 0
2005-06-27 | 1900-06-26 | 14:00 | 14 | 1227 | 1322 | 916 | 2 | 8 | 802 | 2 | 15 | 170 | 2 | 8 | 97200 | 2 | 8 | 81100 | 2 | 15 | 21800 | 2 | 8 | 10070 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 34.4 | 93.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.41 | A | 7 | 980 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.32 | 3 | 0
2005-06-27 | 1900-06-26 | 15:00 | 15 | 1126 | 1322 | 784 | 2 | 8 | 639 | 2 | 15 | 239 | 2 | 8 | 82800 | 2 | 8 | 64800 | 2 | 15 | 27500 | 2 | 8 | 10120 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 34.4 | 93.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.41 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.32 | 3 | 0
2005-06-27 | 1900-06-26 | 16:00 | 16 | 970 | 1322 | 660 | 2 | 8 | 695 | 2 | 15 | 148 | 2 | 8 | 70800 | 2 | 8 | 71300 | 2 | 15 | 18400 | 2 | 8 | 4540 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 33.9 | 93.02 | A | 7 | 20 | 68 | A | 7 | 0.44 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.9 | 3 | 0
2005-06-27 | 1900-06-26 | 17:00 | 17 | 771 | 1322 | 496 | 2 | 8 | 607 | 2 | 15 | 141 | 2 | 8 | 52100 | 2 | 8 | 60800 | 2 | 15 | 16600 | 2 | 8 | 3260 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 33.3 | 91.94 | A | 7 | 20 | 68 | A | 7 | 0.46 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 55.5 | 3 | 0
2005-06-27 | 1900-06-26 | 18:00 | 18 | 543 | 1322 | 293 | 2 | 8 | 377 | 2 | 15 | 138 | 2 | 8 | 30800 | 2 | 8 | 36400 | 2 | 15 | 15800 | 2 | 8 | 2720 | 2 | 19 | 8 | E | 9 | 8 | A | 7 | 31.7 | 89.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.18 | 3 | 0
2005-06-27 | 1900-06-26 | 19:00 | 19 | 300 | 1322 | 128 | 2 | 8 | 220 | 2 | 15 | 78 | 2 | 8 | 13600 | 2 | 8 | 17600 | 2 | 15 | 9600 | 2 | 8 | 1480 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.98 | 3 | 0
2005-06-27 | 1900-06-26 | 20:00 | 20 | 69 | 1046 | 8 | 2 | 8 | 0 | 2 | 15 | 8 | 2 | 8 | 1000 | 2 | 8 | 0 | 2 | 15 | 1000 | 2 | 8 | 310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 27.2 | 80.96 | A | 7 | 20 | 68 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.2 | 3 | 0
2005-06-27 | 1900-06-26 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.22 | 3 | 0
2005-06-27 | 1900-06-26 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.22 | 3 | 0
2005-06-27 | 1900-06-26 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.72 | 3 | 0
2005-06-27 | 1900-06-26 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | E | 9 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.6 | 3 | 0
2005-06-28 | 1900-06-27 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.72 | 4 | 0
2005-06-28 | 1900-06-27 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 4 | E | 9 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.6 | 4 | 0
2005-06-28 | 1900-06-27 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 6 | E | 9 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.62 | 4 | 0
2005-06-28 | 1900-06-27 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 4 | E | 9 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 979 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 6096 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.82 | 4 | 0
2005-06-28 | 1900-06-27 | 5:00 | 5 | 0 | 77 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 4 | E | 9 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 9600 | A | 7 | 4267 | A | 7 | 4.3 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.82 | 4 | 0
2005-06-28 | 1900-06-27 | 6:00 | 6 | 124 | 1322 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 2743 | A | 7 | 4.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 64.1 | 4 | 0
2005-06-28 | 1900-06-27 | 7:00 | 7 | 364 | 1322 | 157 | 2 | 8 | 85 | 2 | 15 | 134 | 2 | 8 | 17200 | 2 | 8 | 7700 | 2 | 15 | 15100 | 2 | 8 | 3270 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 3962 | A | 7 | 4.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 67.78 | 4 | 0
2005-06-28 | 1900-06-27 | 8:00 | 8 | 604 | 1322 | 289 | 2 | 8 | 143 | 2 | 15 | 224 | 2 | 8 | 31200 | 2 | 8 | 14400 | 2 | 15 | 24700 | 2 | 8 | 5430 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 23.3 | 73.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 2743 | A | 7 | 4.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 67.08 | 4 | 0
2005-06-28 | 1900-06-27 | 9:00 | 9 | 827 | 1322 | 398 | 2 | 8 | 159 | 2 | 15 | 298 | 2 | 8 | 43300 | 2 | 8 | 16700 | 2 | 15 | 32800 | 2 | 8 | 8260 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 170 | A | 7 | 10.8 | A | 7 | 6400 | A | 7 | 2195 | A | 7 | 4.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 67.78 | 4 | 0
2005-06-28 | 1900-06-27 | 10:00 | 10 | 1015 | 1322 | 506 | 2 | 8 | 151 | 2 | 15 | 390 | 2 | 8 | 55200 | 2 | 8 | 16000 | 2 | 15 | 42900 | 2 | 8 | 13160 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 24 | 75.2 | A | 7 | 18 | 64.4 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 4500 | A | 7 | 4.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.9 | 4 | 0
2005-06-28 | 1900-06-27 | 11:00 | 11 | 1157 | 1322 | 576 | 2 | 8 | 169 | 2 | 15 | 428 | 2 | 8 | 63300 | 2 | 8 | 18000 | 2 | 15 | 47500 | 2 | 8 | 18730 | 2 | 19 | 2 | E | 9 | 1 | E | 9 | 27.2 | 80.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 4.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.68 | 4 | 0
2005-06-28 | 1900-06-27 | 12:00 | 12 | 1243 | 1322 | 621 | 2 | 8 | 210 | 2 | 15 | 423 | 2 | 8 | 68700 | 2 | 8 | 22400 | 2 | 15 | 47500 | 2 | 8 | 24380 | 2 | 19 | 6 | E | 9 | 3 | E | 9 | 28.3 | 82.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 12800 | A | 7 | 7620 | A | 7 | 4.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.82 | 4 | 0
2005-06-28 | 1900-06-27 | 13:00 | 13 | 1267 | 1322 | 636 | 2 | 8 | 216 | 2 | 15 | 428 | 2 | 8 | 70400 | 2 | 8 | 23100 | 2 | 15 | 48200 | 2 | 8 | 27650 | 2 | 19 | 4 | E | 9 | 2 | E | 9 | 30 | 86 | A | 7 | 20.6 | 69.08 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 12800 | A | 7 | 7620 | A | 7 | 4.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.18 | 4 | 0
2005-06-28 | 1900-06-27 | 14:00 | 14 | 1227 | 1322 | 615 | 2 | 8 | 215 | 2 | 15 | 414 | 2 | 8 | 67900 | 2 | 8 | 23000 | 2 | 15 | 46600 | 2 | 8 | 22330 | 2 | 19 | 3 | E | 9 | 2 | E | 9 | 29.4 | 84.92 | A | 7 | 20 | 68 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.3 | 4 | 0
2005-06-28 | 1900-06-27 | 15:00 | 15 | 1126 | 1322 | 558 | 2 | 8 | 167 | 2 | 15 | 415 | 2 | 8 | 61100 | 2 | 8 | 17800 | 2 | 15 | 46000 | 2 | 8 | 16890 | 2 | 19 | 5 | E | 9 | 4 | E | 9 | 28.9 | 84.02 | A | 7 | 20 | 68 | A | 7 | 0.59 | A | 7 | 977 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 7620 | A | 7 | 4.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.8 | 4 | 0
2005-06-28 | 1900-06-27 | 16:00 | 16 | 970 | 1322 | 478 | 2 | 8 | 172 | 2 | 15 | 351 | 2 | 8 | 52200 | 2 | 8 | 18200 | 2 | 15 | 38800 | 2 | 8 | 11180 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 30 | 86 | A | 7 | 20 | 68 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.8 | 4 | 0
2005-06-28 | 1900-06-27 | 17:00 | 17 | 771 | 1322 | 364 | 2 | 8 | 159 | 2 | 15 | 271 | 2 | 8 | 39600 | 2 | 8 | 16600 | 2 | 15 | 29900 | 2 | 8 | 7210 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.98 | 4 | 0
2005-06-28 | 1900-06-27 | 18:00 | 18 | 543 | 1322 | 246 | 2 | 8 | 127 | 2 | 15 | 193 | 2 | 8 | 26500 | 2 | 8 | 12500 | 2 | 15 | 21300 | 2 | 8 | 4550 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 30 | 86 | A | 7 | 22.2 | 71.96 | A | 7 | 0.63 | A | 7 | 976 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.26 | 4 | 0
2005-06-28 | 1900-06-27 | 19:00 | 19 | 300 | 1322 | 114 | 2 | 8 | 88 | 2 | 15 | 94 | 2 | 8 | 12300 | 2 | 8 | 7200 | 2 | 15 | 10700 | 2 | 8 | 2040 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 22.8 | 73.04 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65.44 | 4 | 0
2005-06-28 | 1900-06-27 | 20:00 | 20 | 69 | 1046 | 12 | 2 | 8 | 35 | 2 | 15 | 10 | 2 | 8 | 1400 | 2 | 8 | 1300 | 2 | 15 | 1300 | 2 | 8 | 160 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 22.8 | 73.04 | A | 7 | 0.77 | A | 7 | 978 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 67.74 | 4 | 0
2005-06-28 | 1900-06-27 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.48 | 4 | 0
2005-06-28 | 1900-06-27 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | A | 7 | 26.1 | 78.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.88 | 4 | 0
2005-06-28 | 1900-06-27 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.2 | 4 | 0
2005-06-28 | 1900-06-27 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.6 | 4 | 0
2005-06-29 | 1900-06-28 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.32 | 5 | 0
2005-06-29 | 1900-06-28 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.32 | 5 | 0
2005-06-29 | 1900-06-28 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 7 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 976 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.32 | 5 | 0
2005-06-29 | 1900-06-28 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 9600 | A | 7 | 7620 | A | 7 | 4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.32 | 5 | 0
2005-06-29 | 1900-06-28 | 5:00 | 5 | 0 | 77 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 7620 | A | 7 | 4.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.32 | 5 | 0
2005-06-29 | 1900-06-28 | 6:00 | 6 | 122 | 1322 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 7620 | A | 7 | 4.4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.22 | 5 | 0
2005-06-29 | 1900-06-28 | 7:00 | 7 | 362 | 1322 | 158 | 2 | 8 | 125 | 2 | 15 | 124 | 2 | 8 | 17000 | 2 | 8 | 11000 | 2 | 15 | 14000 | 2 | 8 | 2740 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.64 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 4572 | A | 7 | 4.4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.02 | 5 | 0
2005-06-29 | 1900-06-28 | 8:00 | 8 | 603 | 1322 | 241 | 2 | 8 | 87 | 2 | 15 | 201 | 2 | 8 | 26400 | 2 | 8 | 8600 | 2 | 15 | 22500 | 2 | 8 | 5770 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 27.2 | 80.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 4572 | A | 7 | 4.4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.52 | 5 | 0
2005-06-29 | 1900-06-28 | 9:00 | 9 | 825 | 1322 | 528 | 2 | 8 | 519 | 2 | 15 | 204 | 2 | 8 | 56500 | 2 | 8 | 53400 | 2 | 15 | 23100 | 2 | 8 | 4980 | 2 | 19 | 7 | E | 9 | 7 | A | 7 | 30 | 86 | A | 7 | 19.4 | 66.92 | A | 7 | 0.53 | A | 7 | 976 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 9600 | A | 7 | 7620 | A | 7 | 4.4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.32 | 5 | 0
2005-06-29 | 1900-06-28 | 10:00 | 10 | 1014 | 1322 | 671 | 2 | 8 | 539 | 2 | 15 | 256 | 2 | 8 | 72200 | 2 | 8 | 56200 | 2 | 15 | 29000 | 2 | 8 | 8390 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 30 | 86 | A | 7 | 20 | 68 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 9600 | A | 7 | 7620 | A | 7 | 4.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.8 | 5 | 0
2005-06-29 | 1900-06-28 | 11:00 | 11 | 1157 | 1322 | 527 | 2 | 8 | 145 | 2 | 15 | 400 | 2 | 8 | 58100 | 2 | 8 | 15500 | 2 | 15 | 44500 | 2 | 8 | 17470 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 4.1 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.48 | 5 | 0
2005-06-29 | 1900-06-28 | 12:00 | 12 | 1243 | 1322 | 761 | 2 | 8 | 433 | 2 | 15 | 353 | 2 | 8 | 81900 | 2 | 8 | 45300 | 2 | 15 | 39200 | 2 | 8 | 24590 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 32.2 | 89.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.52 | A | 7 | 975 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.68 | 5 | 0
2005-06-29 | 1900-06-28 | 13:00 | 13 | 1266 | 1322 | 960 | 2 | 8 | 786 | 2 | 15 | 205 | 2 | 8 | 100300 | 2 | 8 | 78900 | 2 | 15 | 24500 | 2 | 8 | 15020 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 33.9 | 93.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.43 | A | 7 | 977 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.82 | 5 | 0
2005-06-29 | 1900-06-28 | 14:00 | 14 | 1227 | 1322 | 904 | 2 | 8 | 736 | 2 | 15 | 219 | 2 | 8 | 97000 | 2 | 8 | 75400 | 2 | 15 | 26800 | 2 | 8 | 13770 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 33.3 | 91.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.43 | A | 7 | 977 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.12 | 5 | 0
2005-06-29 | 1900-06-28 | 15:00 | 15 | 1126 | 1322 | 755 | 2 | 8 | 573 | 2 | 15 | 266 | 2 | 8 | 79100 | 2 | 8 | 57800 | 2 | 15 | 29800 | 2 | 8 | 11150 | 2 | 19 | 7 | E | 9 | 7 | A | 7 | 34.4 | 93.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.39 | A | 7 | 974 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 3.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 51.24 | 5 | 0
2005-06-29 | 1900-06-28 | 16:00 | 16 | 970 | 1322 | 660 | 2 | 8 | 660 | 2 | 15 | 175 | 2 | 8 | 70100 | 2 | 8 | 67200 | 2 | 15 | 20700 | 2 | 8 | 5280 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 34.4 | 93.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.41 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.32 | 5 | 0
2005-06-29 | 1900-06-28 | 17:00 | 17 | 772 | 1322 | 502 | 2 | 8 | 649 | 2 | 15 | 123 | 2 | 8 | 53300 | 2 | 8 | 65400 | 2 | 15 | 15100 | 2 | 8 | 2900 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 33.9 | 93.02 | A | 7 | 20 | 68 | A | 7 | 0.44 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.9 | 5 | 0
2005-06-29 | 1900-06-28 | 18:00 | 18 | 543 | 1322 | 308 | 2 | 8 | 446 | 2 | 15 | 125 | 2 | 8 | 32700 | 2 | 8 | 43100 | 2 | 15 | 15000 | 2 | 8 | 2440 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.45 | A | 7 | 973 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 53.62 | 5 | 0
2005-06-29 | 1900-06-28 | 19:00 | 19 | 300 | 1322 | 137 | 2 | 8 | 313 | 2 | 15 | 66 | 2 | 8 | 14500 | 2 | 8 | 24900 | 2 | 15 | 8800 | 2 | 8 | 1190 | 2 | 19 | 2 | E | 9 | 1 | E | 9 | 30 | 86 | A | 7 | 18.3 | 64.94 | A | 7 | 0.5 | A | 7 | 976 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.04 | 5 | 0
2005-06-29 | 1900-06-28 | 20:00 | 20 | 69 | 1046 | 16 | 2 | 8 | 105 | 2 | 15 | 11 | 2 | 8 | 1900 | 2 | 8 | 5200 | 2 | 15 | 1600 | 2 | 8 | 210 | 2 | 19 | 9 | E | 9 | 5 | E | 9 | 29.4 | 84.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.51 | A | 7 | 976 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 54.24 | 5 | 0
2005-06-29 | 1900-06-28 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 5 | E | 9 | 28.3 | 82.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.57 | A | 7 | 974 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 12800 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.62 | 5 | 0
2005-06-29 | 1900-06-28 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 7 | E | 9 | 28.3 | 82.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 3.3 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.62 | 5 | 0
2005-06-29 | 1900-06-28 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 3 | E | 9 | 27.8 | 82.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.58 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 3.3 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 56.82 | 5 | 0
2005-06-29 | 1900-06-28 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 2 | E | 9 | 26.7 | 80.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.62 | A | 7 | 975 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 3.4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 57.82 | 5 | 0
2005-06-30 | 1900-06-29 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | E | 9 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 300 | A | 7 | 1.5 | A | 7 | 9600 | A | 7 | 7620 | A | 7 | 3.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 58.52 | 6 | 0
2005-06-30 | 1900-06-29 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 9600 | A | 7 | 2896 | A | 7 | 3.7 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.62 | 6 | 0
2005-06-30 | 1900-06-29 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | E | 9 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.22 | 6 | 0
2005-06-30 | 1900-06-29 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 3048 | A | 7 | 4.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 59.82 | 6 | 0
2005-06-30 | 1900-06-29 | 5:00 | 5 | 0 | 55 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 2743 | A | 7 | 4.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 60.52 | 6 | 0
2005-06-30 | 1900-06-29 | 6:00 | 6 | 120 | 1321 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 20 | 68 | A | 7 | 17.2 | 62.96 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 11200 | A | 7 | 1189 | A | 7 | 5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 7 | 1 | A | 7 | 59.76 | 6 | 0
2005-06-30 | 1900-06-29 | 7:00 | 7 | 361 | 1321 | 71 | 2 | 8 | 0 | 2 | 15 | 71 | 2 | 8 | 8200 | 2 | 8 | 0 | 2 | 15 | 8200 | 2 | 8 | 2770 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 11200 | A | 7 | 2438 | A | 7 | 5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 60.14 | 6 | 0
2005-06-30 | 1900-06-29 | 8:00 | 8 | 602 | 1321 | 62 | 2 | 8 | 0 | 2 | 15 | 62 | 2 | 8 | 7600 | 2 | 8 | 0 | 2 | 15 | 7600 | 2 | 8 | 2940 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 19 | 66.2 | A | 7 | 18 | 64.4 | A | 7 | 0.94 | A | 7 | 980 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 1800 | A | 7 | 4.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 63.2 | 6 | 0
2005-06-30 | 1900-06-29 | 9:00 | 9 | 824 | 1321 | 91 | 2 | 8 | 0 | 2 | 15 | 91 | 2 | 8 | 11300 | 2 | 8 | 0 | 2 | 15 | 11300 | 2 | 8 | 4620 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 20 | 68 | A | 7 | 18.3 | 64.94 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 12800 | A | 7 | 2743 | A | 7 | 4.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 2 | 1 | A | 7 | 62.94 | 6 | 0
2005-06-30 | 1900-06-29 | 10:00 | 10 | 1013 | 1321 | 165 | 2 | 8 | 0 | 2 | 15 | 165 | 2 | 8 | 20200 | 2 | 8 | 0 | 2 | 15 | 20200 | 2 | 8 | 8340 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.1 | 69.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 914 | A | 7 | 4.8 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 13 | 1 | A | 7 | 61.64 | 6 | 0
2005-06-30 | 1900-06-29 | 11:00 | 11 | 1156 | 1321 | 167 | 2 | 8 | 0 | 2 | 15 | 167 | 2 | 8 | 20800 | 2 | 8 | 0 | 2 | 15 | 20800 | 2 | 8 | 8630 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 9600 | A | 7 | 1981 | A | 7 | 4.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 13 | 1 | A | 7 | 58.16 | 6 | 0
2005-06-30 | 1900-06-29 | 12:00 | 12 | 1242 | 1321 | 146 | 2 | 8 | 0 | 2 | 15 | 146 | 2 | 8 | 18600 | 2 | 8 | 0 | 2 | 15 | 18600 | 2 | 8 | 7720 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.7 | 71.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 1981 | A | 7 | 4.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 61.04 | 6 | 0
2005-06-30 | 1900-06-29 | 13:00 | 13 | 1266 | 1321 | 162 | 2 | 8 | 0 | 2 | 15 | 162 | 2 | 8 | 20500 | 2 | 8 | 0 | 2 | 15 | 20500 | 2 | 8 | 8490 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 914 | A | 7 | 4.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 4 | 1 | A | 7 | 63.92 | 6 | 0
2005-06-30 | 1900-06-29 | 14:00 | 14 | 1226 | 1321 | 148 | 2 | 8 | 0 | 2 | 15 | 148 | 2 | 8 | 18800 | 2 | 8 | 0 | 2 | 15 | 18800 | 2 | 8 | 7810 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 1067 | A | 7 | 4.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 22 | 1 | A | 7 | 59.08 | 6 | 0
2005-06-30 | 1900-06-29 | 15:00 | 15 | 1125 | 1321 | 134 | 2 | 8 | 0 | 2 | 15 | 134 | 2 | 8 | 16900 | 2 | 8 | 0 | 2 | 15 | 16900 | 2 | 8 | 7080 | 2 | 19 | 10 | E | 9 | 8 | E | 9 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 2286 | A | 7 | 4.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 3 | 1 | A | 7 | 60.96 | 6 | 0
2005-06-30 | 1900-06-29 | 16:00 | 16 | 970 | 1321 | 108 | 2 | 8 | 0 | 2 | 15 | 108 | 2 | 8 | 13600 | 2 | 8 | 0 | 2 | 15 | 13600 | 2 | 8 | 5670 | 2 | 19 | 9 | E | 9 | 6 | E | 9 | 20 | 68 | A | 7 | 17.2 | 62.96 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 4.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 1 | 1 | A | 7 | 59.76 | 6 | 0
2005-06-30 | 1900-06-29 | 17:00 | 17 | 772 | 1321 | 83 | 2 | 8 | 0 | 2 | 15 | 83 | 2 | 8 | 10300 | 2 | 8 | 0 | 2 | 15 | 10300 | 2 | 8 | 4150 | 2 | 19 | 8 | E | 9 | 5 | E | 9 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 4.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.04 | 6 | 0
2005-06-30 | 1900-06-29 | 18:00 | 18 | 543 | 1321 | 52 | 2 | 8 | 0 | 2 | 15 | 52 | 2 | 8 | 6400 | 2 | 8 | 0 | 2 | 15 | 6400 | 2 | 8 | 2430 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 4.6 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.54 | 6 | 0
2005-06-30 | 1900-06-29 | 19:00 | 19 | 300 | 1321 | 41 | 2 | 8 | 0 | 2 | 15 | 41 | 2 | 8 | 4800 | 2 | 8 | 0 | 2 | 15 | 4800 | 2 | 8 | 1660 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 240 | A | 7 | 1.5 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 4.4 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.64 | 6 | 0
2005-06-30 | 1900-06-29 | 20:00 | 20 | 69 | 1046 | 10 | 2 | 8 | 4 | 2 | 15 | 10 | 2 | 8 | 1100 | 2 | 8 | 200 | 2 | 15 | 1100 | 2 | 8 | 260 | 2 | 19 | 7 | E | 9 | 4 | E | 9 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 3962 | A | 7 | 4.1 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.54 | 6 | 0
2005-06-30 | 1900-06-29 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 2 | E | 9 | 18.9 | 66.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.8 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 62.64 | 6 | 0
2005-06-30 | 1900-06-29 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 2 | E | 9 | 19.5 | 67.1 | A | 7 | 18.4 | 65.12 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 270 | A | 7 | 0.4 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.5 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.72 | 6 | 0
2005-06-30 | 1900-06-29 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 2 | E | 9 | 20.2 | 68.36 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 240 | A | 7 | 0.9 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 63.92 | 6 | 0
2005-06-30 | 1900-06-29 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 2 | E | 9 | 20.8 | 69.44 | A | 7 | 19.5 | 67.1 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 0 | A | 7 | 1.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | 0.152 | F | 8 | 0.19 | F | 8 | 0 | 1 | A | 7 | 65 | 6 | 0
1990-07-01 | 1900-06-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 21.4 | 70.52 | A | 7 | 20 | 68 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 0 | A | 7 | 1.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.8 | 7 | 0
1990-07-01 | 1900-06-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 22 | 71.6 | A | 7 | 20.6 | 69.08 | A | 7 | 0.94 | A | 7 | 979 | A | 7 | 110 | A | 7 | 2.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.78 | 7 | 0
1990-07-01 | 1900-06-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 22.7 | 72.86 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 120 | A | 7 | 2.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.08 | 7 | 0
1990-07-01 | 1900-06-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.86 | 7 | 0
1990-07-01 | 1900-06-30 | 5:00 | 5 | 0 | 55 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 3 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.18 | 7 | 0
1990-07-01 | 1900-06-30 | 6:00 | 6 | 120 | 1321 | 25 | 1 | 13 | 25 | 1 | 13 | 23 | 1 | 13 | 2800 | 1 | 13 | 1300 | 1 | 13 | 2700 | 1 | 13 | 480 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.16 | 7 | 0
1990-07-01 | 1900-06-30 | 7:00 | 7 | 360 | 1321 | 156 | 1 | 9 | 253 | 1 | 9 | 87 | 1 | 13 | 16700 | 1 | 9 | 22000 | 1 | 9 | 10700 | 1 | 13 | 1660 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 21.7 | 71.06 | A | 7 | 0.79 | A | 7 | 979 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.36 | 7 | 0
1990-07-01 | 1900-06-30 | 8:00 | 8 | 601 | 1321 | 359 | 1 | 9 | 503 | 1 | 9 | 129 | 1 | 13 | 38400 | 1 | 9 | 49700 | 1 | 9 | 15800 | 1 | 13 | 2580 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 7 | 0
1990-07-01 | 1900-06-30 | 9:00 | 9 | 823 | 1321 | 553 | 1 | 9 | 617 | 1 | 9 | 167 | 1 | 13 | 57700 | 1 | 9 | 61800 | 1 | 9 | 19100 | 1 | 13 | 4020 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 21.7 | 71.06 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.96 | 7 | 0
1990-07-01 | 1900-06-30 | 10:00 | 10 | 1013 | 1321 | 718 | 1 | 9 | 682 | 1 | 9 | 194 | 1 | 13 | 76000 | 1 | 9 | 69400 | 1 | 9 | 22700 | 1 | 13 | 6290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 22.8 | 73.04 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.14 | 7 | 0
1990-07-01 | 1900-06-30 | 11:00 | 11 | 1155 | 1321 | 847 | 1 | 9 | 723 | 1 | 9 | 213 | 1 | 13 | 90400 | 1 | 9 | 73900 | 1 | 9 | 25600 | 1 | 13 | 10040 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.7 | 89.06 | A | 7 | 22.8 | 73.04 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.14 | 7 | 0
1990-07-01 | 1900-06-30 | 12:00 | 12 | 1242 | 1321 | 929 | 1 | 9 | 749 | 1 | 9 | 223 | 1 | 13 | 99700 | 1 | 9 | 76800 | 1 | 9 | 27400 | 1 | 13 | 15160 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 23.9 | 75.02 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.32 | 7 | 0
1990-07-01 | 1900-06-30 | 13:00 | 13 | 1266 | 1321 | 947 | 1 | 9 | 751 | 1 | 9 | 226 | 1 | 13 | 101800 | 1 | 9 | 77000 | 1 | 9 | 27900 | 1 | 13 | 17780 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.3 | 91.94 | A | 7 | 23.9 | 75.02 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 7 | 0
1990-07-01 | 1900-06-30 | 14:00 | 14 | 1226 | 1321 | 870 | 1 | 9 | 658 | 1 | 9 | 257 | 1 | 13 | 92200 | 1 | 9 | 66900 | 1 | 9 | 30000 | 1 | 13 | 15980 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 33.3 | 91.94 | A | 7 | 23.9 | 75.02 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 7 | 0
1990-07-01 | 1900-06-30 | 15:00 | 15 | 1125 | 1321 | 767 | 1 | 13 | 574 | 1 | 13 | 277 | 1 | 13 | 83200 | 1 | 13 | 60100 | 1 | 13 | 32000 | 1 | 13 | 11960 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 33.9 | 93.02 | A | 7 | 23.9 | 75.02 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.02 | 7 | 0
1990-07-01 | 1900-06-30 | 16:00 | 16 | 970 | 1321 | 648 | 1 | 9 | 605 | 1 | 9 | 203 | 1 | 13 | 68000 | 1 | 9 | 61100 | 1 | 9 | 23000 | 1 | 13 | 6010 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 32.8 | 91.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.58 | A | 7 | 978 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.64 | 7 | 0
1990-07-01 | 1900-06-30 | 17:00 | 17 | 771 | 1321 | 497 | 1 | 9 | 582 | 1 | 9 | 157 | 1 | 13 | 51900 | 1 | 9 | 58000 | 1 | 9 | 17900 | 1 | 13 | 3580 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.3 | 91.94 | A | 7 | 23.3 | 73.94 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.04 | 7 | 0
1990-07-01 | 1900-06-30 | 18:00 | 18 | 543 | 1321 | 310 | 1 | 9 | 468 | 1 | 9 | 118 | 1 | 13 | 33100 | 1 | 9 | 45200 | 1 | 9 | 14500 | 1 | 13 | 2290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.58 | A | 7 | 978 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.64 | 7 | 0
1990-07-01 | 1900-06-30 | 19:00 | 19 | 300 | 1321 | 129 | 1 | 13 | 249 | 1 | 9 | 72 | 1 | 13 | 13400 | 1 | 13 | 19700 | 1 | 9 | 8900 | 1 | 13 | 1310 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 23.3 | 73.94 | A | 7 | 0.63 | A | 7 | 977 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.94 | 7 | 0
1990-07-01 | 1900-06-30 | 20:00 | 20 | 68 | 1046 | 24 | 1 | 13 | 17 | 1 | 9 | 22 | 1 | 13 | 2500 | 1 | 13 | 1000 | 1 | 9 | 2500 | 1 | 13 | 530 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 23.9 | 75.02 | A | 7 | 0.72 | A | 7 | 977 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.243 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.22 | 7 | 0
1990-07-01 | 1900-06-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 23.9 | 75.02 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.52 | 7 | 0
1990-07-01 | 1900-06-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 23.9 | 75.02 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.02 | 7 | 0
1990-07-01 | 1900-06-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.54 | 7 | 0
1990-07-01 | 1900-06-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 27.2 | 80.96 | A | 7 | 22.8 | 73.04 | A | 7 | 0.77 | A | 7 | 978 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.74 | 7 | 0
1990-07-02 | 1900-07-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 22.8 | 73.04 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.14 | 1 | 0
1990-07-02 | 1900-07-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.94 | 1 | 0
1990-07-02 | 1900-07-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.94 | 1 | 0
1990-07-02 | 1900-07-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 25 | 77 | A | 7 | 22.8 | 73.04 | A | 7 | 0.88 | A | 7 | 977 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.34 | 1 | 0
1990-07-02 | 1900-07-01 | 5:00 | 5 | 0 | 55 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 22.8 | 73.04 | A | 7 | 0.85 | A | 7 | 977 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.64 | 1 | 0
1990-07-02 | 1900-07-01 | 6:00 | 6 | 118 | 1321 | 35 | 1 | 13 | 31 | 1 | 13 | 32 | 1 | 13 | 3800 | 1 | 13 | 1900 | 1 | 13 | 3600 | 1 | 13 | 750 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.86 | 1 | 0
1990-07-02 | 1900-07-01 | 7:00 | 7 | 358 | 1321 | 168 | 1 | 13 | 321 | 1 | 13 | 80 | 1 | 13 | 17600 | 1 | 13 | 27400 | 1 | 13 | 10200 | 1 | 13 | 1460 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 977 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.66 | 1 | 0
1990-07-02 | 1900-07-01 | 8:00 | 8 | 599 | 1321 | 336 | 1 | 13 | 520 | 1 | 13 | 99 | 1 | 13 | 35200 | 1 | 13 | 50700 | 1 | 13 | 12200 | 1 | 13 | 2050 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.98 | 1 | 0
1990-07-02 | 1900-07-01 | 9:00 | 9 | 822 | 1321 | 431 | 1 | 13 | 414 | 1 | 13 | 172 | 1 | 13 | 46700 | 1 | 13 | 42700 | 1 | 13 | 20100 | 1 | 13 | 4120 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 30 | 86 | A | 7 | 21.1 | 69.98 | A | 7 | 0.59 | A | 7 | 977 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.48 | 1 | 0
1990-07-02 | 1900-07-01 | 10:00 | 10 | 1011 | 1321 | 753 | 1 | 9 | 868 | 1 | 9 | 87 | 1 | 13 | 78300 | 1 | 9 | 86900 | 1 | 9 | 11700 | 1 | 13 | 2650 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 1 | 0
1990-07-02 | 1900-07-01 | 11:00 | 11 | 1154 | 1321 | 850 | 1 | 9 | 862 | 1 | 9 | 94 | 1 | 13 | 88000 | 1 | 9 | 86500 | 1 | 9 | 12300 | 1 | 13 | 3920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 1 | 0
1990-07-02 | 1900-07-01 | 12:00 | 12 | 1241 | 1321 | 904 | 1 | 9 | 846 | 1 | 9 | 107 | 1 | 13 | 93300 | 1 | 9 | 85000 | 1 | 9 | 13300 | 1 | 13 | 6130 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 34.4 | 93.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.49 | A | 7 | 976 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 1 | 0
1990-07-02 | 1900-07-01 | 13:00 | 13 | 1265 | 1321 | 944 | 1 | 9 | 883 | 1 | 9 | 96 | 1 | 13 | 97700 | 1 | 9 | 88800 | 1 | 9 | 12500 | 1 | 13 | 6500 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 35 | 95 | A | 7 | 22.2 | 71.96 | A | 7 | 0.48 | A | 7 | 976 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.16 | 1 | 0
1990-07-02 | 1900-07-01 | 14:00 | 14 | 1226 | 1321 | 809 | 1 | 13 | 691 | 1 | 13 | 166 | 1 | 13 | 86000 | 1 | 13 | 69900 | 1 | 13 | 21000 | 1 | 13 | 9830 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 36.7 | 98.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.42 | A | 7 | 975 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.76 | 1 | 0
1990-07-02 | 1900-07-01 | 15:00 | 15 | 1125 | 1321 | 789 | 1 | 9 | 791 | 1 | 9 | 114 | 1 | 13 | 81400 | 1 | 9 | 79300 | 1 | 9 | 13800 | 1 | 13 | 4030 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 36.7 | 98.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.42 | A | 7 | 975 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.76 | 1 | 0
1990-07-02 | 1900-07-01 | 16:00 | 16 | 970 | 1321 | 706 | 1 | 9 | 850 | 1 | 9 | 81 | 1 | 13 | 73700 | 1 | 9 | 85000 | 1 | 9 | 11100 | 1 | 13 | 2370 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 36.7 | 98.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.43 | A | 7 | 974 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.76 | 1 | 0
1990-07-02 | 1900-07-01 | 17:00 | 17 | 771 | 1321 | 514 | 1 | 9 | 732 | 1 | 9 | 86 | 1 | 13 | 54900 | 1 | 9 | 73300 | 1 | 9 | 12100 | 1 | 13 | 2080 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 36.1 | 96.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.46 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.54 | 1 | 0
1990-07-02 | 1900-07-01 | 18:00 | 18 | 543 | 1321 | 322 | 1 | 9 | 573 | 1 | 9 | 86 | 1 | 13 | 33800 | 1 | 9 | 54900 | 1 | 9 | 11200 | 1 | 13 | 1740 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 35.6 | 96.08 | A | 7 | 22.8 | 73.04 | A | 7 | 0.48 | A | 7 | 973 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.04 | 1 | 0
1990-07-02 | 1900-07-01 | 19:00 | 19 | 300 | 1321 | 156 | 1 | 13 | 506 | 1 | 9 | 41 | 1 | 13 | 16000 | 1 | 13 | 41800 | 1 | 9 | 6500 | 1 | 13 | 820 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 32.8 | 91.04 | A | 7 | 22.8 | 73.04 | A | 7 | 0.56 | A | 7 | 973 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.34 | 1 | 0
1990-07-02 | 1900-07-01 | 20:00 | 20 | 68 | 1046 | 34 | 1 | 13 | 171 | 1 | 9 | 17 | 1 | 13 | 3000 | 1 | 13 | 8200 | 1 | 9 | 2400 | 1 | 13 | 310 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.59 | A | 7 | 973 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.16 | 1 | 0
1990-07-02 | 1900-07-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 973 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 1 | 0
1990-07-02 | 1900-07-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 973 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 1 | 0
1990-07-02 | 1900-07-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 30 | 86 | A | 7 | 20.6 | 69.08 | A | 7 | 0.57 | A | 7 | 973 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.18 | 1 | 0
1990-07-02 | 1900-07-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 973 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.98 | 1 | 0
1990-07-03 | 1900-07-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 973 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 2 | 0
1990-07-03 | 1900-07-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 28.3 | 82.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.63 | A | 7 | 973 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.68 | 2 | 0
1990-07-03 | 1900-07-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 27.8 | 82.04 | A | 7 | 20 | 68 | A | 7 | 0.63 | A | 7 | 973 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.7 | 2 | 0
1990-07-03 | 1900-07-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 27.2 | 80.96 | A | 7 | 20 | 68 | A | 7 | 0.65 | A | 7 | 974 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.2 | 2 | 0
1990-07-03 | 1900-07-02 | 5:00 | 5 | 0 | 33 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 4 | A | 7 | 4 | A | 7 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 974 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.7 | 2 | 0
1990-07-03 | 1900-07-02 | 6:00 | 6 | 116 | 1321 | 39 | 1 | 13 | 151 | 1 | 13 | 26 | 1 | 13 | 4100 | 1 | 13 | 7100 | 1 | 13 | 3500 | 1 | 13 | 460 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 974 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.2 | 2 | 0
1990-07-03 | 1900-07-02 | 7:00 | 7 | 356 | 1321 | 195 | 1 | 13 | 419 | 1 | 13 | 81 | 1 | 13 | 20400 | 1 | 13 | 35700 | 1 | 13 | 10800 | 1 | 13 | 1490 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.72 | A | 7 | 974 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.9 | 2 | 0
1990-07-03 | 1900-07-02 | 8:00 | 8 | 598 | 1321 | 380 | 1 | 9 | 666 | 1 | 9 | 78 | 1 | 13 | 39700 | 1 | 9 | 64500 | 1 | 9 | 10500 | 1 | 13 | 1630 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 975 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 2 | 0
1990-07-03 | 1900-07-02 | 9:00 | 9 | 821 | 1321 | 593 | 1 | 9 | 828 | 1 | 9 | 76 | 1 | 13 | 61800 | 1 | 9 | 82100 | 1 | 9 | 10700 | 1 | 13 | 1890 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 2 | 0
1990-07-03 | 1900-07-02 | 10:00 | 10 | 1010 | 1321 | 759 | 1 | 9 | 874 | 1 | 9 | 88 | 1 | 13 | 78800 | 1 | 9 | 87500 | 1 | 9 | 11800 | 1 | 13 | 2660 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.52 | A | 7 | 975 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 2 | 0
1990-07-03 | 1900-07-02 | 11:00 | 11 | 1153 | 1321 | 882 | 1 | 9 | 897 | 1 | 9 | 96 | 1 | 13 | 91300 | 1 | 9 | 90000 | 1 | 9 | 12600 | 1 | 13 | 3960 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.46 | A | 7 | 975 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.28 | 2 | 0
1990-07-03 | 1900-07-02 | 12:00 | 12 | 1240 | 1321 | 959 | 1 | 9 | 911 | 1 | 9 | 101 | 1 | 13 | 99100 | 1 | 9 | 91500 | 1 | 9 | 13000 | 1 | 13 | 5840 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 35 | 95 | A | 7 | 21.1 | 69.98 | A | 7 | 0.44 | A | 7 | 975 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 2 | 0
1990-07-03 | 1900-07-02 | 13:00 | 13 | 1265 | 1321 | 982 | 1 | 9 | 917 | 1 | 9 | 102 | 1 | 13 | 101500 | 1 | 9 | 92200 | 1 | 9 | 13100 | 1 | 13 | 6810 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 36.1 | 96.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.42 | A | 7 | 974 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.98 | 2 | 0
1990-07-03 | 1900-07-02 | 14:00 | 14 | 1225 | 1321 | 943 | 1 | 9 | 906 | 1 | 9 | 100 | 1 | 13 | 97500 | 1 | 9 | 91000 | 1 | 9 | 12900 | 1 | 13 | 5390 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 36.7 | 98.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.36 | A | 7 | 974 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 2 | 0
1990-07-03 | 1900-07-02 | 15:00 | 15 | 1125 | 1321 | 856 | 1 | 9 | 892 | 1 | 9 | 94 | 1 | 13 | 88700 | 1 | 9 | 89500 | 1 | 9 | 12400 | 1 | 13 | 3590 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 36.7 | 98.06 | A | 7 | 20 | 68 | A | 7 | 0.38 | A | 7 | 974 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.3 | 2 | 0
1990-07-03 | 1900-07-02 | 16:00 | 16 | 970 | 1321 | 720 | 1 | 9 | 862 | 1 | 9 | 86 | 1 | 13 | 75000 | 1 | 9 | 86100 | 1 | 9 | 11600 | 1 | 13 | 2450 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 36.7 | 98.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.39 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.38 | 2 | 0
1990-07-03 | 1900-07-02 | 17:00 | 17 | 771 | 1321 | 549 | 1 | 9 | 816 | 1 | 9 | 73 | 1 | 13 | 57500 | 1 | 9 | 80600 | 1 | 9 | 10400 | 1 | 13 | 1760 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 35.6 | 96.08 | A | 7 | 20 | 68 | A | 7 | 0.4 | A | 7 | 973 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.9 | 2 | 0
1990-07-03 | 1900-07-02 | 18:00 | 18 | 542 | 1321 | 355 | 1 | 9 | 728 | 1 | 9 | 56 | 1 | 13 | 38000 | 1 | 9 | 70100 | 1 | 9 | 9200 | 1 | 13 | 1250 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 35 | 95 | A | 7 | 20.6 | 69.08 | A | 7 | 0.43 | A | 7 | 973 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.48 | 2 | 0
1990-07-03 | 1900-07-02 | 19:00 | 19 | 299 | 1321 | 163 | 1 | 13 | 553 | 1 | 9 | 38 | 1 | 13 | 16900 | 1 | 13 | 45900 | 1 | 9 | 6500 | 1 | 13 | 780 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 33.3 | 91.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.49 | A | 7 | 973 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 2 | 0
1990-07-03 | 1900-07-02 | 20:00 | 20 | 68 | 1046 | 33 | 1 | 13 | 166 | 1 | 9 | 17 | 1 | 13 | 2900 | 1 | 13 | 7900 | 1 | 9 | 2400 | 1 | 13 | 310 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 974 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.064 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 2 | 0
1990-07-03 | 1900-07-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.55 | A | 7 | 974 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 2 | 0
1990-07-03 | 1900-07-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 21.1 | 69.98 | A | 7 | 0.59 | A | 7 | 975 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.48 | 2 | 0
1990-07-03 | 1900-07-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.63 | A | 7 | 975 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.46 | 2 | 0
1990-07-03 | 1900-07-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 22.2 | 71.96 | A | 7 | 0.67 | A | 7 | 975 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.26 | 2 | 0
1990-07-04 | 1900-07-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 3 | 0
1990-07-04 | 1900-07-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.65 | A | 7 | 976 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.18 | 3 | 0
1990-07-04 | 1900-07-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.68 | 3 | 0
1990-07-04 | 1900-07-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.2 | 3 | 0
1990-07-04 | 1900-07-03 | 5:00 | 5 | 0 | 33 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.22 | 3 | 0
1990-07-04 | 1900-07-03 | 6:00 | 6 | 114 | 1321 | 46 | 1 | 13 | 242 | 1 | 9 | 23 | 1 | 13 | 4400 | 1 | 13 | 12600 | 1 | 9 | 3400 | 1 | 13 | 410 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 3 | 0
1990-07-04 | 1900-07-03 | 7:00 | 7 | 354 | 1321 | 203 | 1 | 9 | 581 | 1 | 9 | 46 | 1 | 13 | 20900 | 1 | 9 | 50500 | 1 | 9 | 7400 | 1 | 13 | 930 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 20 | 68 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.2 | 3 | 0
1990-07-04 | 1900-07-03 | 8:00 | 8 | 596 | 1321 | 399 | 1 | 9 | 733 | 1 | 9 | 66 | 1 | 13 | 42200 | 1 | 9 | 71400 | 1 | 9 | 10000 | 1 | 13 | 1460 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 3 | 0
1990-07-04 | 1900-07-03 | 9:00 | 9 | 819 | 1321 | 591 | 1 | 9 | 815 | 1 | 9 | 83 | 1 | 13 | 61400 | 1 | 9 | 80800 | 1 | 9 | 11200 | 1 | 13 | 1950 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.55 | A | 7 | 977 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 3 | 0
1990-07-04 | 1900-07-03 | 10:00 | 10 | 1009 | 1321 | 759 | 1 | 9 | 864 | 1 | 9 | 96 | 1 | 13 | 78600 | 1 | 9 | 86400 | 1 | 9 | 12400 | 1 | 13 | 2780 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 20 | 68 | A | 7 | 0.48 | A | 7 | 977 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 3 | 0
1990-07-04 | 1900-07-03 | 11:00 | 11 | 1152 | 1321 | 883 | 1 | 9 | 888 | 1 | 9 | 105 | 1 | 13 | 91100 | 1 | 9 | 89100 | 1 | 9 | 13300 | 1 | 13 | 4190 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 20 | 68 | A | 7 | 0.44 | A | 7 | 977 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 3 | 0
1990-07-04 | 1900-07-03 | 12:00 | 12 | 1239 | 1321 | 958 | 1 | 9 | 901 | 1 | 9 | 110 | 1 | 13 | 98800 | 1 | 9 | 90500 | 1 | 9 | 13700 | 1 | 13 | 6210 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 35.6 | 96.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.43 | A | 7 | 977 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.18 | 3 | 0
1990-07-04 | 1900-07-03 | 13:00 | 13 | 1264 | 1321 | 983 | 1 | 9 | 908 | 1 | 9 | 112 | 1 | 13 | 101300 | 1 | 9 | 91200 | 1 | 9 | 13900 | 1 | 13 | 7310 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 36.1 | 96.98 | A | 7 | 20 | 68 | A | 7 | 0.39 | A | 7 | 977 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.6 | 3 | 0
1990-07-04 | 1900-07-03 | 14:00 | 14 | 1225 | 1321 | 950 | 1 | 9 | 904 | 1 | 9 | 110 | 1 | 13 | 98000 | 1 | 9 | 90800 | 1 | 9 | 13700 | 1 | 13 | 5770 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 37.2 | 98.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.34 | A | 7 | 977 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.72 | 3 | 0
1990-07-04 | 1900-07-03 | 15:00 | 15 | 1125 | 1321 | 862 | 1 | 9 | 889 | 1 | 9 | 103 | 1 | 13 | 89100 | 1 | 9 | 89100 | 1 | 9 | 13100 | 1 | 13 | 3800 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 37.2 | 98.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.32 | A | 7 | 976 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.74 | 3 | 0
1990-07-04 | 1900-07-03 | 16:00 | 16 | 970 | 1321 | 723 | 1 | 9 | 855 | 1 | 9 | 94 | 1 | 13 | 75000 | 1 | 9 | 85400 | 1 | 9 | 12200 | 1 | 13 | 2550 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 36.7 | 98.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.35 | A | 7 | 976 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.02 | 3 | 0
1990-07-04 | 1900-07-03 | 17:00 | 17 | 771 | 1321 | 545 | 1 | 9 | 782 | 1 | 9 | 88 | 1 | 13 | 58100 | 1 | 9 | 78200 | 1 | 9 | 12400 | 1 | 13 | 2110 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 36.1 | 96.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.38 | A | 7 | 976 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.52 | 3 | 0
1990-07-04 | 1900-07-03 | 18:00 | 18 | 542 | 1321 | 330 | 1 | 9 | 634 | 1 | 9 | 69 | 1 | 13 | 34400 | 1 | 9 | 60500 | 1 | 9 | 9600 | 1 | 13 | 1430 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 35 | 95 | A | 7 | 21.1 | 69.98 | A | 7 | 0.44 | A | 7 | 976 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 3 | 0
1990-07-04 | 1900-07-03 | 19:00 | 19 | 299 | 1321 | 147 | 1 | 13 | 448 | 1 | 9 | 46 | 1 | 13 | 15400 | 1 | 13 | 36300 | 1 | 9 | 7200 | 1 | 13 | 870 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 33.3 | 91.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.47 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.58 | 3 | 0
1990-07-04 | 1900-07-03 | 20:00 | 20 | 67 | 1046 | 30 | 1 | 13 | 120 | 1 | 9 | 19 | 1 | 13 | 2900 | 1 | 13 | 4900 | 1 | 9 | 2600 | 1 | 13 | 330 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.53 | A | 7 | 976 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.18 | 3 | 0
1990-07-04 | 1900-07-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 20 | 68 | A | 7 | 0.53 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.3 | 3 | 0
1990-07-04 | 1900-07-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 20 | 68 | A | 7 | 0.59 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.8 | 3 | 0
1990-07-04 | 1900-07-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 20 | 68 | A | 7 | 0.59 | A | 7 | 977 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.8 | 3 | 0
1990-07-04 | 1900-07-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 20 | 68 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.3 | 3 | 0
1990-07-05 | 1900-07-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.68 | 4 | 0
1990-07-05 | 1900-07-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.72 | A | 7 | 977 | A | 7 | 350 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.88 | 4 | 0
1990-07-05 | 1900-07-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 21.1 | 69.98 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.28 | 4 | 0
1990-07-05 | 1900-07-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 4 | 0
1990-07-05 | 1900-07-04 | 5:00 | 5 | 0 | 11 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 3 | A | 7 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 4 | 0
1990-07-05 | 1900-07-04 | 6:00 | 6 | 112 | 1321 | 32 | 1 | 13 | 33 | 1 | 13 | 29 | 1 | 13 | 3500 | 1 | 13 | 1700 | 1 | 13 | 3300 | 1 | 13 | 600 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.78 | 4 | 0
1990-07-05 | 1900-07-04 | 7:00 | 7 | 353 | 1321 | 122 | 1 | 13 | 153 | 1 | 13 | 81 | 1 | 13 | 13100 | 1 | 13 | 13200 | 1 | 13 | 9600 | 1 | 13 | 1520 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 80 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.52 | 4 | 0
1990-07-05 | 1900-07-04 | 8:00 | 8 | 594 | 1321 | 330 | 1 | 13 | 334 | 1 | 13 | 179 | 1 | 13 | 35200 | 1 | 13 | 33900 | 1 | 13 | 19900 | 1 | 13 | 3880 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 110 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.9 | 4 | 0
1990-07-05 | 1900-07-04 | 9:00 | 9 | 818 | 1321 | 522 | 1 | 13 | 548 | 1 | 13 | 181 | 1 | 13 | 56300 | 1 | 13 | 56400 | 1 | 13 | 21300 | 1 | 13 | 4330 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 4 | 0
1990-07-05 | 1900-07-04 | 10:00 | 10 | 1008 | 1321 | 532 | 1 | 9 | 408 | 1 | 9 | 220 | 1 | 13 | 58100 | 1 | 9 | 42600 | 1 | 9 | 25500 | 1 | 13 | 7050 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 4 | 0
1990-07-05 | 1900-07-04 | 11:00 | 11 | 1151 | 1321 | 786 | 1 | 9 | 697 | 1 | 9 | 177 | 1 | 13 | 85000 | 1 | 9 | 71800 | 1 | 9 | 22300 | 1 | 13 | 8340 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 29.4 | 84.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.63 | A | 7 | 981 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.46 | 4 | 0
1990-07-05 | 1900-07-04 | 12:00 | 12 | 1239 | 1321 | 908 | 1 | 13 | 685 | 1 | 13 | 264 | 1 | 13 | 96300 | 1 | 13 | 69600 | 1 | 13 | 30900 | 1 | 13 | 17500 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 30 | 86 | A | 7 | 22.2 | 71.96 | A | 7 | 0.63 | A | 7 | 981 | A | 7 | 60 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.26 | 4 | 0
1990-07-05 | 1900-07-04 | 13:00 | 13 | 1264 | 1321 | 891 | 1 | 9 | 702 | 1 | 9 | 217 | 1 | 13 | 95900 | 1 | 9 | 72100 | 1 | 9 | 26800 | 1 | 13 | 16870 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 30.6 | 87.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.61 | A | 7 | 981 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.66 | 4 | 0
1990-07-05 | 1900-07-04 | 14:00 | 14 | 1225 | 1321 | 866 | 1 | 9 | 665 | 1 | 9 | 248 | 1 | 13 | 92100 | 1 | 9 | 67700 | 1 | 9 | 29200 | 1 | 13 | 15350 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 31.1 | 87.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.16 | 4 | 0
1990-07-05 | 1900-07-04 | 15:00 | 15 | 1124 | 1321 | 807 | 1 | 9 | 677 | 1 | 9 | 229 | 1 | 13 | 85400 | 1 | 9 | 68900 | 1 | 9 | 26700 | 1 | 13 | 9710 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 31.1 | 87.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 30 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 4 | 0
1990-07-05 | 1900-07-04 | 16:00 | 16 | 969 | 1321 | 589 | 1 | 9 | 533 | 1 | 9 | 197 | 1 | 13 | 61900 | 1 | 9 | 54000 | 1 | 9 | 22300 | 1 | 13 | 5850 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 31.1 | 87.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 50 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 4 | 0
1990-07-05 | 1900-07-04 | 17:00 | 17 | 771 | 1321 | 486 | 1 | 13 | 528 | 1 | 13 | 177 | 1 | 13 | 52100 | 1 | 13 | 54000 | 1 | 13 | 20600 | 1 | 13 | 4050 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 30 | 86 | A | 7 | 21.7 | 71.06 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 9140 | A | 7 | 3.8 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.96 | 4 | 0
1990-07-05 | 1900-07-04 | 18:00 | 18 | 542 | 1321 | 281 | 1 | 13 | 348 | 1 | 13 | 138 | 1 | 13 | 29500 | 1 | 13 | 33600 | 1 | 13 | 15700 | 1 | 13 | 2720 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 40 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 4 | 0
1990-07-05 | 1900-07-04 | 19:00 | 19 | 298 | 1321 | 104 | 1 | 13 | 96 | 1 | 13 | 82 | 1 | 13 | 11300 | 1 | 13 | 7900 | 1 | 13 | 9500 | 1 | 13 | 1780 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 981 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 1280 | A | 7 | 3.8 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 4 | 0
1990-07-05 | 1900-07-04 | 20:00 | 20 | 67 | 1046 | 14 | 1 | 13 | 7 | 1 | 13 | 14 | 1 | 13 | 1600 | 1 | 13 | 400 | 1 | 13 | 1600 | 1 | 13 | 360 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 3.7 | E | 8 | 0.177 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 4 | 0
1990-07-05 | 1900-07-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.88 | 4 | 0
1990-07-05 | 1900-07-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 25.6 | 78.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 40 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 1430 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.28 | 4 | 0
1990-07-05 | 1900-07-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.3 | 4 | 0
1990-07-05 | 1900-07-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 25 | 77 | A | 7 | 18.3 | 64.94 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.94 | 4 | 0
1990-07-06 | 1900-07-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.14 | 5 | 0
1990-07-06 | 1900-07-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 4270 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.84 | 5 | 0
1990-07-06 | 1900-07-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 4270 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.52 | 5 | 0
1990-07-06 | 1900-07-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 4270 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.82 | 5 | 0
1990-07-06 | 1900-07-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 5 | 0
1990-07-06 | 1900-07-05 | 6:00 | 6 | 110 | 1310 | 21 | 1 | 13 | 3 | 1 | 9 | 20 | 1 | 13 | 2300 | 1 | 13 | 0 | 1 | 9 | 2300 | 1 | 13 | 720 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 3.2 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 5 | 0
1990-07-06 | 1900-07-05 | 7:00 | 7 | 351 | 1321 | 94 | 1 | 9 | 30 | 1 | 9 | 86 | 1 | 13 | 10300 | 1 | 9 | 2600 | 1 | 9 | 9600 | 1 | 13 | 2300 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 3.3 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.52 | 5 | 0
1990-07-06 | 1900-07-05 | 8:00 | 8 | 592 | 1321 | 173 | 1 | 9 | 52 | 1 | 9 | 150 | 1 | 13 | 19100 | 1 | 9 | 5100 | 1 | 9 | 16800 | 1 | 13 | 4520 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 3.3 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.92 | 5 | 0
1990-07-06 | 1900-07-05 | 9:00 | 9 | 816 | 1321 | 296 | 1 | 9 | 56 | 1 | 9 | 261 | 1 | 13 | 32500 | 1 | 9 | 5700 | 1 | 9 | 29000 | 1 | 13 | 8620 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 3.3 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.52 | 5 | 0
1990-07-06 | 1900-07-05 | 10:00 | 10 | 1006 | 1321 | 272 | 1 | 9 | 3 | 1 | 9 | 270 | 1 | 13 | 32100 | 1 | 9 | 300 | 1 | 9 | 31900 | 1 | 13 | 12390 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 3.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.22 | 5 | 0
1990-07-06 | 1900-07-05 | 11:00 | 11 | 1150 | 1321 | 315 | 1 | 9 | 9 | 1 | 9 | 307 | 1 | 13 | 37500 | 1 | 9 | 800 | 1 | 9 | 36800 | 1 | 13 | 14220 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 3.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.22 | 5 | 0
1990-07-06 | 1900-07-05 | 12:00 | 12 | 1238 | 1321 | 427 | 1 | 9 | 11 | 1 | 9 | 416 | 1 | 13 | 50200 | 1 | 9 | 1000 | 1 | 9 | 49200 | 1 | 13 | 17990 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 27.8 | 82.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 3.6 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.18 | 5 | 0
1990-07-06 | 1900-07-05 | 13:00 | 13 | 1263 | 1321 | 329 | 1 | 9 | 0 | 1 | 9 | 329 | 1 | 13 | 39600 | 1 | 9 | 0 | 1 | 9 | 39600 | 1 | 13 | 15330 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 3960 | A | 7 | 3.7 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 5 | 0
1990-07-06 | 1900-07-05 | 14:00 | 14 | 1224 | 1321 | 727 | 1 | 13 | 507 | 1 | 13 | 257 | 1 | 13 | 77200 | 1 | 13 | 51600 | 1 | 13 | 29400 | 1 | 13 | 15840 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 29.4 | 84.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.63 | A | 7 | 981 | A | 7 | 80 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 3960 | A | 7 | 3.8 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.46 | 5 | 0
1990-07-06 | 1900-07-05 | 15:00 | 15 | 1124 | 1321 | 781 | 1 | 9 | 732 | 1 | 9 | 156 | 1 | 13 | 82400 | 1 | 9 | 73900 | 1 | 9 | 19500 | 1 | 13 | 6230 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 30 | 86 | A | 7 | 21.7 | 71.06 | A | 7 | 0.61 | A | 7 | 981 | A | 7 | 80 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.96 | 5 | 0
1990-07-06 | 1900-07-05 | 16:00 | 16 | 969 | 1321 | 666 | 1 | 9 | 665 | 1 | 9 | 177 | 1 | 13 | 70600 | 1 | 9 | 67700 | 1 | 9 | 20800 | 1 | 13 | 5320 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 30 | 86 | A | 7 | 22.2 | 71.96 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 90 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.26 | 5 | 0
1990-07-06 | 1900-07-05 | 17:00 | 17 | 770 | 1321 | 537 | 1 | 9 | 704 | 1 | 9 | 126 | 1 | 13 | 56900 | 1 | 9 | 70900 | 1 | 9 | 15500 | 1 | 13 | 2960 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 30 | 86 | A | 7 | 22.8 | 73.04 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 100 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.64 | 5 | 0
1990-07-06 | 1900-07-05 | 18:00 | 18 | 541 | 1321 | 305 | 1 | 9 | 481 | 1 | 9 | 107 | 1 | 13 | 32800 | 1 | 9 | 46500 | 1 | 9 | 13700 | 1 | 13 | 2060 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 22.2 | 71.96 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.26 | 5 | 0
1990-07-06 | 1900-07-05 | 19:00 | 19 | 298 | 1321 | 138 | 1 | 13 | 341 | 1 | 9 | 61 | 1 | 13 | 14600 | 1 | 13 | 27000 | 1 | 9 | 8500 | 1 | 13 | 1090 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.96 | 5 | 0
1990-07-06 | 1900-07-05 | 20:00 | 20 | 66 | 1024 | 25 | 1 | 13 | 46 | 1 | 9 | 21 | 1 | 13 | 2700 | 1 | 13 | 2100 | 1 | 9 | 2500 | 1 | 13 | 430 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.66 | 5 | 0
1990-07-06 | 1900-07-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 26.7 | 80.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.66 | 5 | 0
1990-07-06 | 1900-07-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 5 | 0
1990-07-06 | 1900-07-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 1 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 5 | 0
1990-07-06 | 1900-07-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.26 | 5 | 0
1990-07-07 | 1900-07-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.26 | 6 | 0
1990-07-07 | 1900-07-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 1 | A | 7 | 23.9 | 75.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.68 | 6 | 0
1990-07-07 | 1900-07-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.16 | 6 | 0
1990-07-07 | 1900-07-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 1 | A | 7 | 23.9 | 75.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.16 | 6 | 0
1990-07-07 | 1900-07-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.78 | 6 | 0
1990-07-07 | 1900-07-06 | 6:00 | 6 | 108 | 1310 | 36 | 1 | 13 | 57 | 1 | 13 | 31 | 1 | 13 | 3900 | 1 | 13 | 2900 | 1 | 13 | 3700 | 1 | 13 | 640 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 22.2 | 71.96 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.76 | 6 | 0
1990-07-07 | 1900-07-06 | 7:00 | 7 | 349 | 1321 | 173 | 1 | 13 | 295 | 1 | 13 | 94 | 1 | 13 | 18200 | 1 | 13 | 25300 | 1 | 13 | 11600 | 1 | 13 | 1820 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 25.6 | 78.08 | A | 7 | 22.8 | 73.04 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 9140 | A | 7 | 4.1 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.64 | 6 | 0
1990-07-07 | 1900-07-06 | 8:00 | 8 | 591 | 1321 | 306 | 1 | 13 | 367 | 1 | 13 | 141 | 1 | 13 | 32400 | 1 | 13 | 36100 | 1 | 13 | 16200 | 1 | 13 | 2830 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 26.7 | 80.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.66 | 6 | 0
1990-07-07 | 1900-07-06 | 9:00 | 9 | 815 | 1321 | 522 | 1 | 9 | 622 | 1 | 9 | 137 | 1 | 13 | 55200 | 1 | 9 | 62800 | 1 | 9 | 16400 | 1 | 13 | 3350 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 22.8 | 73.04 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.94 | 6 | 0
1990-07-07 | 1900-07-06 | 10:00 | 10 | 1005 | 1321 | 740 | 1 | 9 | 816 | 1 | 9 | 117 | 1 | 13 | 79300 | 1 | 9 | 82800 | 1 | 9 | 16200 | 1 | 13 | 3690 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.66 | 6 | 0
1990-07-07 | 1900-07-06 | 11:00 | 11 | 1149 | 1321 | 860 | 1 | 9 | 839 | 1 | 9 | 128 | 1 | 13 | 88300 | 1 | 9 | 84000 | 1 | 9 | 15100 | 1 | 13 | 4650 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 6 | 0
1990-07-07 | 1900-07-06 | 12:00 | 12 | 1237 | 1321 | 910 | 1 | 9 | 836 | 1 | 9 | 124 | 1 | 13 | 93400 | 1 | 9 | 83900 | 1 | 9 | 14700 | 1 | 13 | 6690 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 33.9 | 93.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.76 | 6 | 0
1990-07-07 | 1900-07-06 | 13:00 | 13 | 1262 | 1321 | 907 | 1 | 9 | 820 | 1 | 9 | 121 | 1 | 13 | 93200 | 1 | 9 | 82300 | 1 | 9 | 14400 | 1 | 13 | 7660 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 34.4 | 93.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.46 | A | 7 | 977 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.08 | 6 | 0
1990-07-07 | 1900-07-06 | 14:00 | 14 | 1224 | 1321 | 835 | 1 | 9 | 680 | 1 | 9 | 203 | 1 | 13 | 90000 | 1 | 9 | 69900 | 1 | 9 | 25100 | 1 | 13 | 12640 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 34.4 | 93.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.44 | A | 7 | 977 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.78 | 6 | 0
1990-07-07 | 1900-07-06 | 15:00 | 15 | 1123 | 1321 | 772 | 1 | 9 | 688 | 1 | 9 | 186 | 1 | 13 | 83000 | 1 | 9 | 70600 | 1 | 9 | 22800 | 1 | 13 | 8000 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 35 | 95 | A | 7 | 21.1 | 69.98 | A | 7 | 0.44 | A | 7 | 976 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 6 | 0
1990-07-07 | 1900-07-06 | 16:00 | 16 | 969 | 1321 | 674 | 1 | 13 | 712 | 1 | 13 | 151 | 1 | 13 | 72300 | 1 | 13 | 72900 | 1 | 13 | 18700 | 1 | 13 | 4610 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 34.4 | 93.92 | A | 7 | 20 | 68 | A | 7 | 0.43 | A | 7 | 976 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.7 | 6 | 0
1990-07-07 | 1900-07-06 | 17:00 | 17 | 770 | 1321 | 555 | 1 | 9 | 755 | 1 | 9 | 114 | 1 | 13 | 57500 | 1 | 9 | 74700 | 1 | 9 | 13900 | 1 | 13 | 2470 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 34.4 | 93.92 | A | 7 | 20 | 68 | A | 7 | 0.43 | A | 7 | 976 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.7 | 6 | 0
1990-07-07 | 1900-07-06 | 18:00 | 18 | 540 | 1321 | 326 | 1 | 9 | 609 | 1 | 9 | 77 | 1 | 13 | 34600 | 1 | 9 | 58600 | 1 | 9 | 10600 | 1 | 13 | 1580 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 33.3 | 91.94 | A | 7 | 20 | 68 | A | 7 | 0.46 | A | 7 | 976 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.5 | 6 | 0
1990-07-07 | 1900-07-06 | 19:00 | 19 | 297 | 1321 | 153 | 1 | 13 | 467 | 1 | 9 | 48 | 1 | 13 | 15900 | 1 | 13 | 37600 | 1 | 9 | 7400 | 1 | 13 | 900 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 20 | 68 | A | 7 | 0.48 | A | 7 | 976 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 6 | 0
1990-07-07 | 1900-07-06 | 20:00 | 20 | 65 | 1024 | 28 | 1 | 13 | 98 | 1 | 9 | 19 | 1 | 13 | 2700 | 1 | 13 | 4000 | 1 | 9 | 2500 | 1 | 13 | 330 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 20 | 68 | A | 7 | 0.52 | A | 7 | 976 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57 | 6 | 0
1990-07-07 | 1900-07-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 20.6 | 69.08 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.18 | 6 | 0
1990-07-07 | 1900-07-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.59 | A | 7 | 977 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.68 | 6 | 0
1990-07-07 | 1900-07-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 20 | 68 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.3 | 6 | 0
1990-07-07 | 1900-07-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 6 | 0
1990-07-08 | 1900-07-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 7 | 0
1990-07-08 | 1900-07-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.34 | 7 | 0
1990-07-08 | 1900-07-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 977 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.84 | 7 | 0
1990-07-08 | 1900-07-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.84 | 7 | 0
1990-07-08 | 1900-07-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.04 | 7 | 0
1990-07-08 | 1900-07-07 | 6:00 | 6 | 106 | 1288 | 37 | 1 | 13 | 115 | 1 | 9 | 27 | 1 | 13 | 3900 | 1 | 13 | 5400 | 1 | 9 | 3400 | 1 | 13 | 480 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.24 | 7 | 0
1990-07-08 | 1900-07-07 | 7:00 | 7 | 346 | 1321 | 181 | 1 | 9 | 450 | 1 | 9 | 62 | 1 | 13 | 18600 | 1 | 9 | 38100 | 1 | 9 | 8600 | 1 | 13 | 1150 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.02 | 7 | 0
1990-07-08 | 1900-07-07 | 8:00 | 8 | 589 | 1321 | 375 | 1 | 9 | 631 | 1 | 9 | 92 | 1 | 13 | 39400 | 1 | 9 | 61400 | 1 | 9 | 12000 | 1 | 13 | 1910 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.02 | 7 | 0
1990-07-08 | 1900-07-07 | 9:00 | 9 | 813 | 1321 | 569 | 1 | 9 | 732 | 1 | 9 | 117 | 1 | 13 | 59200 | 1 | 9 | 72800 | 1 | 9 | 14300 | 1 | 13 | 2670 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.82 | 7 | 0
1990-07-08 | 1900-07-07 | 10:00 | 10 | 1004 | 1321 | 738 | 1 | 9 | 791 | 1 | 9 | 136 | 1 | 13 | 77900 | 1 | 9 | 79700 | 1 | 9 | 17200 | 1 | 13 | 4110 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 7 | 0
1990-07-08 | 1900-07-07 | 11:00 | 11 | 1148 | 1321 | 865 | 1 | 9 | 821 | 1 | 9 | 148 | 1 | 13 | 92000 | 1 | 9 | 83200 | 1 | 9 | 19600 | 1 | 13 | 6480 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 20 | 68 | A | 7 | 0.47 | A | 7 | 978 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.7 | 7 | 0
1990-07-08 | 1900-07-07 | 12:00 | 12 | 1236 | 1321 | 947 | 1 | 9 | 843 | 1 | 9 | 156 | 1 | 13 | 101400 | 1 | 9 | 85600 | 1 | 9 | 21200 | 1 | 13 | 9840 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.3 | 91.94 | A | 7 | 20 | 68 | A | 7 | 0.46 | A | 7 | 978 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.5 | 7 | 0
1990-07-08 | 1900-07-07 | 13:00 | 13 | 1262 | 1321 | 971 | 1 | 9 | 851 | 1 | 9 | 157 | 1 | 13 | 99100 | 1 | 9 | 85200 | 1 | 9 | 17600 | 1 | 13 | 9180 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 34.4 | 93.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.44 | A | 7 | 978 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.78 | 7 | 0
1990-07-08 | 1900-07-07 | 14:00 | 14 | 1223 | 1321 | 933 | 1 | 9 | 839 | 1 | 9 | 154 | 1 | 13 | 99900 | 1 | 9 | 85200 | 1 | 9 | 20900 | 1 | 13 | 9090 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 35 | 95 | A | 7 | 20.6 | 69.08 | A | 7 | 0.43 | A | 7 | 978 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.48 | 7 | 0
1990-07-08 | 1900-07-07 | 15:00 | 15 | 1123 | 1321 | 847 | 1 | 9 | 822 | 1 | 9 | 146 | 1 | 13 | 90000 | 1 | 9 | 83200 | 1 | 9 | 19200 | 1 | 13 | 5900 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 35.6 | 96.08 | A | 7 | 20 | 68 | A | 7 | 0.4 | A | 7 | 978 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.9 | 7 | 0
1990-07-08 | 1900-07-07 | 16:00 | 16 | 968 | 1321 | 664 | 1 | 9 | 724 | 1 | 9 | 132 | 1 | 13 | 69900 | 1 | 9 | 72900 | 1 | 9 | 16400 | 1 | 13 | 3740 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 35 | 95 | A | 7 | 20.6 | 69.08 | A | 7 | 0.43 | A | 7 | 978 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.48 | 7 | 0
1990-07-08 | 1900-07-07 | 17:00 | 17 | 769 | 1321 | 486 | 1 | 9 | 561 | 1 | 9 | 158 | 1 | 13 | 50500 | 1 | 9 | 55900 | 1 | 9 | 18000 | 1 | 13 | 3590 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 35 | 95 | A | 7 | 20.6 | 69.08 | A | 7 | 0.43 | A | 7 | 978 | A | 7 | 220 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.48 | 7 | 0
1990-07-08 | 1900-07-07 | 18:00 | 18 | 540 | 1321 | 332 | 1 | 9 | 603 | 1 | 9 | 86 | 1 | 13 | 35000 | 1 | 9 | 57700 | 1 | 9 | 11300 | 1 | 13 | 1730 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 34.4 | 93.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.46 | A | 7 | 977 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.08 | 7 | 0
1990-07-08 | 1900-07-07 | 19:00 | 19 | 296 | 1321 | 136 | 1 | 13 | 338 | 1 | 9 | 60 | 1 | 13 | 14400 | 1 | 13 | 26700 | 1 | 9 | 8400 | 1 | 13 | 1080 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 32.8 | 91.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.08 | 7 | 0
1990-07-08 | 1900-07-07 | 20:00 | 20 | 65 | 1024 | 27 | 1 | 13 | 59 | 1 | 9 | 21 | 1 | 13 | 2700 | 1 | 13 | 2100 | 1 | 9 | 2500 | 1 | 13 | 370 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 20 | 68 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.139 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57 | 7 | 0
1990-07-08 | 1900-07-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 19.4 | 66.92 | A | 7 | 0.53 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.32 | 7 | 0
1990-07-08 | 1900-07-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 19.4 | 66.92 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.32 | 7 | 0
1990-07-08 | 1900-07-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 7 | 0
1990-07-08 | 1900-07-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.55 | A | 7 | 980 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.24 | 7 | 0
1990-07-09 | 1900-07-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 1 | 0
1990-07-09 | 1900-07-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 1 | 0
1990-07-09 | 1900-07-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.34 | 1 | 0
1990-07-09 | 1900-07-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 1 | 0
1990-07-09 | 1900-07-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.04 | 1 | 0
1990-07-09 | 1900-07-08 | 6:00 | 6 | 104 | 1288 | 31 | 1 | 13 | 84 | 1 | 9 | 23 | 1 | 13 | 3300 | 1 | 13 | 3600 | 1 | 9 | 2900 | 1 | 13 | 400 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.92 | 1 | 0
1990-07-09 | 1900-07-08 | 7:00 | 7 | 344 | 1321 | 146 | 1 | 9 | 246 | 1 | 9 | 82 | 1 | 13 | 15700 | 1 | 9 | 21000 | 1 | 9 | 10200 | 1 | 13 | 1550 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 27.8 | 82.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.02 | 1 | 0
1990-07-09 | 1900-07-08 | 8:00 | 8 | 587 | 1321 | 178 | 1 | 9 | 39 | 1 | 9 | 161 | 1 | 13 | 19600 | 1 | 9 | 3800 | 1 | 9 | 17900 | 1 | 13 | 4770 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 28.3 | 82.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 4270 | A | 7 | 3.3 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.62 | 1 | 0
1990-07-09 | 1900-07-08 | 9:00 | 9 | 811 | 1321 | 145 | 1 | 9 | 1 | 1 | 9 | 145 | 1 | 13 | 17400 | 1 | 9 | 100 | 1 | 9 | 17400 | 1 | 13 | 6890 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 28.3 | 82.94 | A | 7 | 20 | 68 | A | 7 | 0.61 | A | 7 | 981 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 3.5 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.3 | 1 | 0
1990-07-09 | 1900-07-08 | 10:00 | 10 | 1002 | 1321 | 399 | 1 | 9 | 139 | 1 | 9 | 293 | 1 | 13 | 44200 | 1 | 9 | 14800 | 1 | 9 | 32900 | 1 | 13 | 9710 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 4270 | A | 7 | 3.7 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 1 | 0
1990-07-09 | 1900-07-08 | 11:00 | 11 | 1147 | 1321 | 735 | 1 | 13 | 521 | 1 | 13 | 281 | 1 | 13 | 79800 | 1 | 13 | 54500 | 1 | 13 | 32400 | 1 | 13 | 12990 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 32.8 | 91.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.49 | A | 7 | 981 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 4270 | A | 7 | 3.6 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.08 | 1 | 0
1990-07-09 | 1900-07-08 | 12:00 | 12 | 1235 | 1321 | 803 | 1 | 13 | 518 | 1 | 13 | 317 | 1 | 13 | 87200 | 1 | 13 | 54300 | 1 | 13 | 36300 | 1 | 13 | 21150 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 32.8 | 91.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.49 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 9140 | A | 7 | 3.6 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.08 | 1 | 0
1990-07-09 | 1900-07-08 | 13:00 | 13 | 1261 | 1321 | 790 | 1 | 13 | 459 | 1 | 13 | 350 | 1 | 13 | 85200 | 1 | 13 | 48000 | 1 | 13 | 39200 | 1 | 13 | 27210 | 1 | 23 | 7 | A | 7 | 4 | A | 7 | 34.4 | 93.92 | A | 7 | 20 | 68 | A | 7 | 0.43 | A | 7 | 980 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 9140 | A | 7 | 3.5 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.7 | 1 | 0
1990-07-09 | 1900-07-08 | 14:00 | 14 | 1222 | 1321 | 761 | 1 | 13 | 491 | 1 | 13 | 305 | 1 | 13 | 82800 | 1 | 13 | 51400 | 1 | 13 | 35100 | 1 | 13 | 19060 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 34.4 | 93.92 | A | 7 | 20 | 68 | A | 7 | 0.43 | A | 7 | 980 | A | 7 | 210 | A | 7 | 8.8 | A | 7 | 12900 | A | 7 | 9140 | A | 7 | 3.5 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.7 | 1 | 0
1990-07-09 | 1900-07-08 | 15:00 | 15 | 1122 | 1321 | 761 | 1 | 13 | 575 | 1 | 13 | 272 | 1 | 13 | 82700 | 1 | 13 | 60200 | 1 | 13 | 31500 | 1 | 13 | 11630 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 34.4 | 93.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.44 | A | 7 | 980 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 9140 | A | 7 | 3.6 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.78 | 1 | 0
1990-07-09 | 1900-07-08 | 16:00 | 16 | 968 | 1321 | 495 | 1 | 13 | 255 | 1 | 13 | 308 | 1 | 13 | 53800 | 1 | 13 | 27500 | 1 | 13 | 33600 | 1 | 13 | 9330 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 29.4 | 84.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.55 | A | 7 | 980 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 4270 | A | 7 | 3.4 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.82 | 1 | 0
1990-07-09 | 1900-07-08 | 17:00 | 17 | 768 | 1321 | 345 | 1 | 9 | 197 | 1 | 9 | 230 | 1 | 13 | 37900 | 1 | 9 | 20600 | 1 | 9 | 25900 | 1 | 13 | 6110 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 28.3 | 82.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 4270 | A | 7 | 3.6 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.68 | 1 | 0
1990-07-09 | 1900-07-08 | 18:00 | 18 | 539 | 1321 | 171 | 1 | 9 | 55 | 1 | 9 | 149 | 1 | 13 | 18800 | 1 | 9 | 5300 | 1 | 9 | 16700 | 1 | 13 | 4290 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 4270 | A | 7 | 3.7 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.98 | 1 | 0
1990-07-09 | 1900-07-08 | 19:00 | 19 | 295 | 1321 | 67 | 1 | 13 | 3 | 1 | 9 | 66 | 1 | 13 | 7600 | 1 | 13 | 100 | 1 | 9 | 7500 | 1 | 13 | 2420 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 4270 | A | 7 | 3.7 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 1 | 0
1990-07-09 | 1900-07-08 | 20:00 | 20 | 64 | 1002 | 11 | 1 | 13 | 1 | 1 | 9 | 11 | 1 | 13 | 1300 | 1 | 13 | 0 | 1 | 9 | 1300 | 1 | 13 | 410 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 2440 | A | 7 | 3.7 | E | 8 | 0.153 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.98 | 1 | 0
1990-07-09 | 1900-07-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 26.1 | 78.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12900 | A | 7 | 2440 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.16 | 1 | 0
1990-07-09 | 1900-07-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 25 | 77 | A | 7 | 22.2 | 71.96 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 130 | A | 7 | 1.5 | A | 7 | 12900 | A | 7 | 7620 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.56 | 1 | 0
1990-07-09 | 1900-07-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 25 | 77 | A | 7 | 22.8 | 73.04 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 3050 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.34 | 1 | 0
1990-07-09 | 1900-07-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 25 | 77 | A | 7 | 22.2 | 71.96 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.56 | 1 | 0
1990-07-10 | 1900-07-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 2 | 0
1990-07-10 | 1900-07-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3350 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 2 | 0
1990-07-10 | 1900-07-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3350 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 2 | 0
1990-07-10 | 1900-07-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.94 | A | 7 | 980 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3350 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.56 | 2 | 0
1990-07-10 | 1900-07-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 3050 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.26 | 2 | 0
1990-07-10 | 1900-07-09 | 6:00 | 6 | 101 | 1266 | 8 | 1 | 13 | 1 | 1 | 9 | 8 | 1 | 13 | 1000 | 1 | 13 | 0 | 1 | 9 | 1000 | 1 | 13 | 320 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 3660 | A | 7 | 3.8 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.16 | 2 | 0
1990-07-10 | 1900-07-09 | 7:00 | 7 | 342 | 1322 | 36 | 1 | 9 | 1 | 1 | 9 | 36 | 1 | 13 | 4400 | 1 | 9 | 0 | 1 | 9 | 4400 | 1 | 13 | 1530 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 2900 | A | 7 | 3.4 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 2 | 0
1990-07-10 | 1900-07-09 | 8:00 | 8 | 585 | 1322 | 137 | 1 | 9 | 1 | 1 | 9 | 136 | 1 | 13 | 15800 | 1 | 9 | 100 | 1 | 9 | 15700 | 1 | 13 | 5640 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 3.5 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 2 | 0
1990-07-10 | 1900-07-09 | 9:00 | 9 | 810 | 1322 | 225 | 1 | 9 | 6 | 1 | 9 | 221 | 1 | 13 | 26000 | 1 | 9 | 500 | 1 | 9 | 25700 | 1 | 13 | 9580 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 26.1 | 78.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 3.6 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.88 | 2 | 0
1990-07-10 | 1900-07-09 | 10:00 | 10 | 1001 | 1322 | 384 | 1 | 9 | 113 | 1 | 9 | 299 | 1 | 13 | 42600 | 1 | 9 | 12000 | 1 | 9 | 33500 | 1 | 13 | 9890 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 3.7 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 2 | 0
1990-07-10 | 1900-07-09 | 11:00 | 11 | 1146 | 1322 | 491 | 1 | 9 | 143 | 1 | 9 | 367 | 1 | 13 | 54400 | 1 | 9 | 15300 | 1 | 9 | 41100 | 1 | 13 | 15620 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 3.7 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 2 | 0
1990-07-10 | 1900-07-09 | 12:00 | 12 | 1234 | 1322 | 394 | 1 | 9 | 3 | 1 | 9 | 391 | 1 | 13 | 46600 | 1 | 9 | 300 | 1 | 9 | 46300 | 1 | 13 | 17240 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 29.4 | 84.92 | A | 7 | 20 | 68 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 3.5 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.3 | 2 | 0
1990-07-10 | 1900-07-09 | 13:00 | 13 | 1260 | 1322 | 457 | 1 | 9 | 37 | 1 | 9 | 422 | 1 | 13 | 50600 | 1 | 9 | 3800 | 1 | 9 | 46900 | 1 | 13 | 24320 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 3.7 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 2 | 0
1990-07-10 | 1900-07-09 | 14:00 | 14 | 1222 | 1322 | 665 | 1 | 9 | 336 | 1 | 9 | 353 | 1 | 13 | 73800 | 1 | 9 | 36600 | 1 | 9 | 39900 | 1 | 13 | 19600 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 31.7 | 89.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 3.9 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.66 | 2 | 0
1990-07-10 | 1900-07-09 | 15:00 | 15 | 1122 | 1322 | 669 | 1 | 13 | 379 | 1 | 13 | 346 | 1 | 13 | 73500 | 1 | 13 | 41200 | 1 | 13 | 38400 | 1 | 13 | 13980 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 33.9 | 93.02 | A | 7 | 22.2 | 71.96 | A | 7 | 0.51 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 4 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 2 | 0
1990-07-10 | 1900-07-09 | 16:00 | 16 | 967 | 1322 | 141 | 1 | 9 | 10 | 1 | 9 | 133 | 1 | 13 | 17300 | 1 | 9 | 700 | 1 | 9 | 16800 | 1 | 13 | 6820 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 23.9 | 75.02 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 330 | A | 7 | 7.2 | A | 7 | 3200 | A | 7 | 310 | A | 7 | 4.3 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 74.32 | 2 | 0
1990-07-10 | 1900-07-09 | 17:00 | 17 | 768 | 1322 | 136 | 1 | 9 | 6 | 1 | 9 | 133 | 1 | 13 | 16300 | 1 | 9 | 400 | 1 | 9 | 16100 | 1 | 13 | 6260 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.94 | A | 7 | 979 | A | 7 | 230 | A | 7 | 8.2 | A | 7 | 1200 | A | 7 | 610 | A | 7 | 4 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.56 | 2 | 0
1990-07-10 | 1900-07-09 | 18:00 | 18 | 538 | 1322 | 125 | 1 | 9 | 1 | 1 | 9 | 124 | 1 | 13 | 14300 | 1 | 9 | 100 | 1 | 9 | 14300 | 1 | 13 | 5050 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.94 | A | 7 | 979 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 4 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.56 | 2 | 0
1990-07-10 | 1900-07-09 | 19:00 | 19 | 294 | 1322 | 73 | 1 | 13 | 2 | 1 | 9 | 73 | 1 | 13 | 8300 | 1 | 13 | 100 | 1 | 9 | 8200 | 1 | 13 | 2590 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 4.1 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 72.34 | 2 | 0
1990-07-10 | 1900-07-09 | 20:00 | 20 | 63 | 1002 | 16 | 1 | 13 | 5 | 1 | 13 | 15 | 1 | 13 | 1700 | 1 | 13 | 300 | 1 | 13 | 1700 | 1 | 13 | 380 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 23.9 | 75.02 | A | 7 | 22.8 | 73.04 | A | 7 | 0.94 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 4.1 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 71.64 | 2 | 0
1990-07-10 | 1900-07-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 23.9 | 75.02 | A | 7 | 22.8 | 73.04 | A | 7 | 0.94 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 71.64 | 2 | 0
1990-07-10 | 1900-07-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 23.3 | 73.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 72.34 | 2 | 0
1990-07-10 | 1900-07-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 23.3 | 73.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.94 | A | 7 | 979 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.56 | 2 | 0
1990-07-10 | 1900-07-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 23.3 | 73.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 3050 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 72.34 | 2 | 0
1990-07-11 | 1900-07-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 3960 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 71.26 | 3 | 0
1990-07-11 | 1900-07-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 70 | A | 7 | 1.5 | A | 7 | 8000 | A | 7 | 3050 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 71.26 | 3 | 0
1990-07-11 | 1900-07-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 2290 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 71.26 | 3 | 0
1990-07-11 | 1900-07-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 30 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.36 | 3 | 0
1990-07-11 | 1900-07-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 21.7 | 71.06 | A | 7 | 1 | A | 7 | 978 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 400 | A | 7 | 150 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.96 | 3 | 0
1990-07-11 | 1900-07-10 | 6:00 | 6 | 99 | 1244 | 23 | 1 | 13 | 1 | 1 | 9 | 23 | 1 | 13 | 2600 | 1 | 13 | 0 | 1 | 9 | 2600 | 1 | 13 | 790 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 21.1 | 69.98 | A | 7 | 1 | A | 7 | 978 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 400 | A | 7 | 60 | A | 7 | 3.7 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.88 | 3 | 0
1990-07-11 | 1900-07-10 | 7:00 | 7 | 340 | 1322 | 80 | 1 | 9 | 11 | 1 | 9 | 77 | 1 | 13 | 9100 | 1 | 9 | 500 | 1 | 9 | 8900 | 1 | 13 | 2870 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 20.6 | 69.08 | A | 7 | 1 | A | 7 | 979 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 200 | A | 7 | 60 | A | 7 | 3.6 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.98 | 3 | 0
1990-07-11 | 1900-07-10 | 8:00 | 8 | 583 | 1322 | 191 | 1 | 9 | 2 | 1 | 9 | 190 | 1 | 13 | 21400 | 1 | 9 | 200 | 1 | 9 | 21400 | 1 | 13 | 7090 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 20 | 68 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 600 | A | 7 | 90 | A | 7 | 3.5 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.3 | 3 | 0
1990-07-11 | 1900-07-10 | 9:00 | 9 | 808 | 1322 | 140 | 1 | 9 | 3 | 1 | 9 | 138 | 1 | 13 | 16800 | 1 | 9 | 200 | 1 | 9 | 16700 | 1 | 13 | 6600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 19.4 | 66.92 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 2400 | A | 7 | 150 | A | 7 | 3.4 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.22 | 3 | 0
1990-07-11 | 1900-07-10 | 10:00 | 10 | 999 | 1322 | 317 | 1 | 9 | 5 | 1 | 9 | 313 | 1 | 13 | 36800 | 1 | 9 | 500 | 1 | 9 | 36500 | 1 | 13 | 13720 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 19.4 | 66.92 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 2000 | A | 7 | 120 | A | 7 | 3.4 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.22 | 3 | 0
1990-07-11 | 1900-07-10 | 11:00 | 11 | 1145 | 1322 | 377 | 1 | 9 | 2 | 1 | 9 | 376 | 1 | 13 | 44200 | 1 | 9 | 200 | 1 | 9 | 44100 | 1 | 13 | 16390 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 2000 | A | 7 | 150 | A | 7 | 3.3 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.42 | 3 | 0
1990-07-11 | 1900-07-10 | 12:00 | 12 | 1233 | 1322 | 438 | 1 | 9 | 5 | 1 | 9 | 433 | 1 | 13 | 51300 | 1 | 9 | 500 | 1 | 9 | 50900 | 1 | 13 | 18440 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 18.9 | 66.02 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 210 | A | 7 | 3.2 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 3 | 0
1990-07-11 | 1900-07-10 | 13:00 | 13 | 1259 | 1322 | 402 | 1 | 9 | 5 | 1 | 9 | 398 | 1 | 13 | 47700 | 1 | 9 | 500 | 1 | 9 | 47300 | 1 | 13 | 17560 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 340 | A | 7 | 3.3 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.92 | 3 | 0
1990-07-11 | 1900-07-10 | 14:00 | 14 | 1221 | 1322 | 433 | 1 | 9 | 1 | 1 | 9 | 432 | 1 | 13 | 50700 | 1 | 9 | 100 | 1 | 9 | 50600 | 1 | 13 | 18350 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 3.2 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 3 | 0
1990-07-11 | 1900-07-10 | 15:00 | 15 | 1121 | 1322 | 390 | 1 | 9 | 2 | 1 | 9 | 389 | 1 | 13 | 45500 | 1 | 9 | 200 | 1 | 9 | 45300 | 1 | 13 | 16640 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 18.3 | 64.94 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 3.1 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.94 | 3 | 0
1990-07-11 | 1900-07-10 | 16:00 | 16 | 966 | 1322 | 344 | 1 | 9 | 0 | 1 | 9 | 344 | 1 | 13 | 39500 | 1 | 9 | 0 | 1 | 9 | 39500 | 1 | 13 | 14330 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 340 | A | 7 | 3.3 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.92 | 3 | 0
1990-07-11 | 1900-07-10 | 17:00 | 17 | 767 | 1322 | 456 | 1 | 13 | 460 | 1 | 13 | 188 | 1 | 13 | 48600 | 1 | 13 | 47000 | 1 | 13 | 21200 | 1 | 13 | 4310 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 4270 | A | 7 | 3.2 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.54 | 3 | 0
1990-07-11 | 1900-07-10 | 18:00 | 18 | 537 | 1322 | 272 | 1 | 13 | 343 | 1 | 13 | 132 | 1 | 13 | 28600 | 1 | 13 | 33000 | 1 | 13 | 15200 | 1 | 13 | 2590 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.84 | 3 | 0
1990-07-11 | 1900-07-10 | 19:00 | 19 | 292 | 1322 | 108 | 1 | 13 | 170 | 1 | 13 | 70 | 1 | 13 | 11500 | 1 | 13 | 13400 | 1 | 13 | 8500 | 1 | 13 | 1310 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.54 | 3 | 0
1990-07-11 | 1900-07-10 | 20:00 | 20 | 62 | 1002 | 23 | 1 | 13 | 59 | 1 | 9 | 17 | 1 | 13 | 2300 | 1 | 13 | 2100 | 1 | 9 | 2100 | 1 | 13 | 290 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.92 | 3 | 0
1990-07-11 | 1900-07-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.54 | 3 | 0
1990-07-11 | 1900-07-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 18.9 | 66.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.34 | 3 | 0
1990-07-11 | 1900-07-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 981 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.04 | 3 | 0
1990-07-11 | 1900-07-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 18.3 | 64.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.44 | 3 | 0
1990-07-12 | 1900-07-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.36 | 4 | 0
1990-07-12 | 1900-07-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 17.8 | 64.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.36 | 4 | 0
1990-07-12 | 1900-07-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.66 | 4 | 0
1990-07-12 | 1900-07-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 1980 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.66 | 4 | 0
1990-07-12 | 1900-07-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 17.2 | 62.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.97 | A | 7 | 982 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 1980 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.46 | 4 | 0
1990-07-12 | 1900-07-11 | 6:00 | 6 | 97 | 1245 | 19 | 1 | 13 | 9 | 1 | 13 | 18 | 1 | 13 | 2100 | 1 | 13 | 500 | 1 | 13 | 2000 | 1 | 13 | 460 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 2.8 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 4 | 0
1990-07-12 | 1900-07-11 | 7:00 | 7 | 337 | 1322 | 146 | 1 | 13 | 262 | 1 | 9 | 78 | 1 | 13 | 15200 | 1 | 13 | 21800 | 1 | 9 | 9700 | 1 | 13 | 1430 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.48 | 4 | 0
1990-07-12 | 1900-07-11 | 8:00 | 8 | 581 | 1322 | 345 | 1 | 9 | 495 | 1 | 9 | 126 | 1 | 13 | 36800 | 1 | 9 | 48600 | 1 | 9 | 15400 | 1 | 13 | 2490 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 19.4 | 66.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.28 | 4 | 0
1990-07-12 | 1900-07-11 | 9:00 | 9 | 806 | 1322 | 379 | 1 | 13 | 278 | 1 | 13 | 209 | 1 | 13 | 41400 | 1 | 13 | 29700 | 1 | 13 | 23300 | 1 | 13 | 5090 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.86 | 4 | 0
1990-07-12 | 1900-07-11 | 10:00 | 10 | 998 | 1322 | 588 | 1 | 9 | 420 | 1 | 9 | 270 | 1 | 13 | 62800 | 1 | 9 | 43700 | 1 | 9 | 29700 | 1 | 13 | 8600 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 21.1 | 69.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.73 | A | 7 | 983 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 550 | A | 7 | 2.8 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.68 | 4 | 0
1990-07-12 | 1900-07-11 | 11:00 | 11 | 1143 | 1322 | 379 | 1 | 9 | 92 | 1 | 9 | 299 | 1 | 13 | 42500 | 1 | 9 | 9900 | 1 | 9 | 33900 | 1 | 13 | 12650 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 21.1 | 69.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.73 | A | 7 | 983 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 2.8 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.68 | 4 | 0
1990-07-12 | 1900-07-11 | 12:00 | 12 | 1232 | 1322 | 294 | 1 | 9 | 1 | 1 | 9 | 293 | 1 | 13 | 35500 | 1 | 9 | 100 | 1 | 9 | 35400 | 1 | 13 | 13940 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 17.2 | 62.96 | A | 7 | 0.84 | A | 7 | 983 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1280 | A | 7 | 3 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.76 | 4 | 0
1990-07-12 | 1900-07-11 | 13:00 | 13 | 1258 | 1322 | 321 | 1 | 9 | 3 | 1 | 9 | 318 | 1 | 13 | 38700 | 1 | 9 | 300 | 1 | 9 | 38400 | 1 | 13 | 14920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 983 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 430 | A | 7 | 2.8 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.48 | 4 | 0
1990-07-12 | 1900-07-11 | 14:00 | 14 | 1220 | 1322 | 202 | 1 | 9 | 9 | 1 | 9 | 194 | 1 | 13 | 25200 | 1 | 9 | 700 | 1 | 9 | 24600 | 1 | 13 | 9910 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.93 | A | 7 | 983 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 370 | A | 7 | 2.8 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.58 | 4 | 0
1990-07-12 | 1900-07-11 | 15:00 | 15 | 1120 | 1322 | 200 | 1 | 9 | 0 | 1 | 9 | 200 | 1 | 13 | 24500 | 1 | 9 | 0 | 1 | 9 | 24500 | 1 | 13 | 10040 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 15 | 59 | A | 7 | 0.97 | A | 7 | 984 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 3200 | A | 7 | 370 | A | 7 | 2.6 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.4 | 4 | 0
1990-07-12 | 1900-07-11 | 16:00 | 16 | 965 | 1322 | 183 | 1 | 9 | 7 | 1 | 9 | 178 | 1 | 13 | 22100 | 1 | 9 | 500 | 1 | 9 | 21700 | 1 | 13 | 8760 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 360 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 2.4 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.72 | 4 | 0
1990-07-12 | 1900-07-11 | 17:00 | 17 | 766 | 1322 | 141 | 1 | 9 | 2 | 1 | 9 | 140 | 1 | 13 | 16800 | 1 | 9 | 100 | 1 | 9 | 16700 | 1 | 13 | 6530 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 985 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 240 | A | 7 | 2.3 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 4 | 0
1990-07-12 | 1900-07-11 | 18:00 | 18 | 536 | 1322 | 85 | 1 | 9 | 2 | 1 | 9 | 84 | 1 | 13 | 10100 | 1 | 9 | 100 | 1 | 9 | 10000 | 1 | 13 | 3690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.97 | A | 7 | 985 | A | 7 | 10 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 240 | A | 7 | 2.4 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.34 | 4 | 0
1990-07-12 | 1900-07-11 | 19:00 | 19 | 291 | 1322 | 40 | 1 | 13 | 1 | 1 | 9 | 40 | 1 | 13 | 4700 | 1 | 13 | 0 | 1 | 9 | 4700 | 1 | 13 | 1610 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 985 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 4800 | A | 7 | 240 | A | 7 | 2.3 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.84 | 4 | 0
1990-07-12 | 1900-07-11 | 20:00 | 20 | 61 | 980 | 11 | 1 | 13 | 0 | 1 | 9 | 11 | 1 | 13 | 1300 | 1 | 13 | 0 | 1 | 9 | 1300 | 1 | 13 | 410 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.97 | A | 7 | 985 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 700 | A | 7 | 2.3 | E | 8 | 0.251 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 4 | 0
1990-07-12 | 1900-07-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.97 | A | 7 | 986 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 550 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.34 | 4 | 0
1990-07-12 | 1900-07-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.97 | A | 7 | 986 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.42 | 4 | 0
1990-07-12 | 1900-07-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.97 | A | 7 | 986 | A | 7 | 10 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.42 | 4 | 0
1990-07-12 | 1900-07-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 14.4 | 57.92 | A | 7 | 0.97 | A | 7 | 987 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 4 | 0
1990-07-13 | 1900-07-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 14.4 | 57.92 | A | 7 | 0.97 | A | 7 | 987 | A | 7 | 10 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 1980 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 5 | 0
1990-07-13 | 1900-07-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 986 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 2290 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.72 | 5 | 0
1990-07-13 | 1900-07-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 986 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.72 | 5 | 0
1990-07-13 | 1900-07-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 986 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.72 | 5 | 0
1990-07-13 | 1900-07-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 986 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.72 | 5 | 0
1990-07-13 | 1900-07-12 | 6:00 | 6 | 95 | 1223 | 30 | 1 | 13 | 0 | 1 | 9 | 30 | 1 | 13 | 3300 | 1 | 13 | 0 | 1 | 9 | 3300 | 1 | 13 | 950 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 987 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 2.4 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.72 | 5 | 0
1990-07-13 | 1900-07-12 | 7:00 | 7 | 335 | 1322 | 87 | 1 | 13 | 0 | 1 | 9 | 87 | 1 | 13 | 9800 | 1 | 13 | 0 | 1 | 9 | 9800 | 1 | 13 | 3110 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.9 | A | 7 | 987 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 3350 | A | 7 | 2.4 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.22 | 5 | 0
1990-07-13 | 1900-07-12 | 8:00 | 8 | 579 | 1322 | 169 | 1 | 9 | 0 | 1 | 9 | 169 | 1 | 13 | 19100 | 1 | 9 | 0 | 1 | 9 | 19100 | 1 | 13 | 6540 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.84 | A | 7 | 987 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.4 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.14 | 5 | 0
1990-07-13 | 1900-07-12 | 9:00 | 9 | 804 | 1322 | 261 | 1 | 9 | 25 | 1 | 9 | 246 | 1 | 13 | 30000 | 1 | 9 | 2200 | 1 | 9 | 28700 | 1 | 13 | 10280 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 20 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.4 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 5 | 0
1990-07-13 | 1900-07-12 | 10:00 | 10 | 996 | 1322 | 423 | 1 | 9 | 112 | 1 | 9 | 338 | 1 | 13 | 46400 | 1 | 9 | 11900 | 1 | 9 | 37400 | 1 | 13 | 11110 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.68 | A | 7 | 987 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.34 | 5 | 0
1990-07-13 | 1900-07-12 | 11:00 | 11 | 1142 | 1322 | 541 | 1 | 9 | 130 | 1 | 9 | 428 | 1 | 13 | 59300 | 1 | 9 | 13800 | 1 | 9 | 47300 | 1 | 13 | 18060 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 20 | 68 | A | 7 | 12.8 | 55.04 | A | 7 | 0.63 | A | 7 | 987 | A | 7 | 30 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.34 | 5 | 0
1990-07-13 | 1900-07-12 | 12:00 | 12 | 1231 | 1322 | 637 | 1 | 9 | 287 | 1 | 9 | 369 | 1 | 13 | 70600 | 1 | 9 | 31300 | 1 | 9 | 41400 | 1 | 13 | 21400 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 19.4 | 66.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.66 | A | 7 | 987 | A | 7 | 30 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.94 | 5 | 0
1990-07-13 | 1900-07-12 | 13:00 | 13 | 1258 | 1322 | 377 | 1 | 9 | 22 | 1 | 9 | 357 | 1 | 13 | 45200 | 1 | 9 | 2000 | 1 | 9 | 43300 | 1 | 13 | 16260 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 20.6 | 69.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.61 | A | 7 | 987 | A | 7 | 30 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.04 | 5 | 0
1990-07-13 | 1900-07-12 | 14:00 | 14 | 1219 | 1322 | 511 | 1 | 9 | 172 | 1 | 9 | 352 | 1 | 13 | 57100 | 1 | 9 | 18500 | 1 | 9 | 40000 | 1 | 13 | 18480 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 21.1 | 69.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.61 | A | 7 | 986 | A | 7 | 10 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.84 | 5 | 0
1990-07-13 | 1900-07-12 | 15:00 | 15 | 1120 | 1322 | 660 | 1 | 13 | 340 | 1 | 13 | 371 | 1 | 13 | 72100 | 1 | 13 | 36900 | 1 | 13 | 40800 | 1 | 13 | 15030 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 22.2 | 71.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.53 | A | 7 | 985 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.2 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.56 | 5 | 0
1990-07-13 | 1900-07-12 | 16:00 | 16 | 964 | 1322 | 289 | 1 | 9 | 7 | 1 | 9 | 284 | 1 | 13 | 33700 | 1 | 9 | 600 | 1 | 9 | 33200 | 1 | 13 | 12600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.76 | A | 7 | 985 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.4 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.62 | 5 | 0
1990-07-13 | 1900-07-12 | 17:00 | 17 | 765 | 1322 | 303 | 1 | 9 | 46 | 1 | 9 | 276 | 1 | 13 | 33200 | 1 | 9 | 4700 | 1 | 9 | 30500 | 1 | 13 | 8580 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.7 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 5 | 0
1990-07-13 | 1900-07-12 | 18:00 | 18 | 535 | 1322 | 138 | 1 | 9 | 9 | 1 | 9 | 135 | 1 | 13 | 15800 | 1 | 9 | 600 | 1 | 9 | 15600 | 1 | 13 | 5360 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.5 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.52 | 5 | 0
1990-07-13 | 1900-07-12 | 19:00 | 19 | 290 | 1322 | 96 | 1 | 13 | 31 | 1 | 9 | 89 | 1 | 13 | 10500 | 1 | 13 | 2600 | 1 | 9 | 9900 | 1 | 13 | 2190 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 17.2 | 62.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.84 | A | 7 | 983 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 4270 | A | 7 | 2.5 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.02 | 5 | 0
1990-07-13 | 1900-07-12 | 20:00 | 20 | 59 | 980 | 20 | 1 | 13 | 18 | 1 | 9 | 18 | 1 | 13 | 2100 | 1 | 13 | 1000 | 1 | 9 | 2000 | 1 | 13 | 440 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.93 | A | 7 | 983 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.62 | 5 | 0
1990-07-13 | 1900-07-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 983 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.72 | 5 | 0
1990-07-13 | 1900-07-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 983 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 5 | 0
1990-07-13 | 1900-07-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 983 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.24 | 5 | 0
1990-07-13 | 1900-07-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 14.4 | 57.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.87 | A | 7 | 983 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.76 | 5 | 0
1990-07-14 | 1900-07-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.97 | A | 7 | 982 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.46 | 6 | 0
1990-07-14 | 1900-07-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 13.3 | 55.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.76 | 6 | 0
1990-07-14 | 1900-07-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 6 | 0
1990-07-14 | 1900-07-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.76 | 6 | 0
1990-07-14 | 1900-07-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3350 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.76 | 6 | 0
1990-07-14 | 1900-07-13 | 6:00 | 6 | 92 | 1201 | 19 | 1 | 13 | 11 | 1 | 9 | 18 | 1 | 13 | 2100 | 1 | 13 | 700 | 1 | 9 | 2000 | 1 | 13 | 460 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 2.3 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 6 | 0
1990-07-14 | 1900-07-13 | 7:00 | 7 | 333 | 1322 | 160 | 1 | 13 | 352 | 1 | 13 | 71 | 1 | 13 | 16900 | 1 | 13 | 29200 | 1 | 13 | 9600 | 1 | 13 | 1290 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 2.3 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 6 | 0
1990-07-14 | 1900-07-13 | 8:00 | 8 | 576 | 1322 | 233 | 1 | 13 | 133 | 1 | 13 | 175 | 1 | 13 | 25500 | 1 | 13 | 13300 | 1 | 13 | 19600 | 1 | 13 | 4180 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 981 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 2.3 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.14 | 6 | 0
1990-07-14 | 1900-07-13 | 9:00 | 9 | 802 | 1322 | 455 | 1 | 13 | 519 | 1 | 13 | 139 | 1 | 13 | 48000 | 1 | 13 | 52300 | 1 | 13 | 16200 | 1 | 13 | 3350 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 6 | 0
1990-07-14 | 1900-07-13 | 10:00 | 10 | 995 | 1322 | 668 | 1 | 9 | 685 | 1 | 9 | 150 | 1 | 13 | 71700 | 1 | 9 | 70300 | 1 | 9 | 18700 | 1 | 13 | 4810 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.04 | 6 | 0
1990-07-14 | 1900-07-13 | 11:00 | 11 | 1141 | 1322 | 861 | 1 | 13 | 857 | 1 | 13 | 119 | 1 | 13 | 88600 | 1 | 13 | 85900 | 1 | 13 | 14400 | 1 | 13 | 4340 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 21.1 | 69.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.59 | A | 7 | 980 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.64 | 6 | 0
1990-07-14 | 1900-07-13 | 12:00 | 12 | 1230 | 1322 | 908 | 1 | 9 | 785 | 1 | 9 | 176 | 1 | 13 | 96000 | 1 | 9 | 79200 | 1 | 9 | 22100 | 1 | 13 | 10540 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.56 | 6 | 0
1990-07-14 | 1900-07-13 | 13:00 | 13 | 1257 | 1322 | 867 | 1 | 9 | 689 | 1 | 9 | 210 | 1 | 13 | 93600 | 1 | 9 | 70800 | 1 | 9 | 26100 | 1 | 13 | 15580 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 22.8 | 73.04 | A | 7 | 11.7 | 53.06 | A | 7 | 0.5 | A | 7 | 979 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.26 | 6 | 0
1990-07-14 | 1900-07-13 | 14:00 | 14 | 1219 | 1322 | 871 | 1 | 13 | 709 | 1 | 13 | 216 | 1 | 13 | 93500 | 1 | 13 | 72700 | 1 | 13 | 26400 | 1 | 13 | 13070 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.45 | A | 7 | 978 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.38 | 6 | 0
1990-07-14 | 1900-07-13 | 15:00 | 15 | 1119 | 1322 | 801 | 1 | 13 | 740 | 1 | 13 | 173 | 1 | 13 | 83600 | 1 | 13 | 74300 | 1 | 13 | 20600 | 1 | 13 | 6610 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.45 | A | 7 | 978 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.68 | 6 | 0
1990-07-14 | 1900-07-13 | 16:00 | 16 | 964 | 1322 | 618 | 1 | 13 | 583 | 1 | 13 | 192 | 1 | 13 | 65100 | 1 | 13 | 59100 | 1 | 13 | 21900 | 1 | 13 | 5650 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 25 | 77 | A | 7 | 10.6 | 51.08 | A | 7 | 0.4 | A | 7 | 977 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.78 | 6 | 0
1990-07-14 | 1900-07-13 | 17:00 | 17 | 764 | 1322 | 513 | 1 | 9 | 768 | 1 | 9 | 68 | 1 | 13 | 53700 | 1 | 9 | 75800 | 1 | 9 | 9800 | 1 | 13 | 1700 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.42 | A | 7 | 977 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.08 | 6 | 0
1990-07-14 | 1900-07-13 | 18:00 | 18 | 533 | 1322 | 336 | 1 | 9 | 670 | 1 | 9 | 64 | 1 | 13 | 35200 | 1 | 9 | 63900 | 1 | 9 | 9400 | 1 | 13 | 1360 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 23.9 | 75.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.43 | A | 7 | 976 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.28 | 6 | 0
1990-07-14 | 1900-07-13 | 19:00 | 19 | 288 | 1322 | 161 | 1 | 13 | 571 | 1 | 9 | 36 | 1 | 13 | 16700 | 1 | 13 | 46900 | 1 | 9 | 6500 | 1 | 13 | 750 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.55 | A | 7 | 976 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.64 | 6 | 0
1990-07-14 | 1900-07-13 | 20:00 | 20 | 58 | 958 | 32 | 1 | 13 | 166 | 1 | 9 | 16 | 1 | 13 | 2700 | 1 | 13 | 7700 | 1 | 9 | 2300 | 1 | 13 | 290 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 12.2 | 53.96 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.06 | 6 | 0
1990-07-14 | 1900-07-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.73 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.24 | 6 | 0
1990-07-14 | 1900-07-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 976 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.96 | 6 | 0
1990-07-14 | 1900-07-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.14 | 6 | 0
1990-07-14 | 1900-07-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.14 | 6 | 0
1990-07-15 | 1900-07-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 12.8 | 55.04 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.74 | 7 | 0
1990-07-15 | 1900-07-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.76 | 7 | 0
1990-07-15 | 1900-07-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.76 | 7 | 0
1990-07-15 | 1900-07-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.86 | 7 | 0
1990-07-15 | 1900-07-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 180 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.36 | 7 | 0
1990-07-15 | 1900-07-14 | 6:00 | 6 | 90 | 1179 | 30 | 1 | 13 | 38 | 1 | 9 | 26 | 1 | 13 | 3200 | 1 | 13 | 1900 | 1 | 9 | 3000 | 1 | 13 | 540 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.26 | 7 | 0
1990-07-15 | 1900-07-14 | 7:00 | 7 | 330 | 1322 | 157 | 1 | 13 | 326 | 1 | 9 | 75 | 1 | 13 | 16500 | 1 | 13 | 26900 | 1 | 9 | 9700 | 1 | 13 | 1370 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.75 | A | 7 | 976 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.66 | 7 | 0
1990-07-15 | 1900-07-14 | 8:00 | 8 | 574 | 1322 | 350 | 1 | 9 | 535 | 1 | 9 | 117 | 1 | 13 | 36100 | 1 | 9 | 51200 | 1 | 9 | 13900 | 1 | 13 | 2300 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.86 | 7 | 0
1990-07-15 | 1900-07-14 | 9:00 | 9 | 800 | 1322 | 547 | 1 | 9 | 649 | 1 | 9 | 152 | 1 | 13 | 57300 | 1 | 9 | 65100 | 1 | 9 | 17800 | 1 | 13 | 3600 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.84 | 7 | 0
1990-07-15 | 1900-07-14 | 10:00 | 10 | 993 | 1322 | 721 | 1 | 9 | 719 | 1 | 9 | 179 | 1 | 13 | 76500 | 1 | 9 | 73300 | 1 | 9 | 21300 | 1 | 13 | 5630 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.56 | A | 7 | 977 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.72 | 7 | 0
1990-07-15 | 1900-07-14 | 11:00 | 11 | 1139 | 1322 | 854 | 1 | 9 | 760 | 1 | 9 | 197 | 1 | 13 | 91500 | 1 | 9 | 77900 | 1 | 9 | 24200 | 1 | 13 | 8850 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.49 | A | 7 | 977 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.32 | 7 | 0
1990-07-15 | 1900-07-14 | 12:00 | 12 | 1229 | 1322 | 939 | 1 | 9 | 786 | 1 | 9 | 206 | 1 | 13 | 97500 | 1 | 9 | 78700 | 1 | 9 | 24200 | 1 | 13 | 11920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.47 | A | 7 | 977 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.62 | 7 | 0
1990-07-15 | 1900-07-14 | 13:00 | 13 | 1256 | 1322 | 965 | 1 | 9 | 792 | 1 | 9 | 209 | 1 | 13 | 100300 | 1 | 9 | 79300 | 1 | 9 | 24700 | 1 | 13 | 14130 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.44 | A | 7 | 976 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.22 | 7 | 0
1990-07-15 | 1900-07-14 | 14:00 | 14 | 1218 | 1322 | 930 | 1 | 9 | 761 | 1 | 9 | 227 | 1 | 13 | 99400 | 1 | 9 | 77800 | 1 | 9 | 27600 | 1 | 13 | 13630 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.4 | A | 7 | 976 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.12 | 7 | 0
1990-07-15 | 1900-07-14 | 15:00 | 15 | 1118 | 1322 | 836 | 1 | 9 | 752 | 1 | 9 | 199 | 1 | 13 | 89400 | 1 | 9 | 77000 | 1 | 9 | 24200 | 1 | 13 | 8360 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 13.3 | 55.94 | A | 7 | 0.36 | A | 7 | 976 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.74 | 7 | 0
1990-07-15 | 1900-07-14 | 16:00 | 16 | 963 | 1322 | 695 | 1 | 9 | 706 | 1 | 9 | 179 | 1 | 13 | 73500 | 1 | 9 | 71800 | 1 | 9 | 21100 | 1 | 13 | 5300 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.34 | A | 7 | 976 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.64 | 7 | 0
1990-07-15 | 1900-07-14 | 17:00 | 17 | 763 | 1322 | 515 | 1 | 9 | 637 | 1 | 9 | 147 | 1 | 13 | 53900 | 1 | 9 | 63600 | 1 | 9 | 17200 | 1 | 13 | 3350 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 12.8 | 55.04 | A | 7 | 0.35 | A | 7 | 975 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.84 | 7 | 0
1990-07-15 | 1900-07-14 | 18:00 | 18 | 532 | 1322 | 301 | 1 | 9 | 473 | 1 | 9 | 110 | 1 | 13 | 32200 | 1 | 9 | 45500 | 1 | 9 | 13900 | 1 | 13 | 2110 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 29.4 | 84.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.39 | A | 7 | 975 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.12 | 7 | 0
1990-07-15 | 1900-07-14 | 19:00 | 19 | 286 | 1322 | 127 | 1 | 13 | 275 | 1 | 9 | 67 | 1 | 13 | 13300 | 1 | 13 | 21400 | 1 | 9 | 8600 | 1 | 13 | 1220 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.43 | A | 7 | 975 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.02 | 7 | 0
1990-07-15 | 1900-07-14 | 20:00 | 20 | 57 | 958 | 22 | 1 | 13 | 19 | 1 | 9 | 20 | 1 | 13 | 2300 | 1 | 13 | 1100 | 1 | 9 | 2300 | 1 | 13 | 480 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.45 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.218 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.42 | 7 | 0
1990-07-15 | 1900-07-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.49 | A | 7 | 976 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.32 | 7 | 0
1990-07-15 | 1900-07-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 13.9 | 57.02 | A | 7 | 0.5 | A | 7 | 977 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.52 | 7 | 0
1990-07-15 | 1900-07-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.52 | A | 7 | 977 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.04 | 7 | 0
1990-07-15 | 1900-07-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.48 | A | 7 | 977 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.44 | 7 | 0
1990-07-16 | 1900-07-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.5 | A | 7 | 978 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.84 | 1 | 0
1990-07-16 | 1900-07-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.53 | A | 7 | 978 | A | 7 | 210 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.44 | 1 | 0
1990-07-16 | 1900-07-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.32 | 1 | 0
1990-07-16 | 1900-07-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.66 | A | 7 | 979 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 1 | 0
1990-07-16 | 1900-07-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 20.6 | 69.08 | A | 7 | 15 | 59 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.5 | 1 | 0
1990-07-16 | 1900-07-15 | 6:00 | 6 | 87 | 1179 | 38 | 1 | 13 | 156 | 1 | 9 | 23 | 1 | 13 | 3700 | 1 | 13 | 7000 | 1 | 9 | 3200 | 1 | 13 | 410 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.88 | 1 | 0
1990-07-16 | 1900-07-15 | 7:00 | 7 | 328 | 1322 | 172 | 1 | 13 | 484 | 1 | 9 | 52 | 1 | 13 | 17900 | 1 | 13 | 40400 | 1 | 9 | 7900 | 1 | 13 | 980 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.88 | 1 | 0
1990-07-16 | 1900-07-15 | 8:00 | 8 | 572 | 1322 | 377 | 1 | 9 | 706 | 1 | 9 | 70 | 1 | 13 | 39500 | 1 | 9 | 68100 | 1 | 9 | 10000 | 1 | 13 | 1490 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.66 | A | 7 | 981 | A | 7 | 210 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.16 | 1 | 0
1990-07-16 | 1900-07-15 | 9:00 | 9 | 799 | 1322 | 568 | 1 | 9 | 789 | 1 | 9 | 89 | 1 | 13 | 60600 | 1 | 9 | 79200 | 1 | 9 | 12700 | 1 | 13 | 2200 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 17.8 | 64.04 | A | 7 | 0.64 | A | 7 | 981 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.54 | 1 | 0
1990-07-16 | 1900-07-15 | 10:00 | 10 | 992 | 1322 | 735 | 1 | 9 | 839 | 1 | 9 | 103 | 1 | 13 | 76000 | 1 | 9 | 83800 | 1 | 9 | 13000 | 1 | 13 | 2760 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 1 | 0
1990-07-16 | 1900-07-15 | 11:00 | 11 | 1138 | 1322 | 867 | 1 | 9 | 872 | 1 | 9 | 113 | 1 | 13 | 89300 | 1 | 9 | 87400 | 1 | 9 | 13900 | 1 | 13 | 4170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 1 | 0
1990-07-16 | 1900-07-15 | 12:00 | 12 | 1228 | 1322 | 947 | 1 | 9 | 889 | 1 | 9 | 119 | 1 | 13 | 97400 | 1 | 9 | 89200 | 1 | 9 | 14400 | 1 | 13 | 6170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.56 | 1 | 0
1990-07-16 | 1900-07-15 | 13:00 | 13 | 1255 | 1322 | 976 | 1 | 9 | 898 | 1 | 9 | 121 | 1 | 13 | 100300 | 1 | 9 | 90100 | 1 | 9 | 14600 | 1 | 13 | 7250 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 16.7 | 62.06 | A | 7 | 0.45 | A | 7 | 981 | A | 7 | 200 | A | 7 | 9.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.46 | 1 | 0
1990-07-16 | 1900-07-15 | 14:00 | 14 | 1217 | 1322 | 944 | 1 | 9 | 894 | 1 | 9 | 118 | 1 | 13 | 97100 | 1 | 9 | 89700 | 1 | 9 | 14300 | 1 | 13 | 5810 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.42 | A | 7 | 981 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.88 | 1 | 0
1990-07-16 | 1900-07-15 | 15:00 | 15 | 1117 | 1322 | 854 | 1 | 9 | 876 | 1 | 9 | 112 | 1 | 13 | 88100 | 1 | 9 | 87800 | 1 | 9 | 13800 | 1 | 13 | 3890 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.4 | A | 7 | 981 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.48 | 1 | 0
1990-07-16 | 1900-07-15 | 16:00 | 16 | 961 | 1322 | 718 | 1 | 9 | 845 | 1 | 9 | 101 | 1 | 13 | 74300 | 1 | 9 | 84300 | 1 | 9 | 12800 | 1 | 13 | 2590 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.4 | A | 7 | 980 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.48 | 1 | 0
1990-07-16 | 1900-07-15 | 17:00 | 17 | 761 | 1322 | 540 | 1 | 9 | 785 | 1 | 9 | 86 | 1 | 13 | 57500 | 1 | 9 | 78500 | 1 | 9 | 12200 | 1 | 13 | 2050 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.45 | A | 7 | 980 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.16 | 1 | 0
1990-07-16 | 1900-07-15 | 18:00 | 18 | 530 | 1322 | 343 | 1 | 9 | 687 | 1 | 9 | 66 | 1 | 13 | 35800 | 1 | 9 | 65400 | 1 | 9 | 9600 | 1 | 13 | 1380 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.45 | A | 7 | 980 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.58 | 1 | 0
1990-07-16 | 1900-07-15 | 19:00 | 19 | 284 | 1322 | 150 | 1 | 13 | 489 | 1 | 9 | 44 | 1 | 13 | 15500 | 1 | 13 | 38900 | 1 | 9 | 7200 | 1 | 13 | 830 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.46 | A | 7 | 981 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.08 | 1 | 0
1990-07-16 | 1900-07-15 | 20:00 | 20 | 55 | 937 | 27 | 1 | 13 | 102 | 1 | 9 | 18 | 1 | 13 | 2600 | 1 | 13 | 4000 | 1 | 9 | 2300 | 1 | 13 | 310 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.48 | 1 | 0
1990-07-16 | 1900-07-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 16.1 | 60.98 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.48 | 1 | 0
1990-07-16 | 1900-07-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.38 | 1 | 0
1990-07-16 | 1900-07-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 15 | 59 | A | 7 | 0.58 | A | 7 | 982 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.8 | 1 | 0
1990-07-16 | 1900-07-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.58 | A | 7 | 982 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.92 | 1 | 0
1990-07-17 | 1900-07-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.57 | A | 7 | 982 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.92 | 2 | 0
1990-07-17 | 1900-07-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.55 | A | 7 | 982 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.64 | 2 | 0
1990-07-17 | 1900-07-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.04 | 2 | 0
1990-07-17 | 1900-07-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 21.7 | 71.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.44 | 2 | 0
1990-07-17 | 1900-07-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 982 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 2 | 0
1990-07-17 | 1900-07-16 | 6:00 | 6 | 85 | 1157 | 21 | 1 | 13 | 2 | 1 | 13 | 21 | 1 | 13 | 2400 | 1 | 13 | 0 | 1 | 13 | 2400 | 1 | 13 | 730 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 21.1 | 69.98 | A | 7 | 15 | 59 | A | 7 | 0.68 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.9 | 2 | 0
1990-07-17 | 1900-07-16 | 7:00 | 7 | 325 | 1322 | 82 | 1 | 13 | 6 | 1 | 9 | 80 | 1 | 13 | 9200 | 1 | 13 | 300 | 1 | 9 | 9100 | 1 | 13 | 2890 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.68 | A | 7 | 983 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 2.7 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.88 | 2 | 0
1990-07-17 | 1900-07-16 | 8:00 | 8 | 570 | 1322 | 204 | 1 | 9 | 28 | 1 | 9 | 192 | 1 | 13 | 22800 | 1 | 9 | 2300 | 1 | 9 | 21800 | 1 | 13 | 7020 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.18 | 2 | 0
1990-07-17 | 1900-07-16 | 9:00 | 9 | 797 | 1322 | 397 | 1 | 13 | 212 | 1 | 13 | 268 | 1 | 13 | 43200 | 1 | 13 | 22200 | 1 | 13 | 29800 | 1 | 13 | 7260 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 23.9 | 75.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.96 | 2 | 0
1990-07-17 | 1900-07-16 | 10:00 | 10 | 990 | 1322 | 643 | 1 | 13 | 400 | 1 | 13 | 342 | 1 | 13 | 69400 | 1 | 13 | 43200 | 1 | 13 | 37000 | 1 | 13 | 10840 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.84 | 2 | 0
1990-07-17 | 1900-07-16 | 11:00 | 11 | 1137 | 1322 | 788 | 1 | 9 | 550 | 1 | 9 | 313 | 1 | 13 | 84500 | 1 | 9 | 57500 | 1 | 9 | 35000 | 1 | 13 | 14060 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 27.2 | 80.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.58 | A | 7 | 983 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.94 | 2 | 0
1990-07-17 | 1900-07-16 | 12:00 | 12 | 1227 | 1322 | 857 | 1 | 9 | 624 | 1 | 9 | 276 | 1 | 13 | 90400 | 1 | 9 | 63200 | 1 | 9 | 31600 | 1 | 13 | 17070 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.57 | A | 7 | 982 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.62 | 2 | 0
1990-07-17 | 1900-07-16 | 13:00 | 13 | 1254 | 1322 | 897 | 1 | 9 | 636 | 1 | 9 | 292 | 1 | 13 | 94500 | 1 | 9 | 64300 | 1 | 9 | 33400 | 1 | 13 | 20870 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 29.4 | 84.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.51 | A | 7 | 982 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.24 | 2 | 0
1990-07-17 | 1900-07-16 | 14:00 | 14 | 1216 | 1322 | 903 | 1 | 13 | 643 | 1 | 13 | 309 | 1 | 13 | 94300 | 1 | 13 | 64600 | 1 | 13 | 34800 | 1 | 13 | 17980 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 28.9 | 84.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.74 | 2 | 0
1990-07-17 | 1900-07-16 | 15:00 | 15 | 1116 | 1322 | 745 | 1 | 13 | 558 | 1 | 13 | 272 | 1 | 13 | 80800 | 1 | 13 | 58400 | 1 | 13 | 31400 | 1 | 13 | 11390 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 30 | 86 | A | 7 | 18.3 | 64.94 | A | 7 | 0.5 | A | 7 | 982 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.04 | 2 | 0
1990-07-17 | 1900-07-16 | 16:00 | 16 | 960 | 1322 | 653 | 1 | 9 | 598 | 1 | 9 | 217 | 1 | 13 | 68000 | 1 | 9 | 60200 | 1 | 9 | 24300 | 1 | 13 | 6240 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 30 | 86 | A | 7 | 18.3 | 64.94 | A | 7 | 0.5 | A | 7 | 982 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.04 | 2 | 0
1990-07-17 | 1900-07-16 | 17:00 | 17 | 760 | 1322 | 489 | 1 | 9 | 546 | 1 | 9 | 174 | 1 | 13 | 52400 | 1 | 9 | 55800 | 1 | 9 | 20300 | 1 | 13 | 3930 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.24 | 2 | 0
1990-07-17 | 1900-07-16 | 18:00 | 18 | 529 | 1322 | 291 | 1 | 9 | 401 | 1 | 9 | 130 | 1 | 13 | 30600 | 1 | 9 | 38500 | 1 | 9 | 15200 | 1 | 13 | 2540 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.53 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.74 | 2 | 0
1990-07-17 | 1900-07-16 | 19:00 | 19 | 283 | 1322 | 118 | 1 | 13 | 161 | 1 | 9 | 83 | 1 | 13 | 12300 | 1 | 13 | 12500 | 1 | 9 | 9700 | 1 | 13 | 1610 | 1 | 21 | 6 | A | 7 | 1 | A | 7 | 27.8 | 82.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.02 | 2 | 0
1990-07-17 | 1900-07-16 | 20:00 | 20 | 54 | 915 | 22 | 1 | 13 | 4 | 1 | 9 | 22 | 1 | 13 | 2500 | 1 | 13 | 0 | 1 | 9 | 2500 | 1 | 13 | 710 | 1 | 21 | 5 | A | 7 | 1 | A | 7 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.292 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.52 | 2 | 0
1990-07-17 | 1900-07-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 1 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 2 | 0
1990-07-17 | 1900-07-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.22 | 2 | 0
1990-07-17 | 1900-07-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.62 | 2 | 0
1990-07-17 | 1900-07-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 2 | 0
1990-07-18 | 1900-07-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 3 | 0
1990-07-18 | 1900-07-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 3 | 0
1990-07-18 | 1900-07-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.12 | 3 | 0
1990-07-18 | 1900-07-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 20 | 68 | A | 7 | 0.87 | A | 7 | 983 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.2 | 3 | 0
1990-07-18 | 1900-07-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.87 | A | 7 | 983 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.22 | 3 | 0
1990-07-18 | 1900-07-17 | 6:00 | 6 | 83 | 1135 | 34 | 1 | 13 | 57 | 1 | 9 | 28 | 1 | 13 | 3500 | 1 | 13 | 2700 | 1 | 9 | 3300 | 1 | 13 | 580 | 1 | 21 | 9 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 20 | 68 | A | 7 | 0.9 | A | 7 | 983 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.9 | 3 | 0
1990-07-18 | 1900-07-17 | 7:00 | 7 | 323 | 1322 | 170 | 1 | 13 | 437 | 1 | 9 | 63 | 1 | 13 | 17400 | 1 | 13 | 35900 | 1 | 9 | 8600 | 1 | 13 | 1140 | 1 | 21 | 5 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.87 | A | 7 | 984 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.28 | 3 | 0
1990-07-18 | 1900-07-17 | 8:00 | 8 | 567 | 1322 | 364 | 1 | 9 | 661 | 1 | 9 | 79 | 1 | 13 | 38600 | 1 | 9 | 64200 | 1 | 9 | 11000 | 1 | 13 | 1640 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 21.1 | 69.98 | A | 7 | 0.79 | A | 7 | 984 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.28 | 3 | 0
1990-07-18 | 1900-07-17 | 9:00 | 9 | 795 | 1322 | 558 | 1 | 9 | 757 | 1 | 9 | 101 | 1 | 13 | 58700 | 1 | 9 | 75600 | 1 | 9 | 13200 | 1 | 13 | 2380 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 983 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 3 | 0
1990-07-18 | 1900-07-17 | 10:00 | 10 | 988 | 1322 | 730 | 1 | 9 | 821 | 1 | 9 | 114 | 1 | 13 | 78200 | 1 | 9 | 83200 | 1 | 9 | 15900 | 1 | 13 | 3500 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 983 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 3 | 0
1990-07-18 | 1900-07-17 | 11:00 | 11 | 1135 | 1322 | 807 | 1 | 9 | 802 | 1 | 9 | 116 | 1 | 13 | 83100 | 1 | 9 | 80400 | 1 | 9 | 14000 | 1 | 13 | 4190 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 984 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.98 | 3 | 0
1990-07-18 | 1900-07-17 | 12:00 | 12 | 1225 | 1322 | 826 | 1 | 9 | 667 | 1 | 9 | 205 | 1 | 13 | 88900 | 1 | 9 | 68600 | 1 | 9 | 25200 | 1 | 13 | 12810 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 29.4 | 84.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.59 | A | 7 | 983 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.68 | 3 | 0
1990-07-18 | 1900-07-17 | 13:00 | 13 | 1252 | 1322 | 885 | 1 | 13 | 688 | 1 | 13 | 231 | 1 | 13 | 94800 | 1 | 13 | 70400 | 1 | 13 | 27900 | 1 | 13 | 16590 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 30.6 | 87.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.55 | A | 7 | 983 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 3 | 0
1990-07-18 | 1900-07-17 | 14:00 | 14 | 1215 | 1322 | 874 | 1 | 13 | 753 | 1 | 13 | 180 | 1 | 13 | 91900 | 1 | 13 | 75900 | 1 | 13 | 22100 | 1 | 13 | 9910 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.18 | 3 | 0
1990-07-18 | 1900-07-17 | 15:00 | 15 | 1115 | 1322 | 759 | 1 | 13 | 522 | 1 | 13 | 318 | 1 | 13 | 81100 | 1 | 13 | 54500 | 1 | 13 | 35100 | 1 | 13 | 13380 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.53 | A | 7 | 983 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1280 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.18 | 3 | 0
1990-07-18 | 1900-07-17 | 16:00 | 16 | 959 | 1322 | 671 | 1 | 13 | 680 | 1 | 13 | 175 | 1 | 13 | 70900 | 1 | 13 | 69200 | 1 | 13 | 20600 | 1 | 13 | 5160 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 31.7 | 89.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.52 | A | 7 | 982 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 3 | 0
1990-07-18 | 1900-07-17 | 17:00 | 17 | 759 | 1322 | 516 | 1 | 9 | 732 | 1 | 9 | 95 | 1 | 13 | 54400 | 1 | 9 | 72900 | 1 | 9 | 12500 | 1 | 13 | 2190 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 20 | 68 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57 | 3 | 0
1990-07-18 | 1900-07-17 | 18:00 | 18 | 527 | 1322 | 331 | 1 | 9 | 646 | 1 | 9 | 72 | 1 | 13 | 35000 | 1 | 9 | 61900 | 1 | 9 | 10300 | 1 | 13 | 1470 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 20 | 68 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.8 | 3 | 0
1990-07-18 | 1900-07-17 | 19:00 | 19 | 280 | 1322 | 142 | 1 | 13 | 441 | 1 | 9 | 47 | 1 | 13 | 14600 | 1 | 13 | 34700 | 1 | 9 | 7200 | 1 | 13 | 870 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.68 | 3 | 0
1990-07-18 | 1900-07-17 | 20:00 | 20 | 52 | 915 | 26 | 1 | 13 | 77 | 1 | 9 | 18 | 1 | 13 | 2400 | 1 | 13 | 2600 | 1 | 9 | 2300 | 1 | 13 | 310 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 20 | 68 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.7 | 3 | 0
1990-07-18 | 1900-07-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.68 | 3 | 0
1990-07-18 | 1900-07-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.7 | 3 | 0
1990-07-18 | 1900-07-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.22 | 3 | 0
1990-07-18 | 1900-07-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 3 | 0
1990-07-19 | 1900-07-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.12 | 4 | 0
1990-07-19 | 1900-07-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.82 | 4 | 0
1990-07-19 | 1900-07-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 4 | 0
1990-07-19 | 1900-07-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 4 | 0
1990-07-19 | 1900-07-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.12 | 4 | 0
1990-07-19 | 1900-07-18 | 6:00 | 6 | 80 | 1113 | 31 | 1 | 13 | 101 | 1 | 13 | 21 | 1 | 13 | 3000 | 1 | 13 | 4400 | 1 | 13 | 2700 | 1 | 13 | 370 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.1 | 4 | 0
1990-07-19 | 1900-07-18 | 7:00 | 7 | 320 | 1323 | 87 | 1 | 13 | 29 | 1 | 13 | 80 | 1 | 13 | 9500 | 1 | 13 | 2500 | 1 | 13 | 8900 | 1 | 13 | 2090 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 3.5 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 4 | 0
1990-07-19 | 1900-07-18 | 8:00 | 8 | 565 | 1323 | 235 | 1 | 9 | 133 | 1 | 9 | 178 | 1 | 13 | 25600 | 1 | 9 | 13300 | 1 | 9 | 19900 | 1 | 13 | 4230 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 3.5 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.3 | 4 | 0
1990-07-19 | 1900-07-18 | 9:00 | 9 | 793 | 1323 | 529 | 1 | 13 | 617 | 1 | 13 | 158 | 1 | 13 | 55200 | 1 | 13 | 61700 | 1 | 13 | 18200 | 1 | 13 | 3690 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.22 | 4 | 0
1990-07-19 | 1900-07-18 | 10:00 | 10 | 987 | 1323 | 666 | 1 | 9 | 713 | 1 | 9 | 133 | 1 | 13 | 70300 | 1 | 9 | 71800 | 1 | 9 | 16600 | 1 | 13 | 3900 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.63 | A | 7 | 981 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.68 | 4 | 0
1990-07-19 | 1900-07-18 | 11:00 | 11 | 1134 | 1323 | 810 | 1 | 9 | 800 | 1 | 9 | 122 | 1 | 13 | 83300 | 1 | 9 | 80100 | 1 | 9 | 14500 | 1 | 13 | 4290 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 28.9 | 84.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.61 | A | 7 | 981 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 4 | 0
1990-07-19 | 1900-07-18 | 12:00 | 12 | 1224 | 1323 | 690 | 1 | 13 | 514 | 1 | 13 | 213 | 1 | 13 | 74200 | 1 | 13 | 52700 | 1 | 13 | 25300 | 1 | 13 | 13200 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 30.6 | 87.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 220 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 4 | 0
1990-07-19 | 1900-07-18 | 13:00 | 13 | 1251 | 1323 | 858 | 1 | 13 | 719 | 1 | 13 | 175 | 1 | 13 | 90900 | 1 | 13 | 72700 | 1 | 13 | 22000 | 1 | 13 | 11780 | 1 | 23 | 7 | A | 7 | 4 | A | 7 | 31.7 | 89.06 | A | 7 | 20 | 68 | A | 7 | 0.5 | A | 7 | 980 | A | 7 | 210 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 3.5 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.5 | 4 | 0
1990-07-19 | 1900-07-18 | 14:00 | 14 | 1214 | 1323 | 807 | 1 | 13 | 642 | 1 | 13 | 216 | 1 | 13 | 86500 | 1 | 13 | 65800 | 1 | 13 | 26000 | 1 | 13 | 12730 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 32.2 | 89.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.47 | A | 7 | 979 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.82 | 4 | 0
1990-07-19 | 1900-07-18 | 15:00 | 15 | 1113 | 1323 | 731 | 1 | 9 | 636 | 1 | 9 | 194 | 1 | 13 | 78200 | 1 | 9 | 65100 | 1 | 9 | 23200 | 1 | 13 | 8050 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 32.2 | 89.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.47 | A | 7 | 978 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.82 | 4 | 0
1990-07-19 | 1900-07-18 | 16:00 | 16 | 958 | 1323 | 527 | 1 | 13 | 408 | 1 | 13 | 231 | 1 | 13 | 56800 | 1 | 13 | 42400 | 1 | 13 | 26000 | 1 | 13 | 6770 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 32.2 | 89.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.47 | A | 7 | 978 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.82 | 4 | 0
1990-07-19 | 1900-07-18 | 17:00 | 17 | 757 | 1323 | 439 | 1 | 13 | 437 | 1 | 13 | 188 | 1 | 13 | 46700 | 1 | 13 | 44600 | 1 | 13 | 21100 | 1 | 13 | 4270 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 32.2 | 89.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.47 | A | 7 | 977 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.82 | 4 | 0
1990-07-19 | 1900-07-18 | 18:00 | 18 | 525 | 1323 | 285 | 1 | 13 | 418 | 1 | 13 | 119 | 1 | 13 | 30300 | 1 | 13 | 40100 | 1 | 13 | 14400 | 1 | 13 | 2300 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 31.1 | 87.98 | A | 7 | 20 | 68 | A | 7 | 0.52 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57 | 4 | 0
1990-07-19 | 1900-07-18 | 19:00 | 19 | 278 | 1323 | 147 | 1 | 13 | 437 | 1 | 9 | 54 | 1 | 13 | 15000 | 1 | 13 | 34000 | 1 | 9 | 7800 | 1 | 13 | 970 | 1 | 21 | 4 | A | 7 | 2 | A | 7 | 29.4 | 84.92 | A | 7 | 20 | 68 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.3 | 4 | 0
1990-07-19 | 1900-07-18 | 20:00 | 20 | 51 | 893 | 27 | 1 | 13 | 62 | 1 | 9 | 21 | 1 | 13 | 2600 | 1 | 13 | 2000 | 1 | 9 | 2500 | 1 | 13 | 370 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 4 | 0
1990-07-19 | 1900-07-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.62 | 4 | 0
1990-07-19 | 1900-07-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 28.3 | 82.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.62 | 4 | 0
1990-07-19 | 1900-07-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 27.8 | 82.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 4 | 0
1990-07-19 | 1900-07-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 978 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.52 | 4 | 0
1990-07-20 | 1900-07-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | 25 | 77 | A | 7 | 18.9 | 66.02 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.42 | 5 | 0
1990-07-20 | 1900-07-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 5 | 0
1990-07-20 | 1900-07-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 5 | 0
1990-07-20 | 1900-07-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 910 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.38 | 5 | 0
1990-07-20 | 1900-07-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 3350 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.38 | 5 | 0
1990-07-20 | 1900-07-19 | 6:00 | 6 | 78 | 1113 | 20 | 1 | 13 | 1 | 1 | 9 | 19 | 1 | 13 | 2200 | 1 | 13 | 0 | 1 | 9 | 2200 | 1 | 13 | 670 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 20 | 68 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 3.5 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.3 | 5 | 0
1990-07-20 | 1900-07-19 | 7:00 | 7 | 317 | 1323 | 99 | 1 | 13 | 25 | 1 | 9 | 93 | 1 | 13 | 10800 | 1 | 13 | 2200 | 1 | 9 | 10300 | 1 | 13 | 2350 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 21.1 | 69.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 3.6 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.38 | 5 | 0
1990-07-20 | 1900-07-19 | 8:00 | 8 | 563 | 1323 | 150 | 1 | 9 | 47 | 1 | 9 | 130 | 1 | 13 | 16500 | 1 | 9 | 4500 | 1 | 9 | 14600 | 1 | 13 | 3910 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 120 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 3.6 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.78 | 5 | 0
1990-07-20 | 1900-07-19 | 9:00 | 9 | 791 | 1323 | 265 | 1 | 9 | 10 | 1 | 9 | 259 | 1 | 13 | 30200 | 1 | 9 | 900 | 1 | 9 | 29700 | 1 | 13 | 10520 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 3.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.78 | 5 | 0
1990-07-20 | 1900-07-19 | 10:00 | 10 | 985 | 1323 | 382 | 1 | 9 | 129 | 1 | 9 | 286 | 1 | 13 | 42400 | 1 | 9 | 13800 | 1 | 9 | 32100 | 1 | 13 | 9260 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 23.9 | 75.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 350 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 4270 | A | 7 | 3.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.68 | 5 | 0
1990-07-20 | 1900-07-19 | 11:00 | 11 | 1132 | 1323 | 685 | 1 | 13 | 409 | 1 | 13 | 334 | 1 | 13 | 73000 | 1 | 13 | 42700 | 1 | 13 | 36400 | 1 | 13 | 14840 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 26.1 | 78.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 4270 | A | 7 | 3.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.86 | 5 | 0
1990-07-20 | 1900-07-19 | 12:00 | 12 | 1223 | 1323 | 730 | 1 | 13 | 503 | 1 | 13 | 264 | 1 | 13 | 80600 | 1 | 13 | 52800 | 1 | 13 | 31700 | 1 | 13 | 16360 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 5 | 0
1990-07-20 | 1900-07-19 | 13:00 | 13 | 1250 | 1323 | 754 | 1 | 13 | 517 | 1 | 13 | 264 | 1 | 13 | 80000 | 1 | 13 | 52600 | 1 | 13 | 30200 | 1 | 13 | 18540 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.96 | 5 | 0
1990-07-20 | 1900-07-19 | 14:00 | 14 | 1212 | 1323 | 706 | 1 | 13 | 441 | 1 | 13 | 301 | 1 | 13 | 76900 | 1 | 13 | 46200 | 1 | 13 | 34400 | 1 | 13 | 17840 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 4270 | A | 7 | 3.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.98 | 5 | 0
1990-07-20 | 1900-07-19 | 15:00 | 15 | 1112 | 1323 | 573 | 1 | 9 | 313 | 1 | 9 | 309 | 1 | 13 | 63400 | 1 | 9 | 34000 | 1 | 9 | 34700 | 1 | 13 | 12020 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 3.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.66 | 5 | 0
1990-07-20 | 1900-07-19 | 16:00 | 16 | 956 | 1323 | 276 | 1 | 9 | 12 | 1 | 9 | 268 | 1 | 13 | 32400 | 1 | 9 | 1000 | 1 | 9 | 31600 | 1 | 13 | 12030 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 3960 | A | 7 | 3.6 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.18 | 5 | 0
1990-07-20 | 1900-07-19 | 17:00 | 17 | 755 | 1323 | 225 | 1 | 9 | 77 | 1 | 9 | 180 | 1 | 13 | 24700 | 1 | 9 | 7700 | 1 | 9 | 20300 | 1 | 13 | 6010 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 27.2 | 80.96 | A | 7 | 22.8 | 73.04 | A | 7 | 0.77 | A | 7 | 978 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 3960 | A | 7 | 4.1 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.74 | 5 | 0
1990-07-20 | 1900-07-19 | 18:00 | 18 | 523 | 1323 | 213 | 1 | 9 | 113 | 1 | 9 | 168 | 1 | 13 | 23100 | 1 | 9 | 11100 | 1 | 9 | 18700 | 1 | 13 | 3930 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 3.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.66 | 5 | 0
1990-07-20 | 1900-07-19 | 19:00 | 19 | 276 | 1323 | 133 | 1 | 13 | 374 | 1 | 13 | 54 | 1 | 13 | 13500 | 1 | 13 | 29000 | 1 | 13 | 7500 | 1 | 13 | 970 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.98 | 5 | 0
1990-07-20 | 1900-07-19 | 20:00 | 20 | 49 | 871 | 16 | 1 | 13 | 7 | 1 | 9 | 15 | 1 | 13 | 1700 | 1 | 13 | 400 | 1 | 9 | 1700 | 1 | 13 | 370 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 3350 | A | 7 | 3.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 5 | 0
1990-07-20 | 1900-07-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 5 | 0
1990-07-20 | 1900-07-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 23.3 | 73.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.08 | 5 | 0
1990-07-20 | 1900-07-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 60 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.86 | 5 | 0
1990-07-20 | 1900-07-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.94 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.76 | 5 | 0
1990-07-21 | 1900-07-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.36 | 6 | 0
1990-07-21 | 1900-07-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 22.2 | 71.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.94 | A | 7 | 979 | A | 7 | 50 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.68 | 6 | 0
1990-07-21 | 1900-07-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | 21.7 | 71.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.28 | 6 | 0
1990-07-21 | 1900-07-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 21.7 | 71.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 70 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.28 | 6 | 0
1990-07-21 | 1900-07-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 21.7 | 71.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 9140 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.58 | 6 | 0
1990-07-21 | 1900-07-20 | 6:00 | 6 | 75 | 1091 | 9 | 1 | 13 | 1 | 1 | 9 | 9 | 1 | 13 | 1100 | 1 | 13 | 0 | 1 | 9 | 1100 | 1 | 13 | 350 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 4800 | A | 7 | 90 | A | 7 | 3.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.28 | 6 | 0
1990-07-21 | 1900-07-20 | 7:00 | 7 | 314 | 1323 | 48 | 1 | 13 | 0 | 1 | 9 | 48 | 1 | 13 | 5600 | 1 | 13 | 0 | 1 | 9 | 5600 | 1 | 13 | 1920 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 1600 | A | 7 | 120 | A | 7 | 3.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.28 | 6 | 0
1990-07-21 | 1900-07-20 | 8:00 | 8 | 560 | 1323 | 87 | 1 | 9 | 1 | 1 | 9 | 86 | 1 | 13 | 10300 | 1 | 9 | 100 | 1 | 9 | 10300 | 1 | 13 | 3830 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 19.4 | 66.92 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 240 | A | 7 | 3.4 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.22 | 6 | 0
1990-07-21 | 1900-07-20 | 9:00 | 9 | 789 | 1323 | 151 | 1 | 9 | 3 | 1 | 9 | 149 | 1 | 13 | 18000 | 1 | 9 | 200 | 1 | 9 | 17800 | 1 | 13 | 6960 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 20 | 68 | A | 7 | 1 | A | 7 | 979 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 3.5 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.9 | 6 | 0
1990-07-21 | 1900-07-20 | 10:00 | 10 | 983 | 1323 | 207 | 1 | 9 | 3 | 1 | 9 | 205 | 1 | 13 | 24800 | 1 | 9 | 200 | 1 | 9 | 24700 | 1 | 13 | 9900 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 20.6 | 69.08 | A | 7 | 1 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12900 | A | 7 | 460 | A | 7 | 3.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.98 | 6 | 0
1990-07-21 | 1900-07-20 | 11:00 | 11 | 1131 | 1323 | 270 | 1 | 9 | 4 | 1 | 9 | 266 | 1 | 13 | 32300 | 1 | 9 | 300 | 1 | 9 | 32100 | 1 | 13 | 12690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 20 | 68 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 610 | A | 7 | 3.5 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.3 | 6 | 0
1990-07-21 | 1900-07-20 | 12:00 | 12 | 1222 | 1323 | 225 | 1 | 9 | 2 | 1 | 9 | 223 | 1 | 13 | 27700 | 1 | 9 | 200 | 1 | 9 | 27500 | 1 | 13 | 11150 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 760 | A | 7 | 3.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.38 | 6 | 0
1990-07-21 | 1900-07-20 | 13:00 | 13 | 1249 | 1323 | 238 | 1 | 9 | 3 | 1 | 9 | 236 | 1 | 13 | 29400 | 1 | 9 | 200 | 1 | 9 | 29200 | 1 | 13 | 11740 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.97 | A | 7 | 977 | A | 7 | 80 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 1070 | A | 7 | 3.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.38 | 6 | 0
1990-07-21 | 1900-07-20 | 14:00 | 14 | 1211 | 1323 | 240 | 1 | 9 | 3 | 1 | 9 | 237 | 1 | 13 | 29400 | 1 | 9 | 200 | 1 | 9 | 29100 | 1 | 13 | 11720 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 210 | A | 7 | 3.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.88 | 6 | 0
1990-07-21 | 1900-07-20 | 15:00 | 15 | 1111 | 1323 | 259 | 1 | 9 | 1 | 1 | 9 | 259 | 1 | 13 | 31200 | 1 | 9 | 100 | 1 | 9 | 31100 | 1 | 13 | 12380 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 460 | A | 7 | 3.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.88 | 6 | 0
1990-07-21 | 1900-07-20 | 16:00 | 16 | 955 | 1323 | 223 | 1 | 9 | 0 | 1 | 9 | 223 | 1 | 13 | 26400 | 1 | 9 | 0 | 1 | 9 | 26400 | 1 | 13 | 10460 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.97 | A | 7 | 976 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 4800 | A | 7 | 460 | A | 7 | 3.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.38 | 6 | 0
1990-07-21 | 1900-07-20 | 17:00 | 17 | 754 | 1323 | 154 | 1 | 9 | 1 | 1 | 9 | 154 | 1 | 13 | 18200 | 1 | 9 | 100 | 1 | 9 | 18200 | 1 | 13 | 7010 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.97 | A | 7 | 976 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 3.6 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.38 | 6 | 0
1990-07-21 | 1900-07-20 | 18:00 | 18 | 521 | 1323 | 110 | 1 | 9 | 1 | 1 | 9 | 109 | 1 | 13 | 12700 | 1 | 9 | 100 | 1 | 9 | 12600 | 1 | 13 | 4500 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 18.9 | 66.02 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 50 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 240 | A | 7 | 3.2 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 6 | 0
1990-07-21 | 1900-07-20 | 19:00 | 19 | 274 | 1323 | 76 | 1 | 13 | 0 | 1 | 9 | 76 | 1 | 13 | 8500 | 1 | 13 | 0 | 1 | 9 | 8500 | 1 | 13 | 2570 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.97 | A | 7 | 977 | A | 7 | 20 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 240 | A | 7 | 3.2 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.42 | 6 | 0
1990-07-21 | 1900-07-20 | 20:00 | 20 | 47 | 871 | 18 | 1 | 13 | 0 | 1 | 9 | 18 | 1 | 13 | 2000 | 1 | 13 | 0 | 1 | 9 | 2000 | 1 | 13 | 610 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 30 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 240 | A | 7 | 2.9 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.96 | 6 | 0
1990-07-21 | 1900-07-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 30 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 460 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 6 | 0
1990-07-21 | 1900-07-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 30 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 910 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.48 | 6 | 0
1990-07-21 | 1900-07-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.48 | 6 | 0
1990-07-21 | 1900-07-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 1310 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.66 | 6 | 0
1990-07-22 | 1900-07-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 1980 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.56 | 7 | 0
1990-07-22 | 1900-07-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 17.2 | 62.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.46 | 7 | 0
1990-07-22 | 1900-07-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 16.7 | 62.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.38 | 7 | 0
1990-07-22 | 1900-07-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 16.7 | 62.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 2130 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.38 | 7 | 0
1990-07-22 | 1900-07-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 16.7 | 62.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.38 | 7 | 0
1990-07-22 | 1900-07-21 | 6:00 | 6 | 73 | 1070 | 23 | 1 | 13 | 4 | 1 | 13 | 23 | 1 | 13 | 2600 | 1 | 13 | 0 | 1 | 13 | 2600 | 1 | 13 | 770 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 16.7 | 62.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.38 | 7 | 0
1990-07-22 | 1900-07-21 | 7:00 | 7 | 312 | 1323 | 123 | 1 | 13 | 200 | 1 | 9 | 76 | 1 | 13 | 13100 | 1 | 13 | 16300 | 1 | 9 | 9300 | 1 | 13 | 1430 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 981 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 7 | 0
1990-07-22 | 1900-07-21 | 8:00 | 8 | 558 | 1323 | 290 | 1 | 13 | 318 | 1 | 13 | 156 | 1 | 13 | 31100 | 1 | 13 | 31900 | 1 | 13 | 17700 | 1 | 13 | 3280 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 19.4 | 66.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 360 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.28 | 7 | 0
1990-07-22 | 1900-07-21 | 9:00 | 9 | 786 | 1323 | 515 | 1 | 9 | 555 | 1 | 9 | 184 | 1 | 13 | 55200 | 1 | 9 | 56900 | 1 | 9 | 21300 | 1 | 13 | 4280 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 21.1 | 69.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.26 | 7 | 0
1990-07-22 | 1900-07-21 | 10:00 | 10 | 981 | 1323 | 642 | 1 | 13 | 508 | 1 | 13 | 264 | 1 | 13 | 68500 | 1 | 13 | 52800 | 1 | 13 | 29200 | 1 | 13 | 8140 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.26 | 7 | 0
1990-07-22 | 1900-07-21 | 11:00 | 11 | 1129 | 1323 | 634 | 1 | 13 | 389 | 1 | 13 | 301 | 1 | 13 | 68200 | 1 | 13 | 40700 | 1 | 13 | 33400 | 1 | 13 | 13160 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 15.6 | 60.08 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 10 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.48 | 7 | 0
1990-07-22 | 1900-07-21 | 12:00 | 12 | 1220 | 1323 | 816 | 1 | 13 | 526 | 1 | 13 | 328 | 1 | 13 | 88000 | 1 | 13 | 55100 | 1 | 13 | 37100 | 1 | 13 | 20180 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 23.3 | 73.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.78 | 7 | 0
1990-07-22 | 1900-07-21 | 13:00 | 13 | 1248 | 1323 | 909 | 1 | 13 | 678 | 1 | 13 | 267 | 1 | 13 | 96300 | 1 | 13 | 68900 | 1 | 13 | 31200 | 1 | 13 | 18430 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 23.3 | 73.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.58 | 7 | 0
1990-07-22 | 1900-07-21 | 14:00 | 14 | 1210 | 1323 | 851 | 1 | 13 | 586 | 1 | 13 | 313 | 1 | 13 | 92100 | 1 | 13 | 61400 | 1 | 13 | 35900 | 1 | 13 | 18340 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 24.4 | 75.92 | A | 7 | 15 | 59 | A | 7 | 0.56 | A | 7 | 982 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.4 | 7 | 0
1990-07-22 | 1900-07-21 | 15:00 | 15 | 1109 | 1323 | 466 | 1 | 9 | 129 | 1 | 9 | 357 | 1 | 13 | 51500 | 1 | 9 | 13800 | 1 | 9 | 39900 | 1 | 13 | 14020 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 15 | 59 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 2.6 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.2 | 7 | 0
1990-07-22 | 1900-07-21 | 16:00 | 16 | 953 | 1323 | 568 | 1 | 13 | 385 | 1 | 13 | 289 | 1 | 13 | 61800 | 1 | 13 | 41600 | 1 | 13 | 31800 | 1 | 13 | 8500 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 25 | 77 | A | 7 | 13.9 | 57.02 | A | 7 | 0.5 | A | 7 | 982 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.52 | 7 | 0
1990-07-22 | 1900-07-21 | 17:00 | 17 | 752 | 1323 | 373 | 1 | 13 | 204 | 1 | 13 | 257 | 1 | 13 | 40600 | 1 | 13 | 21200 | 1 | 13 | 28600 | 1 | 13 | 6750 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 24.4 | 75.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.52 | A | 7 | 982 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.92 | 7 | 0
1990-07-22 | 1900-07-21 | 18:00 | 18 | 519 | 1323 | 260 | 1 | 9 | 336 | 1 | 9 | 127 | 1 | 13 | 27300 | 1 | 9 | 32100 | 1 | 9 | 14700 | 1 | 13 | 2470 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.52 | A | 7 | 982 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.92 | 7 | 0
1990-07-22 | 1900-07-21 | 19:00 | 19 | 271 | 1323 | 114 | 1 | 13 | 222 | 1 | 9 | 68 | 1 | 13 | 12100 | 1 | 13 | 16900 | 1 | 9 | 8600 | 1 | 13 | 1280 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.32 | 7 | 0
1990-07-22 | 1900-07-21 | 20:00 | 20 | 46 | 849 | 19 | 1 | 13 | 8 | 1 | 9 | 18 | 1 | 13 | 2000 | 1 | 13 | 400 | 1 | 9 | 2000 | 1 | 13 | 430 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 15 | 59 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.25 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.5 | 7 | 0
1990-07-22 | 1900-07-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 982 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 7 | 0
1990-07-22 | 1900-07-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 983 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 7 | 0
1990-07-22 | 1900-07-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 983 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 7 | 0
1990-07-22 | 1900-07-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 983 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 7 | 0
1990-07-23 | 1900-07-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 983 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 1 | 0
1990-07-23 | 1900-07-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.72 | 1 | 0
1990-07-23 | 1900-07-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.72 | 1 | 0
1990-07-23 | 1900-07-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.97 | A | 7 | 982 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.34 | 1 | 0
1990-07-23 | 1900-07-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 14.4 | 57.92 | A | 7 | 0.97 | A | 7 | 982 | A | 7 | 230 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 1 | 0
1990-07-23 | 1900-07-22 | 6:00 | 6 | 71 | 1048 | 24 | 1 | 13 | 9 | 1 | 9 | 23 | 1 | 13 | 2600 | 1 | 13 | 500 | 1 | 9 | 2600 | 1 | 13 | 550 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.97 | A | 7 | 983 | A | 7 | 220 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.42 | 1 | 0
1990-07-23 | 1900-07-22 | 7:00 | 7 | 309 | 1323 | 130 | 1 | 13 | 215 | 1 | 9 | 80 | 1 | 13 | 13800 | 1 | 13 | 17400 | 1 | 9 | 9800 | 1 | 13 | 1520 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 15 | 59 | A | 7 | 0.81 | A | 7 | 983 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.4 | 1 | 0
1990-07-23 | 1900-07-22 | 8:00 | 8 | 555 | 1323 | 315 | 1 | 9 | 429 | 1 | 9 | 134 | 1 | 13 | 33200 | 1 | 9 | 41600 | 1 | 9 | 15700 | 1 | 13 | 2640 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 15 | 59 | A | 7 | 0.68 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.9 | 1 | 0
1990-07-23 | 1900-07-22 | 9:00 | 9 | 784 | 1323 | 516 | 1 | 9 | 563 | 1 | 9 | 180 | 1 | 13 | 55300 | 1 | 9 | 57700 | 1 | 9 | 21000 | 1 | 13 | 4170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 15 | 59 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.2 | 1 | 0
1990-07-23 | 1900-07-22 | 10:00 | 10 | 980 | 1323 | 692 | 1 | 9 | 643 | 1 | 9 | 215 | 1 | 13 | 72400 | 1 | 9 | 64800 | 1 | 9 | 24300 | 1 | 13 | 6420 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 15 | 59 | A | 7 | 0.58 | A | 7 | 983 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.8 | 1 | 0
1990-07-23 | 1900-07-22 | 11:00 | 11 | 1128 | 1323 | 791 | 1 | 9 | 614 | 1 | 9 | 266 | 1 | 13 | 82800 | 1 | 9 | 61900 | 1 | 9 | 29900 | 1 | 13 | 11180 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 25.6 | 78.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.5 | A | 7 | 983 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 1 | 0
1990-07-23 | 1900-07-22 | 12:00 | 12 | 1219 | 1323 | 851 | 1 | 13 | 586 | 1 | 13 | 309 | 1 | 13 | 92400 | 1 | 13 | 61400 | 1 | 13 | 35700 | 1 | 13 | 18830 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.49 | A | 7 | 983 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.32 | 1 | 0
1990-07-23 | 1900-07-22 | 13:00 | 13 | 1246 | 1323 | 899 | 1 | 9 | 621 | 1 | 9 | 312 | 1 | 13 | 94200 | 1 | 9 | 62500 | 1 | 9 | 35200 | 1 | 13 | 21140 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.44 | A | 7 | 983 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.34 | 1 | 0
1990-07-23 | 1900-07-22 | 14:00 | 14 | 1208 | 1323 | 849 | 1 | 9 | 556 | 1 | 9 | 339 | 1 | 13 | 91200 | 1 | 9 | 58100 | 1 | 9 | 37900 | 1 | 13 | 19800 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 27.2 | 80.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.44 | A | 7 | 982 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.22 | 1 | 0
1990-07-23 | 1900-07-22 | 15:00 | 15 | 1108 | 1323 | 779 | 1 | 9 | 577 | 1 | 9 | 294 | 1 | 13 | 83700 | 1 | 9 | 60300 | 1 | 9 | 33100 | 1 | 13 | 12060 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 27.2 | 80.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.44 | A | 7 | 981 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.22 | 1 | 0
1990-07-23 | 1900-07-22 | 16:00 | 16 | 951 | 1323 | 673 | 1 | 9 | 640 | 1 | 9 | 210 | 1 | 13 | 70100 | 1 | 9 | 64400 | 1 | 9 | 23700 | 1 | 13 | 5960 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.42 | A | 7 | 981 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.94 | 1 | 0
1990-07-23 | 1900-07-22 | 17:00 | 17 | 750 | 1323 | 482 | 1 | 9 | 540 | 1 | 9 | 174 | 1 | 13 | 51500 | 1 | 9 | 55100 | 1 | 9 | 20200 | 1 | 13 | 3900 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.44 | A | 7 | 981 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.22 | 1 | 0
1990-07-23 | 1900-07-22 | 18:00 | 18 | 517 | 1323 | 284 | 1 | 9 | 403 | 1 | 9 | 126 | 1 | 13 | 29900 | 1 | 9 | 38400 | 1 | 9 | 14800 | 1 | 13 | 2450 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.44 | A | 7 | 980 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.34 | 1 | 0
1990-07-23 | 1900-07-22 | 19:00 | 19 | 268 | 1323 | 107 | 1 | 13 | 175 | 1 | 9 | 71 | 1 | 13 | 11300 | 1 | 13 | 13200 | 1 | 9 | 8600 | 1 | 13 | 1350 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 14.4 | 57.92 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.62 | 1 | 0
1990-07-23 | 1900-07-22 | 20:00 | 20 | 44 | 827 | 13 | 1 | 13 | 4 | 1 | 9 | 12 | 1 | 13 | 1300 | 1 | 13 | 200 | 1 | 9 | 1300 | 1 | 13 | 300 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.295 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.26 | 1 | 0
1990-07-23 | 1900-07-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 1 | 0
1990-07-23 | 1900-07-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 1 | 0
1990-07-23 | 1900-07-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 1 | 0
1990-07-23 | 1900-07-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 1 | 0
1990-07-24 | 1900-07-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 2 | 0
1990-07-24 | 1900-07-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.58 | 2 | 0
1990-07-24 | 1900-07-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 2 | 0
1990-07-24 | 1900-07-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.02 | 2 | 0
1990-07-24 | 1900-07-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.02 | 2 | 0
1990-07-24 | 1900-07-23 | 6:00 | 6 | 68 | 1026 | 26 | 1 | 13 | 71 | 1 | 9 | 19 | 1 | 13 | 2600 | 1 | 13 | 2600 | 1 | 9 | 2400 | 1 | 13 | 330 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 2 | 0
1990-07-24 | 1900-07-23 | 7:00 | 7 | 306 | 1324 | 157 | 1 | 13 | 429 | 1 | 9 | 57 | 1 | 13 | 16100 | 1 | 13 | 34700 | 1 | 9 | 8100 | 1 | 13 | 1040 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.88 | 2 | 0
1990-07-24 | 1900-07-23 | 8:00 | 8 | 553 | 1324 | 249 | 1 | 9 | 287 | 1 | 9 | 128 | 1 | 13 | 27000 | 1 | 9 | 28800 | 1 | 9 | 14900 | 1 | 13 | 2590 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 22.8 | 73.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.64 | A | 7 | 982 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.98 | 2 | 0
1990-07-24 | 1900-07-23 | 9:00 | 9 | 782 | 1324 | 497 | 1 | 13 | 558 | 1 | 13 | 165 | 1 | 13 | 51500 | 1 | 13 | 55600 | 1 | 13 | 18600 | 1 | 13 | 3770 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 23.9 | 75.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.18 | 2 | 0
1990-07-24 | 1900-07-23 | 10:00 | 10 | 978 | 1324 | 683 | 1 | 9 | 769 | 1 | 9 | 113 | 1 | 13 | 73100 | 1 | 9 | 77900 | 1 | 9 | 15500 | 1 | 13 | 3400 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 26.1 | 78.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.56 | A | 7 | 982 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 2 | 0
1990-07-24 | 1900-07-23 | 11:00 | 11 | 1126 | 1324 | 716 | 1 | 9 | 582 | 1 | 9 | 220 | 1 | 13 | 76100 | 1 | 9 | 59300 | 1 | 9 | 25500 | 1 | 13 | 9360 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 27.2 | 80.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.51 | A | 7 | 982 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.98 | 2 | 0
1990-07-24 | 1900-07-23 | 12:00 | 12 | 1217 | 1324 | 862 | 1 | 9 | 717 | 1 | 9 | 199 | 1 | 13 | 92800 | 1 | 9 | 73800 | 1 | 9 | 24900 | 1 | 13 | 11930 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.48 | A | 7 | 981 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.28 | 2 | 0
1990-07-24 | 1900-07-23 | 13:00 | 13 | 1245 | 1324 | 900 | 1 | 13 | 693 | 1 | 13 | 246 | 1 | 13 | 95900 | 1 | 13 | 70700 | 1 | 13 | 29300 | 1 | 13 | 16760 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 28.9 | 84.02 | A | 7 | 15 | 59 | A | 7 | 0.43 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.6 | 2 | 0
1990-07-24 | 1900-07-23 | 14:00 | 14 | 1207 | 1324 | 617 | 1 | 13 | 356 | 1 | 13 | 291 | 1 | 13 | 67300 | 1 | 13 | 37300 | 1 | 13 | 33200 | 1 | 13 | 16770 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 28.3 | 82.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.46 | A | 7 | 981 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.08 | 2 | 0
1990-07-24 | 1900-07-23 | 15:00 | 15 | 1106 | 1324 | 739 | 1 | 13 | 583 | 1 | 13 | 250 | 1 | 13 | 77500 | 1 | 13 | 58900 | 1 | 13 | 28200 | 1 | 13 | 9910 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 28.9 | 84.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.48 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.16 | 2 | 0
1990-07-24 | 1900-07-23 | 16:00 | 16 | 950 | 1324 | 648 | 1 | 9 | 714 | 1 | 9 | 133 | 1 | 13 | 67800 | 1 | 9 | 71700 | 1 | 9 | 16300 | 1 | 13 | 3610 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 28.9 | 84.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.46 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.88 | 2 | 0
1990-07-24 | 1900-07-23 | 17:00 | 17 | 748 | 1324 | 488 | 1 | 9 | 639 | 1 | 9 | 125 | 1 | 13 | 51400 | 1 | 9 | 64100 | 1 | 9 | 15200 | 1 | 13 | 2860 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.94 | 2 | 0
1990-07-24 | 1900-07-23 | 18:00 | 18 | 514 | 1324 | 304 | 1 | 9 | 510 | 1 | 9 | 104 | 1 | 13 | 31200 | 1 | 9 | 47800 | 1 | 9 | 12600 | 1 | 13 | 1990 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 27.8 | 82.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.06 | 2 | 0
1990-07-24 | 1900-07-23 | 19:00 | 19 | 266 | 1324 | 117 | 1 | 13 | 235 | 1 | 13 | 69 | 1 | 13 | 12300 | 1 | 13 | 17600 | 1 | 13 | 8800 | 1 | 13 | 1300 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 2 | 0
1990-07-24 | 1900-07-23 | 20:00 | 20 | 42 | 805 | 19 | 1 | 13 | 9 | 1 | 13 | 18 | 1 | 13 | 2000 | 1 | 13 | 500 | 1 | 13 | 2000 | 1 | 13 | 430 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 23.9 | 75.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.64 | A | 7 | 979 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 2.9 | E | 8 | 0.122 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.76 | 2 | 0
1990-07-24 | 1900-07-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 5 | A | 7 | 22.8 | 73.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.86 | 2 | 0
1990-07-24 | 1900-07-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.06 | 2 | 0
1990-07-24 | 1900-07-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.14 | 2 | 0
1990-07-24 | 1900-07-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 2 | 0
1990-07-25 | 1900-07-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.04 | 3 | 0
1990-07-25 | 1900-07-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 3 | 0
1990-07-25 | 1900-07-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 3 | 0
1990-07-25 | 1900-07-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 3 | 0
1990-07-25 | 1900-07-24 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 21.7 | 71.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.04 | 3 | 0
1990-07-25 | 1900-07-24 | 6:00 | 6 | 66 | 1004 | 29 | 1 | 13 | 76 | 1 | 9 | 21 | 1 | 13 | 2800 | 1 | 13 | 2800 | 1 | 9 | 2600 | 1 | 13 | 370 | 1 | 21 | 5 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.04 | 3 | 0
1990-07-25 | 1900-07-24 | 7:00 | 7 | 303 | 1324 | 154 | 1 | 13 | 349 | 1 | 9 | 73 | 1 | 13 | 16000 | 1 | 13 | 27800 | 1 | 9 | 9600 | 1 | 13 | 1330 | 1 | 21 | 8 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 3 | 0
1990-07-25 | 1900-07-24 | 8:00 | 8 | 550 | 1324 | 298 | 1 | 9 | 441 | 1 | 9 | 114 | 1 | 13 | 31900 | 1 | 9 | 42800 | 1 | 9 | 14100 | 1 | 13 | 2210 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 3 | 0
1990-07-25 | 1900-07-24 | 9:00 | 9 | 780 | 1324 | 527 | 1 | 9 | 701 | 1 | 9 | 113 | 1 | 13 | 56300 | 1 | 9 | 71000 | 1 | 9 | 14400 | 1 | 13 | 2710 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.28 | 3 | 0
1990-07-25 | 1900-07-24 | 10:00 | 10 | 976 | 1324 | 662 | 1 | 9 | 685 | 1 | 9 | 156 | 1 | 13 | 70900 | 1 | 9 | 70100 | 1 | 9 | 19100 | 1 | 13 | 4800 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 140 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 3 | 0
1990-07-25 | 1900-07-24 | 11:00 | 11 | 1125 | 1324 | 638 | 1 | 13 | 369 | 1 | 13 | 323 | 1 | 13 | 68000 | 1 | 13 | 38500 | 1 | 13 | 35300 | 1 | 13 | 13950 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 3 | 0
1990-07-25 | 1900-07-24 | 12:00 | 12 | 1216 | 1324 | 594 | 1 | 13 | 174 | 1 | 13 | 434 | 1 | 13 | 65500 | 1 | 13 | 18600 | 1 | 13 | 48400 | 1 | 13 | 22360 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 1070 | A | 7 | 3.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 3 | 0
1990-07-25 | 1900-07-24 | 13:00 | 13 | 1243 | 1324 | 815 | 1 | 13 | 536 | 1 | 13 | 310 | 1 | 13 | 88800 | 1 | 13 | 56200 | 1 | 13 | 35900 | 1 | 13 | 21350 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 3.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 3 | 0
1990-07-25 | 1900-07-24 | 14:00 | 14 | 1206 | 1324 | 504 | 1 | 9 | 152 | 1 | 9 | 365 | 1 | 13 | 56100 | 1 | 9 | 16300 | 1 | 9 | 41200 | 1 | 13 | 18170 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 28.3 | 82.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 12900 | A | 7 | 1220 | A | 7 | 3.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.68 | 3 | 0
1990-07-25 | 1900-07-24 | 15:00 | 15 | 1105 | 1324 | 433 | 1 | 9 | 135 | 1 | 9 | 320 | 1 | 13 | 48200 | 1 | 9 | 14500 | 1 | 9 | 36100 | 1 | 13 | 12440 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 140 | A | 7 | 7.2 | A | 7 | 12900 | A | 7 | 1520 | A | 7 | 3.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.96 | 3 | 0
1990-07-25 | 1900-07-24 | 16:00 | 16 | 948 | 1324 | 407 | 1 | 13 | 148 | 1 | 13 | 300 | 1 | 13 | 44700 | 1 | 13 | 15700 | 1 | 13 | 33500 | 1 | 13 | 9290 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 12900 | A | 7 | 9140 | A | 7 | 3.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.96 | 3 | 0
1990-07-25 | 1900-07-24 | 17:00 | 17 | 745 | 1324 | 414 | 1 | 13 | 401 | 1 | 13 | 187 | 1 | 13 | 43900 | 1 | 13 | 40800 | 1 | 13 | 20900 | 1 | 13 | 4210 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 27.2 | 80.96 | A | 7 | 22.2 | 71.96 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 140 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.96 | 3 | 0
1990-07-25 | 1900-07-24 | 18:00 | 18 | 512 | 1324 | 235 | 1 | 13 | 223 | 1 | 13 | 148 | 1 | 13 | 25000 | 1 | 13 | 21800 | 1 | 13 | 16500 | 1 | 13 | 3070 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 3.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.88 | 3 | 0
1990-07-25 | 1900-07-24 | 19:00 | 19 | 263 | 1324 | 106 | 1 | 13 | 203 | 1 | 13 | 65 | 1 | 13 | 11200 | 1 | 13 | 15200 | 1 | 13 | 8200 | 1 | 13 | 1210 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 25 | 77 | A | 7 | 20.6 | 69.08 | A | 7 | 0.76 | A | 7 | 979 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.78 | 3 | 0
1990-07-25 | 1900-07-24 | 20:00 | 20 | 40 | 805 | 20 | 1 | 13 | 36 | 1 | 13 | 16 | 1 | 13 | 2000 | 1 | 13 | 1400 | 1 | 13 | 1900 | 1 | 13 | 330 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 24.4 | 75.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.48 | 3 | 0
1990-07-25 | 1900-07-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.18 | 3 | 0
1990-07-25 | 1900-07-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 3 | 0
1990-07-25 | 1900-07-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.68 | 3 | 0
1990-07-25 | 1900-07-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 5 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 3 | 0
1990-07-26 | 1900-07-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 4 | 0
1990-07-26 | 1900-07-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 980 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 4 | 0
1990-07-26 | 1900-07-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 700 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.28 | 4 | 0
1990-07-26 | 1900-07-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.88 | 4 | 0
1990-07-26 | 1900-07-25 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.28 | 4 | 0
1990-07-26 | 1900-07-25 | 6:00 | 6 | 64 | 1004 | 7 | 1 | 13 | 3 | 1 | 9 | 7 | 1 | 13 | 800 | 1 | 13 | 200 | 1 | 9 | 800 | 1 | 13 | 190 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 580 | A | 7 | 3.6 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.88 | 4 | 0
1990-07-26 | 1900-07-25 | 7:00 | 7 | 300 | 1324 | 63 | 1 | 13 | 17 | 1 | 9 | 59 | 1 | 13 | 6900 | 1 | 13 | 1400 | 1 | 9 | 6600 | 1 | 13 | 1590 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 9140 | A | 7 | 3.7 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.78 | 4 | 0
1990-07-26 | 1900-07-25 | 8:00 | 8 | 548 | 1324 | 148 | 1 | 9 | 16 | 1 | 9 | 142 | 1 | 13 | 17000 | 1 | 9 | 1200 | 1 | 9 | 16500 | 1 | 13 | 5620 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 400 | A | 7 | 3.7 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.08 | 4 | 0
1990-07-26 | 1900-07-25 | 9:00 | 9 | 778 | 1324 | 261 | 1 | 9 | 32 | 1 | 9 | 242 | 1 | 13 | 28700 | 1 | 9 | 3200 | 1 | 9 | 26800 | 1 | 13 | 7830 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.88 | A | 7 | 981 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 370 | A | 7 | 4 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.26 | 4 | 0
1990-07-26 | 1900-07-25 | 10:00 | 10 | 974 | 1324 | 280 | 1 | 9 | 0 | 1 | 9 | 280 | 1 | 13 | 32700 | 1 | 9 | 0 | 1 | 9 | 32700 | 1 | 13 | 12520 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 25.6 | 78.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 430 | A | 7 | 4 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.86 | 4 | 0
1990-07-26 | 1900-07-25 | 11:00 | 11 | 1123 | 1324 | 325 | 1 | 9 | 11 | 1 | 9 | 316 | 1 | 13 | 38500 | 1 | 9 | 1000 | 1 | 9 | 37700 | 1 | 13 | 14420 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 27.8 | 82.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 3960 | A | 7 | 4 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.46 | 4 | 0
1990-07-26 | 1900-07-25 | 12:00 | 12 | 1214 | 1324 | 379 | 1 | 9 | 1 | 1 | 9 | 377 | 1 | 13 | 44700 | 1 | 9 | 100 | 1 | 9 | 44600 | 1 | 13 | 16720 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 26.1 | 78.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 3960 | A | 7 | 3.8 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.86 | 4 | 0
1990-07-26 | 1900-07-25 | 13:00 | 13 | 1242 | 1324 | 358 | 1 | 9 | 4 | 1 | 9 | 354 | 1 | 13 | 42700 | 1 | 9 | 400 | 1 | 9 | 42300 | 1 | 13 | 16100 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 26.7 | 80.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 150 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 3960 | A | 7 | 4 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.66 | 4 | 0
1990-07-26 | 1900-07-25 | 14:00 | 14 | 1204 | 1324 | 395 | 1 | 9 | 2 | 1 | 9 | 393 | 1 | 13 | 46500 | 1 | 9 | 200 | 1 | 9 | 46300 | 1 | 13 | 17150 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 28.3 | 82.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 3960 | A | 7 | 4.1 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.44 | 4 | 0
1990-07-26 | 1900-07-25 | 15:00 | 15 | 1103 | 1324 | 548 | 1 | 13 | 374 | 1 | 13 | 235 | 1 | 13 | 60200 | 1 | 13 | 39200 | 1 | 13 | 27500 | 1 | 13 | 9390 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 30 | 86 | A | 7 | 23.3 | 73.94 | A | 7 | 0.68 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.24 | 4 | 0
1990-07-26 | 1900-07-25 | 16:00 | 16 | 946 | 1324 | 625 | 1 | 13 | 595 | 1 | 13 | 198 | 1 | 13 | 65400 | 1 | 13 | 60100 | 1 | 13 | 22400 | 1 | 13 | 5610 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 31.1 | 87.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.64 | 4 | 0
1990-07-26 | 1900-07-25 | 17:00 | 17 | 743 | 1324 | 489 | 1 | 13 | 594 | 1 | 13 | 153 | 1 | 13 | 50700 | 1 | 13 | 58900 | 1 | 13 | 17500 | 1 | 13 | 3380 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 31.1 | 87.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.64 | 4 | 0
1990-07-26 | 1900-07-25 | 18:00 | 18 | 509 | 1324 | 282 | 1 | 9 | 457 | 1 | 9 | 104 | 1 | 13 | 30000 | 1 | 9 | 43500 | 1 | 9 | 13300 | 1 | 13 | 1980 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 30.6 | 87.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.66 | 4 | 0
1990-07-26 | 1900-07-25 | 19:00 | 19 | 260 | 1324 | 110 | 1 | 13 | 275 | 1 | 9 | 55 | 1 | 13 | 11500 | 1 | 13 | 20500 | 1 | 9 | 7500 | 1 | 13 | 980 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 22.2 | 71.96 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.26 | 4 | 0
1990-07-26 | 1900-07-25 | 20:00 | 20 | 38 | 783 | 17 | 1 | 13 | 23 | 1 | 9 | 14 | 1 | 13 | 1700 | 1 | 13 | 900 | 1 | 9 | 1700 | 1 | 13 | 290 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.145 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.96 | 4 | 0
1990-07-26 | 1900-07-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 27.2 | 80.96 | A | 7 | 22.8 | 73.04 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.74 | 4 | 0
1990-07-26 | 1900-07-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 22.8 | 73.04 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.14 | 4 | 0
1990-07-26 | 1900-07-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 25.6 | 78.08 | A | 7 | 22.8 | 73.04 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.64 | 4 | 0
1990-07-26 | 1900-07-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.62 | 4 | 0
1990-07-27 | 1900-07-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.14 | 5 | 0
1990-07-27 | 1900-07-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.64 | 5 | 0
1990-07-27 | 1900-07-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.84 | 5 | 0
1990-07-27 | 1900-07-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.54 | 5 | 0
1990-07-27 | 1900-07-26 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 23.3 | 73.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.04 | 5 | 0
1990-07-27 | 1900-07-26 | 6:00 | 6 | 61 | 982 | 20 | 1 | 13 | 16 | 1 | 13 | 19 | 1 | 13 | 2200 | 1 | 13 | 900 | 1 | 13 | 2100 | 1 | 13 | 460 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 24.4 | 75.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 2900 | A | 7 | 3.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.14 | 5 | 0
1990-07-27 | 1900-07-26 | 7:00 | 7 | 297 | 1324 | 77 | 1 | 13 | 60 | 1 | 9 | 63 | 1 | 13 | 8500 | 1 | 13 | 5000 | 1 | 9 | 7400 | 1 | 13 | 1370 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 24.4 | 75.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.69 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 3.2 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.44 | 5 | 0
1990-07-27 | 1900-07-26 | 8:00 | 8 | 545 | 1324 | 153 | 1 | 9 | 7 | 1 | 9 | 150 | 1 | 13 | 17400 | 1 | 9 | 500 | 1 | 9 | 17100 | 1 | 13 | 5830 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 3.4 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.62 | 5 | 0
1990-07-27 | 1900-07-26 | 9:00 | 9 | 776 | 1324 | 277 | 1 | 9 | 71 | 1 | 9 | 236 | 1 | 13 | 30600 | 1 | 9 | 7200 | 1 | 9 | 26400 | 1 | 13 | 7650 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 3.4 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 5 | 0
1990-07-27 | 1900-07-26 | 10:00 | 10 | 972 | 1324 | 278 | 1 | 9 | 13 | 1 | 9 | 268 | 1 | 13 | 32500 | 1 | 9 | 1100 | 1 | 9 | 31700 | 1 | 13 | 12120 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 27.2 | 80.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.63 | A | 7 | 982 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 3.4 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.82 | 5 | 0
1990-07-27 | 1900-07-26 | 11:00 | 11 | 1121 | 1324 | 420 | 1 | 9 | 115 | 1 | 9 | 323 | 1 | 13 | 46800 | 1 | 9 | 12300 | 1 | 9 | 36400 | 1 | 13 | 12960 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 3.5 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.7 | 5 | 0
1990-07-27 | 1900-07-26 | 12:00 | 12 | 1213 | 1324 | 519 | 1 | 9 | 171 | 1 | 9 | 362 | 1 | 13 | 57800 | 1 | 9 | 18300 | 1 | 9 | 41000 | 1 | 13 | 18420 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 3.5 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.7 | 5 | 0
1990-07-27 | 1900-07-26 | 13:00 | 13 | 1240 | 1324 | 911 | 1 | 13 | 775 | 1 | 13 | 182 | 1 | 13 | 95900 | 1 | 13 | 78100 | 1 | 13 | 22600 | 1 | 13 | 11320 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 28.3 | 82.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.56 | 5 | 0
1990-07-27 | 1900-07-26 | 14:00 | 14 | 1202 | 1324 | 848 | 1 | 13 | 681 | 1 | 13 | 227 | 1 | 13 | 90400 | 1 | 13 | 69600 | 1 | 13 | 27100 | 1 | 13 | 12620 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 28.9 | 84.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.51 | A | 7 | 980 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.54 | 5 | 0
1990-07-27 | 1900-07-26 | 15:00 | 15 | 1101 | 1324 | 756 | 1 | 13 | 691 | 1 | 13 | 178 | 1 | 13 | 81000 | 1 | 13 | 71000 | 1 | 13 | 21900 | 1 | 13 | 7160 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 28.9 | 84.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 4880 | A | 7 | 3.4 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 5 | 0
1990-07-27 | 1900-07-26 | 16:00 | 16 | 944 | 1324 | 486 | 1 | 13 | 345 | 1 | 13 | 238 | 1 | 13 | 51900 | 1 | 13 | 35800 | 1 | 13 | 26400 | 1 | 13 | 6830 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 3.7 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.98 | 5 | 0
1990-07-27 | 1900-07-26 | 17:00 | 17 | 741 | 1324 | 435 | 1 | 13 | 458 | 1 | 13 | 177 | 1 | 13 | 46300 | 1 | 13 | 46600 | 1 | 13 | 20200 | 1 | 13 | 3940 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 28.9 | 84.02 | A | 7 | 22.2 | 71.96 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.26 | 5 | 0
1990-07-27 | 1900-07-26 | 18:00 | 18 | 506 | 1324 | 239 | 1 | 13 | 265 | 1 | 13 | 137 | 1 | 13 | 25500 | 1 | 13 | 25900 | 1 | 13 | 15600 | 1 | 13 | 2800 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2590 | A | 7 | 3.8 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 5 | 0
1990-07-27 | 1900-07-26 | 19:00 | 19 | 257 | 1324 | 69 | 1 | 13 | 13 | 1 | 13 | 67 | 1 | 13 | 7800 | 1 | 13 | 400 | 1 | 13 | 7700 | 1 | 13 | 2300 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 3.8 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.66 | 5 | 0
1990-07-27 | 1900-07-26 | 20:00 | 20 | 37 | 762 | 13 | 1 | 13 | 8 | 1 | 13 | 12 | 1 | 13 | 1400 | 1 | 13 | 400 | 1 | 13 | 1300 | 1 | 13 | 300 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 26.7 | 80.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.16 | 5 | 0
1990-07-27 | 1900-07-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 26.1 | 78.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.86 | 5 | 0
1990-07-27 | 1900-07-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 130 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 5 | 0
1990-07-27 | 1900-07-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 25.6 | 78.08 | A | 7 | 22.8 | 73.04 | A | 7 | 0.85 | A | 7 | 980 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.64 | 5 | 0
1990-07-27 | 1900-07-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 340 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 5 | 0
1990-07-28 | 1900-07-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.78 | 6 | 0
1990-07-28 | 1900-07-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 22.8 | 73.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.28 | 6 | 0
1990-07-28 | 1900-07-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 6 | 0
1990-07-28 | 1900-07-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 6 | 0
1990-07-28 | 1900-07-27 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 210 | A | 7 | 9.3 | A | 7 | 6400 | A | 7 | 1830 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.52 | 6 | 0
1990-07-28 | 1900-07-27 | 6:00 | 6 | 59 | 960 | 5 | 1 | 13 | 1 | 1 | 9 | 5 | 1 | 13 | 600 | 1 | 13 | 0 | 1 | 9 | 600 | 1 | 13 | 200 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 1980 | A | 7 | 3.7 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.08 | 6 | 0
1990-07-28 | 1900-07-27 | 7:00 | 7 | 294 | 1325 | 58 | 1 | 13 | 0 | 1 | 9 | 58 | 1 | 13 | 6600 | 1 | 13 | 0 | 1 | 9 | 6600 | 1 | 13 | 2190 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 2130 | A | 7 | 3.7 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.78 | 6 | 0
1990-07-28 | 1900-07-27 | 8:00 | 8 | 543 | 1325 | 254 | 1 | 13 | 224 | 1 | 13 | 162 | 1 | 13 | 27000 | 1 | 13 | 22300 | 1 | 13 | 17900 | 1 | 13 | 3430 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 25 | 77 | A | 7 | 21.1 | 69.98 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 9140 | A | 7 | 3.7 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.28 | 6 | 0
1990-07-28 | 1900-07-27 | 9:00 | 9 | 773 | 1325 | 437 | 1 | 13 | 396 | 1 | 13 | 205 | 1 | 13 | 46200 | 1 | 13 | 40400 | 1 | 13 | 22500 | 1 | 13 | 4760 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 21.7 | 71.06 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.36 | 6 | 0
1990-07-28 | 1900-07-27 | 10:00 | 10 | 970 | 1325 | 650 | 1 | 13 | 573 | 1 | 13 | 229 | 1 | 13 | 70200 | 1 | 13 | 59700 | 1 | 13 | 26400 | 1 | 13 | 6840 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 6 | 0
1990-07-28 | 1900-07-27 | 11:00 | 11 | 1119 | 1325 | 749 | 1 | 13 | 631 | 1 | 13 | 214 | 1 | 13 | 79600 | 1 | 13 | 64400 | 1 | 13 | 25100 | 1 | 13 | 8920 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.96 | 6 | 0
1990-07-28 | 1900-07-27 | 12:00 | 12 | 1211 | 1325 | 855 | 1 | 13 | 704 | 1 | 13 | 209 | 1 | 13 | 91800 | 1 | 13 | 72200 | 1 | 13 | 25600 | 1 | 13 | 12110 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.98 | 6 | 0
1990-07-28 | 1900-07-27 | 13:00 | 13 | 1239 | 1325 | 824 | 1 | 13 | 642 | 1 | 13 | 222 | 1 | 13 | 88400 | 1 | 13 | 65800 | 1 | 13 | 26800 | 1 | 13 | 14640 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 30 | 86 | A | 7 | 21.1 | 69.98 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.48 | 6 | 0
1990-07-28 | 1900-07-27 | 14:00 | 14 | 1201 | 1325 | 851 | 1 | 13 | 634 | 1 | 13 | 274 | 1 | 13 | 89500 | 1 | 13 | 64100 | 1 | 13 | 31300 | 1 | 13 | 14910 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 30 | 86 | A | 7 | 22.2 | 71.96 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 3.9 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.26 | 6 | 0
1990-07-28 | 1900-07-27 | 15:00 | 15 | 1099 | 1325 | 536 | 1 | 13 | 265 | 1 | 13 | 315 | 1 | 13 | 59100 | 1 | 13 | 28800 | 1 | 13 | 35100 | 1 | 13 | 11890 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 30.6 | 87.08 | A | 7 | 23.3 | 73.94 | A | 7 | 0.65 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.44 | 6 | 0
1990-07-28 | 1900-07-27 | 16:00 | 16 | 942 | 1325 | 623 | 1 | 13 | 657 | 1 | 13 | 153 | 1 | 13 | 66300 | 1 | 13 | 67100 | 1 | 13 | 18500 | 1 | 13 | 4430 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 31.1 | 87.98 | A | 7 | 23.3 | 73.94 | A | 7 | 0.63 | A | 7 | 977 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.94 | 6 | 0
1990-07-28 | 1900-07-27 | 17:00 | 17 | 738 | 1325 | 251 | 1 | 9 | 77 | 1 | 9 | 208 | 1 | 13 | 27600 | 1 | 9 | 7700 | 1 | 9 | 23300 | 1 | 13 | 6680 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 28.9 | 84.02 | A | 7 | 22.8 | 73.04 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 3050 | A | 7 | 4.1 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.94 | 6 | 0
1990-07-28 | 1900-07-27 | 18:00 | 18 | 503 | 1325 | 94 | 1 | 9 | 7 | 1 | 9 | 91 | 1 | 13 | 11000 | 1 | 9 | 400 | 1 | 9 | 10800 | 1 | 13 | 3840 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 27.2 | 80.96 | A | 7 | 23.9 | 75.02 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 1070 | A | 7 | 4.3 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.82 | 6 | 0
1990-07-28 | 1900-07-27 | 19:00 | 19 | 253 | 1325 | 42 | 1 | 13 | 24 | 1 | 9 | 37 | 1 | 13 | 4600 | 1 | 13 | 1900 | 1 | 9 | 4200 | 1 | 13 | 1010 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 3050 | A | 7 | 3.6 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.58 | 6 | 0
1990-07-28 | 1900-07-27 | 20:00 | 20 | 35 | 740 | 13 | 1 | 13 | 4 | 1 | 9 | 13 | 1 | 13 | 1500 | 1 | 13 | 200 | 1 | 9 | 1400 | 1 | 13 | 320 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 22.2 | 71.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 3.6 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.88 | 6 | 0
1990-07-28 | 1900-07-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 22.8 | 73.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.28 | 6 | 0
1990-07-28 | 1900-07-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.94 | A | 7 | 979 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.68 | 6 | 0
1990-07-28 | 1900-07-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.58 | 6 | 0
1990-07-28 | 1900-07-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 21.1 | 69.98 | A | 7 | 20 | 68 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.5 | 6 | 0
1990-07-29 | 1900-07-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 4 | A | 7 | 20.6 | 69.08 | A | 7 | 20.6 | 69.08 | A | 7 | 1 | A | 7 | 978 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.98 | 7 | 0
1990-07-29 | 1900-07-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 21.1 | 69.98 | A | 7 | 20 | 68 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.5 | 7 | 0
1990-07-29 | 1900-07-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 20 | 68 | A | 7 | 18.9 | 66.02 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 7 | 0
1990-07-29 | 1900-07-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 20 | 68 | A | 7 | 18.3 | 64.94 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.94 | 7 | 0
1990-07-29 | 1900-07-28 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 18.9 | 66.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.97 | A | 7 | 979 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.34 | 7 | 0
1990-07-29 | 1900-07-28 | 6:00 | 6 | 57 | 939 | 23 | 1 | 13 | 52 | 1 | 9 | 18 | 1 | 13 | 2300 | 1 | 13 | 1800 | 1 | 9 | 2200 | 1 | 13 | 310 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 18.9 | 66.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.64 | 7 | 0
1990-07-29 | 1900-07-28 | 7:00 | 7 | 291 | 1325 | 146 | 1 | 13 | 375 | 1 | 9 | 63 | 1 | 13 | 15400 | 1 | 13 | 29400 | 1 | 9 | 8900 | 1 | 13 | 1140 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.32 | 7 | 0
1990-07-29 | 1900-07-28 | 8:00 | 8 | 540 | 1325 | 329 | 1 | 9 | 576 | 1 | 9 | 93 | 1 | 13 | 34300 | 1 | 9 | 54900 | 1 | 9 | 11900 | 1 | 13 | 1850 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 7 | 0
1990-07-29 | 1900-07-28 | 9:00 | 9 | 771 | 1325 | 521 | 1 | 9 | 646 | 1 | 9 | 144 | 1 | 13 | 54600 | 1 | 9 | 64600 | 1 | 9 | 16900 | 1 | 13 | 3320 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 7 | 0
1990-07-29 | 1900-07-28 | 10:00 | 10 | 968 | 1325 | 624 | 1 | 13 | 551 | 1 | 13 | 220 | 1 | 13 | 67700 | 1 | 13 | 57400 | 1 | 13 | 25600 | 1 | 13 | 6520 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.9 | 7 | 0
1990-07-29 | 1900-07-28 | 11:00 | 11 | 1118 | 1325 | 774 | 1 | 9 | 718 | 1 | 9 | 166 | 1 | 13 | 81100 | 1 | 9 | 72200 | 1 | 9 | 20000 | 1 | 13 | 6340 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 26.1 | 78.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.18 | 7 | 0
1990-07-29 | 1900-07-28 | 12:00 | 12 | 1210 | 1325 | 917 | 1 | 9 | 851 | 1 | 9 | 136 | 1 | 13 | 93800 | 1 | 9 | 85300 | 1 | 9 | 15800 | 1 | 13 | 6080 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.98 | 7 | 0
1990-07-29 | 1900-07-28 | 13:00 | 13 | 1237 | 1325 | 946 | 1 | 9 | 862 | 1 | 9 | 139 | 1 | 13 | 96900 | 1 | 9 | 86400 | 1 | 9 | 16100 | 1 | 13 | 7110 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.96 | 7 | 0
1990-07-29 | 1900-07-28 | 14:00 | 14 | 1199 | 1325 | 914 | 1 | 9 | 857 | 1 | 9 | 136 | 1 | 13 | 93700 | 1 | 9 | 85900 | 1 | 9 | 15800 | 1 | 13 | 5800 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 21.1 | 69.98 | A | 7 | 0.59 | A | 7 | 980 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.48 | 7 | 0
1990-07-29 | 1900-07-28 | 15:00 | 15 | 1098 | 1325 | 826 | 1 | 9 | 838 | 1 | 9 | 128 | 1 | 13 | 84700 | 1 | 9 | 83800 | 1 | 9 | 15100 | 1 | 13 | 3880 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 20 | 68 | A | 7 | 0.53 | A | 7 | 980 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.3 | 7 | 0
1990-07-29 | 1900-07-28 | 16:00 | 16 | 939 | 1325 | 686 | 1 | 9 | 799 | 1 | 9 | 116 | 1 | 13 | 72700 | 1 | 9 | 80600 | 1 | 9 | 15400 | 1 | 13 | 3230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 7 | 0
1990-07-29 | 1900-07-28 | 17:00 | 17 | 736 | 1325 | 508 | 1 | 9 | 734 | 1 | 9 | 97 | 1 | 13 | 53000 | 1 | 9 | 72700 | 1 | 9 | 12500 | 1 | 13 | 2150 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 20 | 68 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 330 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.3 | 7 | 0
1990-07-29 | 1900-07-28 | 18:00 | 18 | 500 | 1325 | 308 | 1 | 9 | 610 | 1 | 9 | 75 | 1 | 13 | 32200 | 1 | 9 | 57600 | 1 | 9 | 10400 | 1 | 13 | 1500 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 7 | 0
1990-07-29 | 1900-07-28 | 19:00 | 19 | 250 | 1325 | 121 | 1 | 13 | 389 | 1 | 9 | 46 | 1 | 13 | 12300 | 1 | 13 | 29100 | 1 | 9 | 6800 | 1 | 13 | 830 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.82 | 7 | 0
1990-07-29 | 1900-07-28 | 20:00 | 20 | 33 | 718 | 19 | 1 | 13 | 42 | 1 | 9 | 14 | 1 | 13 | 1700 | 1 | 13 | 1200 | 1 | 9 | 1700 | 1 | 13 | 240 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 7 | 0
1990-07-29 | 1900-07-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.62 | 7 | 0
1990-07-29 | 1900-07-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.62 | 7 | 0
1990-07-29 | 1900-07-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 982 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.72 | 7 | 0
1990-07-29 | 1900-07-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.32 | 7 | 0
1990-07-30 | 1900-07-29 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 1 | 0
1990-07-30 | 1900-07-29 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.04 | 1 | 0
1990-07-30 | 1900-07-29 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.64 | 1 | 0
1990-07-30 | 1900-07-29 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.64 | 1 | 0
1990-07-30 | 1900-07-29 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.64 | 1 | 0
1990-07-30 | 1900-07-29 | 6:00 | 6 | 54 | 917 | 26 | 1 | 13 | 92 | 1 | 9 | 17 | 1 | 13 | 2400 | 1 | 13 | 3600 | 1 | 9 | 2200 | 1 | 13 | 300 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 983 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.04 | 1 | 0
1990-07-30 | 1900-07-29 | 7:00 | 7 | 288 | 1325 | 150 | 1 | 13 | 482 | 1 | 9 | 45 | 1 | 13 | 15600 | 1 | 13 | 38500 | 1 | 9 | 7200 | 1 | 13 | 840 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.84 | A | 7 | 983 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.64 | 1 | 0
1990-07-30 | 1900-07-29 | 8:00 | 8 | 537 | 1325 | 346 | 1 | 9 | 682 | 1 | 9 | 68 | 1 | 13 | 36100 | 1 | 9 | 65000 | 1 | 9 | 9700 | 1 | 13 | 1410 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.54 | 1 | 0
1990-07-30 | 1900-07-29 | 9:00 | 9 | 769 | 1325 | 509 | 1 | 9 | 716 | 1 | 9 | 92 | 1 | 13 | 53900 | 1 | 9 | 71500 | 1 | 9 | 12300 | 1 | 13 | 2160 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.24 | 1 | 0
1990-07-30 | 1900-07-29 | 10:00 | 10 | 966 | 1325 | 665 | 1 | 9 | 784 | 1 | 9 | 91 | 1 | 13 | 69000 | 1 | 9 | 78300 | 1 | 9 | 11800 | 1 | 13 | 2490 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 26.7 | 80.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.58 | A | 7 | 984 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.14 | 1 | 0
1990-07-30 | 1900-07-29 | 11:00 | 11 | 1116 | 1325 | 780 | 1 | 13 | 668 | 1 | 13 | 215 | 1 | 13 | 82700 | 1 | 13 | 68100 | 1 | 13 | 25300 | 1 | 13 | 8850 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 27.8 | 82.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.57 | A | 7 | 984 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 1 | 0
1990-07-30 | 1900-07-29 | 12:00 | 12 | 1208 | 1325 | 821 | 1 | 13 | 557 | 1 | 13 | 312 | 1 | 13 | 89000 | 1 | 13 | 58300 | 1 | 13 | 35700 | 1 | 13 | 17970 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 28.3 | 82.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.53 | A | 7 | 984 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.94 | 1 | 0
1990-07-30 | 1900-07-29 | 13:00 | 13 | 1236 | 1325 | 791 | 1 | 13 | 468 | 1 | 13 | 353 | 1 | 13 | 84900 | 1 | 13 | 48900 | 1 | 13 | 39200 | 1 | 13 | 23270 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 26.7 | 80.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 3.2 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.34 | 1 | 0
1990-07-30 | 1900-07-29 | 14:00 | 14 | 1197 | 1325 | 782 | 1 | 13 | 609 | 1 | 13 | 230 | 1 | 13 | 83300 | 1 | 13 | 62200 | 1 | 13 | 27000 | 1 | 13 | 12460 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 27.2 | 80.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.58 | A | 7 | 983 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.94 | 1 | 0
1990-07-30 | 1900-07-29 | 15:00 | 15 | 1095 | 1325 | 809 | 1 | 13 | 715 | 1 | 13 | 215 | 1 | 13 | 85600 | 1 | 13 | 72800 | 1 | 13 | 25300 | 1 | 13 | 8360 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 27.8 | 82.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.55 | A | 7 | 983 | A | 7 | 30 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 1 | 0
1990-07-30 | 1900-07-29 | 16:00 | 16 | 937 | 1325 | 590 | 1 | 13 | 479 | 1 | 13 | 249 | 1 | 13 | 62700 | 1 | 13 | 49700 | 1 | 13 | 27500 | 1 | 13 | 7090 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 26.7 | 80.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.56 | A | 7 | 983 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.76 | 1 | 0
1990-07-30 | 1900-07-29 | 17:00 | 17 | 733 | 1325 | 410 | 1 | 13 | 423 | 1 | 13 | 174 | 1 | 13 | 43600 | 1 | 13 | 43000 | 1 | 13 | 19800 | 1 | 13 | 3850 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 27.2 | 80.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.54 | A | 7 | 983 | A | 7 | 350 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.26 | 1 | 0
1990-07-30 | 1900-07-29 | 18:00 | 18 | 497 | 1325 | 280 | 1 | 13 | 421 | 1 | 13 | 120 | 1 | 13 | 29300 | 1 | 13 | 39800 | 1 | 13 | 14400 | 1 | 13 | 2310 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 24.4 | 75.92 | A | 7 | 15 | 59 | A | 7 | 0.56 | A | 7 | 983 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.4 | 1 | 0
1990-07-30 | 1900-07-29 | 19:00 | 19 | 247 | 1325 | 117 | 1 | 13 | 260 | 1 | 9 | 68 | 1 | 13 | 12000 | 1 | 13 | 18800 | 1 | 9 | 8500 | 1 | 13 | 1250 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | 22.8 | 73.04 | A | 7 | 15 | 59 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.7 | 1 | 0
1990-07-30 | 1900-07-29 | 20:00 | 20 | 31 | 696 | 18 | 1 | 13 | 25 | 1 | 9 | 16 | 1 | 13 | 1900 | 1 | 13 | 900 | 1 | 9 | 1900 | 1 | 13 | 330 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 983 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.9 | 1 | 0
1990-07-30 | 1900-07-29 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 1 | A | 7 | 19.4 | 66.92 | A | 7 | 15 | 59 | A | 7 | 0.76 | A | 7 | 984 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.5 | 1 | 0
1990-07-30 | 1900-07-29 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 984 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 1 | 0
1990-07-30 | 1900-07-29 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 18.3 | 64.94 | A | 7 | 15 | 59 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.4 | 1 | 0
1990-07-30 | 1900-07-29 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 1 | 0
1990-07-31 | 1900-07-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 984 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 2 | 0
1990-07-31 | 1900-07-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.9 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.22 | 2 | 0
1990-07-31 | 1900-07-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.9 | A | 7 | 984 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.22 | 2 | 0
1990-07-31 | 1900-07-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 2 | 0
1990-07-31 | 1900-07-30 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 2 | 0
1990-07-31 | 1900-07-30 | 6:00 | 6 | 52 | 895 | 25 | 1 | 13 | 63 | 1 | 9 | 18 | 1 | 13 | 2400 | 1 | 13 | 2100 | 1 | 9 | 2200 | 1 | 13 | 310 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 985 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 2 | 0
1990-07-31 | 1900-07-30 | 7:00 | 7 | 285 | 1326 | 140 | 1 | 13 | 386 | 1 | 9 | 57 | 1 | 13 | 14300 | 1 | 13 | 30200 | 1 | 9 | 7800 | 1 | 13 | 1020 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 17.2 | 62.96 | A | 7 | 15 | 59 | A | 7 | 0.87 | A | 7 | 985 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.6 | 2 | 0
1990-07-31 | 1900-07-30 | 8:00 | 8 | 535 | 1326 | 312 | 1 | 9 | 554 | 1 | 9 | 88 | 1 | 13 | 32700 | 1 | 9 | 52800 | 1 | 9 | 11300 | 1 | 13 | 1760 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.78 | A | 7 | 985 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.88 | 2 | 0
1990-07-31 | 1900-07-30 | 9:00 | 9 | 766 | 1326 | 506 | 1 | 9 | 716 | 1 | 9 | 90 | 1 | 13 | 53600 | 1 | 9 | 71500 | 1 | 9 | 12200 | 1 | 13 | 2130 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 21.1 | 69.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.73 | A | 7 | 986 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.68 | 2 | 0
1990-07-31 | 1900-07-30 | 10:00 | 10 | 964 | 1326 | 705 | 1 | 9 | 805 | 1 | 9 | 118 | 1 | 13 | 75000 | 1 | 9 | 81300 | 1 | 9 | 15800 | 1 | 13 | 3410 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.69 | A | 7 | 985 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 2 | 0
1990-07-31 | 1900-07-30 | 11:00 | 11 | 1114 | 1326 | 678 | 1 | 13 | 434 | 1 | 13 | 312 | 1 | 13 | 72500 | 1 | 13 | 45300 | 1 | 13 | 34300 | 1 | 13 | 13000 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 23.9 | 75.02 | A | 7 | 15 | 59 | A | 7 | 0.58 | A | 7 | 985 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 1070 | A | 7 | 2.6 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.8 | 2 | 0
1990-07-31 | 1900-07-30 | 12:00 | 12 | 1206 | 1326 | 787 | 1 | 13 | 614 | 1 | 13 | 227 | 1 | 13 | 84100 | 1 | 13 | 62800 | 1 | 13 | 26800 | 1 | 13 | 12760 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.5 | A | 7 | 985 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 2 | 0
1990-07-31 | 1900-07-30 | 13:00 | 13 | 1234 | 1326 | 852 | 1 | 13 | 661 | 1 | 13 | 234 | 1 | 13 | 90900 | 1 | 13 | 67600 | 1 | 13 | 27900 | 1 | 13 | 14930 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.49 | A | 7 | 985 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.32 | 2 | 0
1990-07-31 | 1900-07-30 | 14:00 | 14 | 1195 | 1326 | 885 | 1 | 13 | 706 | 1 | 13 | 245 | 1 | 13 | 93700 | 1 | 13 | 71800 | 1 | 13 | 28800 | 1 | 13 | 13100 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 26.1 | 78.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.49 | A | 7 | 984 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.02 | 2 | 0
1990-07-31 | 1900-07-30 | 15:00 | 15 | 1093 | 1326 | 628 | 1 | 13 | 458 | 1 | 13 | 249 | 1 | 13 | 68500 | 1 | 13 | 47900 | 1 | 13 | 28900 | 1 | 13 | 9690 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 26.7 | 80.06 | A | 7 | 15 | 59 | A | 7 | 0.49 | A | 7 | 983 | A | 7 | 30 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.9 | 2 | 0
1990-07-31 | 1900-07-30 | 16:00 | 16 | 935 | 1326 | 653 | 1 | 9 | 722 | 1 | 9 | 141 | 1 | 13 | 69900 | 1 | 9 | 73900 | 1 | 9 | 17600 | 1 | 13 | 4070 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.47 | A | 7 | 983 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.62 | 2 | 0
1990-07-31 | 1900-07-30 | 17:00 | 17 | 730 | 1326 | 479 | 1 | 9 | 693 | 1 | 9 | 94 | 1 | 13 | 50100 | 1 | 9 | 68700 | 1 | 9 | 12200 | 1 | 13 | 2100 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 26.7 | 80.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.45 | A | 7 | 983 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.42 | 2 | 0
1990-07-31 | 1900-07-30 | 18:00 | 18 | 494 | 1326 | 304 | 1 | 9 | 614 | 1 | 9 | 72 | 1 | 13 | 31800 | 1 | 9 | 57900 | 1 | 9 | 10200 | 1 | 13 | 1440 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.47 | A | 7 | 982 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.92 | 2 | 0
1990-07-31 | 1900-07-30 | 19:00 | 19 | 243 | 1326 | 115 | 1 | 13 | 372 | 1 | 9 | 45 | 1 | 13 | 11600 | 1 | 13 | 27500 | 1 | 9 | 6600 | 1 | 13 | 820 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.12 | 2 | 0
1990-07-31 | 1900-07-30 | 20:00 | 20 | 29 | 674 | 17 | 1 | 13 | 36 | 1 | 9 | 14 | 1 | 13 | 1700 | 1 | 13 | 1000 | 1 | 9 | 1600 | 1 | 13 | 240 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.64 | A | 7 | 982 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.98 | 2 | 0
1990-07-31 | 1900-07-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.48 | 2 | 0
1990-07-31 | 1900-07-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 15.9 | 60.62 | A | 7 | 0.76 | A | 7 | 983 | A | 7 | 60 | A | 7 | 2.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.92 | 2 | 0
1990-07-31 | 1900-07-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20.2 | 68.36 | A | 7 | 16.2 | 61.16 | A | 7 | 0.78 | A | 7 | 983 | A | 7 | 80 | A | 7 | 2.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.86 | 2 | 0
1990-07-31 | 1900-07-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.7 | 67.46 | A | 7 | 16.5 | 61.7 | A | 7 | 0.76 | A | 7 | 983 | A | 7 | 80 | A | 7 | 2.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57 | 2 | 0
1979-08-01 | 1900-07-31 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 19.2 | 66.56 | A | 7 | 16.9 | 62.42 | A | 7 | 0.9 | A | 7 | 981 | A | 7 | 330 | A | 7 | 2.9 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.42 | 3 | 0
1979-08-01 | 1900-07-31 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.7 | 65.66 | A | 7 | 17.2 | 62.96 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 330 | A | 7 | 3 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.36 | 3 | 0
1979-08-01 | 1900-07-31 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 17.5 | 63.5 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 340 | A | 7 | 3 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.9 | 3 | 0
1979-08-01 | 1900-07-31 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 17.8 | 64.04 | A | 7 | 1 | A | 7 | 980 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.94 | 3 | 0
1979-08-01 | 1900-07-31 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 17.2 | 62.96 | A | 7 | 1 | A | 7 | 981 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.86 | 3 | 0
1979-08-01 | 1900-07-31 | 6:00 | 6 | 51 | 895 | 22 | 1 | 13 | 35 | 1 | 9 | 19 | 1 | 13 | 2300 | 1 | 13 | 1500 | 1 | 9 | 2200 | 1 | 13 | 390 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 17.2 | 62.96 | A | 7 | 1 | A | 7 | 981 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 4000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.86 | 3 | 0
1979-08-01 | 1900-07-31 | 7:00 | 7 | 283 | 1326 | 125 | 1 | 13 | 314 | 1 | 9 | 58 | 1 | 13 | 13300 | 1 | 13 | 24300 | 1 | 9 | 8100 | 1 | 13 | 1040 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | 18.3 | 64.94 | A | 7 | 1 | A | 7 | 981 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 4000 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.84 | 3 | 0
1979-08-01 | 1900-07-31 | 8:00 | 8 | 533 | 1326 | 313 | 1 | 9 | 553 | 1 | 9 | 90 | 1 | 13 | 32700 | 1 | 9 | 52600 | 1 | 9 | 11500 | 1 | 13 | 1790 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.32 | 3 | 0
1979-08-01 | 1900-07-31 | 9:00 | 9 | 765 | 1326 | 507 | 1 | 13 | 638 | 1 | 13 | 138 | 1 | 13 | 53300 | 1 | 13 | 63900 | 1 | 13 | 16400 | 1 | 13 | 3170 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 3 | 0
1979-08-01 | 1900-07-31 | 10:00 | 10 | 963 | 1326 | 692 | 1 | 13 | 715 | 1 | 13 | 171 | 1 | 13 | 73400 | 1 | 13 | 72800 | 1 | 13 | 20400 | 1 | 13 | 5070 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.52 | 3 | 0
1979-08-01 | 1900-07-31 | 11:00 | 11 | 1113 | 1326 | 767 | 1 | 13 | 660 | 1 | 13 | 211 | 1 | 13 | 81500 | 1 | 13 | 67300 | 1 | 13 | 24800 | 1 | 13 | 8620 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.66 | 3 | 0
1979-08-01 | 1900-07-31 | 12:00 | 12 | 1205 | 1326 | 908 | 1 | 13 | 726 | 1 | 13 | 246 | 1 | 13 | 96400 | 1 | 13 | 73900 | 1 | 13 | 29000 | 1 | 13 | 13670 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.68 | 3 | 0
1979-08-01 | 1900-07-31 | 13:00 | 13 | 1233 | 1326 | 883 | 1 | 9 | 716 | 1 | 9 | 215 | 1 | 13 | 94900 | 1 | 9 | 73500 | 1 | 9 | 26400 | 1 | 13 | 13680 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.18 | 3 | 0
1979-08-01 | 1900-07-31 | 14:00 | 14 | 1194 | 1326 | 864 | 1 | 13 | 713 | 1 | 13 | 219 | 1 | 13 | 92300 | 1 | 13 | 72900 | 1 | 13 | 26400 | 1 | 13 | 11730 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 27.2 | 80.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.51 | A | 7 | 979 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.98 | 3 | 0
1979-08-01 | 1900-07-31 | 15:00 | 15 | 1092 | 1326 | 779 | 1 | 9 | 726 | 1 | 9 | 178 | 1 | 13 | 83500 | 1 | 9 | 74500 | 1 | 9 | 22000 | 1 | 13 | 6960 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 27.2 | 80.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.36 | 3 | 0
1979-08-01 | 1900-07-31 | 16:00 | 16 | 933 | 1326 | 527 | 1 | 9 | 533 | 1 | 9 | 150 | 1 | 13 | 56200 | 1 | 9 | 54400 | 1 | 9 | 17800 | 1 | 13 | 4290 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 27.8 | 82.04 | A | 7 | 15 | 59 | A | 7 | 0.46 | A | 7 | 978 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.3 | 3 | 0
1979-08-01 | 1900-07-31 | 17:00 | 17 | 729 | 1326 | 495 | 1 | 9 | 694 | 1 | 9 | 112 | 1 | 13 | 52500 | 1 | 9 | 69600 | 1 | 9 | 14100 | 1 | 13 | 2550 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.48 | 3 | 0
1979-08-01 | 1900-07-31 | 18:00 | 18 | 492 | 1326 | 297 | 1 | 9 | 570 | 1 | 9 | 83 | 1 | 13 | 30800 | 1 | 9 | 53300 | 1 | 9 | 11000 | 1 | 13 | 1620 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.26 | 3 | 0
1979-08-01 | 1900-07-31 | 19:00 | 19 | 241 | 1326 | 109 | 1 | 13 | 316 | 1 | 9 | 51 | 1 | 13 | 11400 | 1 | 13 | 22600 | 1 | 9 | 7300 | 1 | 13 | 910 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 350 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.04 | 3 | 0
1979-08-01 | 1900-07-31 | 20:00 | 20 | 28 | 652 | 14 | 1 | 13 | 19 | 1 | 9 | 13 | 1 | 13 | 1600 | 1 | 13 | 700 | 1 | 9 | 1500 | 1 | 13 | 270 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 3 | 0
1979-08-01 | 1900-07-31 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 17.8 | 64.04 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.44 | 3 | 0
1979-08-01 | 1900-07-31 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.86 | 3 | 0
1979-08-01 | 1900-07-31 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 17.2 | 62.96 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.76 | 3 | 0
1979-08-01 | 1900-07-31 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 3 | 0
1979-08-02 | 1900-08-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.68 | 4 | 0
1979-08-02 | 1900-08-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 4 | 0
1979-08-02 | 1900-08-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.04 | 4 | 0
1979-08-02 | 1900-08-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.54 | 4 | 0
1979-08-02 | 1900-08-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.54 | 4 | 0
1979-08-02 | 1900-08-01 | 6:00 | 6 | 49 | 873 | 18 | 1 | 13 | 17 | 1 | 13 | 17 | 1 | 13 | 2000 | 1 | 13 | 900 | 1 | 13 | 1900 | 1 | 13 | 420 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 20 | 68 | A | 7 | 18.3 | 64.94 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.94 | 4 | 0
1979-08-02 | 1900-08-01 | 7:00 | 7 | 280 | 1326 | 80 | 1 | 13 | 39 | 1 | 9 | 72 | 1 | 13 | 8800 | 1 | 13 | 3200 | 1 | 9 | 8100 | 1 | 13 | 1840 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 21.1 | 69.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.64 | 4 | 0
1979-08-02 | 1900-08-01 | 8:00 | 8 | 530 | 1326 | 116 | 1 | 9 | 6 | 1 | 9 | 114 | 1 | 13 | 13500 | 1 | 9 | 400 | 1 | 9 | 13300 | 1 | 13 | 4700 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 1830 | A | 7 | 3.3 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 4 | 0
1979-08-02 | 1900-08-01 | 9:00 | 9 | 763 | 1326 | 179 | 1 | 9 | 81 | 1 | 9 | 132 | 1 | 13 | 20300 | 1 | 9 | 8600 | 1 | 9 | 15400 | 1 | 13 | 3480 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 1680 | A | 7 | 3.2 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.32 | 4 | 0
1979-08-02 | 1900-08-01 | 10:00 | 10 | 961 | 1326 | 226 | 1 | 9 | 93 | 1 | 9 | 159 | 1 | 13 | 26000 | 1 | 9 | 10000 | 1 | 9 | 18700 | 1 | 13 | 4980 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 20 | 68 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 2740 | A | 7 | 3.5 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.9 | 4 | 0
1979-08-02 | 1900-08-01 | 11:00 | 11 | 1111 | 1326 | 783 | 1 | 13 | 587 | 1 | 13 | 290 | 1 | 13 | 84300 | 1 | 13 | 61300 | 1 | 13 | 32800 | 1 | 13 | 11910 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 25.6 | 78.08 | A | 7 | 21.7 | 71.06 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 1980 | A | 7 | 3.8 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.36 | 4 | 0
1979-08-02 | 1900-08-01 | 12:00 | 12 | 1203 | 1326 | 836 | 1 | 13 | 633 | 1 | 13 | 260 | 1 | 13 | 88400 | 1 | 13 | 64200 | 1 | 13 | 30000 | 1 | 13 | 14270 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 4 | 0
1979-08-02 | 1900-08-01 | 13:00 | 13 | 1231 | 1326 | 643 | 1 | 9 | 264 | 1 | 9 | 397 | 1 | 13 | 70800 | 1 | 9 | 28700 | 1 | 9 | 44100 | 1 | 13 | 22720 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 28.3 | 82.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 2740 | A | 7 | 4 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.96 | 4 | 0
1979-08-02 | 1900-08-01 | 14:00 | 14 | 1192 | 1326 | 779 | 1 | 13 | 543 | 1 | 13 | 289 | 1 | 13 | 84800 | 1 | 13 | 56900 | 1 | 13 | 33600 | 1 | 13 | 15510 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 29.4 | 84.92 | A | 7 | 22.8 | 73.04 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 2740 | A | 7 | 4 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.24 | 4 | 0
1979-08-02 | 1900-08-01 | 15:00 | 15 | 1090 | 1326 | 668 | 1 | 13 | 411 | 1 | 13 | 329 | 1 | 13 | 70800 | 1 | 13 | 42800 | 1 | 13 | 35500 | 1 | 13 | 12880 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 30 | 86 | A | 7 | 22.2 | 71.96 | A | 7 | 0.63 | A | 7 | 975 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 3.9 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.26 | 4 | 0
1979-08-02 | 1900-08-01 | 16:00 | 16 | 931 | 1326 | 474 | 1 | 9 | 260 | 1 | 9 | 291 | 1 | 13 | 51400 | 1 | 9 | 28000 | 1 | 9 | 31700 | 1 | 13 | 8330 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 28.3 | 82.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.72 | A | 7 | 975 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 3050 | A | 7 | 4.1 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.44 | 4 | 0
1979-08-02 | 1900-08-01 | 17:00 | 17 | 726 | 1326 | 262 | 1 | 9 | 137 | 1 | 9 | 186 | 1 | 13 | 28900 | 1 | 9 | 14300 | 1 | 9 | 21100 | 1 | 13 | 4800 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 28.3 | 82.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.72 | A | 7 | 975 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 3050 | A | 7 | 4.1 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.44 | 4 | 0
1979-08-02 | 1900-08-01 | 18:00 | 18 | 489 | 1326 | 176 | 1 | 9 | 79 | 1 | 9 | 146 | 1 | 13 | 19200 | 1 | 9 | 7500 | 1 | 9 | 16400 | 1 | 13 | 4020 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 28.3 | 82.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.72 | A | 7 | 975 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 3050 | A | 7 | 4.1 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.44 | 4 | 0
1979-08-02 | 1900-08-01 | 19:00 | 19 | 237 | 1326 | 62 | 1 | 13 | 37 | 1 | 13 | 55 | 1 | 13 | 6800 | 1 | 13 | 2900 | 1 | 13 | 6200 | 1 | 13 | 1400 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 28.3 | 82.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.7 | A | 7 | 975 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 4 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.96 | 4 | 0
1979-08-02 | 1900-08-01 | 20:00 | 20 | 26 | 630 | 10 | 1 | 13 | 7 | 1 | 13 | 9 | 1 | 13 | 1000 | 1 | 13 | 300 | 1 | 13 | 1000 | 1 | 13 | 230 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 25.6 | 78.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.82 | A | 7 | 975 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 3.9 | E | 8 | 0.147 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.86 | 4 | 0
1979-08-02 | 1900-08-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 976 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 4 | 0
1979-08-02 | 1900-08-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.06 | 4 | 0
1979-08-02 | 1900-08-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 976 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 4 | 0
1979-08-02 | 1900-08-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.18 | 4 | 0
1979-08-03 | 1900-08-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 5 | 0
1979-08-03 | 1900-08-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.12 | 5 | 0
1979-08-03 | 1900-08-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 20 | 68 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.6 | 5 | 0
1979-08-03 | 1900-08-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 21.7 | 71.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.22 | 5 | 0
1979-08-03 | 1900-08-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 21.1 | 69.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.82 | 5 | 0
1979-08-03 | 1900-08-02 | 6:00 | 6 | 47 | 851 | 14 | 1 | 13 | 15 | 1 | 13 | 13 | 1 | 13 | 1600 | 1 | 13 | 600 | 1 | 13 | 1500 | 1 | 13 | 270 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 21.1 | 69.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.9 | A | 7 | 977 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.82 | 5 | 0
1979-08-03 | 1900-08-02 | 7:00 | 7 | 277 | 1327 | 122 | 1 | 13 | 279 | 1 | 13 | 64 | 1 | 13 | 12800 | 1 | 13 | 21300 | 1 | 13 | 8400 | 1 | 13 | 1160 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 20 | 68 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.6 | 5 | 0
1979-08-03 | 1900-08-02 | 8:00 | 8 | 527 | 1327 | 285 | 1 | 9 | 409 | 1 | 9 | 122 | 1 | 13 | 30200 | 1 | 9 | 39200 | 1 | 9 | 14600 | 1 | 13 | 2370 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.3 | 5 | 0
1979-08-03 | 1900-08-02 | 9:00 | 9 | 760 | 1327 | 491 | 1 | 9 | 600 | 1 | 9 | 146 | 1 | 13 | 51300 | 1 | 9 | 59800 | 1 | 9 | 17000 | 1 | 13 | 3310 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 5 | 0
1979-08-03 | 1900-08-02 | 10:00 | 10 | 959 | 1327 | 692 | 1 | 9 | 757 | 1 | 9 | 144 | 1 | 13 | 72100 | 1 | 9 | 75800 | 1 | 9 | 17200 | 1 | 13 | 3860 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 5 | 0
1979-08-03 | 1900-08-02 | 11:00 | 11 | 1109 | 1327 | 821 | 1 | 9 | 792 | 1 | 9 | 157 | 1 | 13 | 86500 | 1 | 9 | 79800 | 1 | 9 | 19600 | 1 | 13 | 5900 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 5 | 0
1979-08-03 | 1900-08-02 | 12:00 | 12 | 1201 | 1327 | 907 | 1 | 9 | 817 | 1 | 9 | 165 | 1 | 13 | 96100 | 1 | 9 | 82600 | 1 | 9 | 21200 | 1 | 13 | 8530 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 23.3 | 73.94 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.24 | 5 | 0
1979-08-03 | 1900-08-02 | 13:00 | 13 | 1229 | 1327 | 881 | 1 | 9 | 773 | 1 | 9 | 162 | 1 | 13 | 93800 | 1 | 9 | 78300 | 1 | 9 | 21100 | 1 | 13 | 9560 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 31.1 | 87.98 | A | 7 | 23.3 | 73.94 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.94 | 5 | 0
1979-08-03 | 1900-08-02 | 14:00 | 14 | 1190 | 1327 | 858 | 1 | 9 | 732 | 1 | 9 | 199 | 1 | 13 | 92300 | 1 | 9 | 75200 | 1 | 9 | 24700 | 1 | 13 | 10530 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 31.7 | 89.06 | A | 7 | 23.9 | 75.02 | A | 7 | 0.63 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.92 | 5 | 0
1979-08-03 | 1900-08-02 | 15:00 | 15 | 1088 | 1327 | 699 | 1 | 13 | 575 | 1 | 13 | 225 | 1 | 13 | 73600 | 1 | 13 | 58400 | 1 | 13 | 25700 | 1 | 13 | 8500 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 32.2 | 89.96 | A | 7 | 23.9 | 75.02 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.32 | 5 | 0
1979-08-03 | 1900-08-02 | 16:00 | 16 | 928 | 1327 | 617 | 1 | 13 | 507 | 1 | 13 | 260 | 1 | 13 | 65200 | 1 | 13 | 52500 | 1 | 13 | 28400 | 1 | 13 | 7320 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 32.2 | 89.96 | A | 7 | 23.9 | 75.02 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.32 | 5 | 0
1979-08-03 | 1900-08-02 | 17:00 | 17 | 723 | 1327 | 470 | 1 | 13 | 658 | 1 | 13 | 109 | 1 | 13 | 49700 | 1 | 13 | 66000 | 1 | 13 | 13700 | 1 | 13 | 2470 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 32.2 | 89.96 | A | 7 | 23.9 | 75.02 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.32 | 5 | 0
1979-08-03 | 1900-08-02 | 18:00 | 18 | 485 | 1327 | 278 | 1 | 9 | 522 | 1 | 9 | 85 | 1 | 13 | 28700 | 1 | 9 | 48600 | 1 | 9 | 11000 | 1 | 13 | 1650 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 23.3 | 73.94 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.44 | 5 | 0
1979-08-03 | 1900-08-02 | 19:00 | 19 | 233 | 1327 | 103 | 1 | 13 | 288 | 1 | 9 | 51 | 1 | 13 | 10700 | 1 | 13 | 20300 | 1 | 9 | 7100 | 1 | 13 | 910 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 23.3 | 73.94 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.24 | 5 | 0
1979-08-03 | 1900-08-02 | 20:00 | 20 | 24 | 608 | 13 | 1 | 13 | 13 | 1 | 9 | 12 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.157 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.54 | 5 | 0
1979-08-03 | 1900-08-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 23.3 | 73.94 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.04 | 5 | 0
1979-08-03 | 1900-08-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 22.8 | 73.04 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.14 | 5 | 0
1979-08-03 | 1900-08-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.79 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.16 | 5 | 0
1979-08-03 | 1900-08-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.86 | 5 | 0
1979-08-04 | 1900-08-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 21.7 | 71.06 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.36 | 6 | 0
1979-08-04 | 1900-08-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 21.1 | 69.98 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.28 | 6 | 0
1979-08-04 | 1900-08-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 6 | 0
1979-08-04 | 1900-08-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.16 | 6 | 0
1979-08-04 | 1900-08-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.86 | 6 | 0
1979-08-04 | 1900-08-03 | 6:00 | 6 | 44 | 829 | 23 | 1 | 13 | 62 | 1 | 9 | 16 | 1 | 13 | 2100 | 1 | 13 | 2000 | 1 | 9 | 2000 | 1 | 13 | 270 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.86 | 6 | 0
1979-08-04 | 1900-08-03 | 7:00 | 7 | 274 | 1327 | 136 | 1 | 13 | 435 | 1 | 9 | 46 | 1 | 13 | 14000 | 1 | 13 | 33900 | 1 | 9 | 7100 | 1 | 13 | 850 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.06 | 6 | 0
1979-08-04 | 1900-08-03 | 8:00 | 8 | 525 | 1327 | 327 | 1 | 9 | 645 | 1 | 9 | 71 | 1 | 13 | 34700 | 1 | 9 | 61700 | 1 | 9 | 10200 | 1 | 13 | 1450 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.94 | 6 | 0
1979-08-04 | 1900-08-03 | 9:00 | 9 | 758 | 1327 | 527 | 1 | 9 | 756 | 1 | 9 | 93 | 1 | 13 | 55500 | 1 | 9 | 75300 | 1 | 9 | 12500 | 1 | 13 | 2150 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 23.3 | 73.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.04 | 6 | 0
1979-08-04 | 1900-08-03 | 10:00 | 10 | 957 | 1327 | 698 | 1 | 9 | 813 | 1 | 9 | 110 | 1 | 13 | 74700 | 1 | 9 | 82300 | 1 | 9 | 15300 | 1 | 13 | 3190 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 23.9 | 75.02 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.22 | 6 | 0
1979-08-04 | 1900-08-03 | 11:00 | 11 | 1107 | 1327 | 831 | 1 | 9 | 847 | 1 | 9 | 121 | 1 | 13 | 85400 | 1 | 9 | 84800 | 1 | 9 | 14500 | 1 | 13 | 3880 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 24.4 | 75.92 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.52 | 6 | 0
1979-08-04 | 1900-08-03 | 12:00 | 12 | 1199 | 1327 | 847 | 1 | 9 | 799 | 1 | 9 | 122 | 1 | 13 | 87000 | 1 | 9 | 80100 | 1 | 9 | 14500 | 1 | 13 | 5400 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 31.7 | 89.06 | A | 7 | 24.4 | 75.92 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.52 | 6 | 0
1979-08-04 | 1900-08-03 | 13:00 | 13 | 1227 | 1327 | 924 | 1 | 9 | 859 | 1 | 9 | 126 | 1 | 13 | 94800 | 1 | 9 | 86100 | 1 | 9 | 14900 | 1 | 13 | 6250 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 32.2 | 89.96 | A | 7 | 24.4 | 75.92 | A | 7 | 0.64 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.92 | 6 | 0
1979-08-04 | 1900-08-03 | 14:00 | 14 | 1188 | 1327 | 855 | 1 | 9 | 779 | 1 | 9 | 155 | 1 | 13 | 91000 | 1 | 9 | 78900 | 1 | 9 | 20200 | 1 | 13 | 7660 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 33.3 | 91.94 | A | 7 | 24.4 | 75.92 | A | 7 | 0.6 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.82 | 6 | 0
1979-08-04 | 1900-08-03 | 15:00 | 15 | 1085 | 1327 | 785 | 1 | 9 | 822 | 1 | 9 | 110 | 1 | 13 | 81000 | 1 | 9 | 82300 | 1 | 9 | 13500 | 1 | 13 | 3490 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 33.3 | 91.94 | A | 7 | 23.9 | 75.02 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 6 | 0
1979-08-04 | 1900-08-03 | 16:00 | 16 | 925 | 1327 | 620 | 1 | 9 | 702 | 1 | 9 | 127 | 1 | 13 | 64900 | 1 | 9 | 70500 | 1 | 9 | 15600 | 1 | 13 | 3340 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 33.3 | 91.94 | A | 7 | 23.9 | 75.02 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 6 | 0
1979-08-04 | 1900-08-03 | 17:00 | 17 | 719 | 1327 | 490 | 1 | 9 | 731 | 1 | 9 | 90 | 1 | 13 | 51300 | 1 | 9 | 72400 | 1 | 9 | 12000 | 1 | 13 | 2010 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 23.9 | 75.02 | A | 7 | 0.6 | A | 7 | 979 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.12 | 6 | 0
1979-08-04 | 1900-08-03 | 18:00 | 18 | 482 | 1327 | 296 | 1 | 9 | 623 | 1 | 9 | 67 | 1 | 13 | 31100 | 1 | 9 | 58500 | 1 | 9 | 9800 | 1 | 13 | 1340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 23.9 | 75.02 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.32 | 6 | 0
1979-08-04 | 1900-08-03 | 19:00 | 19 | 229 | 1327 | 109 | 1 | 13 | 380 | 1 | 9 | 42 | 1 | 13 | 11000 | 1 | 13 | 27400 | 1 | 9 | 6300 | 1 | 13 | 760 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 23.9 | 75.02 | A | 7 | 0.68 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.22 | 6 | 0
1979-08-04 | 1900-08-03 | 20:00 | 20 | 22 | 586 | 15 | 1 | 13 | 32 | 1 | 9 | 11 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 23.9 | 75.02 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.82 | 6 | 0
1979-08-04 | 1900-08-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 23.9 | 75.02 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.02 | 6 | 0
1979-08-04 | 1900-08-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.54 | 6 | 0
1979-08-04 | 1900-08-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 23.3 | 73.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.04 | 6 | 0
1979-08-04 | 1900-08-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 23.3 | 73.94 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.04 | 6 | 0
1979-08-05 | 1900-08-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 23.3 | 73.94 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.74 | 7 | 0
1979-08-05 | 1900-08-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.94 | 7 | 0
1979-08-05 | 1900-08-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 7 | 0
1979-08-05 | 1900-08-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 7 | 0
1979-08-05 | 1900-08-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 7 | 0
1979-08-05 | 1900-08-04 | 6:00 | 6 | 42 | 808 | 18 | 1 | 13 | 16 | 1 | 9 | 16 | 1 | 13 | 1900 | 1 | 13 | 900 | 1 | 9 | 1800 | 1 | 13 | 390 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 7 | 0
1979-08-05 | 1900-08-04 | 7:00 | 7 | 270 | 1327 | 118 | 1 | 13 | 285 | 1 | 9 | 60 | 1 | 13 | 12400 | 1 | 13 | 21600 | 1 | 9 | 8000 | 1 | 13 | 1080 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.48 | 7 | 0
1979-08-05 | 1900-08-04 | 8:00 | 8 | 522 | 1327 | 306 | 1 | 9 | 524 | 1 | 9 | 99 | 1 | 13 | 31600 | 1 | 9 | 49400 | 1 | 9 | 12200 | 1 | 13 | 1920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.18 | 7 | 0
1979-08-05 | 1900-08-04 | 9:00 | 9 | 755 | 1327 | 505 | 1 | 9 | 649 | 1 | 9 | 134 | 1 | 13 | 53000 | 1 | 9 | 64900 | 1 | 9 | 16000 | 1 | 13 | 3060 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 983 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 7 | 0
1979-08-05 | 1900-08-04 | 10:00 | 10 | 954 | 1327 | 682 | 1 | 9 | 725 | 1 | 9 | 159 | 1 | 13 | 72600 | 1 | 9 | 74000 | 1 | 9 | 19300 | 1 | 13 | 4670 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 22.2 | 71.96 | A | 7 | 0.63 | A | 7 | 982 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.26 | 7 | 0
1979-08-05 | 1900-08-04 | 11:00 | 11 | 1105 | 1327 | 818 | 1 | 9 | 768 | 1 | 9 | 176 | 1 | 13 | 85000 | 1 | 9 | 77000 | 1 | 9 | 20700 | 1 | 13 | 6330 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.59 | A | 7 | 982 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.16 | 7 | 0
1979-08-05 | 1900-08-04 | 12:00 | 12 | 1198 | 1327 | 901 | 1 | 9 | 790 | 1 | 9 | 185 | 1 | 13 | 94100 | 1 | 9 | 79400 | 1 | 9 | 22400 | 1 | 13 | 9180 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 23.3 | 73.94 | A | 7 | 0.59 | A | 7 | 982 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.84 | 7 | 0
1979-08-05 | 1900-08-04 | 13:00 | 13 | 1225 | 1327 | 923 | 1 | 9 | 793 | 1 | 9 | 188 | 1 | 13 | 96600 | 1 | 9 | 79700 | 1 | 9 | 22900 | 1 | 13 | 10570 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 24.4 | 75.92 | A | 7 | 0.58 | A | 7 | 982 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.32 | 7 | 0
1979-08-05 | 1900-08-04 | 14:00 | 14 | 1186 | 1327 | 889 | 1 | 9 | 786 | 1 | 9 | 184 | 1 | 13 | 92900 | 1 | 9 | 79000 | 1 | 9 | 22200 | 1 | 13 | 8700 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 24.4 | 75.92 | A | 7 | 0.58 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.32 | 7 | 0
1979-08-05 | 1900-08-04 | 15:00 | 15 | 1083 | 1327 | 795 | 1 | 9 | 758 | 1 | 9 | 174 | 1 | 13 | 82400 | 1 | 9 | 75900 | 1 | 9 | 20400 | 1 | 13 | 5870 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 34.4 | 93.92 | A | 7 | 24.4 | 75.92 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.72 | 7 | 0
1979-08-05 | 1900-08-04 | 16:00 | 16 | 922 | 1327 | 654 | 1 | 9 | 713 | 1 | 9 | 155 | 1 | 13 | 69300 | 1 | 9 | 72600 | 1 | 9 | 18700 | 1 | 13 | 4330 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 34.4 | 93.92 | A | 7 | 23.9 | 75.02 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.42 | 7 | 0
1979-08-05 | 1900-08-04 | 17:00 | 17 | 716 | 1327 | 472 | 1 | 9 | 632 | 1 | 9 | 129 | 1 | 13 | 49400 | 1 | 9 | 62800 | 1 | 9 | 15400 | 1 | 13 | 2840 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 23.9 | 75.02 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.02 | 7 | 0
1979-08-05 | 1900-08-04 | 18:00 | 18 | 478 | 1327 | 271 | 1 | 9 | 483 | 1 | 9 | 95 | 1 | 13 | 27700 | 1 | 9 | 44500 | 1 | 9 | 11700 | 1 | 13 | 1790 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 33.3 | 91.94 | A | 7 | 23.9 | 75.02 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 7 | 0
1979-08-05 | 1900-08-04 | 19:00 | 19 | 225 | 1327 | 89 | 1 | 13 | 157 | 1 | 9 | 62 | 1 | 13 | 9300 | 1 | 13 | 10700 | 1 | 9 | 7500 | 1 | 13 | 1170 | 1 | 21 | 5 | A | 7 | 1 | A | 7 | 31.1 | 87.98 | A | 7 | 24.4 | 75.92 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.02 | 7 | 0
1979-08-05 | 1900-08-04 | 20:00 | 20 | 20 | 564 | 9 | 1 | 13 | 4 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 28.9 | 84.02 | A | 7 | 24.4 | 75.92 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.189 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.42 | 7 | 0
1979-08-05 | 1900-08-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 23.9 | 75.02 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.52 | 7 | 0
1979-08-05 | 1900-08-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 23.9 | 75.02 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.82 | 7 | 0
1979-08-05 | 1900-08-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 23.3 | 73.94 | A | 7 | 0.85 | A | 7 | 982 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.44 | 7 | 0
1979-08-05 | 1900-08-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.94 | 7 | 0
1979-08-06 | 1900-08-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.16 | 1 | 0
1979-08-06 | 1900-08-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.86 | 1 | 0
1979-08-06 | 1900-08-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 1 | 0
1979-08-06 | 1900-08-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.06 | 1 | 0
1979-08-06 | 1900-08-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 982 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 1 | 0
1979-08-06 | 1900-08-05 | 6:00 | 6 | 40 | 786 | 16 | 1 | 13 | 4 | 1 | 9 | 16 | 1 | 13 | 1800 | 1 | 13 | 0 | 1 | 9 | 1800 | 1 | 13 | 550 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.86 | 1 | 0
1979-08-06 | 1900-08-05 | 7:00 | 7 | 267 | 1328 | 107 | 1 | 13 | 198 | 1 | 9 | 67 | 1 | 13 | 11400 | 1 | 13 | 14900 | 1 | 9 | 8400 | 1 | 13 | 1260 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 22.2 | 71.96 | A | 7 | 0.85 | A | 7 | 983 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.56 | 1 | 0
1979-08-06 | 1900-08-05 | 8:00 | 8 | 519 | 1328 | 287 | 1 | 9 | 431 | 1 | 9 | 118 | 1 | 13 | 30400 | 1 | 9 | 41200 | 1 | 9 | 14300 | 1 | 13 | 2280 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.66 | 1 | 0
1979-08-06 | 1900-08-05 | 9:00 | 9 | 753 | 1328 | 484 | 1 | 9 | 568 | 1 | 9 | 162 | 1 | 13 | 50300 | 1 | 9 | 56300 | 1 | 9 | 18300 | 1 | 13 | 3580 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.72 | A | 7 | 983 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.46 | 1 | 0
1979-08-06 | 1900-08-05 | 10:00 | 10 | 952 | 1328 | 663 | 1 | 9 | 653 | 1 | 9 | 194 | 1 | 13 | 69700 | 1 | 9 | 66000 | 1 | 9 | 22200 | 1 | 13 | 5540 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 22.8 | 73.04 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.64 | 1 | 0
1979-08-06 | 1900-08-05 | 11:00 | 11 | 1103 | 1328 | 799 | 1 | 9 | 700 | 1 | 9 | 216 | 1 | 13 | 84700 | 1 | 9 | 71300 | 1 | 9 | 25400 | 1 | 13 | 8530 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 23.3 | 73.94 | A | 7 | 0.59 | A | 7 | 982 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.84 | 1 | 0
1979-08-06 | 1900-08-05 | 12:00 | 12 | 1196 | 1328 | 884 | 1 | 9 | 725 | 1 | 9 | 228 | 1 | 13 | 94100 | 1 | 9 | 74000 | 1 | 9 | 27300 | 1 | 13 | 12170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.3 | 91.94 | A | 7 | 23.3 | 73.94 | A | 7 | 0.56 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.04 | 1 | 0
1979-08-06 | 1900-08-05 | 13:00 | 13 | 1223 | 1328 | 913 | 1 | 9 | 737 | 1 | 9 | 232 | 1 | 13 | 97500 | 1 | 9 | 75300 | 1 | 9 | 27900 | 1 | 13 | 13920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 22.8 | 73.04 | A | 7 | 0.52 | A | 7 | 982 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.24 | 1 | 0
1979-08-06 | 1900-08-05 | 14:00 | 14 | 1184 | 1328 | 876 | 1 | 9 | 725 | 1 | 9 | 227 | 1 | 13 | 93200 | 1 | 9 | 74000 | 1 | 9 | 27100 | 1 | 13 | 11570 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 34.4 | 93.92 | A | 7 | 22.8 | 73.04 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.94 | 1 | 0
1979-08-06 | 1900-08-05 | 15:00 | 15 | 1080 | 1328 | 783 | 1 | 9 | 698 | 1 | 9 | 213 | 1 | 13 | 82800 | 1 | 9 | 71000 | 1 | 9 | 24900 | 1 | 13 | 7920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 34.4 | 93.92 | A | 7 | 23.3 | 73.94 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.94 | 1 | 0
1979-08-06 | 1900-08-05 | 16:00 | 16 | 920 | 1328 | 640 | 1 | 9 | 646 | 1 | 9 | 189 | 1 | 13 | 66800 | 1 | 9 | 65200 | 1 | 9 | 21600 | 1 | 13 | 5130 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 34.4 | 93.92 | A | 7 | 22.8 | 73.04 | A | 7 | 0.51 | A | 7 | 980 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.94 | 1 | 0
1979-08-06 | 1900-08-05 | 17:00 | 17 | 713 | 1328 | 455 | 1 | 9 | 555 | 1 | 9 | 155 | 1 | 13 | 48800 | 1 | 9 | 56300 | 1 | 9 | 18500 | 1 | 13 | 3340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 22.8 | 73.04 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.24 | 1 | 0
1979-08-06 | 1900-08-05 | 18:00 | 18 | 474 | 1328 | 256 | 1 | 9 | 403 | 1 | 9 | 110 | 1 | 13 | 26800 | 1 | 9 | 37600 | 1 | 9 | 13400 | 1 | 13 | 2090 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 22.8 | 73.04 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.34 | 1 | 0
1979-08-06 | 1900-08-05 | 19:00 | 19 | 221 | 1328 | 84 | 1 | 13 | 150 | 1 | 9 | 58 | 1 | 13 | 8800 | 1 | 13 | 10100 | 1 | 9 | 7100 | 1 | 13 | 1090 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 23.3 | 73.94 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.94 | 1 | 0
1979-08-06 | 1900-08-05 | 20:00 | 20 | 19 | 542 | 10 | 1 | 13 | 1 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 23.3 | 73.94 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.26 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.74 | 1 | 0
1979-08-06 | 1900-08-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.44 | 1 | 0
1979-08-06 | 1900-08-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 22.8 | 73.04 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.94 | 1 | 0
1979-08-06 | 1900-08-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.46 | 1 | 0
1979-08-06 | 1900-08-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 22.2 | 71.96 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.96 | 1 | 0
1979-08-07 | 1900-08-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.66 | 2 | 0
1979-08-07 | 1900-08-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 2 | 0
1979-08-07 | 1900-08-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.88 | 2 | 0
1979-08-07 | 1900-08-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 21.1 | 69.98 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.28 | 2 | 0
1979-08-07 | 1900-08-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 2 | 0
1979-08-07 | 1900-08-06 | 6:00 | 6 | 38 | 764 | 20 | 1 | 13 | 51 | 1 | 9 | 15 | 1 | 13 | 1900 | 1 | 13 | 1500 | 1 | 9 | 1800 | 1 | 13 | 260 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.48 | 2 | 0
1979-08-07 | 1900-08-06 | 7:00 | 7 | 264 | 1328 | 129 | 1 | 13 | 418 | 1 | 9 | 46 | 1 | 13 | 13300 | 1 | 13 | 32000 | 1 | 9 | 7000 | 1 | 13 | 840 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 21.1 | 69.98 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.28 | 2 | 0
1979-08-07 | 1900-08-06 | 8:00 | 8 | 516 | 1328 | 321 | 1 | 9 | 641 | 1 | 9 | 71 | 1 | 13 | 34000 | 1 | 9 | 61100 | 1 | 9 | 10200 | 1 | 13 | 1440 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.16 | 2 | 0
1979-08-07 | 1900-08-06 | 9:00 | 9 | 750 | 1328 | 520 | 1 | 9 | 751 | 1 | 9 | 94 | 1 | 13 | 54700 | 1 | 9 | 74600 | 1 | 9 | 12500 | 1 | 13 | 2140 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 240 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.44 | 2 | 0
1979-08-07 | 1900-08-06 | 10:00 | 10 | 950 | 1328 | 694 | 1 | 9 | 811 | 1 | 9 | 111 | 1 | 13 | 74000 | 1 | 9 | 82000 | 1 | 9 | 15200 | 1 | 13 | 3170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 22.8 | 73.04 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.64 | 2 | 0
1979-08-07 | 1900-08-06 | 11:00 | 11 | 1101 | 1328 | 826 | 1 | 9 | 845 | 1 | 9 | 123 | 1 | 13 | 84900 | 1 | 9 | 84600 | 1 | 9 | 14700 | 1 | 13 | 3830 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.7 | 89.06 | A | 7 | 23.9 | 75.02 | A | 7 | 0.63 | A | 7 | 981 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.92 | 2 | 0
1979-08-07 | 1900-08-06 | 12:00 | 12 | 1194 | 1328 | 907 | 1 | 9 | 862 | 1 | 9 | 130 | 1 | 13 | 93100 | 1 | 9 | 86400 | 1 | 9 | 15300 | 1 | 13 | 5450 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 23.9 | 75.02 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.12 | 2 | 0
1979-08-07 | 1900-08-06 | 13:00 | 13 | 1221 | 1328 | 931 | 1 | 9 | 866 | 1 | 9 | 131 | 1 | 13 | 95400 | 1 | 9 | 86800 | 1 | 9 | 15400 | 1 | 13 | 6190 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 24.4 | 75.92 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.5 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.32 | 2 | 0
1979-08-07 | 1900-08-06 | 14:00 | 14 | 1181 | 1328 | 897 | 1 | 9 | 860 | 1 | 9 | 129 | 1 | 13 | 92000 | 1 | 9 | 86200 | 1 | 9 | 15200 | 1 | 13 | 5160 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 23.9 | 75.02 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.02 | 2 | 0
1979-08-07 | 1900-08-06 | 15:00 | 15 | 1078 | 1328 | 661 | 1 | 9 | 598 | 1 | 9 | 173 | 1 | 13 | 70800 | 1 | 9 | 61400 | 1 | 9 | 20900 | 1 | 13 | 6500 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 33.9 | 93.02 | A | 7 | 23.9 | 75.02 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.02 | 2 | 0
1979-08-07 | 1900-08-06 | 16:00 | 16 | 917 | 1328 | 661 | 1 | 9 | 795 | 1 | 9 | 109 | 1 | 13 | 70200 | 1 | 9 | 80200 | 1 | 9 | 14700 | 1 | 13 | 2960 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 23.3 | 73.94 | A | 7 | 0.54 | A | 7 | 980 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.54 | 2 | 0
1979-08-07 | 1900-08-06 | 17:00 | 17 | 709 | 1328 | 482 | 1 | 9 | 728 | 1 | 9 | 91 | 1 | 13 | 50500 | 1 | 9 | 71900 | 1 | 9 | 12000 | 1 | 13 | 2000 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 23.9 | 75.02 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.02 | 2 | 0
1979-08-07 | 1900-08-06 | 18:00 | 18 | 470 | 1328 | 287 | 1 | 9 | 613 | 1 | 9 | 67 | 1 | 13 | 30000 | 1 | 9 | 57100 | 1 | 9 | 9800 | 1 | 13 | 1330 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.64 | 2 | 0
1979-08-07 | 1900-08-06 | 19:00 | 19 | 216 | 1328 | 100 | 1 | 13 | 352 | 1 | 9 | 41 | 1 | 13 | 10100 | 1 | 13 | 24700 | 1 | 9 | 6000 | 1 | 13 | 740 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 23.3 | 73.94 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.94 | 2 | 0
1979-08-07 | 1900-08-06 | 20:00 | 20 | 17 | 520 | 11 | 1 | 13 | 22 | 1 | 9 | 9 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 22.8 | 73.04 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.24 | 2 | 0
1979-08-07 | 1900-08-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.54 | 2 | 0
1979-08-07 | 1900-08-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 22.8 | 73.04 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.94 | 2 | 0
1979-08-07 | 1900-08-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 22.2 | 71.96 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.96 | 2 | 0
1979-08-07 | 1900-08-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.66 | 2 | 0
1979-08-08 | 1900-08-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.16 | 3 | 0
1979-08-08 | 1900-08-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 21.7 | 71.06 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.36 | 3 | 0
1979-08-08 | 1900-08-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 3 | 0
1979-08-08 | 1900-08-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 981 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 3 | 0
1979-08-08 | 1900-08-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.16 | 3 | 0
1979-08-08 | 1900-08-07 | 6:00 | 6 | 36 | 742 | 18 | 1 | 13 | 47 | 1 | 9 | 14 | 1 | 13 | 1800 | 1 | 13 | 1400 | 1 | 9 | 1700 | 1 | 13 | 240 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.86 | 3 | 0
1979-08-08 | 1900-08-07 | 7:00 | 7 | 261 | 1329 | 126 | 1 | 13 | 413 | 1 | 9 | 45 | 1 | 13 | 13000 | 1 | 13 | 31500 | 1 | 9 | 6800 | 1 | 13 | 830 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 22.2 | 71.96 | A | 7 | 0.85 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.56 | 3 | 0
1979-08-08 | 1900-08-07 | 8:00 | 8 | 513 | 1329 | 319 | 1 | 9 | 642 | 1 | 9 | 71 | 1 | 13 | 33900 | 1 | 9 | 61100 | 1 | 9 | 10200 | 1 | 13 | 1440 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.66 | 3 | 0
1979-08-08 | 1900-08-07 | 9:00 | 9 | 748 | 1329 | 517 | 1 | 9 | 750 | 1 | 9 | 93 | 1 | 13 | 54400 | 1 | 9 | 74500 | 1 | 9 | 12400 | 1 | 13 | 2120 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.72 | A | 7 | 982 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.44 | 3 | 0
1979-08-08 | 1900-08-07 | 10:00 | 10 | 948 | 1329 | 691 | 1 | 9 | 812 | 1 | 9 | 111 | 1 | 13 | 73900 | 1 | 9 | 82100 | 1 | 9 | 15200 | 1 | 13 | 3160 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 23.3 | 73.94 | A | 7 | 0.7 | A | 7 | 982 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.74 | 3 | 0
1979-08-08 | 1900-08-07 | 11:00 | 11 | 1099 | 1329 | 826 | 1 | 9 | 849 | 1 | 9 | 122 | 1 | 13 | 85000 | 1 | 9 | 85000 | 1 | 9 | 14600 | 1 | 13 | 3790 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 23.3 | 73.94 | A | 7 | 0.63 | A | 7 | 982 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.94 | 3 | 0
1979-08-08 | 1900-08-07 | 12:00 | 12 | 1191 | 1329 | 906 | 1 | 9 | 864 | 1 | 9 | 129 | 1 | 13 | 93000 | 1 | 9 | 86600 | 1 | 9 | 15200 | 1 | 13 | 5370 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 23.9 | 75.02 | A | 7 | 0.61 | A | 7 | 982 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.32 | 3 | 0
1979-08-08 | 1900-08-07 | 13:00 | 13 | 1219 | 1329 | 856 | 1 | 13 | 671 | 1 | 13 | 239 | 1 | 13 | 91200 | 1 | 13 | 68400 | 1 | 13 | 28300 | 1 | 13 | 13990 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 32.8 | 91.04 | A | 7 | 23.9 | 75.02 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.12 | 3 | 0
1979-08-08 | 1900-08-07 | 14:00 | 14 | 1179 | 1329 | 498 | 1 | 13 | 255 | 1 | 13 | 271 | 1 | 13 | 56100 | 1 | 13 | 27800 | 1 | 13 | 31300 | 1 | 13 | 12340 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 32.8 | 91.04 | A | 7 | 23.9 | 75.02 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.12 | 3 | 0
1979-08-08 | 1900-08-07 | 15:00 | 15 | 1075 | 1329 | 662 | 1 | 13 | 484 | 1 | 13 | 269 | 1 | 13 | 71400 | 1 | 13 | 50600 | 1 | 13 | 30400 | 1 | 13 | 9980 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 32.8 | 91.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.64 | 3 | 0
1979-08-08 | 1900-08-07 | 16:00 | 16 | 913 | 1329 | 655 | 1 | 13 | 763 | 1 | 13 | 128 | 1 | 13 | 68500 | 1 | 13 | 76500 | 1 | 13 | 15800 | 1 | 13 | 3280 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 33.3 | 91.94 | A | 7 | 23.3 | 73.94 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.04 | 3 | 0
1979-08-08 | 1900-08-07 | 17:00 | 17 | 706 | 1329 | 477 | 1 | 9 | 724 | 1 | 9 | 90 | 1 | 13 | 49900 | 1 | 9 | 71500 | 1 | 9 | 11900 | 1 | 13 | 1980 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 3 | 0
1979-08-08 | 1900-08-07 | 18:00 | 18 | 466 | 1329 | 282 | 1 | 9 | 608 | 1 | 9 | 66 | 1 | 13 | 29500 | 1 | 9 | 56600 | 1 | 9 | 9700 | 1 | 13 | 1310 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 22.2 | 71.96 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.36 | 3 | 0
1979-08-08 | 1900-08-07 | 19:00 | 19 | 212 | 1329 | 98 | 1 | 13 | 352 | 1 | 9 | 40 | 1 | 13 | 9800 | 1 | 13 | 24500 | 1 | 9 | 5900 | 1 | 13 | 720 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.61 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.66 | 3 | 0
1979-08-08 | 1900-08-07 | 20:00 | 20 | 15 | 498 | 11 | 1 | 13 | 21 | 1 | 9 | 9 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.96 | 3 | 0
1979-08-08 | 1900-08-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 22.8 | 73.04 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.94 | 3 | 0
1979-08-08 | 1900-08-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.66 | 3 | 0
1979-08-08 | 1900-08-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.16 | 3 | 0
1979-08-08 | 1900-08-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.16 | 3 | 0
1979-08-09 | 1900-08-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.86 | 4 | 0
1979-08-09 | 1900-08-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.88 | 4 | 0
1979-08-09 | 1900-08-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 4 | 0
1979-08-09 | 1900-08-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.16 | 4 | 0
1979-08-09 | 1900-08-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.16 | 4 | 0
1979-08-09 | 1900-08-08 | 6:00 | 6 | 34 | 720 | 18 | 1 | 13 | 39 | 1 | 9 | 14 | 1 | 13 | 1700 | 1 | 13 | 1100 | 1 | 9 | 1700 | 1 | 13 | 240 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.9 | A | 7 | 981 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.86 | 4 | 0
1979-08-09 | 1900-08-08 | 7:00 | 7 | 257 | 1329 | 122 | 1 | 13 | 390 | 1 | 9 | 47 | 1 | 13 | 12600 | 1 | 13 | 29500 | 1 | 9 | 6900 | 1 | 13 | 850 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.7 | 71.06 | A | 7 | 0.85 | A | 7 | 981 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.76 | 4 | 0
1979-08-09 | 1900-08-08 | 8:00 | 8 | 510 | 1329 | 313 | 1 | 9 | 622 | 1 | 9 | 74 | 1 | 13 | 33100 | 1 | 9 | 59000 | 1 | 9 | 10400 | 1 | 13 | 1490 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.86 | 4 | 0
1979-08-09 | 1900-08-08 | 9:00 | 9 | 745 | 1329 | 511 | 1 | 9 | 735 | 1 | 9 | 98 | 1 | 13 | 53600 | 1 | 9 | 72900 | 1 | 9 | 12600 | 1 | 13 | 2180 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 22.8 | 73.04 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.94 | 4 | 0
1979-08-09 | 1900-08-08 | 10:00 | 10 | 945 | 1329 | 687 | 1 | 9 | 801 | 1 | 9 | 116 | 1 | 13 | 73100 | 1 | 9 | 80800 | 1 | 9 | 15400 | 1 | 13 | 3250 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.44 | 4 | 0
1979-08-09 | 1900-08-08 | 11:00 | 11 | 1097 | 1329 | 822 | 1 | 9 | 838 | 1 | 9 | 128 | 1 | 13 | 84400 | 1 | 9 | 83800 | 1 | 9 | 15100 | 1 | 13 | 3830 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 22.8 | 73.04 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.64 | 4 | 0
1979-08-09 | 1900-08-08 | 12:00 | 12 | 1189 | 1329 | 845 | 1 | 13 | 676 | 1 | 13 | 238 | 1 | 13 | 89700 | 1 | 13 | 68900 | 1 | 13 | 28000 | 1 | 13 | 12300 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 31.1 | 87.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.64 | 4 | 0
1979-08-09 | 1900-08-08 | 13:00 | 13 | 1216 | 1329 | 856 | 1 | 13 | 678 | 1 | 13 | 233 | 1 | 13 | 91200 | 1 | 13 | 69200 | 1 | 13 | 27700 | 1 | 13 | 13500 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 32.2 | 89.96 | A | 7 | 22.2 | 71.96 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 220 | A | 7 | 10.3 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.36 | 4 | 0
1979-08-09 | 1900-08-08 | 14:00 | 14 | 1176 | 1329 | 831 | 1 | 13 | 630 | 1 | 13 | 271 | 1 | 13 | 87200 | 1 | 13 | 63700 | 1 | 13 | 30800 | 1 | 13 | 13200 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 32.8 | 91.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.56 | 4 | 0
1979-08-09 | 1900-08-08 | 15:00 | 15 | 1072 | 1329 | 671 | 1 | 13 | 575 | 1 | 13 | 204 | 1 | 13 | 71000 | 1 | 13 | 58600 | 1 | 13 | 23600 | 1 | 13 | 7440 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 32.2 | 89.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.54 | A | 7 | 980 | A | 7 | 210 | A | 7 | 8.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 4 | 0
1979-08-09 | 1900-08-08 | 16:00 | 16 | 910 | 1329 | 622 | 1 | 13 | 660 | 1 | 13 | 167 | 1 | 13 | 65500 | 1 | 13 | 66900 | 1 | 13 | 19600 | 1 | 13 | 4530 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 32.2 | 89.96 | A | 7 | 22.2 | 71.96 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.36 | 4 | 0
1979-08-09 | 1900-08-08 | 17:00 | 17 | 702 | 1329 | 480 | 1 | 9 | 724 | 1 | 9 | 94 | 1 | 13 | 49900 | 1 | 9 | 71300 | 1 | 9 | 12100 | 1 | 13 | 2030 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.54 | A | 7 | 979 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 4 | 0
1979-08-09 | 1900-08-08 | 18:00 | 18 | 462 | 1329 | 276 | 1 | 9 | 587 | 1 | 9 | 69 | 1 | 13 | 28800 | 1 | 9 | 54400 | 1 | 9 | 9800 | 1 | 13 | 1360 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 4 | 0
1979-08-09 | 1900-08-08 | 19:00 | 19 | 207 | 1329 | 94 | 1 | 13 | 327 | 1 | 9 | 41 | 1 | 13 | 9400 | 1 | 13 | 22500 | 1 | 9 | 5900 | 1 | 13 | 730 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.65 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.76 | 4 | 0
1979-08-09 | 1900-08-08 | 20:00 | 20 | 14 | 454 | 10 | 1 | 13 | 16 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.115 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.96 | 4 | 0
1979-08-09 | 1900-08-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 4 | 0
1979-08-09 | 1900-08-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 977 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.66 | 4 | 0
1979-08-09 | 1900-08-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.66 | 4 | 0
1979-08-09 | 1900-08-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.98 | 4 | 0
1979-08-10 | 1900-08-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 26.1 | 78.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 2290 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.18 | 5 | 0
1979-08-10 | 1900-08-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 2130 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 5 | 0
1979-08-10 | 1900-08-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.88 | 5 | 0
1979-08-10 | 1900-08-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 3660 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 5 | 0
1979-08-10 | 1900-08-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.28 | 5 | 0
1979-08-10 | 1900-08-09 | 6:00 | 6 | 33 | 698 | 7 | 1 | 13 | 1 | 1 | 9 | 7 | 1 | 13 | 800 | 1 | 13 | 0 | 1 | 9 | 800 | 1 | 13 | 270 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 3.5 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.1 | 5 | 0
1979-08-10 | 1900-08-09 | 7:00 | 7 | 254 | 1330 | 43 | 1 | 13 | 14 | 1 | 9 | 40 | 1 | 13 | 4700 | 1 | 13 | 1100 | 1 | 9 | 4500 | 1 | 13 | 1090 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 3.5 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 5 | 0
1979-08-10 | 1900-08-09 | 8:00 | 8 | 507 | 1330 | 104 | 1 | 9 | 32 | 1 | 9 | 92 | 1 | 13 | 11500 | 1 | 9 | 3000 | 1 | 9 | 10300 | 1 | 13 | 2780 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 3.7 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 5 | 0
1979-08-10 | 1900-08-09 | 9:00 | 9 | 743 | 1330 | 222 | 1 | 9 | 59 | 1 | 9 | 189 | 1 | 13 | 24500 | 1 | 9 | 5900 | 1 | 9 | 21200 | 1 | 13 | 6180 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 3.8 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 5 | 0
1979-08-10 | 1900-08-09 | 10:00 | 10 | 943 | 1330 | 278 | 1 | 9 | 1 | 1 | 9 | 278 | 1 | 13 | 32400 | 1 | 9 | 100 | 1 | 9 | 32300 | 1 | 13 | 12230 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 25 | 77 | A | 7 | 22.2 | 71.96 | A | 7 | 0.85 | A | 7 | 981 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 340 | A | 7 | 4 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.56 | 5 | 0
1979-08-10 | 1900-08-09 | 11:00 | 11 | 1095 | 1330 | 374 | 1 | 9 | 3 | 1 | 9 | 372 | 1 | 13 | 43500 | 1 | 9 | 300 | 1 | 9 | 43300 | 1 | 13 | 16000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 25 | 77 | A | 7 | 22.8 | 73.04 | A | 7 | 0.88 | A | 7 | 981 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 460 | A | 7 | 4.1 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.34 | 5 | 0
1979-08-10 | 1900-08-09 | 12:00 | 12 | 1187 | 1330 | 415 | 1 | 9 | 8 | 1 | 9 | 408 | 1 | 13 | 48600 | 1 | 9 | 800 | 1 | 9 | 47900 | 1 | 13 | 17470 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 3.5 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.3 | 5 | 0
1979-08-10 | 1900-08-09 | 13:00 | 13 | 1214 | 1330 | 321 | 1 | 9 | 9 | 1 | 9 | 312 | 1 | 13 | 38400 | 1 | 9 | 800 | 1 | 9 | 37700 | 1 | 13 | 14560 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 3.2 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 5 | 0
1979-08-10 | 1900-08-09 | 14:00 | 14 | 1174 | 1330 | 343 | 1 | 9 | 1 | 1 | 9 | 342 | 1 | 13 | 40600 | 1 | 9 | 100 | 1 | 9 | 40500 | 1 | 13 | 15440 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 880 | A | 7 | 3.2 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 5 | 0
1979-08-10 | 1900-08-09 | 15:00 | 15 | 1069 | 1330 | 314 | 1 | 9 | 2 | 1 | 9 | 312 | 1 | 13 | 36800 | 1 | 9 | 200 | 1 | 9 | 36700 | 1 | 13 | 14070 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1010 | A | 7 | 3 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.14 | 5 | 0
1979-08-10 | 1900-08-09 | 16:00 | 16 | 907 | 1330 | 251 | 1 | 9 | 3 | 1 | 9 | 249 | 1 | 13 | 29300 | 1 | 9 | 300 | 1 | 9 | 29100 | 1 | 13 | 11070 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 3.1 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.74 | 5 | 0
1979-08-10 | 1900-08-09 | 17:00 | 17 | 698 | 1330 | 145 | 1 | 9 | 1 | 1 | 9 | 145 | 1 | 13 | 17100 | 1 | 9 | 100 | 1 | 9 | 17000 | 1 | 13 | 6430 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 1680 | A | 7 | 3.4 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.42 | 5 | 0
1979-08-10 | 1900-08-09 | 18:00 | 18 | 458 | 1330 | 122 | 1 | 9 | 0 | 1 | 9 | 122 | 1 | 13 | 13800 | 1 | 9 | 0 | 1 | 9 | 13800 | 1 | 13 | 4590 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 3.4 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.82 | 5 | 0
1979-08-10 | 1900-08-09 | 19:00 | 19 | 203 | 1330 | 38 | 1 | 13 | 10 | 1 | 9 | 36 | 1 | 13 | 4100 | 1 | 13 | 700 | 1 | 9 | 4000 | 1 | 13 | 940 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 21.1 | 69.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 360 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 2.9 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.26 | 5 | 0
1979-08-10 | 1900-08-09 | 20:00 | 20 | 12 | 432 | 2 | 1 | 13 | 0 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.186 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.9 | 5 | 0
1979-08-10 | 1900-08-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 20 | 68 | A | 7 | 15.6 | 60.08 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.48 | 5 | 0
1979-08-10 | 1900-08-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 982 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.98 | 5 | 0
1979-08-10 | 1900-08-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 5 | 0
1979-08-10 | 1900-08-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 18.9 | 66.02 | A | 7 | 15 | 59 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 2740 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 5 | 0
1979-08-11 | 1900-08-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 17.2 | 62.96 | A | 7 | 15 | 59 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.6 | 6 | 0
1979-08-11 | 1900-08-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 6 | 0
1979-08-11 | 1900-08-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.62 | 6 | 0
1979-08-11 | 1900-08-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.14 | 6 | 0
1979-08-11 | 1900-08-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.24 | 6 | 0
1979-08-11 | 1900-08-10 | 6:00 | 6 | 31 | 698 | 11 | 1 | 13 | 13 | 1 | 9 | 10 | 1 | 13 | 1200 | 1 | 13 | 500 | 1 | 9 | 1200 | 1 | 13 | 210 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 6 | 0
1979-08-11 | 1900-08-10 | 7:00 | 7 | 251 | 1330 | 111 | 1 | 13 | 304 | 1 | 9 | 54 | 1 | 13 | 11700 | 1 | 13 | 22200 | 1 | 9 | 7600 | 1 | 13 | 970 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 12.8 | 55.04 | A | 7 | 0.87 | A | 7 | 983 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.74 | 6 | 0
1979-08-11 | 1900-08-10 | 8:00 | 8 | 505 | 1330 | 292 | 1 | 9 | 514 | 1 | 9 | 96 | 1 | 13 | 30200 | 1 | 9 | 48000 | 1 | 9 | 11900 | 1 | 13 | 1850 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 983 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 6 | 0
1979-08-11 | 1900-08-10 | 9:00 | 9 | 740 | 1330 | 500 | 1 | 9 | 680 | 1 | 9 | 121 | 1 | 13 | 52900 | 1 | 9 | 68100 | 1 | 9 | 14900 | 1 | 13 | 2750 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.76 | A | 7 | 983 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.42 | 6 | 0
1979-08-11 | 1900-08-10 | 10:00 | 10 | 941 | 1330 | 681 | 1 | 9 | 756 | 1 | 9 | 144 | 1 | 13 | 70600 | 1 | 9 | 75500 | 1 | 9 | 17000 | 1 | 13 | 3700 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 20 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.72 | 6 | 0
1979-08-11 | 1900-08-10 | 11:00 | 11 | 1092 | 1330 | 791 | 1 | 9 | 771 | 1 | 9 | 156 | 1 | 13 | 83200 | 1 | 9 | 77700 | 1 | 9 | 19200 | 1 | 13 | 5550 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.55 | A | 7 | 983 | A | 7 | 40 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.84 | 6 | 0
1979-08-11 | 1900-08-10 | 12:00 | 12 | 1185 | 1330 | 796 | 1 | 13 | 616 | 1 | 13 | 245 | 1 | 13 | 84300 | 1 | 13 | 62600 | 1 | 13 | 28300 | 1 | 13 | 12380 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 21.7 | 71.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.55 | A | 7 | 983 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.96 | 6 | 0
1979-08-11 | 1900-08-10 | 13:00 | 13 | 1212 | 1330 | 795 | 1 | 13 | 586 | 1 | 13 | 259 | 1 | 13 | 84100 | 1 | 13 | 59500 | 1 | 13 | 29700 | 1 | 13 | 14550 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.48 | A | 7 | 983 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.56 | 6 | 0
1979-08-11 | 1900-08-10 | 14:00 | 14 | 1171 | 1330 | 725 | 1 | 13 | 527 | 1 | 13 | 258 | 1 | 13 | 76300 | 1 | 13 | 53400 | 1 | 13 | 29100 | 1 | 13 | 12360 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 23.9 | 75.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.46 | A | 7 | 982 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1070 | A | 7 | 2.1 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.46 | 6 | 0
1979-08-11 | 1900-08-10 | 15:00 | 15 | 1066 | 1330 | 642 | 1 | 13 | 414 | 1 | 13 | 308 | 1 | 13 | 68100 | 1 | 13 | 43100 | 1 | 13 | 33500 | 1 | 13 | 11260 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 24.4 | 75.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.47 | A | 7 | 982 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1340 | A | 7 | 2.2 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.36 | 6 | 0
1979-08-11 | 1900-08-10 | 16:00 | 16 | 904 | 1330 | 498 | 1 | 13 | 342 | 1 | 13 | 265 | 1 | 13 | 54200 | 1 | 13 | 36800 | 1 | 13 | 29200 | 1 | 13 | 7250 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 23.9 | 75.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.5 | A | 7 | 981 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1280 | A | 7 | 2.3 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.84 | 6 | 0
1979-08-11 | 1900-08-10 | 17:00 | 17 | 695 | 1330 | 392 | 1 | 13 | 401 | 1 | 13 | 181 | 1 | 13 | 41200 | 1 | 13 | 40400 | 1 | 13 | 20100 | 1 | 13 | 3910 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 24.4 | 75.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.48 | A | 7 | 981 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 1280 | A | 7 | 2.3 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.44 | 6 | 0
1979-08-11 | 1900-08-10 | 18:00 | 18 | 453 | 1330 | 166 | 1 | 13 | 165 | 1 | 13 | 109 | 1 | 13 | 17800 | 1 | 13 | 15600 | 1 | 13 | 12500 | 1 | 13 | 2130 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 23.9 | 75.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.04 | 6 | 0
1979-08-11 | 1900-08-10 | 19:00 | 19 | 198 | 1330 | 82 | 1 | 13 | 233 | 1 | 9 | 46 | 1 | 13 | 8400 | 1 | 13 | 15000 | 1 | 9 | 6200 | 1 | 13 | 830 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.04 | 6 | 0
1979-08-11 | 1900-08-10 | 20:00 | 20 | 11 | 410 | 7 | 1 | 13 | 4 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.164 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.54 | 6 | 0
1979-08-11 | 1900-08-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 982 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.44 | 6 | 0
1979-08-11 | 1900-08-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.75 | A | 7 | 982 | A | 7 | 90 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.64 | 6 | 0
1979-08-11 | 1900-08-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.16 | 6 | 0
1979-08-11 | 1900-08-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 11.7 | 53.06 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.36 | 6 | 0
1979-08-12 | 1900-08-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 11.1 | 51.98 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.28 | 7 | 0
1979-08-12 | 1900-08-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.48 | 7 | 0
1979-08-12 | 1900-08-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.8 | A | 7 | 982 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.78 | 7 | 0
1979-08-12 | 1900-08-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.8 | A | 7 | 982 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.78 | 7 | 0
1979-08-12 | 1900-08-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 10 | 50 | A | 7 | 0.83 | A | 7 | 982 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.3 | 7 | 0
1979-08-12 | 1900-08-11 | 6:00 | 6 | 29 | 676 | 17 | 1 | 13 | 48 | 1 | 9 | 12 | 1 | 13 | 1600 | 1 | 13 | 1300 | 1 | 9 | 1500 | 1 | 13 | 200 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 10 | 50 | A | 7 | 0.83 | A | 7 | 982 | A | 7 | 140 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.3 | 7 | 0
1979-08-12 | 1900-08-11 | 7:00 | 7 | 247 | 1330 | 122 | 1 | 13 | 428 | 1 | 9 | 42 | 1 | 13 | 12600 | 1 | 13 | 32000 | 1 | 9 | 6600 | 1 | 13 | 770 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 11.7 | 53.06 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.36 | 7 | 0
1979-08-12 | 1900-08-11 | 8:00 | 8 | 502 | 1330 | 319 | 1 | 9 | 675 | 1 | 9 | 64 | 1 | 13 | 33300 | 1 | 9 | 63500 | 1 | 9 | 9300 | 1 | 13 | 1310 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.06 | 7 | 0
1979-08-12 | 1900-08-11 | 9:00 | 9 | 737 | 1330 | 523 | 1 | 9 | 787 | 1 | 9 | 85 | 1 | 13 | 55500 | 1 | 9 | 78300 | 1 | 9 | 12000 | 1 | 13 | 1980 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 11.7 | 53.06 | A | 7 | 0.57 | A | 7 | 982 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.56 | 7 | 0
1979-08-12 | 1900-08-11 | 10:00 | 10 | 938 | 1330 | 701 | 1 | 9 | 849 | 1 | 9 | 100 | 1 | 13 | 72600 | 1 | 9 | 84600 | 1 | 9 | 12800 | 1 | 13 | 2450 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.49 | A | 7 | 982 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.38 | 7 | 0
1979-08-12 | 1900-08-11 | 11:00 | 11 | 1090 | 1330 | 842 | 1 | 9 | 888 | 1 | 9 | 111 | 1 | 13 | 86800 | 1 | 9 | 88900 | 1 | 9 | 13800 | 1 | 13 | 3520 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 10 | 50 | A | 7 | 0.44 | A | 7 | 981 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.6 | 7 | 0
1979-08-12 | 1900-08-11 | 12:00 | 12 | 1183 | 1330 | 925 | 1 | 9 | 905 | 1 | 9 | 117 | 1 | 13 | 95100 | 1 | 9 | 90700 | 1 | 9 | 14300 | 1 | 13 | 4850 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 11.1 | 51.98 | A | 7 | 0.43 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.98 | 7 | 0
1979-08-12 | 1900-08-11 | 13:00 | 13 | 1209 | 1330 | 947 | 1 | 9 | 907 | 1 | 9 | 119 | 1 | 13 | 97400 | 1 | 9 | 91000 | 1 | 9 | 14500 | 1 | 13 | 5470 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 11.1 | 51.98 | A | 7 | 0.42 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.88 | 7 | 0
1979-08-12 | 1900-08-11 | 14:00 | 14 | 1169 | 1330 | 910 | 1 | 9 | 876 | 1 | 9 | 137 | 1 | 13 | 93200 | 1 | 9 | 87700 | 1 | 9 | 15900 | 1 | 13 | 5030 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.41 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.46 | 7 | 0
1979-08-12 | 1900-08-11 | 15:00 | 15 | 1063 | 1330 | 815 | 1 | 9 | 879 | 1 | 9 | 109 | 1 | 13 | 84000 | 1 | 9 | 88000 | 1 | 9 | 13600 | 1 | 13 | 3260 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.42 | A | 7 | 979 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.24 | 7 | 0
1979-08-12 | 1900-08-11 | 16:00 | 16 | 900 | 1330 | 667 | 1 | 9 | 821 | 1 | 9 | 108 | 1 | 13 | 70700 | 1 | 9 | 82700 | 1 | 9 | 14600 | 1 | 13 | 2860 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.42 | A | 7 | 979 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.24 | 7 | 0
1979-08-12 | 1900-08-11 | 17:00 | 17 | 691 | 1330 | 484 | 1 | 9 | 724 | 1 | 9 | 104 | 1 | 13 | 51000 | 1 | 9 | 72200 | 1 | 9 | 13500 | 1 | 13 | 2300 | 1 | 18 | 5 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.42 | A | 7 | 979 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.24 | 7 | 0
1979-08-12 | 1900-08-11 | 18:00 | 18 | 449 | 1330 | 203 | 1 | 13 | 262 | 1 | 13 | 113 | 1 | 13 | 21600 | 1 | 13 | 24700 | 1 | 13 | 13300 | 1 | 13 | 2230 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 11.7 | 53.06 | A | 7 | 0.42 | A | 7 | 978 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.66 | 7 | 0
1979-08-12 | 1900-08-11 | 19:00 | 19 | 193 | 1330 | 79 | 1 | 13 | 143 | 1 | 13 | 58 | 1 | 13 | 8200 | 1 | 13 | 8800 | 1 | 13 | 6900 | 1 | 13 | 1110 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.24 | 7 | 0
1979-08-12 | 1900-08-11 | 20:00 | 20 | 9 | 388 | 5 | 1 | 13 | 4 | 1 | 13 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 20.6 | 69.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.66 | A | 7 | 978 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.72 | 7 | 0
1979-08-12 | 1900-08-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 20 | 68 | A | 7 | 13.9 | 57.02 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.12 | 7 | 0
1979-08-12 | 1900-08-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 7 | 0
1979-08-12 | 1900-08-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.52 | 7 | 0
1979-08-12 | 1900-08-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 18.9 | 66.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.76 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.42 | 7 | 0
1979-08-13 | 1900-08-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.82 | 1 | 0
1979-08-13 | 1900-08-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.82 | 1 | 0
1979-08-13 | 1900-08-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 1 | 0
1979-08-13 | 1900-08-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 1 | 0
1979-08-13 | 1900-08-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 1 | 0
1979-08-13 | 1900-08-12 | 6:00 | 6 | 27 | 654 | 14 | 1 | 13 | 30 | 1 | 9 | 11 | 1 | 13 | 1400 | 1 | 13 | 800 | 1 | 9 | 1300 | 1 | 13 | 180 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 1 | 0
1979-08-13 | 1900-08-12 | 7:00 | 7 | 244 | 1331 | 107 | 1 | 13 | 306 | 1 | 9 | 50 | 1 | 13 | 11200 | 1 | 13 | 22100 | 1 | 9 | 7200 | 1 | 13 | 890 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | 15 | 59 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.4 | 1 | 0
1979-08-13 | 1900-08-12 | 8:00 | 8 | 499 | 1331 | 292 | 1 | 9 | 562 | 1 | 9 | 81 | 1 | 13 | 30600 | 1 | 9 | 52800 | 1 | 9 | 10800 | 1 | 13 | 1600 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 20.6 | 69.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.28 | 1 | 0
1979-08-13 | 1900-08-12 | 9:00 | 9 | 735 | 1331 | 510 | 1 | 9 | 749 | 1 | 9 | 95 | 1 | 13 | 53500 | 1 | 9 | 74200 | 1 | 9 | 12400 | 1 | 13 | 2110 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.18 | 1 | 0
1979-08-13 | 1900-08-12 | 10:00 | 10 | 936 | 1331 | 673 | 1 | 9 | 792 | 1 | 9 | 114 | 1 | 13 | 71500 | 1 | 9 | 79900 | 1 | 9 | 15200 | 1 | 13 | 3150 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.66 | 1 | 0
1979-08-13 | 1900-08-12 | 11:00 | 11 | 1088 | 1331 | 760 | 1 | 9 | 759 | 1 | 9 | 138 | 1 | 13 | 80900 | 1 | 9 | 76800 | 1 | 9 | 18000 | 1 | 13 | 4990 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 27.8 | 82.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.53 | A | 7 | 980 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.06 | 1 | 0
1979-08-13 | 1900-08-12 | 12:00 | 12 | 1180 | 1331 | 869 | 1 | 9 | 809 | 1 | 9 | 149 | 1 | 13 | 92800 | 1 | 9 | 82000 | 1 | 9 | 19900 | 1 | 13 | 7100 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.51 | A | 7 | 979 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.54 | 1 | 0
1979-08-13 | 1900-08-12 | 13:00 | 13 | 1207 | 1331 | 921 | 1 | 9 | 872 | 1 | 9 | 126 | 1 | 13 | 94400 | 1 | 9 | 87400 | 1 | 9 | 15000 | 1 | 13 | 5600 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 29.4 | 84.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.62 | 1 | 0
1979-08-13 | 1900-08-12 | 14:00 | 14 | 1166 | 1331 | 888 | 1 | 9 | 864 | 1 | 9 | 127 | 1 | 13 | 91000 | 1 | 9 | 86500 | 1 | 9 | 15100 | 1 | 13 | 4780 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 20 | 68 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.8 | 1 | 0
1979-08-13 | 1900-08-12 | 15:00 | 15 | 1060 | 1331 | 788 | 1 | 9 | 835 | 1 | 9 | 120 | 1 | 13 | 81000 | 1 | 9 | 83500 | 1 | 9 | 14400 | 1 | 13 | 3370 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 20 | 68 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.3 | 1 | 0
1979-08-13 | 1900-08-12 | 16:00 | 16 | 896 | 1331 | 616 | 1 | 9 | 684 | 1 | 9 | 152 | 1 | 13 | 65200 | 1 | 9 | 69500 | 1 | 9 | 18200 | 1 | 13 | 4080 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.18 | 1 | 0
1979-08-13 | 1900-08-12 | 17:00 | 17 | 686 | 1331 | 472 | 1 | 9 | 705 | 1 | 9 | 105 | 1 | 13 | 49800 | 1 | 9 | 70200 | 1 | 9 | 13500 | 1 | 13 | 2310 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 30.6 | 87.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 1 | 0
1979-08-13 | 1900-08-12 | 18:00 | 18 | 444 | 1331 | 267 | 1 | 9 | 599 | 1 | 9 | 64 | 1 | 13 | 27900 | 1 | 9 | 55000 | 1 | 9 | 9500 | 1 | 13 | 1260 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 20.6 | 69.08 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.18 | 1 | 0
1979-08-13 | 1900-08-12 | 19:00 | 19 | 188 | 1331 | 81 | 1 | 13 | 266 | 1 | 9 | 42 | 1 | 13 | 8300 | 1 | 13 | 16700 | 1 | 9 | 6000 | 1 | 13 | 750 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.98 | 1 | 0
1979-08-13 | 1900-08-12 | 20:00 | 20 | 8 | 344 | 5 | 1 | 13 | 6 | 1 | 13 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 26.1 | 78.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.106 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.88 | 1 | 0
1979-08-13 | 1900-08-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.88 | 1 | 0
1979-08-13 | 1900-08-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | 26.1 | 78.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 1520 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.18 | 1 | 0
1979-08-13 | 1900-08-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 1 | 0
1979-08-13 | 1900-08-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.88 | 1 | 0
1979-08-14 | 1900-08-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | 21.1 | 69.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.82 | 2 | 0
1979-08-14 | 1900-08-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 20.6 | 69.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.42 | 2 | 0
1979-08-14 | 1900-08-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 15.6 | 60.08 | A | 7 | 0.76 | A | 7 | 983 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.48 | 2 | 0
1979-08-14 | 1900-08-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 19.4 | 66.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.94 | 2 | 0
1979-08-14 | 1900-08-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.65 | A | 7 | 984 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 580 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.06 | 2 | 0
1979-08-14 | 1900-08-13 | 6:00 | 6 | 26 | 632 | 5 | 1 | 13 | 0 | 1 | 9 | 5 | 1 | 13 | 600 | 1 | 13 | 0 | 1 | 9 | 600 | 1 | 13 | 190 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.84 | A | 7 | 985 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.14 | 2 | 0
1979-08-14 | 1900-08-13 | 7:00 | 7 | 240 | 1331 | 41 | 1 | 13 | 4 | 1 | 9 | 40 | 1 | 13 | 4700 | 1 | 13 | 100 | 1 | 9 | 4700 | 1 | 13 | 1520 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.87 | A | 7 | 986 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 580 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.62 | 2 | 0
1979-08-14 | 1900-08-13 | 8:00 | 8 | 495 | 1331 | 108 | 1 | 9 | 0 | 1 | 9 | 108 | 1 | 13 | 12400 | 1 | 9 | 0 | 1 | 9 | 12400 | 1 | 13 | 4360 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 987 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 580 | A | 7 | 2.5 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 2 | 0
1979-08-14 | 1900-08-13 | 9:00 | 9 | 732 | 1331 | 211 | 1 | 9 | 7 | 1 | 9 | 207 | 1 | 13 | 24200 | 1 | 9 | 600 | 1 | 9 | 23900 | 1 | 13 | 8600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 988 | A | 7 | 60 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 610 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 2 | 0
1979-08-14 | 1900-08-13 | 10:00 | 10 | 933 | 1331 | 277 | 1 | 9 | 7 | 1 | 9 | 273 | 1 | 13 | 32300 | 1 | 9 | 600 | 1 | 9 | 31900 | 1 | 13 | 12000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 988 | A | 7 | 50 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 610 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 2 | 0
1979-08-14 | 1900-08-13 | 11:00 | 11 | 1085 | 1331 | 189 | 1 | 9 | 1 | 1 | 9 | 188 | 1 | 13 | 23100 | 1 | 9 | 100 | 1 | 9 | 23000 | 1 | 13 | 9470 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.84 | A | 7 | 988 | A | 7 | 70 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 2.3 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.24 | 2 | 0
1979-08-14 | 1900-08-13 | 12:00 | 12 | 1178 | 1331 | 274 | 1 | 9 | 4 | 1 | 9 | 270 | 1 | 13 | 33000 | 1 | 9 | 300 | 1 | 9 | 32700 | 1 | 13 | 12930 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 988 | A | 7 | 60 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 310 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.14 | 2 | 0
1979-08-14 | 1900-08-13 | 13:00 | 13 | 1204 | 1331 | 245 | 1 | 9 | 5 | 1 | 9 | 241 | 1 | 13 | 30000 | 1 | 9 | 400 | 1 | 9 | 29600 | 1 | 13 | 11850 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 988 | A | 7 | 70 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 2 | 0
1979-08-14 | 1900-08-13 | 14:00 | 14 | 1163 | 1331 | 267 | 1 | 9 | 3 | 1 | 9 | 265 | 1 | 13 | 32300 | 1 | 9 | 200 | 1 | 9 | 32000 | 1 | 13 | 12710 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 3200 | A | 7 | 150 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.24 | 2 | 0
1979-08-14 | 1900-08-13 | 15:00 | 15 | 1057 | 1331 | 232 | 1 | 9 | 0 | 1 | 9 | 232 | 1 | 13 | 27800 | 1 | 9 | 0 | 1 | 9 | 27800 | 1 | 13 | 11190 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 988 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 180 | A | 7 | 2.3 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 2 | 0
1979-08-14 | 1900-08-13 | 16:00 | 16 | 893 | 1331 | 185 | 1 | 9 | 0 | 1 | 9 | 185 | 1 | 13 | 22000 | 1 | 9 | 0 | 1 | 9 | 22000 | 1 | 13 | 8740 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.96 | A | 7 | 988 | A | 7 | 50 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 490 | A | 7 | 2.3 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.24 | 2 | 0
1979-08-14 | 1900-08-13 | 17:00 | 17 | 682 | 1331 | 134 | 1 | 9 | 1 | 1 | 9 | 134 | 1 | 13 | 15800 | 1 | 9 | 100 | 1 | 9 | 15800 | 1 | 13 | 5970 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 490 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.24 | 2 | 0
1979-08-14 | 1900-08-13 | 18:00 | 18 | 440 | 1331 | 122 | 1 | 9 | 0 | 1 | 9 | 121 | 1 | 13 | 13600 | 1 | 9 | 0 | 1 | 9 | 13600 | 1 | 13 | 4460 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.96 | A | 7 | 988 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 550 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.32 | 2 | 0
1979-08-14 | 1900-08-13 | 19:00 | 19 | 183 | 1331 | 26 | 1 | 13 | 0 | 1 | 9 | 26 | 1 | 13 | 3000 | 1 | 13 | 0 | 1 | 9 | 3000 | 1 | 13 | 990 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.96 | A | 7 | 988 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 580 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.32 | 2 | 0
1979-08-14 | 1900-08-13 | 20:00 | 20 | 7 | 322 | 6 | 1 | 13 | 0 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 370 | A | 7 | 2.4 | E | 8 | 0.151 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.32 | 2 | 0
1979-08-14 | 1900-08-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 989 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 2 | 0
1979-08-14 | 1900-08-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 990 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 2 | 0
1979-08-14 | 1900-08-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.9 | A | 7 | 989 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.26 | 2 | 0
1979-08-14 | 1900-08-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 990 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 2 | 0
1979-08-15 | 1900-08-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 989 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 3 | 0
1979-08-15 | 1900-08-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.34 | 3 | 0
1979-08-15 | 1900-08-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 989 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 3 | 0
1979-08-15 | 1900-08-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 989 | A | 7 | 60 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 3 | 0
1979-08-15 | 1900-08-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 989 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 3 | 0
1979-08-15 | 1900-08-14 | 6:00 | 6 | 24 | 610 | 11 | 1 | 13 | 0 | 1 | 9 | 11 | 1 | 13 | 1300 | 1 | 13 | 0 | 1 | 9 | 1300 | 1 | 13 | 390 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.9 | A | 7 | 989 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.26 | 3 | 0
1979-08-15 | 1900-08-14 | 7:00 | 7 | 237 | 1332 | 64 | 1 | 13 | 0 | 1 | 9 | 64 | 1 | 13 | 7100 | 1 | 13 | 0 | 1 | 9 | 7100 | 1 | 13 | 2140 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.9 | A | 7 | 989 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.26 | 3 | 0
1979-08-15 | 1900-08-14 | 8:00 | 8 | 492 | 1332 | 166 | 1 | 9 | 1 | 1 | 9 | 165 | 1 | 13 | 18400 | 1 | 9 | 100 | 1 | 9 | 18400 | 1 | 13 | 5800 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.87 | A | 7 | 990 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.76 | 3 | 0
1979-08-15 | 1900-08-14 | 9:00 | 9 | 729 | 1332 | 257 | 1 | 9 | 0 | 1 | 9 | 257 | 1 | 13 | 29000 | 1 | 9 | 0 | 1 | 9 | 29000 | 1 | 13 | 9870 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 12.2 | 53.96 | A | 7 | 0.84 | A | 7 | 990 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.16 | 3 | 0
1979-08-15 | 1900-08-14 | 10:00 | 10 | 931 | 1332 | 350 | 1 | 9 | 1 | 1 | 9 | 349 | 1 | 13 | 39800 | 1 | 9 | 100 | 1 | 9 | 39800 | 1 | 13 | 14040 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.66 | 3 | 0
1979-08-15 | 1900-08-14 | 11:00 | 11 | 1083 | 1332 | 420 | 1 | 9 | 1 | 1 | 9 | 420 | 1 | 13 | 48400 | 1 | 9 | 100 | 1 | 9 | 48300 | 1 | 13 | 17150 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.81 | A | 7 | 991 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.66 | 3 | 0
1979-08-15 | 1900-08-14 | 12:00 | 12 | 1175 | 1332 | 448 | 1 | 9 | 1 | 1 | 9 | 447 | 1 | 13 | 51900 | 1 | 9 | 100 | 1 | 9 | 51800 | 1 | 13 | 18400 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 990 | A | 7 | 80 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.16 | 3 | 0
1979-08-15 | 1900-08-14 | 13:00 | 13 | 1202 | 1332 | 431 | 1 | 9 | 0 | 1 | 9 | 431 | 1 | 13 | 50300 | 1 | 9 | 0 | 1 | 9 | 50300 | 1 | 13 | 18160 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 3 | 0
1979-08-15 | 1900-08-14 | 14:00 | 14 | 1160 | 1332 | 412 | 1 | 9 | 1 | 1 | 9 | 412 | 1 | 13 | 48100 | 1 | 9 | 100 | 1 | 9 | 48000 | 1 | 13 | 17420 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.66 | 3 | 0
1979-08-15 | 1900-08-14 | 15:00 | 15 | 1053 | 1332 | 416 | 1 | 9 | 1 | 1 | 9 | 416 | 1 | 13 | 47700 | 1 | 9 | 100 | 1 | 9 | 47700 | 1 | 13 | 16810 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 80 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 1010 | A | 7 | 2.3 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.64 | 3 | 0
1979-08-15 | 1900-08-14 | 16:00 | 16 | 889 | 1332 | 326 | 1 | 9 | 1 | 1 | 9 | 325 | 1 | 13 | 37100 | 1 | 9 | 100 | 1 | 9 | 37000 | 1 | 13 | 13050 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.81 | A | 7 | 989 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1040 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 3 | 0
1979-08-15 | 1900-08-14 | 17:00 | 17 | 678 | 1332 | 134 | 1 | 9 | 1 | 1 | 9 | 134 | 1 | 13 | 15800 | 1 | 9 | 100 | 1 | 9 | 15800 | 1 | 13 | 5950 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1010 | A | 7 | 2.3 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.74 | 3 | 0
1979-08-15 | 1900-08-14 | 18:00 | 18 | 435 | 1332 | 152 | 1 | 9 | 1 | 1 | 9 | 152 | 1 | 13 | 16800 | 1 | 9 | 100 | 1 | 9 | 16800 | 1 | 13 | 5090 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 988 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 1010 | A | 7 | 2.5 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 3 | 0
1979-08-15 | 1900-08-14 | 19:00 | 19 | 178 | 1332 | 54 | 1 | 13 | 1 | 1 | 9 | 54 | 1 | 13 | 5900 | 1 | 13 | 0 | 1 | 9 | 5900 | 1 | 13 | 1680 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 988 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 1010 | A | 7 | 2.5 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 3 | 0
1979-08-15 | 1900-08-14 | 20:00 | 20 | 6 | 300 | 4 | 1 | 13 | 0 | 1 | 9 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 988 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 2.5 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 3 | 0
1979-08-15 | 1900-08-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 989 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 3 | 0
1979-08-15 | 1900-08-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 988 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 580 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 3 | 0
1979-08-15 | 1900-08-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 988 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 3 | 0
1979-08-15 | 1900-08-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 988 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 3 | 0
1979-08-16 | 1900-08-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 988 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 4 | 0
1979-08-16 | 1900-08-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 987 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 4 | 0
1979-08-16 | 1900-08-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 987 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 4 | 0
1979-08-16 | 1900-08-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 987 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 400 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 4 | 0
1979-08-16 | 1900-08-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 987 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 4 | 0
1979-08-16 | 1900-08-15 | 6:00 | 6 | 22 | 588 | 12 | 1 | 13 | 0 | 1 | 9 | 12 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 988 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 2.5 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 4 | 0
1979-08-16 | 1900-08-15 | 7:00 | 7 | 234 | 1332 | 60 | 1 | 13 | 0 | 1 | 9 | 60 | 1 | 13 | 6700 | 1 | 13 | 0 | 1 | 9 | 6700 | 1 | 13 | 2040 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 987 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 430 | A | 7 | 2.5 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 4 | 0
1979-08-16 | 1900-08-15 | 8:00 | 8 | 489 | 1332 | 148 | 1 | 9 | 0 | 1 | 9 | 148 | 1 | 13 | 16600 | 1 | 9 | 0 | 1 | 9 | 16600 | 1 | 13 | 5410 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 988 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 2.5 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 4 | 0
1979-08-16 | 1900-08-15 | 9:00 | 9 | 727 | 1332 | 238 | 1 | 9 | 1 | 1 | 9 | 238 | 1 | 13 | 27100 | 1 | 9 | 100 | 1 | 9 | 27000 | 1 | 13 | 9390 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 2.5 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 4 | 0
1979-08-16 | 1900-08-15 | 10:00 | 10 | 928 | 1332 | 319 | 1 | 9 | 1 | 1 | 9 | 318 | 1 | 13 | 36600 | 1 | 9 | 100 | 1 | 9 | 36500 | 1 | 13 | 13240 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 2.7 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 4 | 0
1979-08-16 | 1900-08-15 | 11:00 | 11 | 1080 | 1332 | 569 | 1 | 9 | 236 | 1 | 9 | 376 | 1 | 13 | 61600 | 1 | 9 | 25600 | 1 | 9 | 40800 | 1 | 13 | 13810 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 987 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 2.9 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 4 | 0
1979-08-16 | 1900-08-15 | 12:00 | 12 | 1173 | 1332 | 403 | 1 | 9 | 99 | 1 | 9 | 315 | 1 | 13 | 45000 | 1 | 9 | 10600 | 1 | 9 | 35700 | 1 | 13 | 13990 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.73 | A | 7 | 987 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 430 | A | 7 | 3 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.46 | 4 | 0
1979-08-16 | 1900-08-15 | 13:00 | 13 | 1199 | 1332 | 505 | 1 | 9 | 99 | 1 | 9 | 416 | 1 | 13 | 55800 | 1 | 9 | 10200 | 1 | 9 | 46600 | 1 | 13 | 19980 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.74 | A | 7 | 986 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 3.1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.74 | 4 | 0
1979-08-16 | 1900-08-15 | 14:00 | 14 | 1157 | 1332 | 798 | 1 | 13 | 672 | 1 | 13 | 212 | 1 | 13 | 85100 | 1 | 13 | 68700 | 1 | 13 | 25300 | 1 | 13 | 9750 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.82 | 4 | 0
1979-08-16 | 1900-08-15 | 15:00 | 15 | 1050 | 1332 | 639 | 1 | 13 | 515 | 1 | 13 | 231 | 1 | 13 | 69700 | 1 | 13 | 53800 | 1 | 13 | 27100 | 1 | 13 | 7970 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 984 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.6 | 4 | 0
1979-08-16 | 1900-08-15 | 16:00 | 16 | 885 | 1332 | 574 | 1 | 9 | 651 | 1 | 9 | 138 | 1 | 13 | 61000 | 1 | 9 | 66300 | 1 | 9 | 16800 | 1 | 13 | 3680 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 984 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 4 | 0
1979-08-16 | 1900-08-15 | 17:00 | 17 | 674 | 1332 | 448 | 1 | 13 | 637 | 1 | 13 | 123 | 1 | 13 | 46600 | 1 | 13 | 62800 | 1 | 13 | 14800 | 1 | 13 | 2610 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 983 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 4 | 0
1979-08-16 | 1900-08-15 | 18:00 | 18 | 430 | 1332 | 205 | 1 | 13 | 329 | 1 | 13 | 97 | 1 | 13 | 21500 | 1 | 13 | 29800 | 1 | 13 | 11900 | 1 | 13 | 1810 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.88 | 4 | 0
1979-08-16 | 1900-08-15 | 19:00 | 19 | 173 | 1332 | 56 | 1 | 13 | 105 | 1 | 13 | 42 | 1 | 13 | 5900 | 1 | 13 | 6100 | 1 | 13 | 5100 | 1 | 13 | 770 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 4 | 0
1979-08-16 | 1900-08-15 | 20:00 | 20 | 5 | 278 | 4 | 1 | 13 | 8 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.08 | 4 | 0
1979-08-16 | 1900-08-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.48 | 4 | 0
1979-08-16 | 1900-08-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.48 | 4 | 0
1979-08-16 | 1900-08-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.48 | 4 | 0
1979-08-16 | 1900-08-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.48 | 4 | 0
1979-08-17 | 1900-08-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.48 | 5 | 0
1979-08-17 | 1900-08-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.36 | 5 | 0
1979-08-17 | 1900-08-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 70.36 | 5 | 0
1979-08-17 | 1900-08-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 71.26 | 5 | 0
1979-08-17 | 1900-08-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 71.26 | 5 | 0
1979-08-17 | 1900-08-16 | 6:00 | 6 | 21 | 566 | 10 | 1 | 13 | 31 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 71.26 | 5 | 0
1979-08-17 | 1900-08-16 | 7:00 | 7 | 230 | 1333 | 107 | 1 | 13 | 400 | 1 | 9 | 38 | 1 | 13 | 11100 | 1 | 13 | 29000 | 1 | 9 | 6100 | 1 | 13 | 700 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 4000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 71.26 | 5 | 0
1979-08-17 | 1900-08-16 | 8:00 | 8 | 486 | 1333 | 289 | 1 | 9 | 625 | 1 | 9 | 60 | 1 | 13 | 30200 | 1 | 9 | 58500 | 1 | 9 | 8800 | 1 | 13 | 1250 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.06 | 5 | 0
1979-08-17 | 1900-08-16 | 9:00 | 9 | 724 | 1333 | 500 | 1 | 9 | 770 | 1 | 9 | 81 | 1 | 13 | 53300 | 1 | 9 | 76600 | 1 | 9 | 11600 | 1 | 13 | 1880 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.94 | 5 | 0
1979-08-17 | 1900-08-16 | 10:00 | 10 | 926 | 1333 | 669 | 1 | 9 | 822 | 1 | 9 | 96 | 1 | 13 | 69300 | 1 | 9 | 81900 | 1 | 9 | 12300 | 1 | 13 | 2360 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 23.3 | 73.94 | A | 7 | 0.77 | A | 7 | 981 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.54 | 5 | 0
1979-08-17 | 1900-08-16 | 11:00 | 11 | 1078 | 1333 | 809 | 1 | 9 | 865 | 1 | 9 | 107 | 1 | 13 | 83600 | 1 | 9 | 86600 | 1 | 9 | 13400 | 1 | 13 | 3340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 23.3 | 73.94 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 230 | A | 7 | 8.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.74 | 5 | 0
1979-08-17 | 1900-08-16 | 12:00 | 12 | 1170 | 1333 | 890 | 1 | 9 | 882 | 1 | 9 | 113 | 1 | 13 | 91700 | 1 | 9 | 88400 | 1 | 9 | 13900 | 1 | 13 | 4510 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 23.3 | 73.94 | A | 7 | 0.68 | A | 7 | 980 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4.2 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.24 | 5 | 0
1979-08-17 | 1900-08-16 | 13:00 | 13 | 1196 | 1333 | 910 | 1 | 9 | 883 | 1 | 9 | 114 | 1 | 13 | 93700 | 1 | 9 | 88600 | 1 | 9 | 14000 | 1 | 13 | 4990 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 23.9 | 75.02 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.42 | 5 | 0
1979-08-17 | 1900-08-16 | 14:00 | 14 | 1154 | 1333 | 876 | 1 | 9 | 878 | 1 | 9 | 112 | 1 | 13 | 90200 | 1 | 9 | 88000 | 1 | 9 | 13800 | 1 | 13 | 4250 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.7 | 89.06 | A | 7 | 23.9 | 75.02 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4.3 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.92 | 5 | 0
1979-08-17 | 1900-08-16 | 15:00 | 15 | 1047 | 1333 | 786 | 1 | 9 | 862 | 1 | 9 | 105 | 1 | 13 | 81100 | 1 | 9 | 86200 | 1 | 9 | 13200 | 1 | 13 | 3070 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 22.2 | 71.96 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.36 | 5 | 0
1979-08-17 | 1900-08-16 | 16:00 | 16 | 881 | 1333 | 643 | 1 | 9 | 825 | 1 | 9 | 93 | 1 | 13 | 66400 | 1 | 9 | 82000 | 1 | 9 | 12100 | 1 | 13 | 2180 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.56 | 5 | 0
1979-08-17 | 1900-08-16 | 17:00 | 17 | 669 | 1333 | 459 | 1 | 9 | 754 | 1 | 9 | 77 | 1 | 13 | 48400 | 1 | 9 | 74300 | 1 | 9 | 11000 | 1 | 13 | 1730 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 22.2 | 71.96 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.36 | 5 | 0
1979-08-17 | 1900-08-16 | 18:00 | 18 | 425 | 1333 | 258 | 1 | 9 | 624 | 1 | 9 | 55 | 1 | 13 | 26400 | 1 | 9 | 56600 | 1 | 9 | 8300 | 1 | 13 | 1110 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.7 | 89.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.66 | 5 | 0
1979-08-17 | 1900-08-16 | 19:00 | 19 | 167 | 1333 | 75 | 1 | 13 | 331 | 1 | 9 | 32 | 1 | 13 | 7500 | 1 | 13 | 20600 | 1 | 9 | 4900 | 1 | 13 | 570 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.76 | 5 | 0
1979-08-17 | 1900-08-16 | 20:00 | 20 | 4 | 233 | 3 | 1 | 13 | 8 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.085 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.46 | 5 | 0
1979-08-17 | 1900-08-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 5 | 0
1979-08-17 | 1900-08-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.7 | 5 | 0
1979-08-17 | 1900-08-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 5 | 0
1979-08-17 | 1900-08-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.22 | 5 | 0
1979-08-18 | 1900-08-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 6 | 0
1979-08-18 | 1900-08-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.82 | 6 | 0
1979-08-18 | 1900-08-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.82 | 6 | 0
1979-08-18 | 1900-08-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.52 | 6 | 0
1979-08-18 | 1900-08-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 6 | 0
1979-08-18 | 1900-08-17 | 6:00 | 6 | 19 | 544 | 10 | 1 | 13 | 25 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.62 | 6 | 0
1979-08-18 | 1900-08-17 | 7:00 | 7 | 227 | 1333 | 100 | 1 | 13 | 332 | 1 | 9 | 43 | 1 | 13 | 10200 | 1 | 13 | 23700 | 1 | 9 | 6200 | 1 | 13 | 770 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 979 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 6 | 0
1979-08-18 | 1900-08-17 | 8:00 | 8 | 483 | 1333 | 299 | 1 | 9 | 652 | 1 | 9 | 62 | 1 | 13 | 31100 | 1 | 9 | 60800 | 1 | 9 | 9000 | 1 | 13 | 1270 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.3 | 6 | 0
1979-08-18 | 1900-08-17 | 9:00 | 9 | 721 | 1333 | 499 | 1 | 9 | 768 | 1 | 9 | 83 | 1 | 13 | 53000 | 1 | 9 | 76300 | 1 | 9 | 11700 | 1 | 13 | 1910 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 6 | 0
1979-08-18 | 1900-08-17 | 10:00 | 10 | 923 | 1333 | 676 | 1 | 9 | 830 | 1 | 9 | 99 | 1 | 13 | 70000 | 1 | 9 | 82600 | 1 | 9 | 12600 | 1 | 13 | 2370 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 6 | 0
1979-08-18 | 1900-08-17 | 11:00 | 11 | 1075 | 1333 | 807 | 1 | 9 | 862 | 1 | 9 | 109 | 1 | 13 | 83300 | 1 | 9 | 86300 | 1 | 9 | 13500 | 1 | 13 | 3350 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.76 | 6 | 0
1979-08-18 | 1900-08-17 | 12:00 | 12 | 1168 | 1333 | 882 | 1 | 9 | 871 | 1 | 9 | 116 | 1 | 13 | 90800 | 1 | 9 | 87300 | 1 | 9 | 14100 | 1 | 13 | 4530 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.16 | 6 | 0
1979-08-18 | 1900-08-17 | 13:00 | 13 | 1193 | 1333 | 911 | 1 | 9 | 882 | 1 | 9 | 117 | 1 | 13 | 93600 | 1 | 9 | 88500 | 1 | 9 | 14200 | 1 | 13 | 5010 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 22.8 | 73.04 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.54 | 6 | 0
1979-08-18 | 1900-08-17 | 14:00 | 14 | 1151 | 1333 | 877 | 1 | 9 | 879 | 1 | 9 | 115 | 1 | 13 | 90300 | 1 | 9 | 88100 | 1 | 9 | 14100 | 1 | 13 | 4260 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 22.8 | 73.04 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.54 | 6 | 0
1979-08-18 | 1900-08-17 | 15:00 | 15 | 1043 | 1333 | 780 | 1 | 9 | 855 | 1 | 9 | 108 | 1 | 13 | 80500 | 1 | 9 | 85500 | 1 | 9 | 13400 | 1 | 13 | 3090 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 22.8 | 73.04 | A | 7 | 0.56 | A | 7 | 977 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.34 | 6 | 0
1979-08-18 | 1900-08-17 | 16:00 | 16 | 877 | 1333 | 625 | 1 | 9 | 817 | 1 | 9 | 83 | 1 | 13 | 64800 | 1 | 9 | 81200 | 1 | 9 | 11200 | 1 | 13 | 2080 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 32.8 | 91.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.54 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 6 | 0
1979-08-18 | 1900-08-17 | 17:00 | 17 | 665 | 1333 | 452 | 1 | 9 | 743 | 1 | 9 | 78 | 1 | 13 | 47500 | 1 | 9 | 73100 | 1 | 9 | 11000 | 1 | 13 | 1730 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 6 | 0
1979-08-18 | 1900-08-17 | 18:00 | 18 | 420 | 1333 | 251 | 1 | 9 | 608 | 1 | 9 | 57 | 1 | 13 | 25700 | 1 | 9 | 54900 | 1 | 9 | 8400 | 1 | 13 | 1130 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.7 | 89.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.57 | A | 7 | 976 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.66 | 6 | 0
1979-08-18 | 1900-08-17 | 19:00 | 19 | 162 | 1333 | 66 | 1 | 13 | 235 | 1 | 9 | 36 | 1 | 13 | 6800 | 1 | 13 | 13500 | 1 | 9 | 5100 | 1 | 13 | 640 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 30 | 86 | A | 7 | 21.7 | 71.06 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.96 | 6 | 0
1979-08-18 | 1900-08-17 | 20:00 | 20 | 3 | 211 | 2 | 1 | 13 | 5 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 976 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.089 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.96 | 6 | 0
1979-08-18 | 1900-08-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 6 | 0
1979-08-18 | 1900-08-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 977 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.98 | 6 | 0
1979-08-18 | 1900-08-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 4 | A | 7 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 14500 | A | 7 | 7620 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.98 | 6 | 0
1979-08-18 | 1900-08-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 2740 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 6 | 0
1979-08-19 | 1900-08-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 2740 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 7 | 0
1979-08-19 | 1900-08-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.7 | 7 | 0
1979-08-19 | 1900-08-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.7 | 7 | 0
1979-08-19 | 1900-08-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 975 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.6 | 7 | 0
1979-08-19 | 1900-08-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 7 | 0
1979-08-19 | 1900-08-18 | 6:00 | 6 | 18 | 522 | 9 | 1 | 13 | 22 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.82 | 7 | 0
1979-08-19 | 1900-08-18 | 7:00 | 7 | 223 | 1334 | 102 | 1 | 13 | 360 | 1 | 9 | 42 | 1 | 13 | 10500 | 1 | 13 | 25600 | 1 | 9 | 6200 | 1 | 13 | 760 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 7 | 0
1979-08-19 | 1900-08-18 | 8:00 | 8 | 480 | 1334 | 299 | 1 | 9 | 676 | 1 | 9 | 55 | 1 | 13 | 31500 | 1 | 9 | 63300 | 1 | 9 | 8700 | 1 | 13 | 1170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 7 | 0
1979-08-19 | 1900-08-18 | 9:00 | 9 | 718 | 1334 | 498 | 1 | 9 | 786 | 1 | 9 | 74 | 1 | 13 | 53500 | 1 | 9 | 78300 | 1 | 9 | 11300 | 1 | 13 | 1760 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 7 | 0
1979-08-19 | 1900-08-18 | 10:00 | 10 | 920 | 1334 | 678 | 1 | 9 | 851 | 1 | 9 | 88 | 1 | 13 | 70400 | 1 | 9 | 84800 | 1 | 9 | 11700 | 1 | 13 | 2260 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.98 | 7 | 0
1979-08-19 | 1900-08-18 | 11:00 | 11 | 1073 | 1334 | 680 | 1 | 9 | 632 | 1 | 9 | 170 | 1 | 13 | 73000 | 1 | 9 | 64900 | 1 | 9 | 20700 | 1 | 13 | 6260 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 30.6 | 87.08 | A | 7 | 21.7 | 71.06 | A | 7 | 0.59 | A | 7 | 976 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.36 | 7 | 0
1979-08-19 | 1900-08-18 | 12:00 | 12 | 1165 | 1334 | 815 | 1 | 9 | 805 | 1 | 9 | 109 | 1 | 13 | 84000 | 1 | 9 | 80700 | 1 | 9 | 13400 | 1 | 13 | 4320 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 31.7 | 89.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.57 | A | 7 | 976 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.66 | 7 | 0
1979-08-19 | 1900-08-18 | 13:00 | 13 | 1190 | 1334 | 851 | 1 | 9 | 763 | 1 | 9 | 166 | 1 | 13 | 89700 | 1 | 9 | 77000 | 1 | 9 | 20800 | 1 | 13 | 7980 | 1 | 18 | 7 | A | 7 | 1 | A | 7 | 32.8 | 91.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.54 | A | 7 | 975 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 7 | 0
1979-08-19 | 1900-08-18 | 14:00 | 14 | 1148 | 1334 | 765 | 1 | 13 | 588 | 1 | 13 | 257 | 1 | 13 | 80400 | 1 | 13 | 59500 | 1 | 13 | 29100 | 1 | 13 | 11230 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 33.3 | 91.94 | A | 7 | 22.8 | 73.04 | A | 7 | 0.54 | A | 7 | 975 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.74 | 7 | 0
1979-08-19 | 1900-08-18 | 15:00 | 15 | 1039 | 1334 | 646 | 1 | 13 | 533 | 1 | 13 | 229 | 1 | 13 | 70400 | 1 | 13 | 55700 | 1 | 13 | 26900 | 1 | 13 | 7700 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 33.9 | 93.02 | A | 7 | 22.8 | 73.04 | A | 7 | 0.52 | A | 7 | 975 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.24 | 7 | 0
1979-08-19 | 1900-08-18 | 16:00 | 16 | 873 | 1334 | 580 | 1 | 13 | 638 | 1 | 13 | 159 | 1 | 13 | 60900 | 1 | 13 | 64500 | 1 | 13 | 18600 | 1 | 13 | 4090 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 33.3 | 91.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.52 | A | 7 | 974 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.26 | 7 | 0
1979-08-19 | 1900-08-18 | 17:00 | 17 | 660 | 1334 | 375 | 1 | 13 | 405 | 1 | 13 | 172 | 1 | 13 | 39300 | 1 | 13 | 40500 | 1 | 13 | 19200 | 1 | 13 | 3620 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 32.8 | 91.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.54 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 7 | 0
1979-08-19 | 1900-08-18 | 18:00 | 18 | 415 | 1334 | 170 | 1 | 9 | 129 | 1 | 9 | 129 | 1 | 13 | 18400 | 1 | 9 | 11900 | 1 | 9 | 14700 | 1 | 13 | 2900 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 31.7 | 89.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.55 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 12190 | A | 7 | 3.8 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.36 | 7 | 0
1979-08-19 | 1900-08-18 | 19:00 | 19 | 156 | 1334 | 45 | 1 | 13 | 15 | 1 | 9 | 43 | 1 | 13 | 4900 | 1 | 13 | 1000 | 1 | 9 | 4800 | 1 | 13 | 1020 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 4270 | A | 7 | 3.7 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 7 | 0
1979-08-19 | 1900-08-18 | 20:00 | 20 | 2 | 189 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 25.6 | 78.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.58 | A | 7 | 975 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 880 | A | 7 | 2.9 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.46 | 7 | 0
1979-08-19 | 1900-08-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 250 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 520 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.72 | 7 | 0
1979-08-19 | 1900-08-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 850 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.04 | 7 | 0
1979-08-19 | 1900-08-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 18.3 | 64.94 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.94 | 7 | 0
1979-08-19 | 1900-08-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 20 | 68 | A | 7 | 18.9 | 66.02 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 7 | 0
1979-08-20 | 1900-08-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | 20 | 68 | A | 7 | 18.9 | 66.02 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 1 | 0
1979-08-20 | 1900-08-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 1 | 0
1979-08-20 | 1900-08-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 140 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 1 | 0
1979-08-20 | 1900-08-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.84 | 1 | 0
1979-08-20 | 1900-08-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 20 | 68 | A | 7 | 17.8 | 64.04 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.44 | 1 | 0
1979-08-20 | 1900-08-19 | 6:00 | 6 | 17 | 500 | 8 | 1 | 13 | 1 | 1 | 13 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 20.6 | 69.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.87 | A | 7 | 977 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 2740 | A | 7 | 3.1 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.24 | 1 | 0
1979-08-20 | 1900-08-19 | 7:00 | 7 | 220 | 1334 | 77 | 1 | 13 | 52 | 1 | 13 | 69 | 1 | 13 | 8500 | 1 | 13 | 4000 | 1 | 13 | 7800 | 1 | 13 | 1630 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 3050 | A | 7 | 3.3 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 1 | 0
1979-08-20 | 1900-08-19 | 8:00 | 8 | 477 | 1334 | 219 | 1 | 13 | 272 | 1 | 13 | 122 | 1 | 13 | 23500 | 1 | 13 | 26100 | 1 | 13 | 14200 | 1 | 13 | 2440 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 977 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 1 | 0
1979-08-20 | 1900-08-19 | 9:00 | 9 | 715 | 1334 | 449 | 1 | 9 | 575 | 1 | 9 | 139 | 1 | 13 | 46700 | 1 | 9 | 56900 | 1 | 9 | 16100 | 1 | 13 | 3010 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 1 | 0
1979-08-20 | 1900-08-19 | 10:00 | 10 | 918 | 1334 | 654 | 1 | 9 | 719 | 1 | 9 | 157 | 1 | 13 | 69300 | 1 | 9 | 73100 | 1 | 9 | 18900 | 1 | 13 | 4320 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.22 | 1 | 0
1979-08-20 | 1900-08-19 | 11:00 | 11 | 1070 | 1334 | 790 | 1 | 9 | 763 | 1 | 9 | 175 | 1 | 13 | 84500 | 1 | 9 | 78200 | 1 | 9 | 21600 | 1 | 13 | 6380 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.82 | 1 | 0
1979-08-20 | 1900-08-19 | 12:00 | 12 | 1162 | 1334 | 831 | 1 | 9 | 709 | 1 | 9 | 211 | 1 | 13 | 88600 | 1 | 9 | 72500 | 1 | 9 | 25300 | 1 | 13 | 9810 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.59 | A | 7 | 977 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.82 | 1 | 0
1979-08-20 | 1900-08-19 | 13:00 | 13 | 1187 | 1334 | 840 | 1 | 9 | 579 | 1 | 9 | 322 | 1 | 13 | 90200 | 1 | 9 | 60500 | 1 | 9 | 36200 | 1 | 13 | 16590 | 1 | 18 | 10 | A | 7 | 2 | A | 7 | 29.4 | 84.92 | A | 7 | 20 | 68 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.3 | 1 | 0
1979-08-20 | 1900-08-19 | 14:00 | 14 | 1144 | 1334 | 797 | 1 | 13 | 597 | 1 | 13 | 282 | 1 | 13 | 83000 | 1 | 13 | 60000 | 1 | 13 | 31400 | 1 | 13 | 12060 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 29.4 | 84.92 | A | 7 | 20 | 68 | A | 7 | 0.57 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.3 | 1 | 0
1979-08-20 | 1900-08-19 | 15:00 | 15 | 1036 | 1334 | 697 | 1 | 13 | 540 | 1 | 13 | 276 | 1 | 13 | 74500 | 1 | 13 | 56300 | 1 | 13 | 30700 | 1 | 13 | 9310 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 30.6 | 87.08 | A | 7 | 20 | 68 | A | 7 | 0.53 | A | 7 | 976 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.3 | 1 | 0
1979-08-20 | 1900-08-19 | 16:00 | 16 | 869 | 1334 | 394 | 1 | 9 | 171 | 1 | 9 | 282 | 1 | 13 | 43100 | 1 | 9 | 18000 | 1 | 9 | 31400 | 1 | 13 | 8040 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 29.4 | 84.92 | A | 7 | 20 | 68 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.5 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.3 | 1 | 0
1979-08-20 | 1900-08-19 | 17:00 | 17 | 655 | 1334 | 237 | 1 | 9 | 162 | 1 | 9 | 157 | 1 | 13 | 26300 | 1 | 9 | 16700 | 1 | 9 | 18100 | 1 | 13 | 3880 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 30 | 86 | A | 7 | 21.1 | 69.98 | A | 7 | 0.59 | A | 7 | 975 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.7 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.48 | 1 | 0
1979-08-20 | 1900-08-19 | 18:00 | 18 | 410 | 1334 | 95 | 1 | 9 | 55 | 1 | 9 | 78 | 1 | 13 | 10500 | 1 | 9 | 5000 | 1 | 9 | 8900 | 1 | 13 | 2230 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 29.4 | 84.92 | A | 7 | 20 | 68 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.5 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.3 | 1 | 0
1979-08-20 | 1900-08-19 | 19:00 | 19 | 151 | 1334 | 30 | 1 | 13 | 29 | 1 | 9 | 26 | 1 | 13 | 3300 | 1 | 13 | 1700 | 1 | 9 | 3100 | 1 | 13 | 540 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.6 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 1 | 0
1979-08-20 | 1900-08-19 | 20:00 | 20 | 1 | 145 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 975 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.175 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.3 | 1 | 0
1979-08-20 | 1900-08-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 1 | 0
1979-08-20 | 1900-08-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 1 | 0
1979-08-20 | 1900-08-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 1 | 0
1979-08-20 | 1900-08-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 1 | 0
1979-08-21 | 1900-08-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 2 | 0
1979-08-21 | 1900-08-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 2 | 0
1979-08-21 | 1900-08-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 21.7 | 71.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.22 | 2 | 0
1979-08-21 | 1900-08-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.72 | 2 | 0
1979-08-21 | 1900-08-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.72 | 2 | 0
1979-08-21 | 1900-08-20 | 6:00 | 6 | 15 | 478 | 3 | 1 | 13 | 1 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 9140 | A | 7 | 3.3 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.22 | 2 | 0
1979-08-21 | 1900-08-20 | 7:00 | 7 | 216 | 1335 | 27 | 1 | 13 | 12 | 1 | 9 | 25 | 1 | 13 | 3000 | 1 | 13 | 900 | 1 | 9 | 2800 | 1 | 13 | 690 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 1370 | A | 7 | 3.2 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.72 | 2 | 0
1979-08-21 | 1900-08-20 | 8:00 | 8 | 474 | 1335 | 118 | 1 | 9 | 6 | 1 | 9 | 116 | 1 | 13 | 13500 | 1 | 9 | 400 | 1 | 9 | 13300 | 1 | 13 | 4500 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 1520 | A | 7 | 3.3 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.52 | 2 | 0
1979-08-21 | 1900-08-20 | 9:00 | 9 | 712 | 1335 | 291 | 1 | 9 | 161 | 1 | 9 | 205 | 1 | 13 | 32000 | 1 | 9 | 16700 | 1 | 9 | 23100 | 1 | 13 | 5230 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 3.5 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 2 | 0
1979-08-21 | 1900-08-20 | 10:00 | 10 | 915 | 1335 | 549 | 1 | 13 | 367 | 1 | 13 | 296 | 1 | 13 | 59200 | 1 | 13 | 39500 | 1 | 13 | 32100 | 1 | 13 | 8310 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 3.5 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.6 | 2 | 0
1979-08-21 | 1900-08-20 | 11:00 | 11 | 1067 | 1335 | 728 | 1 | 13 | 632 | 1 | 13 | 221 | 1 | 13 | 76700 | 1 | 13 | 64100 | 1 | 13 | 25300 | 1 | 13 | 7820 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 977 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 2 | 0
1979-08-21 | 1900-08-20 | 12:00 | 12 | 1159 | 1335 | 864 | 1 | 9 | 806 | 1 | 9 | 161 | 1 | 13 | 91200 | 1 | 9 | 81400 | 1 | 9 | 20300 | 1 | 13 | 6920 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.98 | 2 | 0
1979-08-21 | 1900-08-20 | 13:00 | 13 | 1184 | 1335 | 890 | 1 | 13 | 752 | 1 | 13 | 220 | 1 | 13 | 94900 | 1 | 13 | 76900 | 1 | 13 | 26500 | 1 | 13 | 11010 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 977 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 2 | 0
1979-08-21 | 1900-08-20 | 14:00 | 14 | 1141 | 1335 | 684 | 1 | 13 | 484 | 1 | 13 | 268 | 1 | 13 | 74400 | 1 | 13 | 50700 | 1 | 13 | 31000 | 1 | 13 | 11710 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.96 | 2 | 0
1979-08-21 | 1900-08-20 | 15:00 | 15 | 1032 | 1335 | 708 | 1 | 13 | 671 | 1 | 13 | 186 | 1 | 13 | 75000 | 1 | 13 | 68400 | 1 | 13 | 22000 | 1 | 13 | 6180 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 30 | 86 | A | 7 | 21.1 | 69.98 | A | 7 | 0.59 | A | 7 | 976 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.48 | 2 | 0
1979-08-21 | 1900-08-20 | 16:00 | 16 | 864 | 1335 | 536 | 1 | 13 | 506 | 1 | 13 | 206 | 1 | 13 | 57400 | 1 | 13 | 52300 | 1 | 13 | 23400 | 1 | 13 | 5200 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.98 | 2 | 0
1979-08-21 | 1900-08-20 | 17:00 | 17 | 650 | 1335 | 368 | 1 | 13 | 423 | 1 | 13 | 160 | 1 | 13 | 38800 | 1 | 13 | 42200 | 1 | 13 | 18200 | 1 | 13 | 3330 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 29.4 | 84.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.59 | A | 7 | 976 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.68 | 2 | 0
1979-08-21 | 1900-08-20 | 18:00 | 18 | 404 | 1335 | 226 | 1 | 9 | 508 | 1 | 9 | 70 | 1 | 13 | 23300 | 1 | 9 | 45000 | 1 | 9 | 9600 | 1 | 13 | 1320 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 975 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.98 | 2 | 0
1979-08-21 | 1900-08-20 | 19:00 | 19 | 145 | 1335 | 56 | 1 | 13 | 187 | 1 | 9 | 35 | 1 | 13 | 5700 | 1 | 13 | 10100 | 1 | 9 | 4700 | 1 | 13 | 630 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 20.6 | 69.08 | A | 7 | 0.69 | A | 7 | 974 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.18 | 2 | 0
1979-08-21 | 1900-08-20 | 20:00 | 20 | 1 | 122 | 1 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.138 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 2 | 0
1979-08-21 | 1900-08-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 2 | 0
1979-08-21 | 1900-08-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 20 | 68 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 90 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.2 | 2 | 0
1979-08-21 | 1900-08-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 21.7 | 71.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.22 | 2 | 0
1979-08-21 | 1900-08-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.72 | 2 | 0
1979-08-22 | 1900-08-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.52 | 3 | 0
1979-08-22 | 1900-08-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | 22.8 | 73.04 | A | 7 | 20 | 68 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.6 | 3 | 0
1979-08-22 | 1900-08-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 21.7 | 71.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.22 | 3 | 0
1979-08-22 | 1900-08-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.92 | 3 | 0
1979-08-22 | 1900-08-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 20 | 68 | A | 7 | 18.9 | 66.02 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.52 | 3 | 0
1979-08-22 | 1900-08-21 | 6:00 | 6 | 14 | 456 | 5 | 1 | 13 | 3 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.92 | 3 | 0
1979-08-22 | 1900-08-21 | 7:00 | 7 | 213 | 1336 | 75 | 1 | 13 | 85 | 1 | 13 | 61 | 1 | 13 | 8100 | 1 | 13 | 6000 | 1 | 13 | 7100 | 1 | 13 | 1300 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 9140 | A | 7 | 3.3 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.52 | 3 | 0
1979-08-22 | 1900-08-21 | 8:00 | 8 | 470 | 1336 | 173 | 1 | 13 | 115 | 1 | 13 | 132 | 1 | 13 | 18900 | 1 | 13 | 11000 | 1 | 13 | 15000 | 1 | 13 | 3020 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 9140 | A | 7 | 3.3 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.62 | 3 | 0
1979-08-22 | 1900-08-21 | 9:00 | 9 | 709 | 1336 | 354 | 1 | 13 | 344 | 1 | 13 | 171 | 1 | 13 | 37700 | 1 | 13 | 34800 | 1 | 13 | 19200 | 1 | 13 | 3700 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.82 | 3 | 0
1979-08-22 | 1900-08-21 | 10:00 | 10 | 912 | 1336 | 608 | 1 | 13 | 537 | 1 | 13 | 240 | 1 | 13 | 64700 | 1 | 13 | 55600 | 1 | 13 | 26600 | 1 | 13 | 6510 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 3.5 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.2 | 3 | 0
1979-08-22 | 1900-08-21 | 11:00 | 11 | 1065 | 1336 | 668 | 1 | 13 | 553 | 1 | 13 | 225 | 1 | 13 | 70200 | 1 | 13 | 56000 | 1 | 13 | 25400 | 1 | 13 | 7880 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.2 | 3 | 0
1979-08-22 | 1900-08-21 | 12:00 | 12 | 1156 | 1336 | 660 | 1 | 9 | 567 | 1 | 9 | 168 | 1 | 13 | 71600 | 1 | 9 | 58500 | 1 | 9 | 20800 | 1 | 13 | 7760 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 27.8 | 82.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.65 | A | 7 | 975 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.18 | 3 | 0
1979-08-22 | 1900-08-21 | 13:00 | 13 | 1181 | 1336 | 888 | 1 | 9 | 796 | 1 | 9 | 181 | 1 | 13 | 92800 | 1 | 9 | 80000 | 1 | 9 | 21900 | 1 | 13 | 8200 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.61 | A | 7 | 974 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 3 | 0
1979-08-22 | 1900-08-21 | 14:00 | 14 | 1137 | 1336 | 818 | 1 | 9 | 760 | 1 | 9 | 167 | 1 | 13 | 85600 | 1 | 9 | 76500 | 1 | 9 | 20300 | 1 | 13 | 6600 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 30 | 86 | A | 7 | 20 | 68 | A | 7 | 0.55 | A | 7 | 974 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.8 | 3 | 0
1979-08-22 | 1900-08-21 | 15:00 | 15 | 1028 | 1336 | 643 | 1 | 9 | 529 | 1 | 9 | 234 | 1 | 13 | 69800 | 1 | 9 | 55200 | 1 | 9 | 27200 | 1 | 13 | 7670 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 30.6 | 87.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.52 | A | 7 | 973 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 3 | 0
1979-08-22 | 1900-08-21 | 16:00 | 16 | 860 | 1336 | 482 | 1 | 13 | 409 | 1 | 13 | 216 | 1 | 13 | 51200 | 1 | 13 | 42200 | 1 | 13 | 24000 | 1 | 13 | 5450 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 30.6 | 87.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.52 | A | 7 | 972 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 3 | 0
1979-08-22 | 1900-08-21 | 17:00 | 17 | 645 | 1336 | 370 | 1 | 13 | 429 | 1 | 13 | 161 | 1 | 13 | 39000 | 1 | 13 | 42700 | 1 | 13 | 18300 | 1 | 13 | 3340 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.53 | A | 7 | 973 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.18 | 3 | 0
1979-08-22 | 1900-08-21 | 18:00 | 18 | 399 | 1336 | 204 | 1 | 13 | 351 | 1 | 13 | 97 | 1 | 13 | 21200 | 1 | 13 | 31000 | 1 | 13 | 11900 | 1 | 13 | 1810 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 29.4 | 84.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.53 | A | 7 | 973 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.62 | 3 | 0
1979-08-22 | 1900-08-21 | 19:00 | 19 | 139 | 1336 | 44 | 1 | 13 | 86 | 1 | 9 | 35 | 1 | 13 | 4600 | 1 | 13 | 4300 | 1 | 9 | 4200 | 1 | 13 | 640 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 973 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.6 | 3 | 0
1979-08-22 | 1900-08-21 | 20:00 | 20 | 0 | 78 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 973 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.184 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 3 | 0
1979-08-22 | 1900-08-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.82 | A | 7 | 974 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.12 | 3 | 0
1979-08-22 | 1900-08-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 974 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 3 | 0
1979-08-22 | 1900-08-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.64 | 3 | 0
1979-08-22 | 1900-08-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 17.2 | 62.96 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.76 | 3 | 0
1979-08-23 | 1900-08-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 4 | 0
1979-08-23 | 1900-08-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.36 | 4 | 0
1979-08-23 | 1900-08-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 4 | 0
1979-08-23 | 1900-08-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 4 | 0
1979-08-23 | 1900-08-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 4 | 0
1979-08-23 | 1900-08-22 | 6:00 | 6 | 13 | 434 | 11 | 1 | 13 | 39 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 4 | 0
1979-08-23 | 1900-08-22 | 7:00 | 7 | 209 | 1336 | 103 | 1 | 13 | 454 | 1 | 9 | 31 | 1 | 13 | 10400 | 1 | 13 | 33100 | 1 | 9 | 5200 | 1 | 13 | 600 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 4 | 0
1979-08-23 | 1900-08-22 | 8:00 | 8 | 467 | 1336 | 294 | 1 | 9 | 695 | 1 | 9 | 50 | 1 | 13 | 31100 | 1 | 9 | 64900 | 1 | 9 | 8400 | 1 | 13 | 1090 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.81 | A | 7 | 976 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.16 | 4 | 0
1979-08-23 | 1900-08-22 | 9:00 | 9 | 706 | 1336 | 472 | 1 | 13 | 666 | 1 | 13 | 119 | 1 | 13 | 49700 | 1 | 13 | 66200 | 1 | 13 | 14600 | 1 | 13 | 2620 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.14 | 4 | 0
1979-08-23 | 1900-08-22 | 10:00 | 10 | 909 | 1336 | 355 | 1 | 13 | 129 | 1 | 13 | 267 | 1 | 13 | 39200 | 1 | 13 | 13700 | 1 | 13 | 29900 | 1 | 13 | 7880 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 23.3 | 73.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 310 | A | 7 | 3 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.04 | 4 | 0
1979-08-23 | 1900-08-22 | 11:00 | 11 | 1062 | 1336 | 595 | 1 | 13 | 454 | 1 | 13 | 233 | 1 | 13 | 65000 | 1 | 13 | 47500 | 1 | 13 | 27200 | 1 | 13 | 8200 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 24.4 | 75.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.66 | A | 7 | 977 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.94 | 4 | 0
1979-08-23 | 1900-08-22 | 12:00 | 12 | 1153 | 1336 | 800 | 1 | 13 | 636 | 1 | 13 | 250 | 1 | 13 | 84400 | 1 | 13 | 64400 | 1 | 13 | 28600 | 1 | 13 | 11090 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.66 | 4 | 0
1979-08-23 | 1900-08-22 | 13:00 | 13 | 1178 | 1336 | 756 | 1 | 13 | 608 | 1 | 13 | 216 | 1 | 13 | 80500 | 1 | 13 | 62200 | 1 | 13 | 25500 | 1 | 13 | 10540 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 26.7 | 80.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.56 | A | 7 | 977 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.76 | 4 | 0
1979-08-23 | 1900-08-22 | 14:00 | 14 | 1134 | 1336 | 289 | 1 | 9 | 71 | 1 | 9 | 228 | 1 | 13 | 32800 | 1 | 9 | 7700 | 1 | 9 | 26300 | 1 | 13 | 9200 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 26.1 | 78.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.58 | A | 7 | 977 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 2.9 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.26 | 4 | 0
1979-08-23 | 1900-08-22 | 15:00 | 15 | 1024 | 1336 | 421 | 1 | 9 | 170 | 1 | 9 | 290 | 1 | 13 | 46700 | 1 | 9 | 18200 | 1 | 9 | 32800 | 1 | 13 | 9750 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 26.7 | 80.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.58 | A | 7 | 976 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 3 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.14 | 4 | 0
1979-08-23 | 1900-08-22 | 16:00 | 16 | 855 | 1336 | 518 | 1 | 9 | 409 | 1 | 9 | 255 | 1 | 13 | 56100 | 1 | 9 | 43800 | 1 | 9 | 28000 | 1 | 13 | 6620 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 26.7 | 80.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.58 | A | 7 | 976 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 3 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.14 | 4 | 0
1979-08-23 | 1900-08-22 | 17:00 | 17 | 640 | 1336 | 271 | 1 | 9 | 167 | 1 | 9 | 190 | 1 | 13 | 29600 | 1 | 9 | 17000 | 1 | 9 | 21400 | 1 | 13 | 4670 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 25.6 | 78.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.58 | A | 7 | 976 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 2.9 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.46 | 4 | 0
1979-08-23 | 1900-08-22 | 18:00 | 18 | 393 | 1336 | 225 | 1 | 9 | 581 | 1 | 9 | 51 | 1 | 13 | 23100 | 1 | 9 | 51700 | 1 | 9 | 7800 | 1 | 13 | 1030 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 25.6 | 78.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.04 | 4 | 0
1979-08-23 | 1900-08-22 | 19:00 | 19 | 134 | 1336 | 59 | 1 | 13 | 329 | 1 | 9 | 24 | 1 | 13 | 5800 | 1 | 13 | 18500 | 1 | 9 | 4000 | 1 | 13 | 440 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 4 | 0
1979-08-23 | 1900-08-22 | 20:00 | 20 | 0 | 56 | 2 | 1 | 13 | 2 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.26 | 4 | 0
1979-08-23 | 1900-08-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 976 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 4 | 0
1979-08-23 | 1900-08-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.88 | 4 | 0
1979-08-23 | 1900-08-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 4 | 0
1979-08-23 | 1900-08-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 977 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 4 | 0
1979-08-24 | 1900-08-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 5 | 0
1979-08-24 | 1900-08-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.87 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.62 | 5 | 0
1979-08-24 | 1900-08-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 11.7 | 53.06 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.36 | 5 | 0
1979-08-24 | 1900-08-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 140 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 5 | 0
1979-08-24 | 1900-08-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.76 | 5 | 0
1979-08-24 | 1900-08-23 | 6:00 | 6 | 12 | 434 | 6 | 1 | 13 | 2 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 977 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.86 | 5 | 0
1979-08-24 | 1900-08-23 | 7:00 | 7 | 205 | 1337 | 79 | 1 | 13 | 188 | 1 | 9 | 50 | 1 | 13 | 8400 | 1 | 13 | 12100 | 1 | 9 | 6500 | 1 | 13 | 920 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 5 | 0
1979-08-24 | 1900-08-23 | 8:00 | 8 | 464 | 1337 | 259 | 1 | 9 | 473 | 1 | 9 | 94 | 1 | 13 | 27700 | 1 | 9 | 43900 | 1 | 9 | 12400 | 1 | 13 | 1750 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 978 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.9 | 5 | 0
1979-08-24 | 1900-08-23 | 9:00 | 9 | 703 | 1337 | 381 | 1 | 13 | 330 | 1 | 13 | 207 | 1 | 13 | 41000 | 1 | 13 | 34500 | 1 | 13 | 22800 | 1 | 13 | 4740 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.12 | 5 | 0
1979-08-24 | 1900-08-23 | 10:00 | 10 | 906 | 1337 | 599 | 1 | 9 | 583 | 1 | 9 | 202 | 1 | 13 | 62300 | 1 | 9 | 58400 | 1 | 9 | 22500 | 1 | 13 | 5260 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.47 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.36 | 5 | 0
1979-08-24 | 1900-08-23 | 11:00 | 11 | 1059 | 1337 | 769 | 1 | 13 | 701 | 1 | 13 | 212 | 1 | 13 | 81200 | 1 | 13 | 71200 | 1 | 13 | 24600 | 1 | 13 | 7360 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 26.1 | 78.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.41 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.46 | 5 | 0
1979-08-24 | 1900-08-23 | 12:00 | 12 | 1150 | 1337 | 838 | 1 | 13 | 672 | 1 | 13 | 257 | 1 | 13 | 88000 | 1 | 13 | 68000 | 1 | 13 | 29400 | 1 | 13 | 11250 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 26.7 | 80.06 | A | 7 | 10 | 50 | A | 7 | 0.35 | A | 7 | 978 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39 | 5 | 0
1979-08-24 | 1900-08-23 | 13:00 | 13 | 1175 | 1337 | 763 | 1 | 13 | 529 | 1 | 13 | 296 | 1 | 13 | 82600 | 1 | 13 | 55400 | 1 | 13 | 33800 | 1 | 13 | 14430 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 27.8 | 82.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.35 | A | 7 | 977 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.48 | 5 | 0
1979-08-24 | 1900-08-23 | 14:00 | 14 | 1130 | 1337 | 745 | 1 | 13 | 533 | 1 | 13 | 292 | 1 | 13 | 80200 | 1 | 13 | 55700 | 1 | 13 | 33000 | 1 | 13 | 12370 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 28.3 | 82.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.38 | A | 7 | 977 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.44 | 5 | 0
1979-08-24 | 1900-08-23 | 15:00 | 15 | 1020 | 1337 | 679 | 1 | 13 | 550 | 1 | 13 | 257 | 1 | 13 | 72900 | 1 | 13 | 57300 | 1 | 13 | 29000 | 1 | 13 | 8330 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 26.7 | 80.06 | A | 7 | 15 | 59 | A | 7 | 0.49 | A | 7 | 977 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.9 | 5 | 0
1979-08-24 | 1900-08-23 | 16:00 | 16 | 851 | 1337 | 349 | 1 | 13 | 155 | 1 | 13 | 249 | 1 | 13 | 38400 | 1 | 13 | 16400 | 1 | 13 | 27900 | 1 | 13 | 6980 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 26.1 | 78.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.49 | A | 7 | 976 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.02 | 5 | 0
1979-08-24 | 1900-08-23 | 17:00 | 17 | 635 | 1337 | 319 | 1 | 9 | 312 | 1 | 9 | 169 | 1 | 13 | 34300 | 1 | 9 | 32100 | 1 | 9 | 19000 | 1 | 13 | 3650 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 24.4 | 75.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.12 | 5 | 0
1979-08-24 | 1900-08-23 | 18:00 | 18 | 388 | 1337 | 113 | 1 | 9 | 60 | 1 | 9 | 95 | 1 | 13 | 12300 | 1 | 9 | 5400 | 1 | 9 | 10800 | 1 | 13 | 2580 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 23.9 | 75.02 | A | 7 | 15 | 59 | A | 7 | 0.58 | A | 7 | 975 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.8 | 5 | 0
1979-08-24 | 1900-08-23 | 19:00 | 19 | 128 | 1337 | 31 | 1 | 13 | 1 | 1 | 9 | 31 | 1 | 13 | 3500 | 1 | 13 | 0 | 1 | 9 | 3500 | 1 | 13 | 1020 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.68 | A | 7 | 976 | A | 7 | 130 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.7 | E | 8 | 0.2 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.68 | 5 | 0
1979-08-24 | 1900-08-23 | 20:00 | 20 | 0 | 11 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 80 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.28 | 5 | 0
1979-08-24 | 1900-08-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.28 | 5 | 0
1979-08-24 | 1900-08-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.66 | A | 7 | 977 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 5 | 0
1979-08-24 | 1900-08-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.66 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 5 | 0
1979-08-24 | 1900-08-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 21.7 | 71.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.44 | 5 | 0
1979-08-25 | 1900-08-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.59 | A | 7 | 977 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.32 | 6 | 0
1979-08-25 | 1900-08-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.66 | A | 7 | 978 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 6 | 0
1979-08-25 | 1900-08-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 15 | 59 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.5 | 6 | 0
1979-08-25 | 1900-08-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 15 | 59 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.5 | 6 | 0
1979-08-25 | 1900-08-24 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 1370 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.52 | 6 | 0
1979-08-25 | 1900-08-24 | 6:00 | 6 | 11 | 412 | 6 | 1 | 13 | 0 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 1370 | A | 7 | 2.5 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.52 | 6 | 0
1979-08-25 | 1900-08-24 | 7:00 | 7 | 202 | 1337 | 45 | 1 | 13 | 1 | 1 | 9 | 45 | 1 | 13 | 5100 | 1 | 13 | 0 | 1 | 9 | 5100 | 1 | 13 | 1570 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 980 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 1370 | A | 7 | 2.5 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 6 | 0
1979-08-25 | 1900-08-24 | 8:00 | 8 | 461 | 1337 | 132 | 1 | 9 | 2 | 1 | 9 | 132 | 1 | 13 | 14900 | 1 | 9 | 100 | 1 | 9 | 14900 | 1 | 13 | 4840 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 2290 | A | 7 | 2.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.88 | 6 | 0
1979-08-25 | 1900-08-24 | 9:00 | 9 | 700 | 1337 | 229 | 1 | 9 | 5 | 1 | 9 | 226 | 1 | 13 | 25900 | 1 | 9 | 400 | 1 | 9 | 25700 | 1 | 13 | 8850 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 2290 | A | 7 | 2.9 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 6 | 0
1979-08-25 | 1900-08-24 | 10:00 | 10 | 904 | 1337 | 159 | 1 | 9 | 3 | 1 | 9 | 157 | 1 | 13 | 19200 | 1 | 9 | 200 | 1 | 9 | 19000 | 1 | 13 | 7660 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 2290 | A | 7 | 3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.16 | 6 | 0
1979-08-25 | 1900-08-24 | 11:00 | 11 | 1056 | 1337 | 299 | 1 | 9 | 3 | 1 | 9 | 296 | 1 | 13 | 35100 | 1 | 9 | 300 | 1 | 9 | 34900 | 1 | 13 | 13450 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 2290 | A | 7 | 3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.14 | 6 | 0
1979-08-25 | 1900-08-24 | 12:00 | 12 | 1147 | 1337 | 369 | 1 | 9 | 5 | 1 | 9 | 365 | 1 | 13 | 43300 | 1 | 9 | 500 | 1 | 9 | 42900 | 1 | 13 | 16020 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 1980 | A | 7 | 3.1 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.74 | 6 | 0
1979-08-25 | 1900-08-24 | 13:00 | 13 | 1171 | 1337 | 252 | 1 | 9 | 5 | 1 | 9 | 247 | 1 | 13 | 30500 | 1 | 9 | 400 | 1 | 9 | 30100 | 1 | 13 | 12020 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 2290 | A | 7 | 3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.14 | 6 | 0
1979-08-25 | 1900-08-24 | 14:00 | 14 | 1126 | 1337 | 218 | 1 | 9 | 0 | 1 | 9 | 218 | 1 | 13 | 26500 | 1 | 9 | 0 | 1 | 9 | 26500 | 1 | 13 | 10780 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 2290 | A | 7 | 3.2 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 6 | 0
1979-08-25 | 1900-08-24 | 15:00 | 15 | 1016 | 1337 | 372 | 1 | 9 | 1 | 1 | 9 | 371 | 1 | 13 | 42700 | 1 | 9 | 100 | 1 | 9 | 42600 | 1 | 13 | 15360 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 2130 | A | 7 | 3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.14 | 6 | 0
1979-08-25 | 1900-08-24 | 16:00 | 16 | 846 | 1337 | 295 | 1 | 9 | 0 | 1 | 9 | 295 | 1 | 13 | 33600 | 1 | 9 | 0 | 1 | 9 | 33600 | 1 | 13 | 11870 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 1980 | A | 7 | 3.1 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.74 | 6 | 0
1979-08-25 | 1900-08-24 | 17:00 | 17 | 630 | 1337 | 219 | 1 | 9 | 1 | 1 | 9 | 218 | 1 | 13 | 24500 | 1 | 9 | 100 | 1 | 9 | 24400 | 1 | 13 | 8060 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 6 | 0
1979-08-25 | 1900-08-24 | 18:00 | 18 | 382 | 1337 | 106 | 1 | 9 | 51 | 1 | 9 | 91 | 1 | 13 | 11600 | 1 | 9 | 4600 | 1 | 9 | 10300 | 1 | 13 | 2470 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.68 | A | 7 | 979 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 2.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.68 | 6 | 0
1979-08-25 | 1900-08-24 | 19:00 | 19 | 122 | 1326 | 34 | 1 | 13 | 7 | 1 | 9 | 34 | 1 | 13 | 3800 | 1 | 13 | 0 | 1 | 9 | 3800 | 1 | 13 | 1090 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 6 | 0
1979-08-25 | 1900-08-24 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.16 | 6 | 0
1979-08-25 | 1900-08-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 20.6 | 69.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.76 | A | 7 | 979 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.28 | 6 | 0
1979-08-25 | 1900-08-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | 20.6 | 69.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.88 | 6 | 0
1979-08-25 | 1900-08-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.68 | 6 | 0
1979-08-25 | 1900-08-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 19.4 | 66.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.28 | 6 | 0
1979-08-26 | 1900-08-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.98 | 7 | 0
1979-08-26 | 1900-08-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 7 | 0
1979-08-26 | 1900-08-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 7 | 0
1979-08-26 | 1900-08-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 979 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 7 | 0
1979-08-26 | 1900-08-25 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.58 | 7 | 0
1979-08-26 | 1900-08-25 | 6:00 | 6 | 10 | 390 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 1980 | A | 7 | 2.7 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.58 | 7 | 0
1979-08-26 | 1900-08-25 | 7:00 | 7 | 198 | 1338 | 36 | 1 | 13 | 14 | 1 | 9 | 34 | 1 | 13 | 4000 | 1 | 13 | 1000 | 1 | 9 | 3800 | 1 | 13 | 890 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 1980 | A | 7 | 2.8 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 7 | 0
1979-08-26 | 1900-08-25 | 8:00 | 8 | 457 | 1338 | 145 | 1 | 9 | 65 | 1 | 9 | 123 | 1 | 13 | 15900 | 1 | 9 | 6100 | 1 | 9 | 13900 | 1 | 13 | 3390 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 20.6 | 69.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.84 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 3200 | A | 7 | 3660 | A | 7 | 3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.84 | 7 | 0
1979-08-26 | 1900-08-25 | 9:00 | 9 | 697 | 1338 | 105 | 1 | 9 | 9 | 1 | 9 | 100 | 1 | 13 | 12600 | 1 | 9 | 600 | 1 | 9 | 12300 | 1 | 13 | 4710 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.84 | A | 7 | 979 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 2400 | A | 7 | 210 | A | 7 | 3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.84 | 7 | 0
1979-08-26 | 1900-08-25 | 10:00 | 10 | 901 | 1338 | 128 | 1 | 9 | 4 | 1 | 9 | 126 | 1 | 13 | 15800 | 1 | 9 | 300 | 1 | 9 | 15600 | 1 | 13 | 6330 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 3660 | A | 7 | 2.9 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.36 | 7 | 0
1979-08-26 | 1900-08-25 | 11:00 | 11 | 1053 | 1338 | 178 | 1 | 9 | 0 | 1 | 9 | 178 | 1 | 13 | 21800 | 1 | 9 | 0 | 1 | 9 | 21800 | 1 | 13 | 8970 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 17.8 | 64.04 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 3200 | A | 7 | 1400 | A | 7 | 3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.44 | 7 | 0
1979-08-26 | 1900-08-25 | 12:00 | 12 | 1144 | 1338 | 290 | 1 | 9 | 68 | 1 | 9 | 232 | 1 | 13 | 33000 | 1 | 9 | 7300 | 1 | 9 | 26700 | 1 | 13 | 9540 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 3660 | A | 7 | 3.1 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.74 | 7 | 0
1979-08-26 | 1900-08-25 | 13:00 | 13 | 1168 | 1338 | 788 | 1 | 13 | 575 | 1 | 13 | 283 | 1 | 13 | 85500 | 1 | 13 | 60200 | 1 | 13 | 32800 | 1 | 13 | 13410 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.54 | 7 | 0
1979-08-26 | 1900-08-25 | 14:00 | 14 | 1123 | 1338 | 631 | 1 | 9 | 343 | 1 | 9 | 341 | 1 | 13 | 69200 | 1 | 9 | 37300 | 1 | 9 | 37800 | 1 | 13 | 13360 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 3.3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.62 | 7 | 0
1979-08-26 | 1900-08-25 | 15:00 | 15 | 1011 | 1338 | 437 | 1 | 9 | 181 | 1 | 9 | 299 | 1 | 13 | 48300 | 1 | 9 | 19300 | 1 | 9 | 33700 | 1 | 13 | 9870 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 976 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 400 | A | 7 | 3.3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.52 | 7 | 0
1979-08-26 | 1900-08-25 | 16:00 | 16 | 841 | 1338 | 411 | 1 | 13 | 226 | 1 | 13 | 268 | 1 | 13 | 45000 | 1 | 13 | 23800 | 1 | 13 | 30000 | 1 | 13 | 7460 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 26.7 | 80.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.82 | 7 | 0
1979-08-26 | 1900-08-25 | 17:00 | 17 | 625 | 1338 | 338 | 1 | 13 | 324 | 1 | 13 | 185 | 1 | 13 | 36000 | 1 | 13 | 33200 | 1 | 13 | 20500 | 1 | 13 | 4060 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 26.7 | 80.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.82 | 7 | 0
1979-08-26 | 1900-08-25 | 18:00 | 18 | 376 | 1338 | 192 | 1 | 13 | 266 | 1 | 13 | 116 | 1 | 13 | 20100 | 1 | 13 | 23400 | 1 | 13 | 13500 | 1 | 13 | 2340 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 976 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.52 | 7 | 0
1979-08-26 | 1900-08-25 | 19:00 | 19 | 116 | 1282 | 36 | 1 | 13 | 11 | 1 | 13 | 35 | 1 | 13 | 3900 | 1 | 13 | 700 | 1 | 13 | 3900 | 1 | 13 | 820 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 23.9 | 75.02 | A | 7 | 20 | 68 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 610 | A | 7 | 3.5 | E | 8 | 0.112 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.5 | 7 | 0
1979-08-26 | 1900-08-25 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 22.8 | 73.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.94 | 7 | 0
1979-08-26 | 1900-08-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.74 | 7 | 0
1979-08-26 | 1900-08-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 7 | 0
1979-08-26 | 1900-08-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 270 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 7 | 0
1979-08-26 | 1900-08-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.58 | 7 | 0
1979-08-27 | 1900-08-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 15 | 59 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.6 | 1 | 0
1979-08-27 | 1900-08-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 15.6 | 60.08 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.18 | 1 | 0
1979-08-27 | 1900-08-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 1 | 0
1979-08-27 | 1900-08-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 1 | 0
1979-08-27 | 1900-08-26 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 15 | 59 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.1 | 1 | 0
1979-08-27 | 1900-08-26 | 6:00 | 6 | 9 | 368 | 3 | 1 | 13 | 0 | 1 | 13 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 16.7 | 62.06 | A | 7 | 15 | 59 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.1 | 1 | 0
1979-08-27 | 1900-08-26 | 7:00 | 7 | 195 | 1338 | 39 | 1 | 13 | 12 | 1 | 13 | 37 | 1 | 13 | 4300 | 1 | 13 | 900 | 1 | 13 | 4100 | 1 | 13 | 950 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 1 | 0
1979-08-27 | 1900-08-26 | 8:00 | 8 | 454 | 1338 | 200 | 1 | 13 | 203 | 1 | 13 | 131 | 1 | 13 | 21200 | 1 | 13 | 19100 | 1 | 13 | 14700 | 1 | 13 | 2660 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.68 | 1 | 0
1979-08-27 | 1900-08-26 | 9:00 | 9 | 694 | 1338 | 338 | 1 | 13 | 149 | 1 | 13 | 261 | 1 | 13 | 36600 | 1 | 13 | 15300 | 1 | 13 | 28600 | 1 | 13 | 6590 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 260 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.86 | 1 | 0
1979-08-27 | 1900-08-26 | 10:00 | 10 | 898 | 1338 | 451 | 1 | 13 | 176 | 1 | 13 | 332 | 1 | 13 | 49000 | 1 | 13 | 18500 | 1 | 13 | 36500 | 1 | 13 | 9690 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 22.2 | 71.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.26 | 1 | 0
1979-08-27 | 1900-08-26 | 11:00 | 11 | 1050 | 1338 | 560 | 1 | 13 | 247 | 1 | 13 | 365 | 1 | 13 | 60600 | 1 | 13 | 26700 | 1 | 13 | 39500 | 1 | 13 | 12550 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 23.3 | 73.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.16 | 1 | 0
1979-08-27 | 1900-08-26 | 12:00 | 12 | 1141 | 1338 | 787 | 1 | 13 | 507 | 1 | 13 | 353 | 1 | 13 | 83300 | 1 | 13 | 52800 | 1 | 13 | 38100 | 1 | 13 | 15530 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 24.4 | 75.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 110 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.98 | 1 | 0
1979-08-27 | 1900-08-26 | 13:00 | 13 | 1165 | 1338 | 830 | 1 | 13 | 573 | 1 | 13 | 329 | 1 | 13 | 88700 | 1 | 13 | 59800 | 1 | 13 | 36500 | 1 | 13 | 15500 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.46 | 1 | 0
1979-08-27 | 1900-08-26 | 14:00 | 14 | 1119 | 1338 | 407 | 1 | 13 | 140 | 1 | 13 | 289 | 1 | 13 | 45500 | 1 | 13 | 15000 | 1 | 13 | 32900 | 1 | 13 | 11280 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 26.1 | 78.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 1 | 0
1979-08-27 | 1900-08-26 | 15:00 | 15 | 1007 | 1338 | 381 | 1 | 9 | 53 | 1 | 9 | 341 | 1 | 13 | 42000 | 1 | 9 | 5400 | 1 | 9 | 37900 | 1 | 13 | 12780 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 26.1 | 78.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 1 | 0
1979-08-27 | 1900-08-26 | 16:00 | 16 | 837 | 1338 | 226 | 1 | 9 | 1 | 1 | 9 | 225 | 1 | 13 | 26200 | 1 | 9 | 100 | 1 | 9 | 26100 | 1 | 13 | 9810 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 25.6 | 78.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 3 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.66 | 1 | 0
1979-08-27 | 1900-08-26 | 17:00 | 17 | 619 | 1338 | 138 | 1 | 9 | 1 | 1 | 9 | 137 | 1 | 13 | 15900 | 1 | 9 | 100 | 1 | 9 | 15900 | 1 | 13 | 5800 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 24.4 | 75.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.66 | A | 7 | 977 | A | 7 | 30 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 3 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.94 | 1 | 0
1979-08-27 | 1900-08-26 | 18:00 | 18 | 370 | 1338 | 65 | 1 | 9 | 1 | 1 | 9 | 64 | 1 | 13 | 7500 | 1 | 9 | 0 | 1 | 9 | 7500 | 1 | 13 | 2560 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.69 | A | 7 | 977 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 3 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 1 | 0
1979-08-27 | 1900-08-26 | 19:00 | 19 | 110 | 1260 | 37 | 1 | 13 | 0 | 1 | 9 | 37 | 1 | 13 | 4100 | 1 | 13 | 0 | 1 | 9 | 4100 | 1 | 13 | 1130 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 22.2 | 71.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.9 | E | 8 | 0.249 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.46 | 1 | 0
1979-08-27 | 1900-08-26 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.16 | 1 | 0
1979-08-27 | 1900-08-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.76 | 1 | 0
1979-08-27 | 1900-08-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 1 | 0
1979-08-27 | 1900-08-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 977 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 1 | 0
1979-08-27 | 1900-08-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 977 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 6100 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 1 | 0
1979-08-28 | 1900-08-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 2 | 0
1979-08-28 | 1900-08-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.98 | 2 | 0
1979-08-28 | 1900-08-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.98 | 2 | 0
1979-08-28 | 1900-08-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 2 | 0
1979-08-28 | 1900-08-27 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 2 | 0
1979-08-28 | 1900-08-27 | 6:00 | 6 | 8 | 346 | 2 | 1 | 13 | 4 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 2 | 0
1979-08-28 | 1900-08-27 | 7:00 | 7 | 191 | 1339 | 80 | 1 | 13 | 270 | 1 | 9 | 41 | 1 | 13 | 8400 | 1 | 13 | 17100 | 1 | 9 | 5900 | 1 | 13 | 730 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.56 | 2 | 0
1979-08-28 | 1900-08-27 | 8:00 | 8 | 451 | 1339 | 259 | 1 | 9 | 551 | 1 | 9 | 72 | 1 | 13 | 27000 | 1 | 9 | 50500 | 1 | 9 | 9900 | 1 | 13 | 1400 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.64 | 2 | 0
1979-08-28 | 1900-08-27 | 9:00 | 9 | 691 | 1339 | 373 | 1 | 13 | 359 | 1 | 13 | 187 | 1 | 13 | 40300 | 1 | 13 | 37500 | 1 | 13 | 20900 | 1 | 13 | 4180 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 3.3 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 2 | 0
1979-08-28 | 1900-08-27 | 10:00 | 10 | 895 | 1339 | 525 | 1 | 13 | 544 | 1 | 13 | 160 | 1 | 13 | 55400 | 1 | 13 | 55100 | 1 | 13 | 18500 | 1 | 13 | 4220 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 974 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.62 | 2 | 0
1979-08-28 | 1900-08-27 | 11:00 | 11 | 1047 | 1339 | 729 | 1 | 9 | 718 | 1 | 9 | 165 | 1 | 13 | 78100 | 1 | 9 | 73700 | 1 | 9 | 20400 | 1 | 13 | 5690 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 973 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.7 | 2 | 0
1979-08-28 | 1900-08-27 | 12:00 | 12 | 1138 | 1339 | 803 | 1 | 9 | 711 | 1 | 9 | 197 | 1 | 13 | 85900 | 1 | 9 | 72800 | 1 | 9 | 23900 | 1 | 13 | 8430 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 27.8 | 82.04 | A | 7 | 20 | 68 | A | 7 | 0.63 | A | 7 | 973 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.7 | 2 | 0
1979-08-28 | 1900-08-27 | 13:00 | 13 | 1161 | 1339 | 880 | 1 | 9 | 844 | 1 | 9 | 144 | 1 | 13 | 93800 | 1 | 9 | 85600 | 1 | 9 | 19400 | 1 | 13 | 6290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.57 | A | 7 | 972 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 2 | 0
1979-08-28 | 1900-08-27 | 14:00 | 14 | 1115 | 1339 | 841 | 1 | 9 | 838 | 1 | 9 | 140 | 1 | 13 | 89500 | 1 | 9 | 84900 | 1 | 9 | 18600 | 1 | 13 | 5340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 20.6 | 69.08 | A | 7 | 0.57 | A | 7 | 971 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.18 | 2 | 0
1979-08-28 | 1900-08-27 | 15:00 | 15 | 1002 | 1339 | 693 | 1 | 9 | 690 | 1 | 9 | 173 | 1 | 13 | 73500 | 1 | 9 | 70400 | 1 | 9 | 20700 | 1 | 13 | 5420 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 970 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 2 | 0
1979-08-28 | 1900-08-27 | 16:00 | 16 | 832 | 1339 | 564 | 1 | 13 | 629 | 1 | 13 | 170 | 1 | 13 | 58600 | 1 | 13 | 63000 | 1 | 13 | 19400 | 1 | 13 | 4070 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 970 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 2 | 0
1979-08-28 | 1900-08-27 | 17:00 | 17 | 614 | 1339 | 339 | 1 | 13 | 357 | 1 | 13 | 173 | 1 | 13 | 36200 | 1 | 13 | 36400 | 1 | 13 | 19400 | 1 | 13 | 3730 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 969 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 2 | 0
1979-08-28 | 1900-08-27 | 18:00 | 18 | 364 | 1339 | 174 | 1 | 13 | 290 | 1 | 13 | 93 | 1 | 13 | 17900 | 1 | 13 | 24700 | 1 | 13 | 11100 | 1 | 13 | 1730 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 30 | 86 | A | 7 | 21.7 | 71.06 | A | 7 | 0.61 | A | 7 | 969 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.96 | 2 | 0
1979-08-28 | 1900-08-27 | 19:00 | 19 | 104 | 1239 | 34 | 1 | 13 | 72 | 1 | 13 | 26 | 1 | 13 | 3500 | 1 | 13 | 3200 | 1 | 13 | 3200 | 1 | 13 | 460 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 968 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 2 | 0
1979-08-28 | 1900-08-27 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 969 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 2 | 0
1979-08-28 | 1900-08-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 27.8 | 82.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.67 | A | 7 | 969 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.48 | 2 | 0
1979-08-28 | 1900-08-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 969 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.98 | 2 | 0
1979-08-28 | 1900-08-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 969 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.98 | 2 | 0
1979-08-28 | 1900-08-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 27.2 | 80.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.67 | A | 7 | 969 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.68 | 2 | 0
1979-08-29 | 1900-08-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 15 | 59 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 60 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.2 | 3 | 0
1979-08-29 | 1900-08-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.79 | A | 7 | 972 | A | 7 | 30 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.86 | 3 | 0
1979-08-29 | 1900-08-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 3200 | A | 7 | 310 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.68 | 3 | 0
1979-08-29 | 1900-08-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 340 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 3 | 0
1979-08-29 | 1900-08-28 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 150 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 3 | 0
1979-08-29 | 1900-08-28 | 6:00 | 6 | 7 | 324 | 1 | 1 | 13 | 0 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 972 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 2.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 3 | 0
1979-08-29 | 1900-08-28 | 7:00 | 7 | 187 | 1340 | 34 | 1 | 13 | 5 | 1 | 9 | 33 | 1 | 13 | 3900 | 1 | 13 | 0 | 1 | 9 | 3900 | 1 | 13 | 1210 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 2.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 3 | 0
1979-08-29 | 1900-08-28 | 8:00 | 8 | 447 | 1340 | 107 | 1 | 9 | 5 | 1 | 9 | 105 | 1 | 13 | 12200 | 1 | 9 | 300 | 1 | 9 | 12100 | 1 | 13 | 4060 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 2.9 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.96 | 3 | 0
1979-08-29 | 1900-08-28 | 9:00 | 9 | 688 | 1340 | 176 | 1 | 9 | 6 | 1 | 9 | 173 | 1 | 13 | 20300 | 1 | 9 | 500 | 1 | 9 | 20100 | 1 | 13 | 7280 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 976 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 270 | A | 7 | 2.8 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 3 | 0
1979-08-29 | 1900-08-28 | 10:00 | 10 | 891 | 1340 | 472 | 1 | 13 | 387 | 1 | 13 | 214 | 1 | 13 | 50700 | 1 | 13 | 40000 | 1 | 13 | 24000 | 1 | 13 | 5580 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.76 | 3 | 0
1979-08-29 | 1900-08-28 | 11:00 | 11 | 1044 | 1340 | 657 | 1 | 13 | 514 | 1 | 13 | 255 | 1 | 13 | 70900 | 1 | 13 | 53600 | 1 | 13 | 29000 | 1 | 13 | 8630 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.74 | A | 7 | 976 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.74 | 3 | 0
1979-08-29 | 1900-08-28 | 12:00 | 12 | 1134 | 1340 | 739 | 1 | 13 | 495 | 1 | 13 | 318 | 1 | 13 | 78900 | 1 | 13 | 51700 | 1 | 13 | 35100 | 1 | 13 | 13600 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 976 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.1 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.24 | 3 | 0
1979-08-29 | 1900-08-28 | 13:00 | 13 | 1157 | 1340 | 757 | 1 | 13 | 550 | 1 | 13 | 279 | 1 | 13 | 82100 | 1 | 13 | 57600 | 1 | 13 | 32200 | 1 | 13 | 12690 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 26.7 | 80.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.82 | 3 | 0
1979-08-29 | 1900-08-28 | 14:00 | 14 | 1111 | 1340 | 785 | 1 | 13 | 709 | 1 | 13 | 194 | 1 | 13 | 83700 | 1 | 13 | 72500 | 1 | 13 | 23400 | 1 | 13 | 7690 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 27.8 | 82.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.32 | 3 | 0
1979-08-29 | 1900-08-28 | 15:00 | 15 | 998 | 1340 | 637 | 1 | 9 | 629 | 1 | 9 | 165 | 1 | 13 | 67700 | 1 | 9 | 64300 | 1 | 9 | 19700 | 1 | 13 | 5150 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 20 | 68 | A | 7 | 0.59 | A | 7 | 976 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.8 | 3 | 0
1979-08-29 | 1900-08-28 | 16:00 | 16 | 827 | 1340 | 543 | 1 | 9 | 646 | 1 | 9 | 141 | 1 | 13 | 57100 | 1 | 9 | 65200 | 1 | 9 | 16800 | 1 | 13 | 3450 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 3 | 0
1979-08-29 | 1900-08-28 | 17:00 | 17 | 608 | 1340 | 382 | 1 | 9 | 578 | 1 | 9 | 116 | 1 | 13 | 39400 | 1 | 9 | 55900 | 1 | 9 | 13900 | 1 | 13 | 2340 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 3 | 0
1979-08-29 | 1900-08-28 | 18:00 | 18 | 358 | 1340 | 195 | 1 | 9 | 532 | 1 | 9 | 50 | 1 | 13 | 20300 | 1 | 9 | 45900 | 1 | 9 | 8000 | 1 | 13 | 960 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 976 | A | 7 | 70 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 3 | 0
1979-08-29 | 1900-08-28 | 19:00 | 19 | 99 | 1195 | 45 | 1 | 13 | 167 | 1 | 9 | 27 | 1 | 13 | 4300 | 1 | 13 | 7900 | 1 | 9 | 3700 | 1 | 13 | 480 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 26.1 | 78.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.74 | A | 7 | 976 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.18 | 3 | 0
1979-08-29 | 1900-08-28 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.48 | 3 | 0
1979-08-29 | 1900-08-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.18 | 3 | 0
1979-08-29 | 1900-08-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 3 | 0
1979-08-29 | 1900-08-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 3 | 0
1979-08-29 | 1900-08-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 3 | 0
1979-08-30 | 1900-08-29 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 4 | 0
1979-08-30 | 1900-08-29 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 4 | 0
1979-08-30 | 1900-08-29 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 20 | 68 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 1490 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.6 | 4 | 0
1979-08-30 | 1900-08-29 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | 22.8 | 73.04 | A | 7 | 20 | 68 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.6 | 4 | 0
1979-08-30 | 1900-08-29 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 20 | 68 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.6 | 4 | 0
1979-08-30 | 1900-08-29 | 6:00 | 6 | 6 | 302 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 22.8 | 73.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 140 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 3.6 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.28 | 4 | 0
1979-08-30 | 1900-08-29 | 7:00 | 7 | 184 | 1340 | 60 | 1 | 13 | 35 | 1 | 13 | 55 | 1 | 13 | 6500 | 1 | 13 | 2500 | 1 | 13 | 6200 | 1 | 13 | 1290 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 22.8 | 73.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 3.6 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.28 | 4 | 0
1979-08-30 | 1900-08-29 | 8:00 | 8 | 444 | 1340 | 154 | 1 | 13 | 93 | 1 | 13 | 124 | 1 | 13 | 16900 | 1 | 13 | 8700 | 1 | 13 | 14000 | 1 | 13 | 2810 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 3.5 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.1 | 4 | 0
1979-08-30 | 1900-08-29 | 9:00 | 9 | 685 | 1340 | 337 | 1 | 13 | 315 | 1 | 13 | 175 | 1 | 13 | 36500 | 1 | 13 | 32800 | 1 | 13 | 19700 | 1 | 13 | 3860 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 25.6 | 78.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.6 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.28 | 4 | 0
1979-08-30 | 1900-08-29 | 10:00 | 10 | 888 | 1340 | 634 | 1 | 13 | 675 | 1 | 13 | 184 | 1 | 13 | 66100 | 1 | 13 | 67800 | 1 | 13 | 21000 | 1 | 13 | 4710 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 28.3 | 82.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.8 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.46 | 4 | 0
1979-08-30 | 1900-08-29 | 11:00 | 11 | 1041 | 1340 | 643 | 1 | 13 | 542 | 1 | 13 | 220 | 1 | 13 | 67400 | 1 | 13 | 54800 | 1 | 13 | 24800 | 1 | 13 | 7250 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 29.4 | 84.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.76 | 4 | 0
1979-08-30 | 1900-08-29 | 12:00 | 12 | 1131 | 1340 | 780 | 1 | 13 | 792 | 1 | 13 | 107 | 1 | 13 | 80300 | 1 | 13 | 79400 | 1 | 13 | 13200 | 1 | 13 | 3780 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 30.6 | 87.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.66 | 4 | 0
1979-08-30 | 1900-08-29 | 13:00 | 13 | 1154 | 1340 | 775 | 1 | 13 | 639 | 1 | 13 | 221 | 1 | 13 | 82100 | 1 | 13 | 65200 | 1 | 13 | 25900 | 1 | 13 | 9810 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 31.1 | 87.98 | A | 7 | 22.8 | 73.04 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 210 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.64 | 4 | 0
1979-08-30 | 1900-08-29 | 14:00 | 14 | 1107 | 1340 | 657 | 1 | 13 | 528 | 1 | 13 | 218 | 1 | 13 | 69400 | 1 | 13 | 53700 | 1 | 13 | 24900 | 1 | 13 | 8450 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 31.7 | 89.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.66 | 4 | 0
1979-08-30 | 1900-08-29 | 15:00 | 15 | 993 | 1340 | 610 | 1 | 13 | 537 | 1 | 13 | 210 | 1 | 13 | 63800 | 1 | 13 | 54200 | 1 | 13 | 23600 | 1 | 13 | 6310 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 32.2 | 89.96 | A | 7 | 22.2 | 71.96 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.36 | 4 | 0
1979-08-30 | 1900-08-29 | 16:00 | 16 | 821 | 1340 | 551 | 1 | 9 | 717 | 1 | 9 | 107 | 1 | 13 | 57500 | 1 | 9 | 71600 | 1 | 9 | 13600 | 1 | 13 | 2520 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 32.2 | 89.96 | A | 7 | 22.8 | 73.04 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.54 | 4 | 0
1979-08-30 | 1900-08-29 | 17:00 | 17 | 603 | 1340 | 394 | 1 | 9 | 685 | 1 | 9 | 82 | 1 | 13 | 41600 | 1 | 9 | 67100 | 1 | 9 | 11300 | 1 | 13 | 1730 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.7 | 89.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.36 | 4 | 0
1979-08-30 | 1900-08-29 | 18:00 | 18 | 352 | 1340 | 194 | 1 | 9 | 513 | 1 | 9 | 56 | 1 | 13 | 19900 | 1 | 9 | 43700 | 1 | 9 | 8400 | 1 | 13 | 1060 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30.6 | 87.08 | A | 7 | 21.7 | 71.06 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.36 | 4 | 0
1979-08-30 | 1900-08-29 | 19:00 | 19 | 93 | 1150 | 41 | 1 | 13 | 149 | 1 | 9 | 26 | 1 | 13 | 4000 | 1 | 13 | 6900 | 1 | 9 | 3500 | 1 | 13 | 460 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.109 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.96 | 4 | 0
1979-08-30 | 1900-08-29 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.16 | 4 | 0
1979-08-30 | 1900-08-29 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 4 | 0
1979-08-30 | 1900-08-29 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.86 | 4 | 0
1979-08-30 | 1900-08-29 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.88 | 4 | 0
1979-08-30 | 1900-08-29 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.88 | 4 | 0
1979-08-31 | 1900-08-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 21.7 | 71.06 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.06 | 5 | 0
1979-08-31 | 1900-08-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 5 | 0
1979-08-31 | 1900-08-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.68 | 5 | 0
1979-08-31 | 1900-08-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.08 | 5 | 0
1979-08-31 | 1900-08-30 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.08 | 5 | 0
1979-08-31 | 1900-08-30 | 6:00 | 6 | 5 | 279 | 5 | 1 | 13 | 15 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 5 | 0
1979-08-31 | 1900-08-30 | 7:00 | 7 | 180 | 1341 | 81 | 1 | 13 | 376 | 1 | 9 | 31 | 1 | 13 | 8400 | 1 | 13 | 24400 | 1 | 9 | 5100 | 1 | 13 | 570 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.08 | 5 | 0
1979-08-31 | 1900-08-30 | 8:00 | 8 | 441 | 1341 | 231 | 1 | 9 | 506 | 1 | 9 | 64 | 1 | 13 | 24300 | 1 | 9 | 46200 | 1 | 9 | 9000 | 1 | 13 | 1250 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.77 | A | 7 | 978 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.88 | 5 | 0
1979-08-31 | 1900-08-30 | 9:00 | 9 | 682 | 1341 | 278 | 1 | 13 | 259 | 1 | 13 | 146 | 1 | 13 | 30600 | 1 | 13 | 27000 | 1 | 13 | 16800 | 1 | 13 | 3120 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 27.2 | 80.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.66 | 5 | 0
1979-08-31 | 1900-08-30 | 10:00 | 10 | 885 | 1341 | 596 | 1 | 9 | 693 | 1 | 9 | 136 | 1 | 13 | 63500 | 1 | 9 | 70600 | 1 | 9 | 16800 | 1 | 13 | 3600 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.96 | 5 | 0
1979-08-31 | 1900-08-30 | 11:00 | 11 | 1037 | 1341 | 444 | 1 | 13 | 254 | 1 | 13 | 246 | 1 | 13 | 49300 | 1 | 13 | 27600 | 1 | 13 | 27900 | 1 | 13 | 7840 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 29.4 | 84.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 7620 | A | 7 | 3.9 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.76 | 5 | 0
1979-08-31 | 1900-08-30 | 12:00 | 12 | 1128 | 1341 | 474 | 1 | 9 | 209 | 1 | 9 | 298 | 1 | 13 | 52600 | 1 | 9 | 22700 | 1 | 9 | 33500 | 1 | 13 | 11570 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 30.6 | 87.08 | A | 7 | 22.8 | 73.04 | A | 7 | 0.63 | A | 7 | 977 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 910 | A | 7 | 4.1 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.14 | 5 | 0
1979-08-31 | 1900-08-30 | 13:00 | 13 | 1150 | 1341 | 632 | 1 | 9 | 355 | 1 | 9 | 326 | 1 | 13 | 69800 | 1 | 9 | 38600 | 1 | 9 | 36600 | 1 | 13 | 13480 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 31.1 | 87.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.59 | A | 7 | 976 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 910 | A | 7 | 3.9 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.16 | 5 | 0
1979-08-31 | 1900-08-30 | 14:00 | 14 | 1102 | 1341 | 608 | 1 | 9 | 397 | 1 | 9 | 280 | 1 | 13 | 65500 | 1 | 9 | 41500 | 1 | 9 | 31300 | 1 | 13 | 10880 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 31.1 | 87.98 | A | 7 | 21.7 | 71.06 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 910 | A | 7 | 3.8 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 5 | 0
1979-08-31 | 1900-08-30 | 15:00 | 15 | 989 | 1341 | 560 | 1 | 13 | 434 | 1 | 13 | 237 | 1 | 13 | 60200 | 1 | 13 | 45200 | 1 | 13 | 26800 | 1 | 13 | 7180 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 30.6 | 87.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.61 | A | 7 | 975 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 910 | A | 7 | 3.9 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.66 | 5 | 0
1979-08-31 | 1900-08-30 | 16:00 | 16 | 816 | 1341 | 374 | 1 | 13 | 228 | 1 | 13 | 234 | 1 | 13 | 40400 | 1 | 13 | 24300 | 1 | 13 | 25600 | 1 | 13 | 5800 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 30 | 86 | A | 7 | 21.1 | 69.98 | A | 7 | 0.59 | A | 7 | 974 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 910 | A | 7 | 3.7 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.48 | 5 | 0
1979-08-31 | 1900-08-30 | 17:00 | 17 | 597 | 1341 | 244 | 1 | 9 | 69 | 1 | 9 | 213 | 1 | 13 | 26700 | 1 | 9 | 6800 | 1 | 9 | 23700 | 1 | 13 | 5940 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 975 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 3.7 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.98 | 5 | 0
1979-08-31 | 1900-08-30 | 18:00 | 18 | 346 | 1341 | 80 | 1 | 9 | 19 | 1 | 9 | 75 | 1 | 13 | 8800 | 1 | 9 | 1700 | 1 | 9 | 8400 | 1 | 13 | 2030 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 27.8 | 82.04 | A | 7 | 20 | 68 | A | 7 | 0.63 | A | 7 | 975 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 3.5 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.7 | 5 | 0
1979-08-31 | 1900-08-30 | 19:00 | 19 | 88 | 1129 | 24 | 1 | 13 | 12 | 1 | 9 | 22 | 1 | 13 | 2500 | 1 | 13 | 700 | 1 | 9 | 2500 | 1 | 13 | 540 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 25.6 | 78.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | A | 7 | 975 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.66 | 5 | 0
1979-08-31 | 1900-08-30 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 23.3 | 73.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.69 | A | 7 | 974 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 5 | 0
1979-08-31 | 1900-08-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 22.8 | 73.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.86 | 5 | 0
1979-08-31 | 1900-08-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 4 | A | 7 | 22.3 | 72.14 | A | 7 | 16.8 | 62.24 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 120 | A | 7 | 5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.04 | 5 | 0
1979-08-31 | 1900-08-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 3 | A | 7 | 21.8 | 71.24 | A | 7 | 16.8 | 62.24 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 120 | A | 7 | 4.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.04 | 5 | 0
1979-08-31 | 1900-08-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 21.3 | 70.34 | A | 7 | 16.9 | 62.42 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 140 | A | 7 | 4.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.62 | 5 | 0
1980-09-01 | 1900-08-31 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20.9 | 69.62 | A | 7 | 17 | 62.6 | A | 7 | 0.84 | A | 7 | 972 | A | 7 | 130 | A | 7 | 4.3 | A | 7 | 9700 | A | 7 | 1220 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.4 | 6 | 0
1980-09-01 | 1900-08-31 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 20.4 | 68.72 | A | 7 | 17.1 | 62.78 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.58 | 6 | 0
1980-09-01 | 1900-08-31 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 19.9 | 67.82 | A | 7 | 17.1 | 62.78 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 60 | A | 7 | 3.8 | A | 7 | 12900 | A | 7 | 2440 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 6 | 0
1980-09-01 | 1900-08-31 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 610 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.36 | 6 | 0
1980-09-01 | 1900-08-31 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 12900 | A | 7 | 910 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.04 | 6 | 0
1980-09-01 | 1900-08-31 | 6:00 | 6 | 4 | 257 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1280 | A | 7 | 2.9 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.36 | 6 | 0
1980-09-01 | 1900-08-31 | 7:00 | 7 | 173 | 1342 | 21 | 1 | 13 | 11 | 1 | 9 | 20 | 1 | 13 | 2400 | 1 | 13 | 800 | 1 | 9 | 2300 | 1 | 13 | 540 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 1400 | A | 7 | 2.9 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.96 | 6 | 0
1980-09-01 | 1900-08-31 | 8:00 | 8 | 435 | 1342 | 176 | 1 | 9 | 81 | 1 | 9 | 150 | 1 | 13 | 19300 | 1 | 9 | 7600 | 1 | 9 | 16800 | 1 | 13 | 3850 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 2.9 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.36 | 6 | 0
1980-09-01 | 1900-08-31 | 9:00 | 9 | 676 | 1342 | 319 | 1 | 13 | 179 | 1 | 13 | 228 | 1 | 13 | 34600 | 1 | 13 | 18300 | 1 | 13 | 25300 | 1 | 13 | 5700 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 120 | A | 7 | 3.2 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.92 | 6 | 0
1980-09-01 | 1900-08-31 | 10:00 | 10 | 880 | 1342 | 419 | 1 | 9 | 227 | 1 | 9 | 269 | 1 | 13 | 45300 | 1 | 9 | 24300 | 1 | 9 | 29300 | 1 | 13 | 7160 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 22.2 | 71.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 180 | A | 7 | 3.3 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.22 | 6 | 0
1980-09-01 | 1900-08-31 | 11:00 | 11 | 1032 | 1342 | 764 | 1 | 13 | 684 | 1 | 13 | 236 | 1 | 13 | 79700 | 1 | 13 | 68900 | 1 | 13 | 26600 | 1 | 13 | 7530 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 25 | 77 | A | 7 | 20.6 | 69.08 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 140 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 3.6 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.78 | 6 | 0
1980-09-01 | 1900-08-31 | 12:00 | 12 | 1122 | 1342 | 788 | 1 | 13 | 637 | 1 | 13 | 253 | 1 | 13 | 82500 | 1 | 13 | 64300 | 1 | 13 | 28600 | 1 | 13 | 10020 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.74 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.18 | 6 | 0
1980-09-01 | 1900-08-31 | 13:00 | 13 | 1143 | 1342 | 280 | 1 | 9 | 3 | 1 | 9 | 277 | 1 | 13 | 33400 | 1 | 9 | 300 | 1 | 9 | 33200 | 1 | 13 | 13080 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 26.1 | 78.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.72 | A | 7 | 976 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 3.6 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.88 | 6 | 0
1980-09-01 | 1900-08-31 | 14:00 | 14 | 1095 | 1342 | 312 | 1 | 9 | 5 | 1 | 9 | 307 | 1 | 13 | 36700 | 1 | 9 | 400 | 1 | 9 | 36300 | 1 | 13 | 13970 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 26.1 | 78.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.74 | A | 7 | 976 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 880 | A | 7 | 3.7 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.18 | 6 | 0
1980-09-01 | 1900-08-31 | 15:00 | 15 | 980 | 1342 | 396 | 1 | 9 | 98 | 1 | 9 | 324 | 1 | 13 | 43600 | 1 | 9 | 10000 | 1 | 9 | 36300 | 1 | 13 | 11880 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 976 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 790 | A | 7 | 3.5 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.3 | 6 | 0
1980-09-01 | 1900-08-31 | 16:00 | 16 | 807 | 1342 | 496 | 1 | 13 | 480 | 1 | 13 | 205 | 1 | 13 | 52500 | 1 | 13 | 49200 | 1 | 13 | 22900 | 1 | 13 | 4850 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.74 | A | 7 | 976 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.28 | 6 | 0
1980-09-01 | 1900-08-31 | 17:00 | 17 | 587 | 1342 | 308 | 1 | 13 | 285 | 1 | 13 | 182 | 1 | 13 | 32600 | 1 | 13 | 28800 | 1 | 13 | 20000 | 1 | 13 | 3960 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.6 | 6 | 0
1980-09-01 | 1900-08-31 | 18:00 | 18 | 335 | 1342 | 176 | 1 | 13 | 405 | 1 | 13 | 73 | 1 | 13 | 18400 | 1 | 13 | 33500 | 1 | 13 | 10000 | 1 | 13 | 1330 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.6 | 6 | 0
1980-09-01 | 1900-08-31 | 19:00 | 19 | 79 | 1063 | 26 | 1 | 13 | 15 | 1 | 13 | 25 | 1 | 13 | 2900 | 1 | 13 | 900 | 1 | 13 | 2800 | 1 | 13 | 600 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 70 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 3.4 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 6 | 0
1980-09-01 | 1900-08-31 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 60 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.1 | 6 | 0
1980-09-01 | 1900-08-31 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.1 | 6 | 0
1980-09-01 | 1900-08-31 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 22.8 | 73.04 | A | 7 | 20 | 68 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.6 | 6 | 0
1980-09-01 | 1900-08-31 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | 21.7 | 71.06 | A | 7 | 20 | 68 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.9 | 6 | 0
1980-09-01 | 1900-08-31 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 21.1 | 69.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.82 | 6 | 0
1980-09-02 | 1900-09-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 20.6 | 69.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.92 | 7 | 0
1980-09-02 | 1900-09-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.04 | 7 | 0
1980-09-02 | 1900-09-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.96 | 7 | 0
1980-09-02 | 1900-09-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 17.8 | 64.04 | A | 7 | 16.1 | 60.98 | A | 7 | 0.9 | A | 7 | 980 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.08 | 7 | 0
1980-09-02 | 1900-09-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.48 | 7 | 0
1980-09-02 | 1900-09-01 | 6:00 | 6 | 3 | 235 | 1 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 17.2 | 62.96 | A | 7 | 15.6 | 60.08 | A | 7 | 0.9 | A | 7 | 981 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.18 | 7 | 0
1980-09-02 | 1900-09-01 | 7:00 | 7 | 170 | 1343 | 59 | 1 | 13 | 135 | 1 | 9 | 42 | 1 | 13 | 6300 | 1 | 13 | 7700 | 1 | 9 | 5300 | 1 | 13 | 770 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.93 | A | 7 | 982 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.78 | 7 | 0
1980-09-02 | 1900-09-01 | 8:00 | 8 | 431 | 1343 | 233 | 1 | 9 | 470 | 1 | 9 | 81 | 1 | 13 | 24000 | 1 | 9 | 42200 | 1 | 9 | 10400 | 1 | 13 | 1520 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.76 | 7 | 0
1980-09-02 | 1900-09-01 | 9:00 | 9 | 673 | 1343 | 428 | 1 | 9 | 608 | 1 | 9 | 122 | 1 | 13 | 44700 | 1 | 9 | 59800 | 1 | 9 | 14600 | 1 | 13 | 2580 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.76 | 7 | 0
1980-09-02 | 1900-09-01 | 10:00 | 10 | 876 | 1343 | 561 | 1 | 9 | 591 | 1 | 9 | 174 | 1 | 13 | 58700 | 1 | 9 | 59500 | 1 | 9 | 19800 | 1 | 13 | 4400 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.24 | 7 | 0
1980-09-02 | 1900-09-01 | 11:00 | 11 | 1028 | 1343 | 719 | 1 | 13 | 707 | 1 | 13 | 175 | 1 | 13 | 76500 | 1 | 13 | 72200 | 1 | 13 | 21100 | 1 | 13 | 5730 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.22 | 7 | 0
1980-09-02 | 1900-09-01 | 12:00 | 12 | 1118 | 1343 | 813 | 1 | 9 | 784 | 1 | 9 | 157 | 1 | 13 | 85400 | 1 | 9 | 79000 | 1 | 9 | 19500 | 1 | 13 | 5830 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 27.2 | 80.96 | A | 7 | 20 | 68 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.2 | 7 | 0
1980-09-02 | 1900-09-01 | 13:00 | 13 | 1139 | 1343 | 816 | 1 | 9 | 717 | 1 | 9 | 205 | 1 | 13 | 86900 | 1 | 9 | 73300 | 1 | 9 | 24600 | 1 | 13 | 8700 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 7 | 0
1980-09-02 | 1900-09-01 | 14:00 | 14 | 1091 | 1343 | 774 | 1 | 9 | 750 | 1 | 9 | 162 | 1 | 13 | 80800 | 1 | 9 | 75300 | 1 | 9 | 19400 | 1 | 13 | 5520 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 29.4 | 84.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.82 | 7 | 0
1980-09-02 | 1900-09-01 | 15:00 | 15 | 975 | 1343 | 679 | 1 | 9 | 770 | 1 | 9 | 116 | 1 | 13 | 72200 | 1 | 9 | 77900 | 1 | 9 | 15500 | 1 | 13 | 3370 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 29.4 | 84.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.55 | A | 7 | 980 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.82 | 7 | 0
1980-09-02 | 1900-09-01 | 16:00 | 16 | 801 | 1343 | 551 | 1 | 9 | 658 | 1 | 9 | 155 | 1 | 13 | 57400 | 1 | 9 | 65800 | 1 | 9 | 18000 | 1 | 13 | 3620 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 29.4 | 84.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.59 | A | 7 | 980 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.68 | 7 | 0
1980-09-02 | 1900-09-01 | 17:00 | 17 | 581 | 1343 | 353 | 1 | 9 | 605 | 1 | 9 | 88 | 1 | 13 | 37000 | 1 | 9 | 58600 | 1 | 9 | 11500 | 1 | 13 | 1810 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.98 | 7 | 0
1980-09-02 | 1900-09-01 | 18:00 | 18 | 329 | 1343 | 160 | 1 | 13 | 382 | 1 | 9 | 65 | 1 | 13 | 16900 | 1 | 13 | 31400 | 1 | 9 | 9200 | 1 | 13 | 1170 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.98 | 7 | 0
1980-09-02 | 1900-09-01 | 19:00 | 19 | 74 | 1041 | 29 | 1 | 13 | 67 | 1 | 9 | 22 | 1 | 13 | 2900 | 1 | 13 | 2600 | 1 | 9 | 2700 | 1 | 13 | 380 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.128 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 7 | 0
1980-09-02 | 1900-09-01 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 20 | 68 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.6 | 7 | 0
1980-09-02 | 1900-09-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 25 | 77 | A | 7 | 20 | 68 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.3 | 7 | 0
1980-09-02 | 1900-09-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.82 | 7 | 0
1980-09-02 | 1900-09-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 7 | 0
1980-09-02 | 1900-09-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.58 | 7 | 0
1980-09-03 | 1900-09-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 20 | 68 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.6 | 1 | 0
1980-09-03 | 1900-09-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 20 | 68 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.2 | 1 | 0
1980-09-03 | 1900-09-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.22 | 1 | 0
1980-09-03 | 1900-09-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 140 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.32 | 1 | 0
1980-09-03 | 1900-09-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.32 | 1 | 0
1980-09-03 | 1900-09-02 | 6:00 | 6 | 3 | 213 | 3 | 1 | 13 | 7 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.32 | 1 | 0
1980-09-03 | 1900-09-02 | 7:00 | 7 | 166 | 1344 | 71 | 1 | 13 | 329 | 1 | 9 | 31 | 1 | 13 | 7300 | 1 | 13 | 20400 | 1 | 9 | 4800 | 1 | 13 | 560 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.72 | 1 | 0
1980-09-03 | 1900-09-02 | 8:00 | 8 | 428 | 1344 | 254 | 1 | 9 | 625 | 1 | 9 | 54 | 1 | 13 | 26400 | 1 | 9 | 56700 | 1 | 9 | 8300 | 1 | 13 | 1100 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.82 | 1 | 0
1980-09-03 | 1900-09-02 | 9:00 | 9 | 669 | 1344 | 458 | 1 | 9 | 767 | 1 | 9 | 75 | 1 | 13 | 48600 | 1 | 9 | 75600 | 1 | 9 | 10900 | 1 | 13 | 1690 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 1 | 0
1980-09-03 | 1900-09-02 | 10:00 | 10 | 873 | 1344 | 634 | 1 | 9 | 834 | 1 | 9 | 90 | 1 | 13 | 65800 | 1 | 9 | 82800 | 1 | 9 | 11900 | 1 | 13 | 2110 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 20 | 68 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.7 | 1 | 0
1980-09-03 | 1900-09-02 | 11:00 | 11 | 1025 | 1344 | 762 | 1 | 9 | 864 | 1 | 9 | 101 | 1 | 13 | 78900 | 1 | 9 | 86400 | 1 | 9 | 12900 | 1 | 13 | 2840 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 1 | 0
1980-09-03 | 1900-09-02 | 12:00 | 12 | 1114 | 1344 | 843 | 1 | 9 | 885 | 1 | 9 | 107 | 1 | 13 | 87100 | 1 | 9 | 88700 | 1 | 9 | 13400 | 1 | 13 | 3590 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 21.7 | 71.06 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.96 | 1 | 0
1980-09-03 | 1900-09-02 | 13:00 | 13 | 1135 | 1344 | 819 | 1 | 9 | 847 | 1 | 9 | 101 | 1 | 13 | 84800 | 1 | 9 | 84900 | 1 | 9 | 12800 | 1 | 13 | 3670 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 30.6 | 87.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.98 | 1 | 0
1980-09-03 | 1900-09-02 | 14:00 | 14 | 1086 | 1344 | 768 | 1 | 9 | 788 | 1 | 9 | 128 | 1 | 13 | 82200 | 1 | 9 | 80000 | 1 | 9 | 17400 | 1 | 13 | 4570 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 977 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 1 | 0
1980-09-03 | 1900-09-02 | 15:00 | 15 | 970 | 1344 | 693 | 1 | 9 | 825 | 1 | 9 | 94 | 1 | 13 | 71800 | 1 | 9 | 82300 | 1 | 9 | 12200 | 1 | 13 | 2490 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 32.2 | 89.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.5 | A | 7 | 976 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.38 | 1 | 0
1980-09-03 | 1900-09-02 | 16:00 | 16 | 796 | 1344 | 532 | 1 | 13 | 650 | 1 | 13 | 144 | 1 | 13 | 55700 | 1 | 13 | 65200 | 1 | 13 | 17000 | 1 | 13 | 3370 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 32.2 | 89.96 | A | 7 | 20 | 68 | A | 7 | 0.48 | A | 7 | 976 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 1 | 0
1980-09-03 | 1900-09-02 | 17:00 | 17 | 575 | 1344 | 380 | 1 | 9 | 725 | 1 | 9 | 67 | 1 | 13 | 39800 | 1 | 9 | 69900 | 1 | 9 | 9900 | 1 | 13 | 1440 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.61 | A | 7 | 977 | A | 7 | 130 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 1 | 0
1980-09-03 | 1900-09-02 | 18:00 | 18 | 322 | 1344 | 179 | 1 | 13 | 547 | 1 | 9 | 46 | 1 | 13 | 18600 | 1 | 13 | 45400 | 1 | 9 | 7700 | 1 | 13 | 880 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 20 | 68 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.3 | 1 | 0
1980-09-03 | 1900-09-02 | 19:00 | 19 | 69 | 997 | 37 | 1 | 13 | 148 | 1 | 9 | 21 | 1 | 13 | 3400 | 1 | 13 | 6300 | 1 | 9 | 2900 | 1 | 13 | 370 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.63 | A | 7 | 976 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.82 | 1 | 0
1980-09-03 | 1900-09-02 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.65 | A | 7 | 976 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.22 | 1 | 0
1980-09-03 | 1900-09-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 1 | 0
1980-09-03 | 1900-09-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 1 | 0
1980-09-03 | 1900-09-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 1 | 0
1980-09-03 | 1900-09-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 1 | 0
1980-09-04 | 1900-09-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 2 | 0
1980-09-04 | 1900-09-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 3350 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.92 | 2 | 0
1980-09-04 | 1900-09-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 25 | 77 | A | 7 | 18.9 | 66.02 | A | 7 | 0.69 | A | 7 | 977 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.42 | 2 | 0
1980-09-04 | 1900-09-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 24.4 | 75.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.44 | 2 | 0
1980-09-04 | 1900-09-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.54 | 2 | 0
1980-09-04 | 1900-09-03 | 6:00 | 6 | 2 | 190 | 2 | 1 | 13 | 3 | 1 | 13 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 21.7 | 71.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.04 | 2 | 0
1980-09-04 | 1900-09-03 | 7:00 | 7 | 162 | 1344 | 50 | 1 | 13 | 5 | 1 | 13 | 49 | 1 | 13 | 5400 | 1 | 13 | 0 | 1 | 13 | 5400 | 1 | 13 | 1510 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 22.2 | 71.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.64 | 2 | 0
1980-09-04 | 1900-09-03 | 8:00 | 8 | 424 | 1344 | 205 | 1 | 13 | 353 | 1 | 13 | 93 | 1 | 13 | 21700 | 1 | 13 | 31800 | 1 | 13 | 11600 | 1 | 13 | 1730 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 24.4 | 75.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.32 | 2 | 0
1980-09-04 | 1900-09-03 | 9:00 | 9 | 666 | 1344 | 366 | 1 | 13 | 470 | 1 | 13 | 132 | 1 | 13 | 39500 | 1 | 13 | 47200 | 1 | 13 | 16100 | 1 | 13 | 2710 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 2 | 0
1980-09-04 | 1900-09-03 | 10:00 | 10 | 870 | 1344 | 518 | 1 | 13 | 536 | 1 | 13 | 170 | 1 | 13 | 54300 | 1 | 13 | 53900 | 1 | 13 | 19300 | 1 | 13 | 4270 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 30 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.2 | 2 | 0
1980-09-04 | 1900-09-03 | 11:00 | 11 | 1021 | 1344 | 248 | 1 | 9 | 108 | 1 | 9 | 165 | 1 | 13 | 28400 | 1 | 9 | 11600 | 1 | 9 | 19500 | 1 | 13 | 5480 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 26.7 | 80.06 | A | 7 | 21.1 | 69.98 | A | 7 | 0.72 | A | 7 | 983 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 3.7 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.68 | 2 | 0
1980-09-04 | 1900-09-03 | 12:00 | 12 | 1110 | 1344 | 661 | 1 | 13 | 449 | 1 | 13 | 288 | 1 | 13 | 71000 | 1 | 13 | 46900 | 1 | 13 | 32200 | 1 | 13 | 11360 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 27.2 | 80.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 40 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.98 | 2 | 0
1980-09-04 | 1900-09-03 | 13:00 | 13 | 1131 | 1344 | 647 | 1 | 9 | 425 | 1 | 9 | 287 | 1 | 13 | 69700 | 1 | 9 | 44400 | 1 | 9 | 32200 | 1 | 13 | 11960 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 28.3 | 82.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 3.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.46 | 2 | 0
1980-09-04 | 1900-09-03 | 14:00 | 14 | 1081 | 1344 | 424 | 1 | 9 | 200 | 1 | 9 | 263 | 1 | 13 | 47300 | 1 | 9 | 21800 | 1 | 9 | 29700 | 1 | 13 | 9090 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 982 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 3.7 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 2 | 0
1980-09-04 | 1900-09-03 | 15:00 | 15 | 965 | 1344 | 434 | 1 | 13 | 246 | 1 | 13 | 256 | 1 | 13 | 47600 | 1 | 13 | 26600 | 1 | 13 | 28500 | 1 | 13 | 7370 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 3.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 2 | 0
1980-09-04 | 1900-09-03 | 16:00 | 16 | 790 | 1344 | 535 | 1 | 9 | 771 | 1 | 9 | 78 | 1 | 13 | 55600 | 1 | 9 | 76100 | 1 | 9 | 10700 | 1 | 13 | 1820 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 28.9 | 84.02 | A | 7 | 21.7 | 71.06 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.96 | 2 | 0
1980-09-04 | 1900-09-03 | 17:00 | 17 | 569 | 1344 | 375 | 1 | 9 | 686 | 1 | 9 | 82 | 1 | 13 | 39500 | 1 | 9 | 66400 | 1 | 9 | 11300 | 1 | 13 | 1690 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 30 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.46 | 2 | 0
1980-09-04 | 1900-09-03 | 18:00 | 18 | 316 | 1344 | 135 | 1 | 13 | 278 | 1 | 13 | 68 | 1 | 13 | 14100 | 1 | 13 | 22400 | 1 | 13 | 8800 | 1 | 13 | 1230 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 27.8 | 82.04 | A | 7 | 21.7 | 71.06 | A | 7 | 0.69 | A | 7 | 981 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.96 | 2 | 0
1980-09-04 | 1900-09-03 | 19:00 | 19 | 64 | 975 | 37 | 1 | 13 | 164 | 1 | 9 | 19 | 1 | 13 | 3100 | 1 | 13 | 7800 | 1 | 9 | 2600 | 1 | 13 | 340 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 26.7 | 80.06 | A | 7 | 21.7 | 71.06 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.16 | 2 | 0
1980-09-04 | 1900-09-03 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 21.1 | 69.98 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.88 | 2 | 0
1980-09-04 | 1900-09-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 983 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 2 | 0
1980-09-04 | 1900-09-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.82 | A | 7 | 983 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.98 | 2 | 0
1980-09-04 | 1900-09-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.85 | A | 7 | 983 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.68 | 2 | 0
1980-09-04 | 1900-09-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.85 | A | 7 | 983 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 66.68 | 2 | 0
1980-09-05 | 1900-09-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 983 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.78 | 3 | 0
1980-09-05 | 1900-09-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.78 | 3 | 0
1980-09-05 | 1900-09-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 21.1 | 69.98 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.08 | 3 | 0
1980-09-05 | 1900-09-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.1 | 3 | 0
1980-09-05 | 1900-09-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 22.8 | 73.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.82 | A | 7 | 983 | A | 7 | 20 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.12 | 3 | 0
1980-09-05 | 1900-09-04 | 6:00 | 6 | 2 | 168 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.84 | A | 7 | 983 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 3350 | A | 7 | 3.4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.52 | 3 | 0
1980-09-05 | 1900-09-04 | 7:00 | 7 | 159 | 1345 | 45 | 1 | 13 | 20 | 1 | 9 | 43 | 1 | 13 | 5000 | 1 | 13 | 1400 | 1 | 9 | 4800 | 1 | 13 | 1020 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 20 | 68 | A | 7 | 0.87 | A | 7 | 984 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 3350 | A | 7 | 3.5 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.2 | 3 | 0
1980-09-05 | 1900-09-04 | 8:00 | 8 | 420 | 1345 | 168 | 1 | 13 | 133 | 1 | 13 | 126 | 1 | 13 | 18200 | 1 | 13 | 12300 | 1 | 13 | 14400 | 1 | 13 | 2830 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 23.3 | 73.94 | A | 7 | 20 | 68 | A | 7 | 0.82 | A | 7 | 985 | A | 7 | 90 | A | 7 | 6.7 | A | 7 | 9700 | A | 7 | 3660 | A | 7 | 3.5 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 64.1 | 3 | 0
1980-09-05 | 1900-09-04 | 9:00 | 9 | 662 | 1345 | 354 | 1 | 13 | 417 | 1 | 13 | 148 | 1 | 13 | 37800 | 1 | 13 | 41700 | 1 | 13 | 17200 | 1 | 13 | 3070 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 24.4 | 75.92 | A | 7 | 20 | 68 | A | 7 | 0.76 | A | 7 | 985 | A | 7 | 80 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.8 | 3 | 0
1980-09-05 | 1900-09-04 | 10:00 | 10 | 866 | 1345 | 603 | 1 | 9 | 733 | 1 | 9 | 129 | 1 | 13 | 64400 | 1 | 9 | 74600 | 1 | 9 | 16200 | 1 | 13 | 3340 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 985 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.24 | 3 | 0
1980-09-05 | 1900-09-04 | 11:00 | 11 | 1018 | 1345 | 726 | 1 | 9 | 758 | 1 | 9 | 150 | 1 | 13 | 75700 | 1 | 9 | 76000 | 1 | 9 | 18000 | 1 | 13 | 4360 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.67 | A | 7 | 984 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.68 | 3 | 0
1980-09-05 | 1900-09-04 | 12:00 | 12 | 1107 | 1345 | 817 | 1 | 9 | 795 | 1 | 9 | 159 | 1 | 13 | 85500 | 1 | 9 | 80000 | 1 | 9 | 19500 | 1 | 13 | 5670 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 21.7 | 71.06 | A | 7 | 0.61 | A | 7 | 984 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.96 | 3 | 0
1980-09-05 | 1900-09-04 | 13:00 | 13 | 1127 | 1345 | 838 | 1 | 9 | 804 | 1 | 9 | 161 | 1 | 13 | 87900 | 1 | 9 | 81000 | 1 | 9 | 19900 | 1 | 13 | 6070 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 22.2 | 71.96 | A | 7 | 0.63 | A | 7 | 983 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 63.26 | 3 | 0
1980-09-05 | 1900-09-04 | 14:00 | 14 | 1077 | 1345 | 796 | 1 | 9 | 794 | 1 | 9 | 156 | 1 | 13 | 83100 | 1 | 9 | 79800 | 1 | 9 | 19000 | 1 | 13 | 5160 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.7 | 89.06 | A | 7 | 22.2 | 71.96 | A | 7 | 0.57 | A | 7 | 983 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.66 | 3 | 0
1980-09-05 | 1900-09-04 | 15:00 | 15 | 960 | 1345 | 694 | 1 | 9 | 765 | 1 | 9 | 145 | 1 | 13 | 71900 | 1 | 9 | 76500 | 1 | 9 | 17200 | 1 | 13 | 3790 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 22.8 | 73.04 | A | 7 | 0.57 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.54 | 3 | 0
1980-09-05 | 1900-09-04 | 16:00 | 16 | 785 | 1345 | 538 | 1 | 9 | 703 | 1 | 9 | 125 | 1 | 13 | 56800 | 1 | 9 | 70800 | 1 | 9 | 15400 | 1 | 13 | 2940 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.8 | 91.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.86 | 3 | 0
1980-09-05 | 1900-09-04 | 17:00 | 17 | 562 | 1345 | 348 | 1 | 9 | 595 | 1 | 9 | 97 | 1 | 13 | 36200 | 1 | 9 | 57000 | 1 | 9 | 12300 | 1 | 13 | 1940 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.3 | 91.94 | A | 7 | 22.2 | 71.96 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.26 | 3 | 0
1980-09-05 | 1900-09-04 | 18:00 | 18 | 309 | 1345 | 142 | 1 | 13 | 339 | 1 | 9 | 63 | 1 | 13 | 15000 | 1 | 13 | 27100 | 1 | 9 | 8700 | 1 | 13 | 1130 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 32.2 | 89.96 | A | 7 | 22.8 | 73.04 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.54 | 3 | 0
1980-09-05 | 1900-09-04 | 19:00 | 19 | 60 | 930 | 27 | 1 | 13 | 45 | 1 | 9 | 22 | 1 | 13 | 2800 | 1 | 13 | 2000 | 1 | 9 | 2600 | 1 | 13 | 450 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 22.8 | 73.04 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4.1 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.24 | 3 | 0
1980-09-05 | 1900-09-04 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 22.2 | 71.96 | A | 7 | 0.72 | A | 7 | 982 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 65.46 | 3 | 0
1980-09-05 | 1900-09-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 22.2 | 71.96 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.16 | 3 | 0
1980-09-05 | 1900-09-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 22.2 | 71.96 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.86 | 3 | 0
1980-09-05 | 1900-09-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 22.2 | 71.96 | A | 7 | 0.85 | A | 7 | 982 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 68.56 | 3 | 0
1980-09-05 | 1900-09-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 22.2 | 71.96 | A | 7 | 0.87 | A | 7 | 982 | A | 7 | 100 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 69.06 | 3 | 0
1980-09-06 | 1900-09-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 21.1 | 69.98 | A | 7 | 0.9 | A | 7 | 982 | A | 7 | 180 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 67.78 | 4 | 0
1980-09-06 | 1900-09-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.62 | 4 | 0
1980-09-06 | 1900-09-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.04 | 4 | 0
1980-09-06 | 1900-09-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.14 | 4 | 0
1980-09-06 | 1900-09-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.14 | 4 | 0
1980-09-06 | 1900-09-05 | 6:00 | 6 | 1 | 146 | 1 | 1 | 13 | 0 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 170 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.74 | 4 | 0
1980-09-06 | 1900-09-05 | 7:00 | 7 | 155 | 1346 | 54 | 1 | 13 | 116 | 1 | 9 | 41 | 1 | 13 | 5700 | 1 | 13 | 6200 | 1 | 9 | 5000 | 1 | 13 | 760 | 1 | 21 | 7 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.76 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.94 | 4 | 0
1980-09-06 | 1900-09-05 | 8:00 | 8 | 417 | 1346 | 213 | 1 | 9 | 402 | 1 | 9 | 88 | 1 | 13 | 22600 | 1 | 9 | 36000 | 1 | 9 | 11400 | 1 | 13 | 1630 | 1 | 18 | 6 | A | 7 | 1 | A | 7 | 25.6 | 78.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.69 | A | 7 | 984 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.22 | 4 | 0
1980-09-06 | 1900-09-05 | 9:00 | 9 | 659 | 1346 | 431 | 1 | 9 | 608 | 1 | 9 | 132 | 1 | 13 | 44600 | 1 | 9 | 59300 | 1 | 9 | 15500 | 1 | 13 | 2720 | 1 | 18 | 5 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 20 | 68 | A | 7 | 0.63 | A | 7 | 984 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.7 | 4 | 0
1980-09-06 | 1900-09-05 | 10:00 | 10 | 863 | 1346 | 607 | 1 | 9 | 701 | 1 | 9 | 156 | 1 | 13 | 63900 | 1 | 9 | 70800 | 1 | 9 | 18400 | 1 | 13 | 3920 | 1 | 18 | 4 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 21.1 | 69.98 | A | 7 | 0.61 | A | 7 | 984 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.98 | 4 | 0
1980-09-06 | 1900-09-05 | 11:00 | 11 | 1014 | 1346 | 733 | 1 | 9 | 745 | 1 | 9 | 169 | 1 | 13 | 78100 | 1 | 9 | 76100 | 1 | 9 | 20600 | 1 | 13 | 5380 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 4 | 0
1980-09-06 | 1900-09-05 | 12:00 | 12 | 1103 | 1346 | 738 | 1 | 9 | 646 | 1 | 9 | 206 | 1 | 13 | 78300 | 1 | 9 | 65900 | 1 | 9 | 24100 | 1 | 13 | 7850 | 1 | 18 | 6 | A | 7 | 1 | A | 7 | 32.2 | 89.96 | A | 7 | 21.7 | 71.06 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.9 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.06 | 4 | 0
1980-09-06 | 1900-09-05 | 13:00 | 13 | 1123 | 1346 | 814 | 1 | 9 | 764 | 1 | 9 | 173 | 1 | 13 | 84600 | 1 | 9 | 76600 | 1 | 9 | 20500 | 1 | 13 | 6300 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 33.3 | 91.94 | A | 7 | 21.7 | 71.06 | A | 7 | 0.5 | A | 7 | 983 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.8 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 4 | 0
1980-09-06 | 1900-09-05 | 14:00 | 14 | 1072 | 1346 | 734 | 1 | 9 | 709 | 1 | 9 | 167 | 1 | 13 | 78800 | 1 | 9 | 72800 | 1 | 9 | 20700 | 1 | 13 | 6020 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 33.9 | 93.02 | A | 7 | 20 | 68 | A | 7 | 0.44 | A | 7 | 982 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 4 | 0
1980-09-06 | 1900-09-05 | 15:00 | 15 | 955 | 1346 | 651 | 1 | 9 | 695 | 1 | 9 | 154 | 1 | 13 | 69200 | 1 | 9 | 70900 | 1 | 9 | 18700 | 1 | 13 | 4450 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 34.4 | 93.92 | A | 7 | 20 | 68 | A | 7 | 0.43 | A | 7 | 982 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.7 | 4 | 0
1980-09-06 | 1900-09-05 | 16:00 | 16 | 779 | 1346 | 497 | 1 | 9 | 627 | 1 | 9 | 132 | 1 | 13 | 52300 | 1 | 9 | 62900 | 1 | 9 | 15800 | 1 | 13 | 3070 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 33.9 | 93.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.43 | A | 7 | 981 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.82 | 4 | 0
1980-09-06 | 1900-09-05 | 17:00 | 17 | 556 | 1346 | 322 | 1 | 9 | 503 | 1 | 9 | 112 | 1 | 13 | 34400 | 1 | 9 | 48800 | 1 | 9 | 14200 | 1 | 13 | 2170 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 33.3 | 91.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.44 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 4 | 0
1980-09-06 | 1900-09-05 | 18:00 | 18 | 302 | 1346 | 134 | 1 | 13 | 278 | 1 | 9 | 71 | 1 | 13 | 14000 | 1 | 13 | 22000 | 1 | 9 | 9000 | 1 | 13 | 1290 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 31.7 | 89.06 | A | 7 | 20 | 68 | A | 7 | 0.5 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.5 | 4 | 0
1980-09-06 | 1900-09-05 | 19:00 | 19 | 55 | 886 | 18 | 1 | 13 | 19 | 1 | 9 | 16 | 1 | 13 | 1900 | 1 | 13 | 800 | 1 | 9 | 1900 | 1 | 13 | 330 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 29.4 | 84.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.53 | A | 7 | 980 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.62 | 4 | 0
1980-09-06 | 1900-09-05 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 28.3 | 82.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.59 | A | 7 | 980 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.82 | 4 | 0
1980-09-06 | 1900-09-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 20 | 68 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.7 | 4 | 0
1980-09-06 | 1900-09-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.82 | 4 | 0
1980-09-06 | 1900-09-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 4 | 0
1980-09-06 | 1900-09-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 17.2 | 62.96 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.06 | 4 | 0
1980-09-07 | 1900-09-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.46 | 5 | 0
1980-09-07 | 1900-09-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.16 | 5 | 0
1980-09-07 | 1900-09-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 23.9 | 75.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.64 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.76 | 5 | 0
1980-09-07 | 1900-09-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.86 | 5 | 0
1980-09-07 | 1900-09-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.26 | 5 | 0
1980-09-07 | 1900-09-06 | 6:00 | 6 | 1 | 123 | 1 | 1 | 13 | 1 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 5 | 0
1980-09-07 | 1900-09-06 | 7:00 | 7 | 151 | 1346 | 54 | 1 | 13 | 68 | 1 | 13 | 46 | 1 | 13 | 5800 | 1 | 13 | 4000 | 1 | 13 | 5300 | 1 | 13 | 960 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 22.8 | 73.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.06 | 5 | 0
1980-09-07 | 1900-09-06 | 8:00 | 8 | 413 | 1346 | 156 | 1 | 13 | 142 | 1 | 13 | 112 | 1 | 13 | 17000 | 1 | 13 | 13100 | 1 | 13 | 13000 | 1 | 13 | 2510 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 4270 | A | 7 | 3.1 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.24 | 5 | 0
1980-09-07 | 1900-09-06 | 9:00 | 9 | 655 | 1346 | 405 | 1 | 9 | 578 | 1 | 9 | 123 | 1 | 13 | 42200 | 1 | 9 | 56600 | 1 | 9 | 14600 | 1 | 13 | 2550 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 27.8 | 82.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.61 | A | 7 | 981 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.32 | 5 | 0
1980-09-07 | 1900-09-06 | 10:00 | 10 | 859 | 1346 | 554 | 1 | 13 | 563 | 1 | 13 | 193 | 1 | 13 | 59600 | 1 | 13 | 58100 | 1 | 13 | 22500 | 1 | 13 | 4780 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 29.4 | 84.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.68 | 5 | 0
1980-09-07 | 1900-09-06 | 11:00 | 11 | 1010 | 1346 | 662 | 1 | 13 | 627 | 1 | 13 | 190 | 1 | 13 | 70000 | 1 | 13 | 63700 | 1 | 13 | 22000 | 1 | 13 | 5930 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 31.1 | 87.98 | A | 7 | 20.6 | 69.08 | A | 7 | 0.53 | A | 7 | 981 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.18 | 5 | 0
1980-09-07 | 1900-09-06 | 12:00 | 12 | 1099 | 1346 | 750 | 1 | 9 | 703 | 1 | 9 | 173 | 1 | 13 | 80400 | 1 | 9 | 72200 | 1 | 9 | 21400 | 1 | 13 | 6620 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 32.2 | 89.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 5 | 0
1980-09-07 | 1900-09-06 | 13:00 | 13 | 1118 | 1346 | 729 | 1 | 13 | 575 | 1 | 13 | 248 | 1 | 13 | 76300 | 1 | 13 | 58100 | 1 | 13 | 27900 | 1 | 13 | 9660 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 33.3 | 91.94 | A | 7 | 20 | 68 | A | 7 | 0.45 | A | 7 | 980 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.2 | 5 | 0
1980-09-07 | 1900-09-06 | 14:00 | 14 | 1067 | 1346 | 695 | 1 | 13 | 588 | 1 | 13 | 227 | 1 | 13 | 73000 | 1 | 13 | 59500 | 1 | 13 | 25700 | 1 | 13 | 7840 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 32.8 | 91.04 | A | 7 | 20 | 68 | A | 7 | 0.47 | A | 7 | 979 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.7 | 5 | 0
1980-09-07 | 1900-09-06 | 15:00 | 15 | 950 | 1346 | 612 | 1 | 13 | 577 | 1 | 13 | 203 | 1 | 13 | 63900 | 1 | 13 | 58100 | 1 | 13 | 22800 | 1 | 13 | 5610 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 32.2 | 89.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.44 | A | 7 | 979 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 5 | 0
1980-09-07 | 1900-09-06 | 16:00 | 16 | 773 | 1346 | 460 | 1 | 13 | 409 | 1 | 13 | 223 | 1 | 13 | 48000 | 1 | 13 | 41600 | 1 | 13 | 24000 | 1 | 13 | 5170 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 31.7 | 89.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.47 | A | 7 | 979 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.3 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 5 | 0
1980-09-07 | 1900-09-06 | 17:00 | 17 | 550 | 1346 | 281 | 1 | 13 | 302 | 1 | 13 | 157 | 1 | 13 | 30000 | 1 | 13 | 30000 | 1 | 13 | 17700 | 1 | 13 | 3300 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 31.1 | 87.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.48 | A | 7 | 979 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 3.2 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 5 | 0
1980-09-07 | 1900-09-06 | 18:00 | 18 | 296 | 1346 | 144 | 1 | 13 | 268 | 1 | 13 | 84 | 1 | 13 | 15100 | 1 | 13 | 21100 | 1 | 13 | 10400 | 1 | 13 | 1630 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 31.1 | 87.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.48 | A | 7 | 979 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 5 | 0
1980-09-07 | 1900-09-06 | 19:00 | 19 | 51 | 864 | 24 | 1 | 13 | 49 | 1 | 9 | 19 | 1 | 13 | 2400 | 1 | 13 | 1600 | 1 | 9 | 2300 | 1 | 13 | 330 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 28.9 | 84.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.107 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 5 | 0
1980-09-07 | 1900-09-06 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 27.2 | 80.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.6 | A | 7 | 979 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 5 | 0
1980-09-07 | 1900-09-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 26.7 | 80.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.82 | 5 | 0
1980-09-07 | 1900-09-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.92 | 5 | 0
1980-09-07 | 1900-09-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 25 | 77 | A | 7 | 19.4 | 66.92 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.62 | 5 | 0
1980-09-07 | 1900-09-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.82 | 5 | 0
1980-09-08 | 1900-09-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 23.3 | 73.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.54 | 6 | 0
1980-09-08 | 1900-09-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.74 | 6 | 0
1980-09-08 | 1900-09-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.46 | 6 | 0
1980-09-08 | 1900-09-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 140 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.16 | 6 | 0
1980-09-08 | 1900-09-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.76 | 6 | 0
1980-09-08 | 1900-09-07 | 6:00 | 6 | 1 | 101 | 1 | 1 | 13 | 0 | 1 | 13 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.16 | 6 | 0
1980-09-08 | 1900-09-07 | 7:00 | 7 | 147 | 1347 | 48 | 1 | 13 | 144 | 1 | 9 | 32 | 1 | 13 | 5000 | 1 | 13 | 7800 | 1 | 9 | 4200 | 1 | 13 | 570 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.14 | 6 | 0
1980-09-08 | 1900-09-07 | 8:00 | 8 | 409 | 1347 | 229 | 1 | 9 | 524 | 1 | 9 | 69 | 1 | 13 | 23800 | 1 | 9 | 46600 | 1 | 9 | 9600 | 1 | 13 | 1310 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.52 | 6 | 0
1980-09-08 | 1900-09-07 | 9:00 | 9 | 652 | 1347 | 427 | 1 | 9 | 678 | 1 | 9 | 98 | 1 | 13 | 45200 | 1 | 9 | 66900 | 1 | 9 | 12700 | 1 | 13 | 2100 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.61 | A | 7 | 981 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.32 | 6 | 0
1980-09-08 | 1900-09-07 | 10:00 | 10 | 856 | 1347 | 570 | 1 | 9 | 704 | 1 | 9 | 121 | 1 | 13 | 61000 | 1 | 9 | 71700 | 1 | 9 | 15400 | 1 | 13 | 3100 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 29.4 | 84.92 | A | 7 | 20.6 | 69.08 | A | 7 | 0.59 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.68 | 6 | 0
1980-09-08 | 1900-09-07 | 11:00 | 11 | 1007 | 1347 | 686 | 1 | 9 | 633 | 1 | 9 | 211 | 1 | 13 | 71900 | 1 | 9 | 64000 | 1 | 9 | 24000 | 1 | 13 | 6440 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 982 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 6 | 0
1980-09-08 | 1900-09-07 | 12:00 | 12 | 1095 | 1347 | 783 | 1 | 9 | 761 | 1 | 9 | 162 | 1 | 13 | 81800 | 1 | 9 | 76500 | 1 | 9 | 19500 | 1 | 13 | 5530 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 32.2 | 89.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 6 | 0
1980-09-08 | 1900-09-07 | 13:00 | 13 | 1114 | 1347 | 758 | 1 | 13 | 658 | 1 | 13 | 211 | 1 | 13 | 80300 | 1 | 13 | 67100 | 1 | 13 | 24700 | 1 | 13 | 8240 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 32.8 | 91.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.49 | A | 7 | 981 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.08 | 6 | 0
1980-09-08 | 1900-09-07 | 14:00 | 14 | 1062 | 1347 | 711 | 1 | 13 | 616 | 1 | 13 | 222 | 1 | 13 | 74600 | 1 | 13 | 62400 | 1 | 13 | 25300 | 1 | 13 | 7590 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 32.8 | 91.04 | A | 7 | 20.6 | 69.08 | A | 7 | 0.49 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.08 | 6 | 0
1980-09-08 | 1900-09-07 | 15:00 | 15 | 944 | 1347 | 681 | 1 | 13 | 682 | 1 | 13 | 200 | 1 | 13 | 71000 | 1 | 13 | 68700 | 1 | 13 | 22800 | 1 | 13 | 5490 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 33.3 | 91.94 | A | 7 | 20 | 68 | A | 7 | 0.45 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.2 | 6 | 0
1980-09-08 | 1900-09-07 | 16:00 | 16 | 767 | 1347 | 440 | 1 | 13 | 475 | 1 | 13 | 168 | 1 | 13 | 47300 | 1 | 13 | 48500 | 1 | 13 | 19600 | 1 | 13 | 3770 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 33.3 | 91.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.44 | A | 7 | 979 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 6 | 0
1980-09-08 | 1900-09-07 | 17:00 | 17 | 544 | 1347 | 283 | 1 | 13 | 397 | 1 | 13 | 121 | 1 | 13 | 29900 | 1 | 13 | 38200 | 1 | 13 | 14500 | 1 | 13 | 2350 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 32.8 | 91.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.45 | A | 7 | 980 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.32 | 6 | 0
1980-09-08 | 1900-09-07 | 18:00 | 18 | 289 | 1347 | 133 | 1 | 13 | 277 | 1 | 9 | 72 | 1 | 13 | 13700 | 1 | 13 | 21400 | 1 | 9 | 9100 | 1 | 13 | 1320 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 31.7 | 89.06 | A | 7 | 20 | 68 | A | 7 | 0.5 | A | 7 | 979 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.5 | 6 | 0
1980-09-08 | 1900-09-07 | 19:00 | 19 | 47 | 819 | 20 | 1 | 13 | 40 | 1 | 9 | 16 | 1 | 13 | 2000 | 1 | 13 | 1300 | 1 | 9 | 1900 | 1 | 13 | 270 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 30 | 86 | A | 7 | 18.9 | 66.02 | A | 7 | 0.51 | A | 7 | 979 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.12 | 6 | 0
1980-09-08 | 1900-09-07 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 6 | 0
1980-09-08 | 1900-09-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 19.4 | 66.92 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.72 | 6 | 0
1980-09-08 | 1900-09-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 19.4 | 66.92 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.22 | 6 | 0
1980-09-08 | 1900-09-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.92 | 6 | 0
1980-09-08 | 1900-09-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 981 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.84 | 6 | 0
1980-09-09 | 1900-09-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 24.4 | 75.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.69 | A | 7 | 981 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.44 | 7 | 0
1980-09-09 | 1900-09-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 981 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.24 | 7 | 0
1980-09-09 | 1900-09-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.92 | 7 | 0
1980-09-09 | 1900-09-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 24.4 | 75.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.44 | 7 | 0
1980-09-09 | 1900-09-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.52 | 7 | 0
1980-09-09 | 1900-09-08 | 6:00 | 6 | 0 | 79 | 1 | 1 | 13 | 1 | 1 | 13 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.76 | A | 7 | 983 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.94 | 7 | 0
1980-09-09 | 1900-09-08 | 7:00 | 7 | 143 | 1348 | 46 | 1 | 13 | 127 | 1 | 13 | 32 | 1 | 13 | 4900 | 1 | 13 | 6400 | 1 | 13 | 4200 | 1 | 13 | 570 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.69 | A | 7 | 985 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.86 | 7 | 0
1980-09-09 | 1900-09-08 | 8:00 | 8 | 406 | 1348 | 112 | 1 | 13 | 70 | 1 | 13 | 90 | 1 | 13 | 12300 | 1 | 13 | 6400 | 1 | 13 | 10400 | 1 | 13 | 2010 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 23.3 | 73.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.69 | A | 7 | 986 | A | 7 | 10 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 3660 | A | 7 | 3 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 7 | 0
1980-09-09 | 1900-09-08 | 9:00 | 9 | 648 | 1348 | 122 | 1 | 9 | 16 | 1 | 9 | 114 | 1 | 13 | 14400 | 1 | 9 | 1100 | 1 | 9 | 13900 | 1 | 13 | 5090 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 2.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.86 | 7 | 0
1980-09-09 | 1900-09-08 | 10:00 | 10 | 852 | 1348 | 220 | 1 | 9 | 9 | 1 | 9 | 215 | 1 | 13 | 25800 | 1 | 9 | 700 | 1 | 9 | 25300 | 1 | 13 | 9550 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 22.8 | 73.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 2.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.86 | 7 | 0
1980-09-09 | 1900-09-08 | 11:00 | 11 | 1003 | 1348 | 633 | 1 | 13 | 563 | 1 | 13 | 212 | 1 | 13 | 66300 | 1 | 13 | 56800 | 1 | 13 | 23800 | 1 | 13 | 6410 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 23.3 | 73.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.66 | A | 7 | 987 | A | 7 | 10 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 2.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.16 | 7 | 0
1980-09-09 | 1900-09-08 | 12:00 | 12 | 1091 | 1348 | 627 | 1 | 13 | 513 | 1 | 13 | 210 | 1 | 13 | 66300 | 1 | 13 | 52200 | 1 | 13 | 24000 | 1 | 13 | 7720 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 987 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 4570 | A | 7 | 2.8 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.38 | 7 | 0
1980-09-09 | 1900-09-08 | 13:00 | 13 | 1109 | 1348 | 674 | 1 | 13 | 558 | 1 | 13 | 212 | 1 | 13 | 71300 | 1 | 13 | 56800 | 1 | 13 | 24400 | 1 | 13 | 8160 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 25 | 77 | A | 7 | 16.7 | 62.06 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 340 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 4570 | A | 7 | 2.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.86 | 7 | 0
1980-09-09 | 1900-09-08 | 14:00 | 14 | 1058 | 1348 | 654 | 1 | 13 | 595 | 1 | 13 | 185 | 1 | 13 | 69600 | 1 | 13 | 60800 | 1 | 13 | 21700 | 1 | 13 | 6370 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.56 | A | 7 | 987 | A | 7 | 350 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.08 | 7 | 0
1980-09-09 | 1900-09-08 | 15:00 | 15 | 939 | 1348 | 541 | 1 | 13 | 462 | 1 | 13 | 217 | 1 | 13 | 58200 | 1 | 13 | 48000 | 1 | 13 | 24700 | 1 | 13 | 5990 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 24.4 | 75.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.54 | A | 7 | 987 | A | 7 | 20 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.12 | 7 | 0
1980-09-09 | 1900-09-08 | 16:00 | 16 | 761 | 1348 | 427 | 1 | 13 | 456 | 1 | 13 | 168 | 1 | 13 | 45800 | 1 | 13 | 46500 | 1 | 13 | 19500 | 1 | 13 | 3750 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 23.9 | 75.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.43 | A | 7 | 987 | A | 7 | 360 | A | 7 | 10.3 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.28 | 7 | 0
1980-09-09 | 1900-09-08 | 17:00 | 17 | 537 | 1348 | 323 | 1 | 13 | 514 | 1 | 13 | 116 | 1 | 13 | 34200 | 1 | 13 | 49400 | 1 | 13 | 14500 | 1 | 13 | 2240 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 10 | 50 | A | 7 | 0.44 | A | 7 | 988 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.6 | 7 | 0
1980-09-09 | 1900-09-08 | 18:00 | 18 | 282 | 1348 | 75 | 1 | 13 | 15 | 1 | 13 | 71 | 1 | 13 | 8300 | 1 | 13 | 600 | 1 | 13 | 8200 | 1 | 13 | 2480 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 20.6 | 69.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.46 | A | 7 | 988 | A | 7 | 10 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 1.8 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.54 | 7 | 0
1980-09-09 | 1900-09-08 | 19:00 | 19 | 43 | 797 | 23 | 1 | 13 | 27 | 1 | 13 | 20 | 1 | 13 | 2400 | 1 | 13 | 1100 | 1 | 13 | 2300 | 1 | 13 | 410 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 18.9 | 66.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.49 | A | 7 | 989 | A | 7 | 10 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 3350 | A | 7 | 1.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.24 | 7 | 0
1980-09-09 | 1900-09-08 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 9.4 | 48.92 | A | 7 | 0.56 | A | 7 | 989 | A | 7 | 360 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.82 | 7 | 0
1980-09-09 | 1900-09-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 17.8 | 64.04 | A | 7 | 10 | 50 | A | 7 | 0.61 | A | 7 | 990 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.6 | 7 | 0
1980-09-09 | 1900-09-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 17.2 | 62.96 | A | 7 | 10 | 50 | A | 7 | 0.63 | A | 7 | 990 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44 | 7 | 0
1980-09-09 | 1900-09-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | 10 | 50 | A | 7 | 0.65 | A | 7 | 990 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.3 | 7 | 0
1980-09-09 | 1900-09-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.7 | A | 7 | 989 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.1 | 7 | 0
1980-09-10 | 1900-09-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.7 | A | 7 | 989 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.1 | 1 | 0
1980-09-10 | 1900-09-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 15.6 | 60.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.67 | A | 7 | 989 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.72 | 1 | 0
1980-09-10 | 1900-09-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 15 | 59 | A | 7 | 9.4 | 48.92 | A | 7 | 0.7 | A | 7 | 989 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.22 | 1 | 0
1980-09-10 | 1900-09-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 13.9 | 57.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.72 | 1 | 0
1980-09-10 | 1900-09-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 12.8 | 55.04 | A | 7 | 8.3 | 46.94 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.14 | 1 | 0
1980-09-10 | 1900-09-09 | 6:00 | 6 | 0 | 56 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 5 | A | 7 | 4 | A | 7 | 12.8 | 55.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.72 | A | 7 | 990 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.84 | 1 | 0
1980-09-10 | 1900-09-09 | 7:00 | 7 | 140 | 1348 | 55 | 1 | 13 | 140 | 1 | 13 | 40 | 1 | 13 | 5700 | 1 | 13 | 6900 | 1 | 13 | 5000 | 1 | 13 | 750 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 12.8 | 55.04 | A | 7 | 8.3 | 46.94 | A | 7 | 0.75 | A | 7 | 990 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.14 | 1 | 0
1980-09-10 | 1900-09-09 | 8:00 | 8 | 402 | 1348 | 210 | 1 | 13 | 417 | 1 | 13 | 85 | 1 | 13 | 22200 | 1 | 13 | 36900 | 1 | 13 | 11200 | 1 | 13 | 1560 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | 15 | 59 | A | 7 | 8.3 | 46.94 | A | 7 | 0.65 | A | 7 | 991 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.64 | 1 | 0
1980-09-10 | 1900-09-09 | 9:00 | 9 | 645 | 1348 | 339 | 1 | 13 | 429 | 1 | 13 | 133 | 1 | 13 | 36400 | 1 | 13 | 42800 | 1 | 13 | 15900 | 1 | 13 | 2700 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 18.3 | 64.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.54 | A | 7 | 991 | A | 7 | 60 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.72 | 1 | 0
1980-09-10 | 1900-09-09 | 10:00 | 10 | 848 | 1348 | 586 | 1 | 9 | 723 | 1 | 9 | 129 | 1 | 13 | 62400 | 1 | 9 | 73400 | 1 | 9 | 16100 | 1 | 13 | 3250 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.47 | A | 7 | 990 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.52 | 1 | 0
1980-09-10 | 1900-09-09 | 11:00 | 11 | 999 | 1348 | 698 | 1 | 9 | 762 | 1 | 9 | 131 | 1 | 13 | 73600 | 1 | 9 | 76800 | 1 | 9 | 16600 | 1 | 13 | 3810 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 21.7 | 71.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.41 | A | 7 | 990 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.94 | 1 | 0
1980-09-10 | 1900-09-09 | 12:00 | 12 | 1086 | 1348 | 768 | 1 | 13 | 633 | 1 | 13 | 255 | 1 | 13 | 80000 | 1 | 13 | 63700 | 1 | 13 | 28500 | 1 | 13 | 9060 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 23.3 | 73.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.38 | A | 7 | 989 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.14 | 1 | 0
1980-09-10 | 1900-09-09 | 13:00 | 13 | 1105 | 1348 | 789 | 1 | 13 | 725 | 1 | 13 | 192 | 1 | 13 | 84100 | 1 | 13 | 74200 | 1 | 13 | 23200 | 1 | 13 | 7360 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.36 | A | 7 | 988 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.14 | 1 | 0
1980-09-10 | 1900-09-09 | 14:00 | 14 | 1052 | 1348 | 722 | 1 | 13 | 635 | 1 | 13 | 223 | 1 | 13 | 75600 | 1 | 13 | 64200 | 1 | 13 | 25300 | 1 | 13 | 7430 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 24.4 | 75.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.37 | A | 7 | 987 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.82 | 1 | 0
1980-09-10 | 1900-09-09 | 15:00 | 15 | 933 | 1348 | 642 | 1 | 13 | 697 | 1 | 13 | 156 | 1 | 13 | 68000 | 1 | 13 | 70900 | 1 | 13 | 18800 | 1 | 13 | 4330 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.35 | A | 7 | 986 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.52 | 1 | 0
1980-09-10 | 1900-09-09 | 16:00 | 16 | 755 | 1348 | 451 | 1 | 13 | 501 | 1 | 13 | 168 | 1 | 13 | 48200 | 1 | 13 | 51100 | 1 | 13 | 19600 | 1 | 13 | 3730 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 25.6 | 78.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.35 | A | 7 | 985 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.52 | 1 | 0
1980-09-10 | 1900-09-09 | 17:00 | 17 | 531 | 1348 | 330 | 1 | 9 | 604 | 1 | 9 | 89 | 1 | 13 | 34200 | 1 | 9 | 57200 | 1 | 9 | 11600 | 1 | 13 | 1760 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 10 | 50 | A | 7 | 0.42 | A | 7 | 985 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.3 | 1 | 0
1980-09-10 | 1900-09-09 | 18:00 | 18 | 275 | 1348 | 115 | 1 | 13 | 253 | 1 | 13 | 62 | 1 | 13 | 11900 | 1 | 13 | 19200 | 1 | 13 | 8000 | 1 | 13 | 1120 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.46 | A | 7 | 984 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.88 | 1 | 0
1980-09-10 | 1900-09-09 | 19:00 | 19 | 39 | 753 | 24 | 1 | 13 | 69 | 1 | 13 | 17 | 1 | 13 | 2200 | 1 | 13 | 2100 | 1 | 13 | 2100 | 1 | 13 | 300 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 20 | 68 | A | 7 | 10 | 50 | A | 7 | 0.53 | A | 7 | 983 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.2 | 1 | 0
1980-09-10 | 1900-09-09 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 4 | A | 7 | 18.9 | 66.02 | A | 7 | 10 | 50 | A | 7 | 0.57 | A | 7 | 983 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.9 | 1 | 0
1980-09-10 | 1900-09-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 18.3 | 64.94 | A | 7 | 10 | 50 | A | 7 | 0.59 | A | 7 | 983 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.3 | 1 | 0
1980-09-10 | 1900-09-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 18.3 | 64.94 | A | 7 | 9.4 | 48.92 | A | 7 | 0.56 | A | 7 | 983 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.82 | 1 | 0
1980-09-10 | 1900-09-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | 10 | 50 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.3 | 1 | 0
1980-09-10 | 1900-09-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 16.7 | 62.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.63 | A | 7 | 982 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.02 | 1 | 0
1980-09-11 | 1900-09-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 16.1 | 60.98 | A | 7 | 10 | 50 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.6 | 2 | 0
1980-09-11 | 1900-09-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 16.1 | 60.98 | A | 7 | 10 | 50 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.6 | 2 | 0
1980-09-11 | 1900-09-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.1 | 2 | 0
1980-09-11 | 1900-09-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 10 | 50 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46 | 2 | 0
1980-09-11 | 1900-09-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.5 | 2 | 0
1980-09-11 | 1900-09-10 | 6:00 | 6 | 0 | 34 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 7 | A | 7 | 3 | A | 7 | 15 | 59 | A | 7 | 10 | 50 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.5 | 2 | 0
1980-09-11 | 1900-09-10 | 7:00 | 7 | 136 | 1349 | 47 | 1 | 13 | 152 | 1 | 13 | 32 | 1 | 13 | 4900 | 1 | 13 | 7800 | 1 | 13 | 4100 | 1 | 13 | 570 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 16.1 | 60.98 | A | 7 | 10 | 50 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.6 | 2 | 0
1980-09-11 | 1900-09-10 | 8:00 | 8 | 398 | 1349 | 178 | 1 | 13 | 245 | 1 | 13 | 105 | 1 | 13 | 18900 | 1 | 13 | 22000 | 1 | 13 | 12400 | 1 | 13 | 2060 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 19.4 | 66.92 | A | 7 | 11.1 | 51.98 | A | 7 | 0.59 | A | 7 | 980 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.98 | 2 | 0
1980-09-11 | 1900-09-10 | 9:00 | 9 | 641 | 1349 | 345 | 1 | 13 | 441 | 1 | 13 | 135 | 1 | 13 | 37000 | 1 | 13 | 43900 | 1 | 13 | 16100 | 1 | 13 | 2740 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 22.2 | 71.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.84 | 2 | 0
1980-09-11 | 1900-09-10 | 10:00 | 10 | 844 | 1349 | 457 | 1 | 13 | 427 | 1 | 13 | 189 | 1 | 13 | 49200 | 1 | 13 | 44000 | 1 | 13 | 21600 | 1 | 13 | 4590 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.64 | 2 | 0
1980-09-11 | 1900-09-10 | 11:00 | 11 | 995 | 1349 | 646 | 1 | 13 | 570 | 1 | 13 | 224 | 1 | 13 | 70000 | 1 | 13 | 59400 | 1 | 13 | 26100 | 1 | 13 | 6760 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 25.6 | 78.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.5 | A | 7 | 979 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 2 | 0
1980-09-11 | 1900-09-10 | 12:00 | 12 | 1082 | 1349 | 795 | 1 | 13 | 742 | 1 | 13 | 196 | 1 | 13 | 84300 | 1 | 13 | 75700 | 1 | 13 | 23400 | 1 | 13 | 7080 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 26.7 | 80.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.56 | 2 | 0
1980-09-11 | 1900-09-10 | 13:00 | 13 | 1100 | 1349 | 606 | 1 | 9 | 308 | 1 | 9 | 354 | 1 | 13 | 66100 | 1 | 9 | 33400 | 1 | 9 | 38800 | 1 | 13 | 13050 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 27.8 | 82.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.53 | A | 7 | 977 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 3 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.06 | 2 | 0
1980-09-11 | 1900-09-10 | 14:00 | 14 | 1047 | 1349 | 215 | 1 | 9 | 11 | 1 | 9 | 207 | 1 | 13 | 26000 | 1 | 9 | 900 | 1 | 9 | 25300 | 1 | 13 | 10130 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 26.7 | 80.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.6 | A | 7 | 976 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 3.1 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.34 | 2 | 0
1980-09-11 | 1900-09-10 | 15:00 | 15 | 928 | 1349 | 180 | 1 | 9 | 12 | 1 | 9 | 172 | 1 | 13 | 21700 | 1 | 9 | 900 | 1 | 9 | 21000 | 1 | 13 | 8320 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 27.8 | 82.04 | A | 7 | 18.9 | 66.02 | A | 7 | 0.58 | A | 7 | 975 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 2440 | A | 7 | 3.2 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.82 | 2 | 0
1980-09-11 | 1900-09-10 | 16:00 | 16 | 749 | 1349 | 257 | 1 | 9 | 73 | 1 | 9 | 216 | 1 | 13 | 28200 | 1 | 9 | 7300 | 1 | 9 | 24200 | 1 | 13 | 6880 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 27.2 | 80.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.63 | A | 7 | 974 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 2290 | A | 7 | 3.4 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.82 | 2 | 0
1980-09-11 | 1900-09-10 | 17:00 | 17 | 524 | 1349 | 178 | 1 | 9 | 57 | 1 | 9 | 155 | 1 | 13 | 19400 | 1 | 9 | 5500 | 1 | 9 | 17300 | 1 | 13 | 4330 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 27.8 | 82.04 | A | 7 | 19.4 | 66.92 | A | 7 | 0.61 | A | 7 | 974 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 4270 | A | 7 | 3.4 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.32 | 2 | 0
1980-09-11 | 1900-09-10 | 18:00 | 18 | 268 | 1349 | 80 | 1 | 13 | 55 | 1 | 9 | 69 | 1 | 13 | 8800 | 1 | 13 | 4500 | 1 | 9 | 7900 | 1 | 13 | 1740 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 27.2 | 80.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.63 | A | 7 | 973 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 4270 | A | 7 | 3.4 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.82 | 2 | 0
1980-09-11 | 1900-09-10 | 19:00 | 19 | 35 | 708 | 20 | 1 | 13 | 14 | 1 | 13 | 18 | 1 | 13 | 2100 | 1 | 13 | 700 | 1 | 13 | 2000 | 1 | 13 | 430 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 973 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 4270 | A | 7 | 3.3 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.92 | 2 | 0
1980-09-11 | 1900-09-10 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 23.9 | 75.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.74 | A | 7 | 973 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.52 | 2 | 0
1980-09-11 | 1900-09-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 2 | 0
1980-09-11 | 1900-09-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 23.3 | 73.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.76 | A | 7 | 973 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.92 | 2 | 0
1980-09-11 | 1900-09-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 973 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.84 | 2 | 0
1980-09-11 | 1900-09-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 25.6 | 78.08 | A | 7 | 18.3 | 64.94 | A | 7 | 0.64 | A | 7 | 972 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.24 | 2 | 0
1980-09-12 | 1900-09-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | A | 7 | 972 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.64 | 3 | 0
1980-09-12 | 1900-09-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 25 | 77 | A | 7 | 17.2 | 62.96 | A | 7 | 0.62 | A | 7 | 972 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.06 | 3 | 0
1980-09-12 | 1900-09-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 25 | 77 | A | 7 | 17.2 | 62.96 | A | 7 | 0.62 | A | 7 | 971 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.06 | 3 | 0
1980-09-12 | 1900-09-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 16.7 | 62.06 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.86 | 3 | 0
1980-09-12 | 1900-09-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 16.7 | 62.06 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.86 | 3 | 0
1980-09-12 | 1900-09-11 | 6:00 | 6 | 0 | 34 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 2 | A | 7 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.62 | A | 7 | 972 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.36 | 3 | 0
1980-09-12 | 1900-09-11 | 7:00 | 7 | 132 | 1350 | 54 | 1 | 13 | 247 | 1 | 9 | 28 | 1 | 13 | 5300 | 1 | 13 | 13600 | 1 | 9 | 4000 | 1 | 13 | 490 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.62 | A | 7 | 972 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.36 | 3 | 0
1980-09-12 | 1900-09-11 | 8:00 | 8 | 395 | 1350 | 229 | 1 | 9 | 593 | 1 | 9 | 54 | 1 | 13 | 24000 | 1 | 9 | 52600 | 1 | 9 | 8600 | 1 | 13 | 1050 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.56 | A | 7 | 972 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.76 | 3 | 0
1980-09-12 | 1900-09-11 | 9:00 | 9 | 637 | 1350 | 429 | 1 | 9 | 742 | 1 | 9 | 77 | 1 | 13 | 45000 | 1 | 9 | 72400 | 1 | 9 | 10800 | 1 | 13 | 1660 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.55 | A | 7 | 972 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.24 | 3 | 0
1980-09-12 | 1900-09-11 | 10:00 | 10 | 841 | 1350 | 604 | 1 | 9 | 815 | 1 | 9 | 94 | 1 | 13 | 64400 | 1 | 9 | 81900 | 1 | 9 | 13200 | 1 | 13 | 2350 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 19.4 | 66.92 | A | 7 | 0.53 | A | 7 | 972 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.32 | 3 | 0
1980-09-12 | 1900-09-11 | 11:00 | 11 | 991 | 1350 | 735 | 1 | 9 | 853 | 1 | 9 | 105 | 1 | 13 | 75800 | 1 | 9 | 85100 | 1 | 9 | 13200 | 1 | 13 | 2670 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 19.4 | 66.92 | A | 7 | 0.47 | A | 7 | 972 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.82 | 3 | 0
1980-09-12 | 1900-09-11 | 12:00 | 12 | 1078 | 1350 | 810 | 1 | 9 | 871 | 1 | 9 | 111 | 1 | 13 | 83500 | 1 | 9 | 87100 | 1 | 9 | 13700 | 1 | 13 | 3290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.43 | A | 7 | 971 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.82 | 3 | 0
1980-09-12 | 1900-09-11 | 13:00 | 13 | 1095 | 1350 | 775 | 1 | 9 | 768 | 1 | 9 | 149 | 1 | 13 | 81700 | 1 | 9 | 77500 | 1 | 9 | 18600 | 1 | 13 | 5190 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 34.4 | 93.92 | A | 7 | 19.4 | 66.92 | A | 7 | 0.41 | A | 7 | 971 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.32 | 3 | 0
1980-09-12 | 1900-09-11 | 14:00 | 14 | 1042 | 1350 | 662 | 1 | 9 | 591 | 1 | 9 | 203 | 1 | 13 | 69800 | 1 | 9 | 60000 | 1 | 9 | 23300 | 1 | 13 | 6670 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 35.6 | 96.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.39 | A | 7 | 971 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.72 | 3 | 0
1980-09-12 | 1900-09-11 | 15:00 | 15 | 922 | 1350 | 430 | 1 | 13 | 290 | 1 | 13 | 231 | 1 | 13 | 47300 | 1 | 13 | 31300 | 1 | 13 | 25900 | 1 | 13 | 6220 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 33.3 | 91.94 | A | 7 | 20.6 | 69.08 | A | 7 | 0.47 | A | 7 | 970 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 1520 | A | 7 | 3.5 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.58 | 3 | 0
1980-09-12 | 1900-09-11 | 16:00 | 16 | 743 | 1350 | 363 | 1 | 9 | 321 | 1 | 9 | 184 | 1 | 13 | 39400 | 1 | 9 | 33800 | 1 | 9 | 20700 | 1 | 13 | 4190 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 34.4 | 93.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.38 | A | 7 | 970 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 1830 | A | 7 | 3.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.04 | 3 | 0
1980-09-12 | 1900-09-11 | 17:00 | 17 | 517 | 1350 | 198 | 1 | 13 | 164 | 1 | 13 | 135 | 1 | 13 | 21800 | 1 | 13 | 16000 | 1 | 13 | 15600 | 1 | 13 | 3140 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 28.3 | 82.94 | A | 7 | 18.9 | 66.02 | A | 7 | 0.57 | A | 7 | 970 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 3.2 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.62 | 3 | 0
1980-09-12 | 1900-09-11 | 18:00 | 18 | 261 | 1350 | 69 | 1 | 13 | 11 | 1 | 9 | 66 | 1 | 13 | 7600 | 1 | 13 | 400 | 1 | 9 | 7500 | 1 | 13 | 2270 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 28.9 | 84.02 | A | 7 | 19.4 | 66.92 | A | 7 | 0.57 | A | 7 | 970 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 3.3 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 3 | 0
1980-09-12 | 1900-09-11 | 19:00 | 19 | 32 | 686 | 13 | 1 | 13 | 4 | 1 | 9 | 12 | 1 | 13 | 1300 | 1 | 13 | 200 | 1 | 9 | 1300 | 1 | 13 | 300 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 27.2 | 80.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.53 | A | 7 | 971 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 2.9 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.36 | 3 | 0
1980-09-12 | 1900-09-11 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | 28.3 | 82.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.55 | A | 7 | 971 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 12900 | A | 7 | 1520 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.24 | 3 | 0
1980-09-12 | 1900-09-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | 27.2 | 80.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.54 | A | 7 | 972 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 3050 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.26 | 3 | 0
1980-09-12 | 1900-09-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.66 | A | 7 | 972 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.96 | 3 | 0
1980-09-12 | 1900-09-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.58 | A | 7 | 972 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.26 | 3 | 0
1980-09-12 | 1900-09-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 26.7 | 80.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.56 | A | 7 | 972 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.76 | 3 | 0
1980-09-13 | 1900-09-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.66 | A | 7 | 973 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.96 | 4 | 0
1980-09-13 | 1900-09-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 973 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 4 | 0
1980-09-13 | 1900-09-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.79 | A | 7 | 973 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.86 | 4 | 0
1980-09-13 | 1900-09-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 4 | 0
1980-09-13 | 1900-09-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 4 | 0
1980-09-13 | 1900-09-12 | 6:00 | 6 | 0 | 11 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | A | 7 | 1 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 4 | 0
1980-09-13 | 1900-09-12 | 7:00 | 7 | 128 | 1351 | 55 | 1 | 13 | 287 | 1 | 9 | 25 | 1 | 13 | 5300 | 1 | 13 | 15700 | 1 | 9 | 3800 | 1 | 13 | 450 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 4 | 0
1980-09-13 | 1900-09-12 | 8:00 | 8 | 391 | 1351 | 226 | 1 | 9 | 610 | 1 | 9 | 48 | 1 | 13 | 23400 | 1 | 9 | 54200 | 1 | 9 | 7700 | 1 | 13 | 990 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.26 | 4 | 0
1980-09-13 | 1900-09-12 | 9:00 | 9 | 633 | 1351 | 429 | 1 | 9 | 768 | 1 | 9 | 67 | 1 | 13 | 45700 | 1 | 9 | 75300 | 1 | 9 | 10300 | 1 | 13 | 1510 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 16.7 | 62.06 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.26 | 4 | 0
1980-09-13 | 1900-09-12 | 10:00 | 10 | 837 | 1351 | 609 | 1 | 9 | 846 | 1 | 9 | 82 | 1 | 13 | 63300 | 1 | 9 | 83800 | 1 | 9 | 11300 | 1 | 13 | 1940 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.66 | A | 7 | 979 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.96 | 4 | 0
1980-09-13 | 1900-09-12 | 11:00 | 11 | 987 | 1351 | 739 | 1 | 9 | 881 | 1 | 9 | 93 | 1 | 13 | 76700 | 1 | 9 | 88000 | 1 | 9 | 12200 | 1 | 13 | 2530 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 17.2 | 62.96 | A | 7 | 0.62 | A | 7 | 979 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.06 | 4 | 0
1980-09-13 | 1900-09-12 | 12:00 | 12 | 1074 | 1351 | 817 | 1 | 9 | 901 | 1 | 9 | 98 | 1 | 13 | 84600 | 1 | 9 | 90200 | 1 | 9 | 12700 | 1 | 13 | 3060 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.14 | 4 | 0
1980-09-13 | 1900-09-12 | 13:00 | 13 | 1091 | 1351 | 833 | 1 | 9 | 905 | 1 | 9 | 99 | 1 | 13 | 86200 | 1 | 9 | 90700 | 1 | 9 | 12800 | 1 | 13 | 3200 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 4 | 0
1980-09-13 | 1900-09-12 | 14:00 | 14 | 1037 | 1351 | 785 | 1 | 9 | 893 | 1 | 9 | 96 | 1 | 13 | 81300 | 1 | 9 | 89300 | 1 | 9 | 12500 | 1 | 13 | 2810 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 17.8 | 64.04 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.94 | 4 | 0
1980-09-13 | 1900-09-12 | 15:00 | 15 | 916 | 1351 | 682 | 1 | 9 | 870 | 1 | 9 | 88 | 1 | 13 | 70700 | 1 | 9 | 86600 | 1 | 9 | 11800 | 1 | 13 | 2210 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.49 | A | 7 | 980 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.16 | 4 | 0
1980-09-13 | 1900-09-12 | 16:00 | 16 | 737 | 1351 | 495 | 1 | 9 | 727 | 1 | 9 | 96 | 1 | 13 | 51700 | 1 | 9 | 71900 | 1 | 9 | 12400 | 1 | 13 | 2110 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 28.9 | 84.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.46 | A | 7 | 980 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.88 | 4 | 0
1980-09-13 | 1900-09-12 | 17:00 | 17 | 511 | 1351 | 322 | 1 | 9 | 684 | 1 | 9 | 61 | 1 | 13 | 33600 | 1 | 9 | 64500 | 1 | 9 | 9100 | 1 | 13 | 1280 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 28.3 | 82.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.46 | A | 7 | 980 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.08 | 4 | 0
1980-09-13 | 1900-09-12 | 18:00 | 18 | 254 | 1351 | 84 | 1 | 13 | 119 | 1 | 13 | 61 | 1 | 13 | 8900 | 1 | 13 | 8700 | 1 | 13 | 7300 | 1 | 13 | 1130 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 26.1 | 78.98 | A | 7 | 15 | 59 | A | 7 | 0.5 | A | 7 | 980 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.1 | 4 | 0
1980-09-13 | 1900-09-12 | 19:00 | 19 | 28 | 642 | 18 | 1 | 13 | 32 | 1 | 13 | 14 | 1 | 13 | 1700 | 1 | 13 | 1200 | 1 | 13 | 1700 | 1 | 13 | 290 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 15 | 59 | A | 7 | 0.62 | A | 7 | 981 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.071 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.7 | 4 | 0
1980-09-13 | 1900-09-12 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 4 | A | 7 | 21.1 | 69.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.66 | A | 7 | 981 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 4 | 0
1980-09-13 | 1900-09-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 982 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 4 | 0
1980-09-13 | 1900-09-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 19.4 | 66.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.7 | A | 7 | 982 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 4 | 0
1980-09-13 | 1900-09-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.73 | A | 7 | 983 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.02 | 4 | 0
1980-09-13 | 1900-09-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 983 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.44 | 4 | 0
1980-09-14 | 1900-09-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.81 | A | 7 | 983 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 5 | 0
1980-09-14 | 1900-09-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 16.1 | 60.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.74 | 5 | 0
1980-09-14 | 1900-09-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 16.1 | 60.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.74 | 5 | 0
1980-09-14 | 1900-09-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 15.6 | 60.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.84 | A | 7 | 984 | A | 7 | 20 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.24 | 5 | 0
1980-09-14 | 1900-09-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.24 | 5 | 0
1980-09-14 | 1900-09-13 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 14.4 | 57.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.87 | A | 7 | 985 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.76 | 5 | 0
1980-09-14 | 1900-09-13 | 7:00 | 7 | 124 | 1340 | 50 | 1 | 13 | 190 | 1 | 9 | 31 | 1 | 13 | 5200 | 1 | 13 | 9600 | 1 | 9 | 4200 | 1 | 13 | 550 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | 15 | 59 | A | 7 | 12.2 | 53.96 | A | 7 | 0.84 | A | 7 | 985 | A | 7 | 350 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.16 | 5 | 0
1980-09-14 | 1900-09-13 | 8:00 | 8 | 387 | 1351 | 158 | 1 | 13 | 227 | 1 | 13 | 92 | 1 | 13 | 16900 | 1 | 13 | 20200 | 1 | 13 | 11100 | 1 | 13 | 1760 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 986 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.44 | 5 | 0
1980-09-14 | 1900-09-13 | 9:00 | 9 | 630 | 1351 | 396 | 1 | 13 | 644 | 1 | 13 | 95 | 1 | 13 | 41800 | 1 | 13 | 63200 | 1 | 13 | 12300 | 1 | 13 | 2000 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 19.4 | 66.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.66 | A | 7 | 986 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.94 | 5 | 0
1980-09-14 | 1900-09-13 | 10:00 | 10 | 833 | 1351 | 452 | 1 | 9 | 488 | 1 | 9 | 149 | 1 | 13 | 47400 | 1 | 9 | 49100 | 1 | 9 | 17100 | 1 | 13 | 3610 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 21.1 | 69.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.59 | A | 7 | 986 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.64 | 5 | 0
1980-09-14 | 1900-09-13 | 11:00 | 11 | 983 | 1351 | 661 | 1 | 9 | 721 | 1 | 9 | 134 | 1 | 13 | 69300 | 1 | 9 | 72500 | 1 | 9 | 16500 | 1 | 13 | 3730 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.55 | A | 7 | 986 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.84 | 5 | 0
1980-09-14 | 1900-09-13 | 12:00 | 12 | 1069 | 1351 | 735 | 1 | 9 | 698 | 1 | 9 | 180 | 1 | 13 | 78400 | 1 | 9 | 71400 | 1 | 9 | 21700 | 1 | 13 | 6340 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.52 | A | 7 | 985 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.04 | 5 | 0
1980-09-14 | 1900-09-13 | 13:00 | 13 | 1086 | 1351 | 743 | 1 | 9 | 740 | 1 | 9 | 145 | 1 | 13 | 78300 | 1 | 9 | 74700 | 1 | 9 | 18200 | 1 | 13 | 4950 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 25 | 77 | A | 7 | 13.9 | 57.02 | A | 7 | 0.5 | A | 7 | 985 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.52 | 5 | 0
1980-09-14 | 1900-09-13 | 14:00 | 14 | 1032 | 1351 | 724 | 1 | 9 | 729 | 1 | 9 | 164 | 1 | 13 | 77300 | 1 | 9 | 74700 | 1 | 9 | 20200 | 1 | 13 | 5380 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 25 | 77 | A | 7 | 13.9 | 57.02 | A | 7 | 0.5 | A | 7 | 985 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.52 | 5 | 0
1980-09-14 | 1900-09-13 | 15:00 | 15 | 911 | 1351 | 537 | 1 | 13 | 422 | 1 | 13 | 251 | 1 | 13 | 56700 | 1 | 13 | 43600 | 1 | 13 | 27300 | 1 | 13 | 6730 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 24.4 | 75.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.52 | A | 7 | 984 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.92 | 5 | 0
1980-09-14 | 1900-09-13 | 16:00 | 16 | 730 | 1351 | 496 | 1 | 13 | 644 | 1 | 13 | 145 | 1 | 13 | 51400 | 1 | 13 | 63700 | 1 | 13 | 16900 | 1 | 13 | 3140 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 24.4 | 75.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.54 | A | 7 | 983 | A | 7 | 10 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 2.5 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.12 | 5 | 0
1980-09-14 | 1900-09-13 | 17:00 | 17 | 504 | 1351 | 256 | 1 | 13 | 331 | 1 | 13 | 131 | 1 | 13 | 27300 | 1 | 13 | 32100 | 1 | 13 | 15300 | 1 | 13 | 2650 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.54 | A | 7 | 983 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.32 | 5 | 0
1980-09-14 | 1900-09-13 | 18:00 | 18 | 247 | 1351 | 88 | 1 | 13 | 88 | 1 | 13 | 71 | 1 | 13 | 9500 | 1 | 13 | 6600 | 1 | 13 | 8200 | 1 | 13 | 1520 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 22.2 | 71.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.57 | A | 7 | 983 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.04 | 5 | 0
1980-09-14 | 1900-09-13 | 19:00 | 19 | 25 | 619 | 18 | 1 | 13 | 20 | 1 | 13 | 15 | 1 | 13 | 1800 | 1 | 13 | 700 | 1 | 13 | 1700 | 1 | 13 | 310 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 20 | 68 | A | 7 | 13.3 | 55.94 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.74 | 5 | 0
1980-09-14 | 1900-09-13 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 18.9 | 66.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.7 | A | 7 | 983 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.54 | 5 | 0
1980-09-14 | 1900-09-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 17.2 | 62.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.78 | A | 7 | 984 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.04 | 5 | 0
1980-09-14 | 1900-09-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 983 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.14 | 5 | 0
1980-09-14 | 1900-09-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.81 | A | 7 | 983 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.66 | 5 | 0
1980-09-14 | 1900-09-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.66 | 5 | 0
1980-09-15 | 1900-09-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 70 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.66 | 6 | 0
1980-09-15 | 1900-09-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 14.4 | 57.92 | A | 7 | 11.7 | 53.06 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.36 | 6 | 0
1980-09-15 | 1900-09-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 981 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.86 | 6 | 0
1980-09-15 | 1900-09-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 14.4 | 57.92 | A | 7 | 11.7 | 53.06 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.36 | 6 | 0
1980-09-15 | 1900-09-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 12.2 | 53.96 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.16 | 6 | 0
1980-09-15 | 1900-09-14 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 15 | 59 | A | 7 | 12.2 | 53.96 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.16 | 6 | 0
1980-09-15 | 1900-09-14 | 7:00 | 7 | 121 | 1318 | 38 | 1 | 13 | 9 | 1 | 13 | 37 | 1 | 13 | 4200 | 1 | 13 | 0 | 1 | 13 | 4200 | 1 | 13 | 1160 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 15 | 59 | A | 7 | 12.2 | 53.96 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.16 | 6 | 0
1980-09-15 | 1900-09-14 | 8:00 | 8 | 383 | 1352 | 146 | 1 | 13 | 75 | 1 | 13 | 124 | 1 | 13 | 15900 | 1 | 13 | 6800 | 1 | 13 | 14000 | 1 | 13 | 3140 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 2.2 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.16 | 6 | 0
1980-09-15 | 1900-09-14 | 9:00 | 9 | 626 | 1352 | 173 | 1 | 13 | 31 | 1 | 13 | 159 | 1 | 13 | 19100 | 1 | 13 | 3000 | 1 | 13 | 17700 | 1 | 13 | 4820 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 2.3 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.14 | 6 | 0
1980-09-15 | 1900-09-14 | 10:00 | 10 | 829 | 1352 | 151 | 1 | 9 | 71 | 1 | 9 | 107 | 1 | 13 | 17400 | 1 | 9 | 7600 | 1 | 9 | 12800 | 1 | 13 | 2920 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 40 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 1520 | A | 7 | 2.4 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 6 | 0
1980-09-15 | 1900-09-14 | 11:00 | 11 | 979 | 1352 | 359 | 1 | 9 | 104 | 1 | 9 | 283 | 1 | 13 | 39700 | 1 | 9 | 11100 | 1 | 9 | 31600 | 1 | 13 | 8870 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 2.5 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 6 | 0
1980-09-15 | 1900-09-14 | 12:00 | 12 | 1065 | 1352 | 269 | 1 | 9 | 5 | 1 | 9 | 265 | 1 | 13 | 31900 | 1 | 9 | 400 | 1 | 9 | 31600 | 1 | 13 | 12380 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 15.6 | 60.08 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 2.7 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.48 | 6 | 0
1980-09-15 | 1900-09-14 | 13:00 | 13 | 1081 | 1352 | 263 | 1 | 9 | 1 | 1 | 9 | 262 | 1 | 13 | 31300 | 1 | 9 | 100 | 1 | 9 | 31200 | 1 | 13 | 12330 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 2.7 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.68 | 6 | 0
1980-09-15 | 1900-09-14 | 14:00 | 14 | 1026 | 1352 | 267 | 1 | 9 | 3 | 1 | 9 | 265 | 1 | 13 | 31500 | 1 | 9 | 300 | 1 | 9 | 31300 | 1 | 13 | 12200 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 16.1 | 60.98 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 2.7 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.68 | 6 | 0
1980-09-15 | 1900-09-14 | 15:00 | 15 | 905 | 1352 | 160 | 1 | 9 | 3 | 1 | 9 | 158 | 1 | 13 | 19300 | 1 | 9 | 200 | 1 | 9 | 19100 | 1 | 13 | 7670 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 17.2 | 62.96 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 2.9 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.76 | 6 | 0
1980-09-15 | 1900-09-14 | 16:00 | 16 | 724 | 1352 | 331 | 1 | 13 | 254 | 1 | 13 | 194 | 1 | 13 | 35800 | 1 | 13 | 26700 | 1 | 13 | 21500 | 1 | 13 | 4410 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 20.6 | 69.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.84 | A | 7 | 974 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 2130 | A | 7 | 3 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.84 | 6 | 0
1980-09-15 | 1900-09-14 | 17:00 | 17 | 497 | 1352 | 224 | 1 | 9 | 222 | 1 | 9 | 141 | 1 | 13 | 23700 | 1 | 9 | 21400 | 1 | 9 | 15800 | 1 | 13 | 2900 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 21.7 | 71.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 3.1 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.74 | 6 | 0
1980-09-15 | 1900-09-14 | 18:00 | 18 | 240 | 1352 | 32 | 1 | 13 | 6 | 1 | 9 | 31 | 1 | 13 | 3800 | 1 | 13 | 100 | 1 | 9 | 3800 | 1 | 13 | 1220 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.79 | A | 7 | 973 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.9 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.76 | 6 | 0
1980-09-15 | 1900-09-14 | 19:00 | 19 | 22 | 575 | 9 | 1 | 13 | 0 | 1 | 9 | 9 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.79 | A | 7 | 972 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 2.9 | E | 8 | 0.171 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.76 | 6 | 0
1980-09-15 | 1900-09-14 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.79 | A | 7 | 972 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.86 | 6 | 0
1980-09-15 | 1900-09-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.79 | A | 7 | 972 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.86 | 6 | 0
1980-09-15 | 1900-09-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 5 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 971 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 6 | 0
1980-09-15 | 1900-09-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 971 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 6 | 0
1980-09-15 | 1900-09-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 970 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 6 | 0
1980-09-16 | 1900-09-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 160 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 7 | 0
1980-09-16 | 1900-09-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 969 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 7 | 0
1980-09-16 | 1900-09-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 969 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 7 | 0
1980-09-16 | 1900-09-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.81 | A | 7 | 969 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.28 | 7 | 0
1980-09-16 | 1900-09-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 969 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.98 | 7 | 0
1980-09-16 | 1900-09-15 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.58 | 7 | 0
1980-09-16 | 1900-09-15 | 7:00 | 7 | 117 | 1297 | 39 | 1 | 13 | 65 | 1 | 9 | 32 | 1 | 13 | 4200 | 1 | 13 | 3500 | 1 | 9 | 3800 | 1 | 13 | 670 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 4000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.58 | 7 | 0
1980-09-16 | 1900-09-15 | 8:00 | 8 | 379 | 1353 | 160 | 1 | 9 | 185 | 1 | 9 | 108 | 1 | 13 | 16900 | 1 | 9 | 16300 | 1 | 9 | 12300 | 1 | 13 | 2140 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.48 | 7 | 0
1980-09-16 | 1900-09-15 | 9:00 | 9 | 622 | 1353 | 76 | 1 | 9 | 3 | 1 | 9 | 74 | 1 | 13 | 9200 | 1 | 9 | 200 | 1 | 9 | 9100 | 1 | 13 | 3460 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 970 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 2.8 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 7 | 0
1980-09-16 | 1900-09-15 | 10:00 | 10 | 825 | 1353 | 247 | 1 | 9 | 14 | 1 | 9 | 239 | 1 | 13 | 28500 | 1 | 9 | 1200 | 1 | 9 | 27800 | 1 | 13 | 10100 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 971 | A | 7 | 10 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 240 | A | 7 | 2.7 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 7 | 0
1980-09-16 | 1900-09-15 | 11:00 | 11 | 975 | 1353 | 307 | 1 | 9 | 9 | 1 | 9 | 301 | 1 | 13 | 35600 | 1 | 9 | 800 | 1 | 9 | 35000 | 1 | 13 | 13030 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.81 | A | 7 | 971 | A | 7 | 10 | A | 7 | 9.3 | A | 7 | 12900 | A | 7 | 270 | A | 7 | 2.3 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 7 | 0
1980-09-16 | 1900-09-15 | 12:00 | 12 | 1060 | 1353 | 307 | 1 | 9 | 2 | 1 | 9 | 305 | 1 | 13 | 35900 | 1 | 9 | 200 | 1 | 9 | 35800 | 1 | 13 | 13700 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 10 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 2.2 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.16 | 7 | 0
1980-09-16 | 1900-09-15 | 13:00 | 13 | 1076 | 1353 | 343 | 1 | 9 | 4 | 1 | 9 | 340 | 1 | 13 | 40000 | 1 | 9 | 400 | 1 | 9 | 39700 | 1 | 13 | 14870 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 20 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 1.9 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.1 | 7 | 0
1980-09-16 | 1900-09-15 | 14:00 | 14 | 1021 | 1353 | 182 | 1 | 9 | 3 | 1 | 9 | 180 | 1 | 13 | 22100 | 1 | 9 | 200 | 1 | 9 | 21900 | 1 | 13 | 8940 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.83 | A | 7 | 973 | A | 7 | 40 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 1.8 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.22 | 7 | 0
1980-09-16 | 1900-09-15 | 15:00 | 15 | 899 | 1353 | 163 | 1 | 9 | 2 | 1 | 9 | 162 | 1 | 13 | 19600 | 1 | 9 | 200 | 1 | 9 | 19500 | 1 | 13 | 7810 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 10 | 50 | A | 7 | 0.9 | A | 7 | 971 | A | 7 | 40 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 1.9 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.4 | 7 | 0
1980-09-16 | 1900-09-15 | 16:00 | 16 | 718 | 1353 | 119 | 1 | 9 | 2 | 1 | 9 | 117 | 1 | 13 | 14100 | 1 | 9 | 100 | 1 | 9 | 14000 | 1 | 13 | 5420 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.86 | A | 7 | 971 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 1.8 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.72 | 7 | 0
1980-09-16 | 1900-09-15 | 17:00 | 17 | 490 | 1353 | 80 | 1 | 9 | 1 | 1 | 9 | 80 | 1 | 13 | 9500 | 1 | 9 | 100 | 1 | 9 | 9400 | 1 | 13 | 3400 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 10 | 50 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 310 | A | 7 | 1.9 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.9 | 7 | 0
1980-09-16 | 1900-09-15 | 18:00 | 18 | 233 | 1353 | 37 | 1 | 13 | 0 | 1 | 9 | 37 | 1 | 13 | 4300 | 1 | 13 | 0 | 1 | 9 | 4300 | 1 | 13 | 1410 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 310 | A | 7 | 1.9 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.32 | 7 | 0
1980-09-16 | 1900-09-15 | 19:00 | 19 | 19 | 530 | 11 | 1 | 13 | 0 | 1 | 9 | 11 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.83 | A | 7 | 974 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 1.7 | E | 8 | 0.204 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.54 | 7 | 0
1980-09-16 | 1900-09-15 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 2740 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.24 | 7 | 0
1980-09-16 | 1900-09-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 2740 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.24 | 7 | 0
1980-09-16 | 1900-09-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.44 | 7 | 0
1980-09-16 | 1900-09-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.96 | 7 | 0
1980-09-16 | 1900-09-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.48 | 7 | 0
1980-09-17 | 1900-09-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.98 | 1 | 0
1980-09-17 | 1900-09-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.5 | 1 | 0
1980-09-17 | 1900-09-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.52 | 1 | 0
1980-09-17 | 1900-09-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.52 | 1 | 0
1980-09-17 | 1900-09-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 978 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 1 | 0
1980-09-17 | 1900-09-16 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.04 | 1 | 0
1980-09-17 | 1900-09-16 | 7:00 | 7 | 113 | 1275 | 54 | 1 | 13 | 290 | 1 | 9 | 24 | 1 | 13 | 5200 | 1 | 13 | 15800 | 1 | 9 | 3800 | 1 | 13 | 430 | 1 | 21 | 3 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 979 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 1 | 0
1980-09-17 | 1900-09-16 | 8:00 | 8 | 375 | 1354 | 213 | 1 | 9 | 534 | 1 | 9 | 64 | 1 | 13 | 22000 | 1 | 9 | 46100 | 1 | 9 | 9200 | 1 | 13 | 1200 | 1 | 18 | 7 | A | 7 | 1 | A | 7 | 8.3 | 46.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.46 | 1 | 0
1980-09-17 | 1900-09-16 | 9:00 | 9 | 618 | 1354 | 401 | 1 | 9 | 722 | 1 | 9 | 70 | 1 | 13 | 42400 | 1 | 9 | 70300 | 1 | 9 | 10200 | 1 | 13 | 1530 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 11.7 | 53.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 60 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.68 | 1 | 0
1980-09-17 | 1900-09-16 | 10:00 | 10 | 821 | 1354 | 559 | 1 | 9 | 781 | 1 | 9 | 83 | 1 | 13 | 58100 | 1 | 9 | 77300 | 1 | 9 | 11100 | 1 | 13 | 1910 | 1 | 18 | 6 | A | 7 | 1 | A | 7 | 12.8 | 55.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.36 | 1 | 0
1980-09-17 | 1900-09-16 | 11:00 | 11 | 970 | 1354 | 676 | 1 | 9 | 786 | 1 | 9 | 110 | 1 | 13 | 72300 | 1 | 9 | 79600 | 1 | 9 | 15100 | 1 | 13 | 3170 | 1 | 18 | 6 | A | 7 | 1 | A | 7 | 14.4 | 57.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.08 | 1 | 0
1980-09-17 | 1900-09-16 | 12:00 | 12 | 1056 | 1354 | 820 | 1 | 9 | 926 | 1 | 9 | 94 | 1 | 13 | 84900 | 1 | 9 | 92700 | 1 | 9 | 12400 | 1 | 13 | 2870 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.54 | A | 7 | 979 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.36 | 1 | 0
1980-09-17 | 1900-09-16 | 13:00 | 13 | 1071 | 1354 | 835 | 1 | 9 | 945 | 1 | 9 | 84 | 1 | 13 | 86800 | 1 | 9 | 94700 | 1 | 9 | 11700 | 1 | 13 | 2770 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.34 | 1 | 0
1980-09-17 | 1900-09-16 | 14:00 | 14 | 1015 | 1354 | 786 | 1 | 9 | 935 | 1 | 9 | 81 | 1 | 13 | 81800 | 1 | 9 | 93600 | 1 | 9 | 11400 | 1 | 13 | 2460 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.36 | 1 | 0
1980-09-17 | 1900-09-16 | 15:00 | 15 | 893 | 1354 | 679 | 1 | 9 | 912 | 1 | 9 | 74 | 1 | 13 | 70800 | 1 | 9 | 90800 | 1 | 9 | 10800 | 1 | 13 | 1980 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.47 | A | 7 | 977 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.06 | 1 | 0
1980-09-17 | 1900-09-16 | 16:00 | 16 | 711 | 1354 | 515 | 1 | 9 | 854 | 1 | 9 | 63 | 1 | 13 | 53900 | 1 | 9 | 83700 | 1 | 9 | 9800 | 1 | 13 | 1540 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.42 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.68 | 1 | 0
1980-09-17 | 1900-09-16 | 17:00 | 17 | 484 | 1354 | 322 | 1 | 9 | 761 | 1 | 9 | 47 | 1 | 13 | 33700 | 1 | 9 | 70800 | 1 | 9 | 8300 | 1 | 13 | 1120 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.45 | A | 7 | 977 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.76 | 1 | 0
1980-09-17 | 1900-09-16 | 18:00 | 18 | 226 | 1354 | 121 | 1 | 13 | 532 | 1 | 9 | 30 | 1 | 13 | 12200 | 1 | 13 | 39900 | 1 | 9 | 5600 | 1 | 13 | 610 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.5 | A | 7 | 977 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.56 | 1 | 0
1980-09-17 | 1900-09-16 | 19:00 | 19 | 17 | 508 | 17 | 1 | 13 | 66 | 1 | 9 | 9 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.052 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.04 | 1 | 0
1980-09-17 | 1900-09-16 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.74 | 1 | 0
1980-09-17 | 1900-09-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 1 | 0
1980-09-17 | 1900-09-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.84 | 1 | 0
1980-09-17 | 1900-09-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.84 | 1 | 0
1980-09-17 | 1900-09-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.8 | A | 7 | 979 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 1 | 0
1980-09-18 | 1900-09-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.44 | 2 | 0
1980-09-18 | 1900-09-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.44 | 2 | 0
1980-09-18 | 1900-09-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.84 | 2 | 0
1980-09-18 | 1900-09-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.86 | 2 | 0
1980-09-18 | 1900-09-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.8 | A | 7 | 979 | A | 7 | 180 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.06 | 2 | 0
1980-09-18 | 1900-09-17 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 6.7 | 44.06 | A | 7 | 0.8 | A | 7 | 980 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.26 | 2 | 0
1980-09-18 | 1900-09-17 | 7:00 | 7 | 109 | 1253 | 41 | 1 | 13 | 104 | 1 | 9 | 30 | 1 | 13 | 4200 | 1 | 13 | 4700 | 1 | 9 | 3800 | 1 | 13 | 540 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.83 | A | 7 | 980 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.34 | 2 | 0
1980-09-18 | 1900-09-17 | 8:00 | 8 | 371 | 1354 | 199 | 1 | 9 | 463 | 1 | 9 | 71 | 1 | 13 | 20400 | 1 | 9 | 39600 | 1 | 9 | 9500 | 1 | 13 | 1300 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.48 | 2 | 0
1980-09-18 | 1900-09-17 | 9:00 | 9 | 614 | 1354 | 397 | 1 | 9 | 645 | 1 | 9 | 103 | 1 | 13 | 41500 | 1 | 9 | 62700 | 1 | 9 | 13000 | 1 | 13 | 2120 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.63 | A | 7 | 981 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.66 | 2 | 0
1980-09-18 | 1900-09-17 | 10:00 | 10 | 817 | 1354 | 577 | 1 | 9 | 739 | 1 | 9 | 128 | 1 | 13 | 61100 | 1 | 9 | 74700 | 1 | 9 | 15900 | 1 | 13 | 3100 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.96 | 2 | 0
1980-09-18 | 1900-09-17 | 11:00 | 11 | 966 | 1354 | 710 | 1 | 9 | 789 | 1 | 9 | 144 | 1 | 13 | 73600 | 1 | 9 | 78900 | 1 | 9 | 17200 | 1 | 13 | 3760 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.5 | A | 7 | 981 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.84 | 2 | 0
1980-09-18 | 1900-09-17 | 12:00 | 12 | 1051 | 1354 | 786 | 1 | 9 | 811 | 1 | 9 | 153 | 1 | 13 | 81900 | 1 | 9 | 81400 | 1 | 9 | 18600 | 1 | 13 | 4690 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.47 | A | 7 | 981 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.04 | 2 | 0
1980-09-18 | 1900-09-17 | 13:00 | 13 | 1066 | 1354 | 804 | 1 | 9 | 820 | 1 | 9 | 154 | 1 | 13 | 83900 | 1 | 9 | 82400 | 1 | 9 | 18800 | 1 | 13 | 4880 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.41 | A | 7 | 981 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.16 | 2 | 0
1980-09-18 | 1900-09-17 | 14:00 | 14 | 1010 | 1354 | 751 | 1 | 9 | 802 | 1 | 9 | 149 | 1 | 13 | 78000 | 1 | 9 | 80400 | 1 | 9 | 17900 | 1 | 13 | 4210 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.4 | A | 7 | 980 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.84 | 2 | 0
1980-09-18 | 1900-09-17 | 15:00 | 15 | 887 | 1354 | 639 | 1 | 9 | 762 | 1 | 9 | 136 | 1 | 13 | 67900 | 1 | 9 | 77600 | 1 | 9 | 17000 | 1 | 13 | 3570 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.4 | A | 7 | 980 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.54 | 2 | 0
1980-09-18 | 1900-09-17 | 16:00 | 16 | 705 | 1354 | 478 | 1 | 9 | 693 | 1 | 9 | 115 | 1 | 13 | 50200 | 1 | 9 | 68800 | 1 | 9 | 14300 | 1 | 13 | 2510 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.38 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.44 | 2 | 0
1980-09-18 | 1900-09-17 | 17:00 | 17 | 477 | 1354 | 282 | 1 | 9 | 553 | 1 | 9 | 85 | 1 | 13 | 29100 | 1 | 9 | 50900 | 1 | 9 | 11100 | 1 | 13 | 1630 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.4 | A | 7 | 979 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.54 | 2 | 0
1980-09-18 | 1900-09-17 | 18:00 | 18 | 219 | 1354 | 94 | 1 | 13 | 274 | 1 | 9 | 49 | 1 | 13 | 9800 | 1 | 13 | 18500 | 1 | 9 | 6800 | 1 | 13 | 880 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.45 | A | 7 | 979 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.42 | 2 | 0
1980-09-18 | 1900-09-17 | 19:00 | 19 | 14 | 463 | 9 | 1 | 13 | 7 | 1 | 9 | 9 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.52 | A | 7 | 979 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.92 | 2 | 0
1980-09-18 | 1900-09-17 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.72 | 2 | 0
1980-09-18 | 1900-09-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 15.6 | 60.08 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.88 | 2 | 0
1980-09-18 | 1900-09-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.66 | 2 | 0
1980-09-18 | 1900-09-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 981 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 2 | 0
1980-09-18 | 1900-09-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 2 | 0
1980-09-19 | 1900-09-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 15.6 | 60.08 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.48 | 3 | 0
1980-09-19 | 1900-09-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.88 | 3 | 0
1980-09-19 | 1900-09-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.68 | 3 | 0
1980-09-19 | 1900-09-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.68 | 3 | 0
1980-09-19 | 1900-09-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.36 | 3 | 0
1980-09-19 | 1900-09-18 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.46 | 3 | 0
1980-09-19 | 1900-09-18 | 7:00 | 7 | 106 | 1231 | 44 | 1 | 13 | 152 | 1 | 9 | 28 | 1 | 13 | 4400 | 1 | 13 | 7400 | 1 | 9 | 3700 | 1 | 13 | 500 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 16.7 | 62.06 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.96 | 3 | 0
1980-09-19 | 1900-09-18 | 8:00 | 8 | 367 | 1355 | 203 | 1 | 9 | 523 | 1 | 9 | 60 | 1 | 13 | 21000 | 1 | 9 | 44900 | 1 | 9 | 8800 | 1 | 13 | 1130 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 17.8 | 64.04 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.74 | 3 | 0
1980-09-19 | 1900-09-18 | 9:00 | 9 | 610 | 1355 | 397 | 1 | 9 | 680 | 1 | 9 | 89 | 1 | 13 | 41900 | 1 | 9 | 66500 | 1 | 9 | 11900 | 1 | 13 | 1860 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 19.4 | 66.92 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 62.42 | 3 | 0
1980-09-19 | 1900-09-18 | 10:00 | 10 | 813 | 1355 | 496 | 1 | 9 | 605 | 1 | 9 | 131 | 1 | 13 | 52400 | 1 | 9 | 61000 | 1 | 9 | 15700 | 1 | 13 | 3140 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 26.1 | 78.98 | A | 7 | 20 | 68 | A | 7 | 0.69 | A | 7 | 979 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.2 | 3 | 0
1980-09-19 | 1900-09-18 | 11:00 | 11 | 961 | 1355 | 538 | 1 | 13 | 376 | 1 | 13 | 269 | 1 | 13 | 58700 | 1 | 13 | 40600 | 1 | 13 | 29800 | 1 | 13 | 7700 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 26.7 | 80.06 | A | 7 | 20 | 68 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 610 | A | 7 | 3.5 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.7 | 3 | 0
1980-09-19 | 1900-09-18 | 12:00 | 12 | 1046 | 1355 | 643 | 1 | 13 | 525 | 1 | 13 | 236 | 1 | 13 | 69800 | 1 | 13 | 54800 | 1 | 13 | 27400 | 1 | 13 | 7800 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 28.9 | 84.02 | A | 7 | 21.1 | 69.98 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 7620 | A | 7 | 3.7 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 61.48 | 3 | 0
1980-09-19 | 1900-09-18 | 13:00 | 13 | 1061 | 1355 | 740 | 1 | 9 | 743 | 1 | 9 | 155 | 1 | 13 | 77100 | 1 | 9 | 74600 | 1 | 9 | 18600 | 1 | 13 | 4840 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 30 | 86 | A | 7 | 20.6 | 69.08 | A | 7 | 0.57 | A | 7 | 976 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.18 | 3 | 0
1980-09-19 | 1900-09-18 | 14:00 | 14 | 1004 | 1355 | 684 | 1 | 9 | 680 | 1 | 9 | 177 | 1 | 13 | 72400 | 1 | 9 | 69300 | 1 | 9 | 21000 | 1 | 13 | 5430 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 30.6 | 87.08 | A | 7 | 20.6 | 69.08 | A | 7 | 0.55 | A | 7 | 975 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 3 | 0
1980-09-19 | 1900-09-18 | 15:00 | 15 | 881 | 1355 | 578 | 1 | 13 | 616 | 1 | 13 | 175 | 1 | 13 | 60300 | 1 | 13 | 61900 | 1 | 13 | 20000 | 1 | 13 | 4400 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 32.2 | 89.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.5 | A | 7 | 974 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.38 | 3 | 0
1980-09-19 | 1900-09-18 | 16:00 | 16 | 698 | 1355 | 444 | 1 | 9 | 648 | 1 | 9 | 108 | 1 | 13 | 46800 | 1 | 9 | 64400 | 1 | 9 | 13500 | 1 | 13 | 2370 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 32.2 | 89.96 | A | 7 | 20.6 | 69.08 | A | 7 | 0.5 | A | 7 | 974 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.38 | 3 | 0
1980-09-19 | 1900-09-18 | 17:00 | 17 | 470 | 1355 | 262 | 1 | 9 | 507 | 1 | 9 | 84 | 1 | 13 | 27000 | 1 | 9 | 46500 | 1 | 9 | 10800 | 1 | 13 | 1600 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 32.2 | 89.96 | A | 7 | 20 | 68 | A | 7 | 0.48 | A | 7 | 973 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 3 | 0
1980-09-19 | 1900-09-18 | 18:00 | 18 | 212 | 1355 | 90 | 1 | 13 | 269 | 1 | 9 | 47 | 1 | 13 | 9300 | 1 | 13 | 17900 | 1 | 9 | 6500 | 1 | 13 | 840 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | 30.6 | 87.08 | A | 7 | 19.4 | 66.92 | A | 7 | 0.52 | A | 7 | 973 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 3 | 0
1980-09-19 | 1900-09-18 | 19:00 | 19 | 12 | 418 | 8 | 1 | 13 | 12 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 28.9 | 84.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.55 | A | 7 | 973 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.117 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 3 | 0
1980-09-19 | 1900-09-18 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 28.9 | 84.02 | A | 7 | 18.9 | 66.02 | A | 7 | 0.55 | A | 7 | 973 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.12 | 3 | 0
1980-09-19 | 1900-09-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.55 | A | 7 | 973 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.24 | 3 | 0
1980-09-19 | 1900-09-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.55 | A | 7 | 973 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 3 | 0
1980-09-19 | 1900-09-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.55 | A | 7 | 973 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.44 | 3 | 0
1980-09-19 | 1900-09-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.53 | A | 7 | 972 | A | 7 | 180 | A | 7 | 9.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.06 | 3 | 0
1980-09-20 | 1900-09-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.56 | A | 7 | 972 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.76 | 4 | 0
1980-09-20 | 1900-09-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.56 | A | 7 | 972 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.96 | 4 | 0
1980-09-20 | 1900-09-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 15.6 | 60.08 | A | 7 | 0.54 | A | 7 | 972 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.88 | 4 | 0
1980-09-20 | 1900-09-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 25 | 77 | A | 7 | 15.6 | 60.08 | A | 7 | 0.56 | A | 7 | 972 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.28 | 4 | 0
1980-09-20 | 1900-09-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.58 | A | 7 | 972 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.78 | 4 | 0
1980-09-20 | 1900-09-19 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.6 | A | 7 | 972 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.98 | 4 | 0
1980-09-20 | 1900-09-19 | 7:00 | 7 | 102 | 1209 | 36 | 1 | 13 | 57 | 1 | 9 | 30 | 1 | 13 | 3800 | 1 | 13 | 3000 | 1 | 9 | 3600 | 1 | 13 | 620 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.64 | A | 7 | 972 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.76 | 4 | 0
1980-09-20 | 1900-09-19 | 8:00 | 8 | 363 | 1356 | 181 | 1 | 9 | 380 | 1 | 9 | 78 | 1 | 13 | 19000 | 1 | 9 | 32300 | 1 | 9 | 10400 | 1 | 13 | 1420 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | A | 7 | 972 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.66 | 4 | 0
1980-09-20 | 1900-09-19 | 9:00 | 9 | 606 | 1356 | 374 | 1 | 9 | 571 | 1 | 9 | 117 | 1 | 13 | 38700 | 1 | 9 | 55000 | 1 | 9 | 14000 | 1 | 13 | 2340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.58 | A | 7 | 972 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.94 | 4 | 0
1980-09-20 | 1900-09-19 | 10:00 | 10 | 808 | 1356 | 554 | 1 | 9 | 678 | 1 | 9 | 147 | 1 | 13 | 58000 | 1 | 9 | 68000 | 1 | 9 | 17400 | 1 | 13 | 3450 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 29.4 | 84.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.53 | A | 7 | 972 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.62 | 4 | 0
1980-09-20 | 1900-09-19 | 11:00 | 11 | 957 | 1356 | 685 | 1 | 9 | 730 | 1 | 9 | 167 | 1 | 13 | 72500 | 1 | 9 | 74200 | 1 | 9 | 19900 | 1 | 13 | 4740 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 31.1 | 87.98 | A | 7 | 18.9 | 66.02 | A | 7 | 0.48 | A | 7 | 972 | A | 7 | 200 | A | 7 | 11.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.42 | 4 | 0
1980-09-20 | 1900-09-19 | 12:00 | 12 | 1041 | 1356 | 758 | 1 | 9 | 753 | 1 | 9 | 177 | 1 | 13 | 80700 | 1 | 9 | 76900 | 1 | 9 | 21400 | 1 | 13 | 5830 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.45 | A | 7 | 971 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.62 | 4 | 0
1980-09-20 | 1900-09-19 | 13:00 | 13 | 1055 | 1356 | 775 | 1 | 9 | 762 | 1 | 9 | 179 | 1 | 13 | 82500 | 1 | 9 | 77900 | 1 | 9 | 21700 | 1 | 13 | 6070 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.3 | 91.94 | A | 7 | 18.3 | 64.94 | A | 7 | 0.41 | A | 7 | 970 | A | 7 | 190 | A | 7 | 12.4 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.74 | 4 | 0
1980-09-20 | 1900-09-19 | 14:00 | 14 | 999 | 1356 | 726 | 1 | 9 | 747 | 1 | 9 | 172 | 1 | 13 | 76900 | 1 | 9 | 76100 | 1 | 9 | 20700 | 1 | 13 | 5230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.38 | A | 7 | 969 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.34 | 4 | 0
1980-09-20 | 1900-09-19 | 15:00 | 15 | 875 | 1356 | 613 | 1 | 9 | 704 | 1 | 9 | 156 | 1 | 13 | 64500 | 1 | 9 | 71100 | 1 | 9 | 18500 | 1 | 13 | 3950 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.4 | A | 7 | 969 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.54 | 4 | 0
1980-09-20 | 1900-09-19 | 16:00 | 16 | 692 | 1356 | 451 | 1 | 9 | 624 | 1 | 9 | 130 | 1 | 13 | 46800 | 1 | 9 | 61400 | 1 | 9 | 15400 | 1 | 13 | 2750 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.4 | A | 7 | 969 | A | 7 | 190 | A | 7 | 11.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.54 | 4 | 0
1980-09-20 | 1900-09-19 | 17:00 | 17 | 463 | 1356 | 204 | 1 | 9 | 316 | 1 | 9 | 95 | 1 | 13 | 21700 | 1 | 9 | 29200 | 1 | 9 | 11700 | 1 | 13 | 1770 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 33.3 | 91.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.38 | A | 7 | 968 | A | 7 | 190 | A | 7 | 12.4 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.46 | 4 | 0
1980-09-20 | 1900-09-19 | 18:00 | 18 | 205 | 1356 | 66 | 1 | 13 | 66 | 1 | 13 | 56 | 1 | 13 | 7200 | 1 | 13 | 4500 | 1 | 13 | 6500 | 1 | 13 | 1190 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 32.2 | 89.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.41 | A | 7 | 968 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.26 | 4 | 0
1980-09-20 | 1900-09-19 | 19:00 | 19 | 10 | 395 | 4 | 1 | 13 | 1 | 1 | 13 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 30.6 | 87.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.42 | A | 7 | 969 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.201 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.88 | 4 | 0
1980-09-20 | 1900-09-19 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 27.8 | 82.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.47 | A | 7 | 970 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.38 | 4 | 0
1980-09-20 | 1900-09-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 25.6 | 78.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.56 | A | 7 | 972 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 1830 | A | 7 | 2.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.08 | 4 | 0
1980-09-20 | 1900-09-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 24.4 | 75.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.58 | A | 7 | 972 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 1520 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.78 | 4 | 0
1980-09-20 | 1900-09-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 22.8 | 73.04 | A | 7 | 14.4 | 57.92 | A | 7 | 0.59 | A | 7 | 973 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.12 | 4 | 0
1980-09-20 | 1900-09-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 21.1 | 69.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.66 | A | 7 | 973 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 1830 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 4 | 0
1980-09-21 | 1900-09-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 20.6 | 69.08 | A | 7 | 15 | 59 | A | 7 | 0.71 | A | 7 | 973 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 1830 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.5 | 5 | 0
1980-09-21 | 1900-09-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.78 | A | 7 | 973 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 1400 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.88 | 5 | 0
1980-09-21 | 1900-09-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 2130 | A | 7 | 2.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.88 | 5 | 0
1980-09-21 | 1900-09-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | 15 | 59 | A | 7 | 0.81 | A | 7 | 973 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.4 | 5 | 0
1980-09-21 | 1900-09-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56 | 5 | 0
1980-09-21 | 1900-09-20 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.87 | A | 7 | 973 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.52 | 5 | 0
1980-09-21 | 1900-09-20 | 7:00 | 7 | 99 | 1187 | 36 | 1 | 13 | 93 | 1 | 9 | 26 | 1 | 13 | 3700 | 1 | 13 | 4100 | 1 | 9 | 3300 | 1 | 13 | 460 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 17.2 | 62.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.02 | 5 | 0
1980-09-21 | 1900-09-20 | 8:00 | 8 | 359 | 1357 | 190 | 1 | 9 | 464 | 1 | 9 | 66 | 1 | 13 | 19500 | 1 | 9 | 39300 | 1 | 9 | 9000 | 1 | 13 | 1210 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.76 | A | 7 | 973 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.26 | 5 | 0
1980-09-21 | 1900-09-20 | 9:00 | 9 | 602 | 1357 | 382 | 1 | 9 | 641 | 1 | 9 | 96 | 1 | 13 | 40100 | 1 | 9 | 62300 | 1 | 9 | 12400 | 1 | 13 | 1970 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 18.9 | 66.02 | A | 7 | 0.67 | A | 7 | 973 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.3 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.92 | 5 | 0
1980-09-21 | 1900-09-20 | 10:00 | 10 | 804 | 1357 | 556 | 1 | 9 | 732 | 1 | 9 | 119 | 1 | 13 | 59100 | 1 | 9 | 74000 | 1 | 9 | 15000 | 1 | 13 | 2860 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 20 | 68 | A | 7 | 0.65 | A | 7 | 972 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.5 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.2 | 5 | 0
1980-09-21 | 1900-09-20 | 11:00 | 11 | 953 | 1357 | 690 | 1 | 9 | 786 | 1 | 9 | 135 | 1 | 13 | 71900 | 1 | 9 | 78700 | 1 | 9 | 16500 | 1 | 13 | 3520 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.61 | A | 7 | 972 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 5 | 0
1980-09-21 | 1900-09-20 | 12:00 | 12 | 1036 | 1357 | 728 | 1 | 9 | 761 | 1 | 9 | 144 | 1 | 13 | 76300 | 1 | 9 | 76500 | 1 | 9 | 17700 | 1 | 13 | 4340 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 31.1 | 87.98 | A | 7 | 21.1 | 69.98 | A | 7 | 0.55 | A | 7 | 971 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.48 | 5 | 0
1980-09-21 | 1900-09-20 | 13:00 | 13 | 1050 | 1357 | 654 | 1 | 9 | 658 | 1 | 9 | 142 | 1 | 13 | 70700 | 1 | 9 | 67800 | 1 | 9 | 18100 | 1 | 13 | 4850 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 32.2 | 89.96 | A | 7 | 21.1 | 69.98 | A | 7 | 0.52 | A | 7 | 970 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.7 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.68 | 5 | 0
1980-09-21 | 1900-09-20 | 14:00 | 14 | 993 | 1357 | 715 | 1 | 9 | 782 | 1 | 9 | 139 | 1 | 13 | 74700 | 1 | 9 | 78500 | 1 | 9 | 17100 | 1 | 13 | 3870 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 20.6 | 69.08 | A | 7 | 0.46 | A | 7 | 969 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.6 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.28 | 5 | 0
1980-09-21 | 1900-09-20 | 15:00 | 15 | 868 | 1357 | 616 | 1 | 9 | 761 | 1 | 9 | 126 | 1 | 13 | 63800 | 1 | 9 | 75800 | 1 | 9 | 15200 | 1 | 13 | 2930 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 34.4 | 93.92 | A | 7 | 20 | 68 | A | 7 | 0.43 | A | 7 | 968 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.4 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.7 | 5 | 0
1980-09-21 | 1900-09-20 | 16:00 | 16 | 685 | 1357 | 459 | 1 | 9 | 693 | 1 | 9 | 106 | 1 | 13 | 48300 | 1 | 9 | 68700 | 1 | 9 | 13500 | 1 | 13 | 2300 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 34.4 | 93.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.38 | A | 7 | 968 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.04 | 5 | 0
1980-09-21 | 1900-09-20 | 17:00 | 17 | 456 | 1357 | 265 | 1 | 9 | 550 | 1 | 9 | 78 | 1 | 13 | 27400 | 1 | 9 | 50200 | 1 | 9 | 10500 | 1 | 13 | 1490 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 33.9 | 93.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.4 | A | 7 | 968 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.54 | 5 | 0
1980-09-21 | 1900-09-20 | 18:00 | 18 | 197 | 1357 | 83 | 1 | 13 | 261 | 1 | 9 | 44 | 1 | 13 | 8600 | 1 | 13 | 16700 | 1 | 9 | 6200 | 1 | 13 | 790 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 31.7 | 89.06 | A | 7 | 18.9 | 66.02 | A | 7 | 0.47 | A | 7 | 968 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.12 | 5 | 0
1980-09-21 | 1900-09-20 | 19:00 | 19 | 8 | 350 | 6 | 1 | 13 | 4 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 30 | 86 | A | 7 | 18.9 | 66.02 | A | 7 | 0.51 | A | 7 | 969 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | 0.144 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.12 | 5 | 0
1980-09-21 | 1900-09-20 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 28.9 | 84.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.53 | A | 7 | 969 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.74 | 5 | 0
1980-09-21 | 1900-09-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.56 | A | 7 | 969 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.44 | 5 | 0
1980-09-21 | 1900-09-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 18.9 | 66.02 | A | 7 | 0.6 | A | 7 | 969 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.32 | 5 | 0
1980-09-21 | 1900-09-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.56 | A | 7 | 969 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.44 | 5 | 0
1980-09-21 | 1900-09-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 18.3 | 64.94 | A | 7 | 0.56 | A | 7 | 969 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.44 | 5 | 0
1980-09-22 | 1900-09-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 27.2 | 80.96 | A | 7 | 17.8 | 64.04 | A | 7 | 0.56 | A | 7 | 969 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 6 | 0
1980-09-22 | 1900-09-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 18.3 | 64.94 | A | 7 | 0.58 | A | 7 | 969 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.94 | 6 | 0
1980-09-22 | 1900-09-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 18.3 | 64.94 | A | 7 | 0.6 | A | 7 | 969 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.34 | 6 | 0
1980-09-22 | 1900-09-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 26.1 | 78.98 | A | 7 | 18.3 | 64.94 | A | 7 | 0.62 | A | 7 | 971 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 56.84 | 6 | 0
1980-09-22 | 1900-09-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 23.9 | 75.02 | A | 7 | 18.3 | 64.94 | A | 7 | 0.71 | A | 7 | 971 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.84 | 6 | 0
1980-09-22 | 1900-09-21 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 17.8 | 64.04 | A | 7 | 0.74 | A | 7 | 973 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 1520 | A | 7 | 3.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 58.74 | 6 | 0
1980-09-22 | 1900-09-21 | 7:00 | 7 | 95 | 1165 | 27 | 1 | 13 | 2 | 1 | 9 | 27 | 1 | 13 | 3000 | 1 | 13 | 0 | 1 | 9 | 3000 | 1 | 13 | 900 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 15.6 | 60.08 | A | 7 | 0.66 | A | 7 | 974 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 1160 | A | 7 | 2.7 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.48 | 6 | 0
1980-09-22 | 1900-09-21 | 8:00 | 8 | 355 | 1357 | 79 | 1 | 9 | 5 | 1 | 9 | 78 | 1 | 13 | 9000 | 1 | 9 | 200 | 1 | 9 | 9000 | 1 | 13 | 2920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 975 | A | 7 | 350 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1160 | A | 7 | 2.5 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 6 | 0
1980-09-22 | 1900-09-21 | 9:00 | 9 | 598 | 1357 | 118 | 1 | 9 | 2 | 1 | 9 | 118 | 1 | 13 | 13900 | 1 | 9 | 100 | 1 | 9 | 13800 | 1 | 13 | 5040 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 13.3 | 55.94 | A | 7 | 0.66 | A | 7 | 977 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1280 | A | 7 | 2.4 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.74 | 6 | 0
1980-09-22 | 1900-09-21 | 10:00 | 10 | 800 | 1357 | 333 | 1 | 9 | 86 | 1 | 9 | 282 | 1 | 13 | 36600 | 1 | 9 | 8700 | 1 | 9 | 31400 | 1 | 13 | 8850 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 11.7 | 53.06 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 350 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 2.1 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.26 | 6 | 0
1980-09-22 | 1900-09-21 | 11:00 | 11 | 948 | 1357 | 658 | 1 | 9 | 643 | 1 | 9 | 206 | 1 | 13 | 68400 | 1 | 9 | 64600 | 1 | 9 | 23200 | 1 | 13 | 5600 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 21.7 | 71.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.76 | 6 | 0
1980-09-22 | 1900-09-21 | 12:00 | 12 | 1031 | 1357 | 706 | 1 | 9 | 698 | 1 | 9 | 173 | 1 | 13 | 75200 | 1 | 9 | 71300 | 1 | 9 | 20800 | 1 | 13 | 5590 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 23.9 | 75.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.45 | A | 7 | 978 | A | 7 | 10 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.38 | 6 | 0
1980-09-22 | 1900-09-21 | 13:00 | 13 | 1045 | 1357 | 709 | 1 | 13 | 662 | 1 | 13 | 196 | 1 | 13 | 74800 | 1 | 13 | 67300 | 1 | 13 | 22900 | 1 | 13 | 6420 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 23.9 | 75.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.43 | A | 7 | 979 | A | 7 | 10 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.28 | 6 | 0
1980-09-22 | 1900-09-21 | 14:00 | 14 | 987 | 1357 | 675 | 1 | 9 | 677 | 1 | 9 | 180 | 1 | 13 | 71300 | 1 | 9 | 68800 | 1 | 9 | 21100 | 1 | 13 | 5330 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 23.3 | 73.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.45 | A | 7 | 979 | A | 7 | 340 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.68 | 6 | 0
1980-09-22 | 1900-09-21 | 15:00 | 15 | 862 | 1357 | 586 | 1 | 9 | 706 | 1 | 9 | 135 | 1 | 13 | 62200 | 1 | 9 | 71600 | 1 | 9 | 16600 | 1 | 13 | 3420 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 22.8 | 73.04 | A | 7 | 10 | 50 | A | 7 | 0.44 | A | 7 | 980 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.6 | 6 | 0
1980-09-22 | 1900-09-21 | 16:00 | 16 | 679 | 1357 | 422 | 1 | 9 | 614 | 1 | 9 | 113 | 1 | 13 | 44200 | 1 | 9 | 60600 | 1 | 9 | 13800 | 1 | 13 | 2420 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 22.2 | 71.96 | A | 7 | 10 | 50 | A | 7 | 0.46 | A | 7 | 980 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41 | 6 | 0
1980-09-22 | 1900-09-21 | 17:00 | 17 | 449 | 1357 | 211 | 1 | 9 | 348 | 1 | 9 | 95 | 1 | 13 | 22400 | 1 | 9 | 31800 | 1 | 9 | 11800 | 1 | 13 | 1770 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 21.7 | 71.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.44 | A | 7 | 980 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.02 | 6 | 0
1980-09-22 | 1900-09-21 | 18:00 | 18 | 190 | 1357 | 75 | 1 | 13 | 184 | 1 | 9 | 49 | 1 | 13 | 7900 | 1 | 13 | 11200 | 1 | 9 | 6300 | 1 | 13 | 910 | 1 | 21 | 5 | A | 7 | 1 | A | 7 | 19.4 | 66.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.47 | A | 7 | 981 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 6 | 0
1980-09-22 | 1900-09-21 | 19:00 | 19 | 7 | 328 | 3 | 1 | 13 | 3 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | 16.7 | 62.06 | A | 7 | 7.2 | 44.96 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.134 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.16 | 6 | 0
1980-09-22 | 1900-09-21 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 15.6 | 60.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.58 | A | 7 | 982 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.76 | 6 | 0
1980-09-22 | 1900-09-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.36 | 6 | 0
1980-09-22 | 1900-09-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.86 | 6 | 0
1980-09-22 | 1900-09-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.67 | A | 7 | 984 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.36 | 6 | 0
1980-09-22 | 1900-09-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 11.7 | 53.06 | A | 7 | 6.7 | 44.06 | A | 7 | 0.72 | A | 7 | 984 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.06 | 6 | 0
1980-09-23 | 1900-09-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 11.1 | 51.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.72 | A | 7 | 984 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.08 | 7 | 0
1980-09-23 | 1900-09-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 6.1 | 42.98 | A | 7 | 0.74 | A | 7 | 984 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.38 | 7 | 0
1980-09-23 | 1900-09-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.77 | A | 7 | 984 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.98 | 7 | 0
1980-09-23 | 1900-09-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 984 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.78 | 7 | 0
1980-09-23 | 1900-09-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 5 | 41 | A | 7 | 0.8 | A | 7 | 984 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.3 | 7 | 0
1980-09-23 | 1900-09-22 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.86 | A | 7 | 984 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.12 | 7 | 0
1980-09-23 | 1900-09-22 | 7:00 | 7 | 92 | 1143 | 32 | 1 | 13 | 55 | 1 | 9 | 27 | 1 | 13 | 3500 | 1 | 13 | 2800 | 1 | 9 | 3200 | 1 | 13 | 560 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 7.8 | 46.04 | A | 7 | 5 | 41 | A | 7 | 0.83 | A | 7 | 985 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.7 | 7 | 0
1980-09-23 | 1900-09-22 | 8:00 | 8 | 351 | 1358 | 179 | 1 | 9 | 384 | 1 | 9 | 79 | 1 | 13 | 18800 | 1 | 9 | 32200 | 1 | 9 | 10400 | 1 | 13 | 1450 | 1 | 18 | 4 | A | 7 | 2 | A | 7 | 11.1 | 51.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.72 | A | 7 | 985 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.08 | 7 | 0
1980-09-23 | 1900-09-22 | 9:00 | 9 | 593 | 1358 | 371 | 1 | 9 | 521 | 1 | 9 | 142 | 1 | 13 | 39100 | 1 | 9 | 51000 | 1 | 9 | 16800 | 1 | 13 | 2840 | 1 | 18 | 8 | A | 7 | 1 | A | 7 | 15 | 59 | A | 7 | 3.9 | 39.02 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.32 | 7 | 0
1980-09-23 | 1900-09-22 | 10:00 | 10 | 796 | 1358 | 521 | 1 | 9 | 557 | 1 | 9 | 192 | 1 | 13 | 55300 | 1 | 9 | 57000 | 1 | 9 | 21900 | 1 | 13 | 4440 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | 17.2 | 62.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.4 | A | 7 | 985 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.94 | 7 | 0
1980-09-23 | 1900-09-22 | 11:00 | 11 | 943 | 1358 | 653 | 1 | 9 | 641 | 1 | 9 | 205 | 1 | 13 | 67900 | 1 | 9 | 64400 | 1 | 9 | 23100 | 1 | 13 | 5520 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 18.9 | 66.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.37 | A | 7 | 985 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.32 | 7 | 0
1980-09-23 | 1900-09-22 | 12:00 | 12 | 1027 | 1358 | 722 | 1 | 9 | 723 | 1 | 9 | 172 | 1 | 13 | 76800 | 1 | 9 | 73900 | 1 | 9 | 20800 | 1 | 13 | 5500 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 20 | 68 | A | 7 | 2.8 | 37.04 | A | 7 | 0.32 | A | 7 | 984 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 7 | 0
1980-09-23 | 1900-09-22 | 13:00 | 13 | 1039 | 1358 | 704 | 1 | 9 | 549 | 1 | 9 | 281 | 1 | 13 | 74900 | 1 | 9 | 57100 | 1 | 9 | 31000 | 1 | 13 | 9230 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.31 | A | 7 | 983 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 40200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.04 | 7 | 0
1980-09-23 | 1900-09-22 | 14:00 | 14 | 981 | 1358 | 690 | 1 | 9 | 685 | 1 | 9 | 192 | 1 | 13 | 72400 | 1 | 9 | 69300 | 1 | 9 | 22200 | 1 | 13 | 5570 | 1 | 18 | 8 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.29 | A | 7 | 982 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 40200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.36 | 7 | 0
1980-09-23 | 1900-09-22 | 15:00 | 15 | 856 | 1358 | 602 | 1 | 13 | 629 | 1 | 13 | 203 | 1 | 13 | 64300 | 1 | 13 | 64800 | 1 | 13 | 23300 | 1 | 13 | 4990 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 20.6 | 69.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.28 | A | 7 | 982 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.38 | 7 | 0
1980-09-23 | 1900-09-22 | 16:00 | 16 | 672 | 1358 | 335 | 1 | 13 | 287 | 1 | 13 | 192 | 1 | 13 | 35900 | 1 | 13 | 29700 | 1 | 13 | 21200 | 1 | 13 | 4280 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 20.6 | 69.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.28 | A | 7 | 981 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 6100 | A | 7 | 1.2 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.38 | 7 | 0
1980-09-23 | 1900-09-22 | 17:00 | 17 | 442 | 1358 | 202 | 1 | 13 | 268 | 1 | 13 | 114 | 1 | 13 | 21500 | 1 | 13 | 24900 | 1 | 13 | 13400 | 1 | 13 | 2260 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 20 | 68 | A | 7 | 1.7 | 35.06 | A | 7 | 0.3 | A | 7 | 981 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.46 | 7 | 0
1980-09-23 | 1900-09-22 | 18:00 | 18 | 183 | 1358 | 68 | 1 | 13 | 157 | 1 | 13 | 47 | 1 | 13 | 7200 | 1 | 13 | 9300 | 1 | 13 | 5900 | 1 | 13 | 870 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 17.8 | 64.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.34 | A | 7 | 981 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.96 | 7 | 0
1980-09-23 | 1900-09-22 | 19:00 | 19 | 5 | 283 | 2 | 1 | 13 | 2 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 15.6 | 60.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.41 | A | 7 | 981 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.159 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.56 | 7 | 0
1980-09-23 | 1900-09-22 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 13.3 | 55.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.49 | A | 7 | 981 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.44 | 7 | 0
1980-09-23 | 1900-09-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.53 | A | 7 | 981 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.94 | 7 | 0
1980-09-23 | 1900-09-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 2.8 | 37.04 | A | 7 | 0.55 | A | 7 | 982 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.24 | 7 | 0
1980-09-23 | 1900-09-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.66 | A | 7 | 981 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.74 | 7 | 0
1980-09-23 | 1900-09-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 3.3 | 37.94 | A | 7 | 0.64 | A | 7 | 981 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.44 | 7 | 0
1980-09-24 | 1900-09-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 3.3 | 37.94 | A | 7 | 0.64 | A | 7 | 980 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.44 | 1 | 0
1980-09-24 | 1900-09-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.74 | 1 | 0
1980-09-24 | 1900-09-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 3.3 | 37.94 | A | 7 | 0.68 | A | 7 | 979 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.94 | 1 | 0
1980-09-24 | 1900-09-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 8.9 | 48.02 | A | 7 | 3.3 | 37.94 | A | 7 | 0.68 | A | 7 | 979 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.94 | 1 | 0
1980-09-24 | 1900-09-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 8.9 | 48.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.32 | 1 | 0
1980-09-24 | 1900-09-23 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.32 | 1 | 0
1980-09-24 | 1900-09-23 | 7:00 | 7 | 89 | 1144 | 40 | 1 | 13 | 144 | 1 | 9 | 25 | 1 | 13 | 3900 | 1 | 13 | 6600 | 1 | 9 | 3300 | 1 | 13 | 440 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 4.4 | 39.92 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 80 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.12 | 1 | 0
1980-09-24 | 1900-09-23 | 8:00 | 8 | 347 | 1359 | 188 | 1 | 9 | 439 | 1 | 9 | 75 | 1 | 13 | 19800 | 1 | 9 | 36600 | 1 | 9 | 10400 | 1 | 13 | 1370 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 90 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.68 | 1 | 0
1980-09-24 | 1900-09-23 | 9:00 | 9 | 589 | 1359 | 362 | 1 | 9 | 528 | 1 | 9 | 131 | 1 | 13 | 38400 | 1 | 9 | 51600 | 1 | 9 | 15900 | 1 | 13 | 2590 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.52 | 1 | 0
1980-09-24 | 1900-09-23 | 10:00 | 10 | 791 | 1359 | 368 | 1 | 9 | 199 | 1 | 9 | 252 | 1 | 13 | 40300 | 1 | 9 | 20800 | 1 | 9 | 28100 | 1 | 13 | 6700 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 18.3 | 64.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 2 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.58 | 1 | 0
1980-09-24 | 1900-09-23 | 11:00 | 11 | 939 | 1359 | 393 | 1 | 9 | 54 | 1 | 9 | 355 | 1 | 13 | 43100 | 1 | 9 | 5600 | 1 | 9 | 39300 | 1 | 13 | 12090 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 11.1 | 51.98 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 2.1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.98 | 1 | 0
1980-09-24 | 1900-09-23 | 12:00 | 12 | 1021 | 1359 | 676 | 1 | 13 | 578 | 1 | 13 | 239 | 1 | 13 | 72900 | 1 | 13 | 60200 | 1 | 13 | 27500 | 1 | 13 | 7500 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 20.6 | 69.08 | A | 7 | 11.1 | 51.98 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 170 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.28 | 1 | 0
1980-09-24 | 1900-09-23 | 13:00 | 13 | 1034 | 1359 | 359 | 1 | 9 | 187 | 1 | 9 | 216 | 1 | 13 | 40200 | 1 | 9 | 20300 | 1 | 9 | 24700 | 1 | 13 | 6600 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 21.1 | 69.98 | A | 7 | 10 | 50 | A | 7 | 0.49 | A | 7 | 979 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 1980 | A | 7 | 1.9 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.5 | 1 | 0
1980-09-24 | 1900-09-23 | 14:00 | 14 | 975 | 1359 | 275 | 1 | 9 | 7 | 1 | 9 | 270 | 1 | 13 | 32100 | 1 | 9 | 600 | 1 | 9 | 31700 | 1 | 13 | 12050 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 10.6 | 51.08 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 2440 | A | 7 | 2 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.48 | 1 | 0
1980-09-24 | 1900-09-23 | 15:00 | 15 | 850 | 1359 | 268 | 1 | 9 | 3 | 1 | 9 | 266 | 1 | 13 | 30700 | 1 | 9 | 300 | 1 | 9 | 30500 | 1 | 13 | 11030 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 10.6 | 51.08 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 2290 | A | 7 | 2 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.48 | 1 | 0
1980-09-24 | 1900-09-23 | 16:00 | 16 | 665 | 1359 | 187 | 1 | 9 | 68 | 1 | 9 | 154 | 1 | 13 | 20600 | 1 | 9 | 6700 | 1 | 9 | 17400 | 1 | 13 | 4840 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 11.7 | 53.06 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 2130 | A | 7 | 2.1 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.56 | 1 | 0
1980-09-24 | 1900-09-23 | 17:00 | 17 | 435 | 1359 | 82 | 1 | 9 | 67 | 1 | 9 | 60 | 1 | 13 | 9300 | 1 | 9 | 6300 | 1 | 9 | 7300 | 1 | 13 | 1350 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 977 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 2130 | A | 7 | 2 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.28 | 1 | 0
1980-09-24 | 1900-09-23 | 18:00 | 18 | 176 | 1359 | 27 | 1 | 13 | 53 | 1 | 9 | 20 | 1 | 13 | 3000 | 1 | 13 | 3100 | 1 | 9 | 2600 | 1 | 13 | 330 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12900 | A | 7 | 2130 | A | 7 | 2.4 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 1 | 0
1980-09-24 | 1900-09-23 | 19:00 | 19 | 4 | 238 | 1 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 15 | 59 | A | 7 | 12.8 | 55.04 | A | 7 | 0.87 | A | 7 | 977 | A | 7 | 120 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 2130 | A | 7 | 2.3 | E | 8 | 0.105 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.74 | 1 | 0
1980-09-24 | 1900-09-23 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 14.4 | 57.92 | A | 7 | 12.2 | 53.96 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 2290 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.76 | 1 | 0
1980-09-24 | 1900-09-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.28 | 1 | 0
1980-09-24 | 1900-09-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 11.1 | 51.98 | A | 7 | 10 | 50 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 800 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.9 | 1 | 0
1980-09-24 | 1900-09-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 90 | A | 7 | 1.5 | A | 7 | 400 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 1 | 0
1980-09-24 | 1900-09-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 2400 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.82 | 1 | 0
1980-09-25 | 1900-09-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 2400 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.92 | 2 | 0
1980-09-25 | 1900-09-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 3200 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.84 | 2 | 0
1980-09-25 | 1900-09-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.94 | 2 | 0
1980-09-25 | 1900-09-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.96 | 2 | 0
1980-09-25 | 1900-09-24 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.96 | 2 | 0
1980-09-25 | 1900-09-24 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 8.9 | 48.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.89 | A | 7 | 981 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.36 | 2 | 0
1980-09-25 | 1900-09-24 | 7:00 | 7 | 85 | 1122 | 25 | 1 | 13 | 5 | 1 | 9 | 24 | 1 | 13 | 2700 | 1 | 13 | 0 | 1 | 9 | 2700 | 1 | 13 | 810 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.9 | A | 7 | 983 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.52 | 2 | 0
1980-09-25 | 1900-09-24 | 8:00 | 8 | 343 | 1360 | 126 | 1 | 13 | 102 | 1 | 9 | 100 | 1 | 13 | 13700 | 1 | 13 | 8700 | 1 | 9 | 11400 | 1 | 13 | 2190 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 11.7 | 53.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.86 | A | 7 | 983 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 1.9 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.72 | 2 | 0
1980-09-25 | 1900-09-24 | 9:00 | 9 | 585 | 1360 | 148 | 1 | 9 | 49 | 1 | 9 | 127 | 1 | 13 | 16300 | 1 | 9 | 4700 | 1 | 9 | 14300 | 1 | 13 | 3860 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 12.2 | 53.96 | A | 7 | 8.9 | 48.02 | A | 7 | 0.8 | A | 7 | 984 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.92 | 2 | 0
1980-09-25 | 1900-09-24 | 10:00 | 10 | 787 | 1360 | 398 | 1 | 9 | 224 | 1 | 9 | 268 | 1 | 13 | 43300 | 1 | 9 | 23300 | 1 | 9 | 29800 | 1 | 13 | 7110 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 13.3 | 55.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.75 | A | 7 | 986 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.12 | 2 | 0
1980-09-25 | 1900-09-24 | 11:00 | 11 | 934 | 1360 | 424 | 1 | 13 | 216 | 1 | 13 | 275 | 1 | 13 | 46100 | 1 | 13 | 23200 | 1 | 13 | 30100 | 1 | 13 | 7640 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 15 | 59 | A | 7 | 8.3 | 46.94 | A | 7 | 0.65 | A | 7 | 986 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 1.8 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.64 | 2 | 0
1980-09-25 | 1900-09-24 | 12:00 | 12 | 1016 | 1360 | 684 | 1 | 13 | 657 | 1 | 13 | 190 | 1 | 13 | 72100 | 1 | 13 | 66700 | 1 | 13 | 22100 | 1 | 13 | 5880 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 17.8 | 64.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.52 | A | 7 | 987 | A | 7 | 340 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.74 | 2 | 0
1980-09-25 | 1900-09-24 | 13:00 | 13 | 1029 | 1360 | 771 | 1 | 9 | 837 | 1 | 9 | 134 | 1 | 13 | 81200 | 1 | 9 | 84400 | 1 | 9 | 17200 | 1 | 13 | 4040 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.49 | A | 7 | 987 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.36 | 2 | 0
1980-09-25 | 1900-09-24 | 14:00 | 14 | 969 | 1360 | 725 | 1 | 9 | 831 | 1 | 9 | 129 | 1 | 13 | 76100 | 1 | 9 | 83500 | 1 | 9 | 16400 | 1 | 13 | 3510 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.47 | A | 7 | 987 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.06 | 2 | 0
1980-09-25 | 1900-09-24 | 15:00 | 15 | 843 | 1360 | 609 | 1 | 9 | 788 | 1 | 9 | 117 | 1 | 13 | 63300 | 1 | 9 | 78500 | 1 | 9 | 14500 | 1 | 13 | 2700 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.47 | A | 7 | 987 | A | 7 | 360 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.06 | 2 | 0
1980-09-25 | 1900-09-24 | 16:00 | 16 | 658 | 1360 | 449 | 1 | 9 | 720 | 1 | 9 | 97 | 1 | 13 | 47300 | 1 | 9 | 71100 | 1 | 9 | 12800 | 1 | 13 | 2080 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.43 | A | 7 | 986 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.78 | 2 | 0
1980-09-25 | 1900-09-24 | 17:00 | 17 | 428 | 1360 | 230 | 1 | 9 | 494 | 1 | 9 | 73 | 1 | 13 | 23800 | 1 | 9 | 44300 | 1 | 9 | 9800 | 1 | 13 | 1380 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.43 | A | 7 | 987 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.08 | 2 | 0
1980-09-25 | 1900-09-24 | 18:00 | 18 | 169 | 1360 | 53 | 1 | 13 | 137 | 1 | 9 | 35 | 1 | 13 | 5600 | 1 | 13 | 7700 | 1 | 9 | 4600 | 1 | 13 | 620 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | 5 | 41 | A | 7 | 0.46 | A | 7 | 987 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.6 | 2 | 0
1980-09-25 | 1900-09-24 | 19:00 | 19 | 3 | 215 | 1 | 1 | 13 | 2 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.53 | A | 7 | 987 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.13 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.72 | 2 | 0
1980-09-25 | 1900-09-24 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 12.8 | 55.04 | A | 7 | 4.4 | 39.92 | A | 7 | 0.57 | A | 7 | 988 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.22 | 2 | 0
1980-09-25 | 1900-09-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 10.6 | 51.08 | A | 7 | 4.4 | 39.92 | A | 7 | 0.66 | A | 7 | 989 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.52 | 2 | 0
1980-09-25 | 1900-09-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 10 | 50 | A | 7 | 3.9 | 39.02 | A | 7 | 0.66 | A | 7 | 990 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.72 | 2 | 0
1980-09-25 | 1900-09-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 8.9 | 48.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.71 | A | 7 | 991 | A | 7 | 60 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.32 | 2 | 0
1980-09-25 | 1900-09-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 8.9 | 48.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.71 | A | 7 | 991 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.32 | 2 | 0
1980-09-26 | 1900-09-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 7.8 | 46.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.74 | A | 7 | 991 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.74 | 3 | 0
1980-09-26 | 1900-09-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 6.7 | 44.06 | A | 7 | 2.8 | 37.04 | A | 7 | 0.76 | A | 7 | 992 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.14 | 3 | 0
1980-09-26 | 1900-09-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 6.1 | 42.98 | A | 7 | 2.8 | 37.04 | A | 7 | 0.79 | A | 7 | 992 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.54 | 3 | 0
1980-09-26 | 1900-09-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | 2.2 | 35.96 | A | 7 | 0.82 | A | 7 | 992 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.86 | 3 | 0
1980-09-26 | 1900-09-25 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 3.3 | 37.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.89 | A | 7 | 991 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.76 | 3 | 0
1980-09-26 | 1900-09-25 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 3.9 | 39.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.82 | A | 7 | 992 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 3 | 0
1980-09-26 | 1900-09-25 | 7:00 | 7 | 82 | 1100 | 31 | 1 | 13 | 12 | 1 | 13 | 30 | 1 | 13 | 3400 | 1 | 13 | 700 | 1 | 13 | 3300 | 1 | 13 | 700 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 4.4 | 39.92 | A | 7 | 2.2 | 35.96 | A | 7 | 0.86 | A | 7 | 992 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.26 | 3 | 0
1980-09-26 | 1900-09-25 | 8:00 | 8 | 338 | 1361 | 142 | 1 | 13 | 169 | 1 | 13 | 99 | 1 | 13 | 14900 | 1 | 13 | 14100 | 1 | 13 | 11300 | 1 | 13 | 1960 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 993 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.9 | 3 | 0
1980-09-26 | 1900-09-25 | 9:00 | 9 | 581 | 1361 | 241 | 1 | 13 | 143 | 1 | 13 | 179 | 1 | 13 | 26200 | 1 | 13 | 14300 | 1 | 13 | 20000 | 1 | 13 | 4260 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 12.8 | 55.04 | A | 7 | 5 | 41 | A | 7 | 0.59 | A | 7 | 993 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.5 | 3 | 0
1980-09-26 | 1900-09-25 | 10:00 | 10 | 782 | 1361 | 501 | 1 | 13 | 520 | 1 | 13 | 201 | 1 | 13 | 53000 | 1 | 13 | 53000 | 1 | 13 | 22400 | 1 | 13 | 4610 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 15.6 | 60.08 | A | 7 | 4.4 | 39.92 | A | 7 | 0.48 | A | 7 | 992 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 6100 | A | 7 | 1.4 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.02 | 3 | 0
1980-09-26 | 1900-09-25 | 11:00 | 11 | 929 | 1361 | 594 | 1 | 13 | 466 | 1 | 13 | 273 | 1 | 13 | 62200 | 1 | 13 | 48100 | 1 | 13 | 29300 | 1 | 13 | 7500 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 17.8 | 64.04 | A | 7 | 3.9 | 39.02 | A | 7 | 0.4 | A | 7 | 992 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 6100 | A | 7 | 1.4 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 3 | 0
1980-09-26 | 1900-09-25 | 12:00 | 12 | 1011 | 1361 | 630 | 1 | 13 | 459 | 1 | 13 | 287 | 1 | 13 | 66600 | 1 | 13 | 47700 | 1 | 13 | 31100 | 1 | 13 | 8950 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 18.9 | 66.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.34 | A | 7 | 992 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.44 | 3 | 0
1980-09-26 | 1900-09-25 | 13:00 | 13 | 1023 | 1361 | 699 | 1 | 13 | 537 | 1 | 13 | 293 | 1 | 13 | 73900 | 1 | 13 | 55800 | 1 | 13 | 31800 | 1 | 13 | 9340 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 18.3 | 64.94 | A | 7 | 3.9 | 39.02 | A | 7 | 0.39 | A | 7 | 991 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.62 | 3 | 0
1980-09-26 | 1900-09-25 | 14:00 | 14 | 963 | 1361 | 641 | 1 | 13 | 533 | 1 | 13 | 262 | 1 | 13 | 68000 | 1 | 13 | 55300 | 1 | 13 | 28700 | 1 | 13 | 7520 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 18.3 | 64.94 | A | 7 | 3.3 | 37.94 | A | 7 | 0.37 | A | 7 | 993 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.54 | 3 | 0
1980-09-26 | 1900-09-25 | 15:00 | 15 | 837 | 1361 | 429 | 1 | 13 | 347 | 1 | 13 | 214 | 1 | 13 | 46800 | 1 | 13 | 37100 | 1 | 13 | 23900 | 1 | 13 | 5260 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 19.4 | 66.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.33 | A | 7 | 989 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.34 | 3 | 0
1980-09-26 | 1900-09-25 | 16:00 | 16 | 652 | 1361 | 346 | 1 | 13 | 312 | 1 | 13 | 195 | 1 | 13 | 36900 | 1 | 13 | 32100 | 1 | 13 | 21400 | 1 | 13 | 4340 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 20 | 68 | A | 7 | 2.8 | 37.04 | A | 7 | 0.32 | A | 7 | 989 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 3 | 0
1980-09-26 | 1900-09-25 | 17:00 | 17 | 421 | 1361 | 209 | 1 | 13 | 328 | 1 | 13 | 107 | 1 | 13 | 21700 | 1 | 13 | 29300 | 1 | 13 | 12700 | 1 | 13 | 2020 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 19.4 | 66.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.33 | A | 7 | 989 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.34 | 3 | 0
1980-09-26 | 1900-09-25 | 18:00 | 18 | 162 | 1361 | 43 | 1 | 13 | 20 | 1 | 13 | 41 | 1 | 13 | 4700 | 1 | 13 | 1400 | 1 | 13 | 4600 | 1 | 13 | 990 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 3.9 | 39.02 | A | 7 | 0.41 | A | 7 | 988 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.92 | 3 | 0
1980-09-26 | 1900-09-25 | 19:00 | 19 | 2 | 170 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 14.4 | 57.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.49 | A | 7 | 988 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.154 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.42 | 3 | 0
1980-09-26 | 1900-09-25 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 13.9 | 57.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.51 | A | 7 | 989 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.72 | 3 | 0
1980-09-26 | 1900-09-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 4.4 | 39.92 | A | 7 | 0.55 | A | 7 | 989 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.02 | 3 | 0
1980-09-26 | 1900-09-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 13.9 | 57.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.51 | A | 7 | 989 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.72 | 3 | 0
1980-09-26 | 1900-09-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 4.4 | 39.92 | A | 7 | 0.55 | A | 7 | 989 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.02 | 3 | 0
1980-09-26 | 1900-09-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 13.9 | 57.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.53 | A | 7 | 988 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.72 | 3 | 0
1980-09-27 | 1900-09-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 4.4 | 39.92 | A | 7 | 0.55 | A | 7 | 988 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.02 | 4 | 0
1980-09-27 | 1900-09-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 14.4 | 57.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.49 | A | 7 | 988 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.42 | 4 | 0
1980-09-27 | 1900-09-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.51 | A | 7 | 988 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.72 | 4 | 0
1980-09-27 | 1900-09-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.51 | A | 7 | 987 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.72 | 4 | 0
1980-09-27 | 1900-09-26 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 3.9 | 39.02 | A | 7 | 0.53 | A | 7 | 988 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.92 | 4 | 0
1980-09-27 | 1900-09-26 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 12.2 | 53.96 | A | 7 | 5 | 41 | A | 7 | 0.62 | A | 7 | 988 | A | 7 | 140 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 2440 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.9 | 4 | 0
1980-09-27 | 1900-09-26 | 7:00 | 7 | 79 | 1078 | 23 | 1 | 13 | 4 | 1 | 9 | 22 | 1 | 13 | 2500 | 1 | 13 | 0 | 1 | 9 | 2500 | 1 | 13 | 750 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 12.2 | 53.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.64 | A | 7 | 988 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 1520 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.08 | 4 | 0
1980-09-27 | 1900-09-26 | 8:00 | 8 | 334 | 1361 | 67 | 1 | 13 | 2 | 1 | 9 | 66 | 1 | 13 | 7600 | 1 | 13 | 100 | 1 | 9 | 7600 | 1 | 13 | 2510 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 14.4 | 57.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.58 | A | 7 | 988 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 1680 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.08 | 4 | 0
1980-09-27 | 1900-09-26 | 9:00 | 9 | 576 | 1361 | 119 | 1 | 9 | 13 | 1 | 9 | 114 | 1 | 13 | 13900 | 1 | 9 | 900 | 1 | 9 | 13500 | 1 | 13 | 4820 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 1980 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.18 | 4 | 0
1980-09-27 | 1900-09-26 | 10:00 | 10 | 778 | 1361 | 396 | 1 | 9 | 207 | 1 | 9 | 276 | 1 | 13 | 42800 | 1 | 9 | 21500 | 1 | 9 | 30500 | 1 | 13 | 7270 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 18.3 | 64.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.47 | A | 7 | 988 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 1980 | A | 7 | 1.6 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.26 | 4 | 0
1980-09-27 | 1900-09-26 | 11:00 | 11 | 924 | 1361 | 521 | 1 | 13 | 313 | 1 | 13 | 307 | 1 | 13 | 56000 | 1 | 13 | 33600 | 1 | 13 | 33100 | 1 | 13 | 8610 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 19.4 | 66.92 | A | 7 | 5 | 41 | A | 7 | 0.39 | A | 7 | 988 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.6 | 4 | 0
1980-09-27 | 1900-09-26 | 12:00 | 12 | 1006 | 1361 | 654 | 1 | 13 | 485 | 1 | 13 | 294 | 1 | 13 | 69000 | 1 | 13 | 50300 | 1 | 13 | 31700 | 1 | 13 | 9100 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 21.1 | 69.98 | A | 7 | 5 | 41 | A | 7 | 0.35 | A | 7 | 987 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 4 | 0
1980-09-27 | 1900-09-26 | 13:00 | 13 | 1017 | 1361 | 625 | 1 | 13 | 428 | 1 | 13 | 303 | 1 | 13 | 65700 | 1 | 13 | 44400 | 1 | 13 | 32400 | 1 | 13 | 9580 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 22.2 | 71.96 | A | 7 | 3.9 | 39.02 | A | 7 | 0.3 | A | 7 | 987 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 4 | 0
1980-09-27 | 1900-09-26 | 14:00 | 14 | 957 | 1361 | 295 | 1 | 9 | 21 | 1 | 9 | 281 | 1 | 13 | 34300 | 1 | 9 | 1900 | 1 | 9 | 33000 | 1 | 13 | 12270 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 3.9 | 39.02 | A | 7 | 0.3 | A | 7 | 985 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.3 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 4 | 0
1980-09-27 | 1900-09-26 | 15:00 | 15 | 830 | 1361 | 411 | 1 | 9 | 237 | 1 | 9 | 265 | 1 | 13 | 44900 | 1 | 9 | 24900 | 1 | 9 | 29700 | 1 | 13 | 7230 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 3.9 | 39.02 | A | 7 | 0.31 | A | 7 | 985 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.3 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.52 | 4 | 0
1980-09-27 | 1900-09-26 | 16:00 | 16 | 645 | 1361 | 315 | 1 | 13 | 268 | 1 | 13 | 187 | 1 | 13 | 33700 | 1 | 13 | 27500 | 1 | 13 | 20600 | 1 | 13 | 4120 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 22.2 | 71.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.31 | A | 7 | 984 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.4 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.12 | 4 | 0
1980-09-27 | 1900-09-26 | 17:00 | 17 | 414 | 1361 | 181 | 1 | 13 | 159 | 1 | 13 | 133 | 1 | 13 | 19600 | 1 | 13 | 14500 | 1 | 13 | 15200 | 1 | 13 | 2980 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 20.6 | 69.08 | A | 7 | 4.4 | 39.92 | A | 7 | 0.35 | A | 7 | 984 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.4 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.72 | 4 | 0
1980-09-27 | 1900-09-26 | 18:00 | 18 | 154 | 1361 | 25 | 1 | 13 | 4 | 1 | 9 | 25 | 1 | 13 | 2900 | 1 | 13 | 0 | 1 | 9 | 2900 | 1 | 13 | 920 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 3.9 | 39.02 | A | 7 | 0.4 | A | 7 | 984 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.3 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 4 | 0
1980-09-27 | 1900-09-26 | 19:00 | 19 | 1 | 125 | 2 | 1 | 13 | 0 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 16.1 | 60.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.46 | A | 7 | 984 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.4 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.72 | 4 | 0
1980-09-27 | 1900-09-26 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 5 | 41 | A | 7 | 0.48 | A | 7 | 984 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 4270 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.9 | 4 | 0
1980-09-27 | 1900-09-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 5 | 41 | A | 7 | 0.5 | A | 7 | 984 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 4270 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.2 | 4 | 0
1980-09-27 | 1900-09-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 4270 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.88 | 4 | 0
1980-09-27 | 1900-09-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.8 | 55.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.88 | 4 | 0
1980-09-27 | 1900-09-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 12.2 | 53.96 | A | 7 | 5 | 41 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.9 | 4 | 0
1980-09-28 | 1900-09-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 10.6 | 51.08 | A | 7 | 5 | 41 | A | 7 | 0.69 | A | 7 | 983 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.9 | 5 | 0
1980-09-28 | 1900-09-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.9 | 5 | 0
1980-09-28 | 1900-09-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.9 | 5 | 0
1980-09-28 | 1900-09-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 4 | A | 7 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 170 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.9 | 5 | 0
1980-09-28 | 1900-09-27 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 8.9 | 48.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.8 | A | 7 | 983 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.38 | 5 | 0
1980-09-28 | 1900-09-27 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 7.8 | 46.04 | A | 7 | 5 | 41 | A | 7 | 0.83 | A | 7 | 983 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.7 | 5 | 0
1980-09-28 | 1900-09-27 | 7:00 | 7 | 76 | 1056 | 27 | 1 | 13 | 49 | 1 | 13 | 22 | 1 | 13 | 2900 | 1 | 13 | 2400 | 1 | 13 | 2700 | 1 | 13 | 460 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 7.2 | 44.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.83 | A | 7 | 983 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.72 | 5 | 0
1980-09-28 | 1900-09-27 | 8:00 | 8 | 330 | 1362 | 153 | 1 | 13 | 261 | 1 | 9 | 89 | 1 | 13 | 16100 | 1 | 13 | 21500 | 1 | 9 | 10900 | 1 | 13 | 1720 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.69 | A | 7 | 982 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.46 | 5 | 0
1980-09-28 | 1900-09-27 | 9:00 | 9 | 572 | 1362 | 251 | 1 | 13 | 184 | 1 | 13 | 173 | 1 | 13 | 27300 | 1 | 13 | 18300 | 1 | 13 | 19600 | 1 | 13 | 4100 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 13.9 | 57.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.72 | A | 7 | 982 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 2290 | A | 7 | 1.8 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.72 | 5 | 0
1980-09-28 | 1900-09-27 | 10:00 | 10 | 773 | 1362 | 352 | 1 | 13 | 314 | 1 | 13 | 173 | 1 | 13 | 38700 | 1 | 13 | 33300 | 1 | 13 | 19700 | 1 | 13 | 3950 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 15.6 | 60.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 4570 | A | 7 | 1.7 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.14 | 5 | 0
1980-09-28 | 1900-09-27 | 11:00 | 11 | 919 | 1362 | 596 | 1 | 13 | 548 | 1 | 13 | 224 | 1 | 13 | 63700 | 1 | 13 | 56700 | 1 | 13 | 25300 | 1 | 13 | 5960 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 18.3 | 64.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.49 | A | 7 | 982 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.36 | 5 | 0
1980-09-28 | 1900-09-27 | 12:00 | 12 | 1001 | 1362 | 499 | 1 | 13 | 271 | 1 | 13 | 298 | 1 | 13 | 54300 | 1 | 13 | 29300 | 1 | 13 | 32700 | 1 | 13 | 9030 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 18.9 | 66.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.49 | A | 7 | 981 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.7 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.24 | 5 | 0
1980-09-28 | 1900-09-27 | 13:00 | 13 | 1012 | 1362 | 466 | 1 | 9 | 212 | 1 | 9 | 308 | 1 | 13 | 51400 | 1 | 9 | 22600 | 1 | 9 | 34600 | 1 | 13 | 9950 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 20 | 68 | A | 7 | 8.3 | 46.94 | A | 7 | 0.47 | A | 7 | 981 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.7 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.64 | 5 | 0
1980-09-28 | 1900-09-27 | 14:00 | 14 | 951 | 1362 | 356 | 1 | 9 | 13 | 1 | 9 | 347 | 1 | 13 | 40600 | 1 | 9 | 1300 | 1 | 9 | 39700 | 1 | 13 | 14000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.51 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 880 | A | 7 | 1.8 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.22 | 5 | 0
1980-09-28 | 1900-09-27 | 15:00 | 15 | 824 | 1362 | 276 | 1 | 9 | 4 | 1 | 9 | 273 | 1 | 13 | 31300 | 1 | 9 | 400 | 1 | 9 | 31100 | 1 | 13 | 10980 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 790 | A | 7 | 1.8 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.42 | 5 | 0
1980-09-28 | 1900-09-27 | 16:00 | 16 | 638 | 1362 | 217 | 1 | 9 | 63 | 1 | 9 | 188 | 1 | 13 | 23900 | 1 | 9 | 6200 | 1 | 9 | 21000 | 1 | 13 | 5560 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 790 | A | 7 | 1.8 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.42 | 5 | 0
1980-09-28 | 1900-09-27 | 17:00 | 17 | 407 | 1362 | 85 | 1 | 9 | 3 | 1 | 9 | 84 | 1 | 13 | 9700 | 1 | 9 | 200 | 1 | 9 | 9700 | 1 | 13 | 3270 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.54 | A | 7 | 980 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 1.8 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.72 | 5 | 0
1980-09-28 | 1900-09-27 | 18:00 | 18 | 147 | 1362 | 28 | 1 | 13 | 0 | 1 | 9 | 28 | 1 | 13 | 3200 | 1 | 13 | 0 | 1 | 9 | 3200 | 1 | 13 | 990 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.88 | 5 | 0
1980-09-28 | 1900-09-27 | 19:00 | 19 | 1 | 102 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 2 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.28 | 5 | 0
1980-09-28 | 1900-09-27 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 580 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.98 | 5 | 0
1980-09-28 | 1900-09-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 580 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.08 | 5 | 0
1980-09-28 | 1900-09-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 11.1 | 51.98 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 170 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 580 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.78 | 5 | 0
1980-09-28 | 1900-09-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.76 | 5 | 0
1980-09-28 | 1900-09-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.66 | 5 | 0
1980-09-29 | 1900-09-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 240 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.24 | 6 | 0
1980-09-29 | 1900-09-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 210 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.24 | 6 | 0
1980-09-29 | 1900-09-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 6 | 0
1980-09-29 | 1900-09-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.24 | 6 | 0
1980-09-29 | 1900-09-28 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 240 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.24 | 6 | 0
1980-09-29 | 1900-09-28 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 240 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.66 | 6 | 0
1980-09-29 | 1900-09-28 | 7:00 | 7 | 72 | 1034 | 15 | 1 | 13 | 0 | 1 | 9 | 15 | 1 | 13 | 1700 | 1 | 13 | 0 | 1 | 9 | 1700 | 1 | 13 | 550 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 12.8 | 55.04 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 240 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.74 | 6 | 0
1980-09-29 | 1900-09-28 | 8:00 | 8 | 326 | 1363 | 58 | 1 | 13 | 2 | 1 | 9 | 57 | 1 | 13 | 6600 | 1 | 13 | 100 | 1 | 9 | 6600 | 1 | 13 | 2220 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 270 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.24 | 6 | 0
1980-09-29 | 1900-09-28 | 9:00 | 9 | 567 | 1363 | 131 | 1 | 9 | 2 | 1 | 9 | 130 | 1 | 13 | 15000 | 1 | 9 | 100 | 1 | 9 | 15000 | 1 | 13 | 5290 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 270 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.74 | 6 | 0
1980-09-29 | 1900-09-28 | 10:00 | 10 | 768 | 1363 | 226 | 1 | 9 | 2 | 1 | 9 | 225 | 1 | 13 | 25900 | 1 | 9 | 200 | 1 | 9 | 25800 | 1 | 13 | 9250 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 400 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.14 | 6 | 0
1980-09-29 | 1900-09-28 | 11:00 | 11 | 914 | 1363 | 264 | 1 | 9 | 0 | 1 | 9 | 264 | 1 | 13 | 30600 | 1 | 9 | 0 | 1 | 9 | 30600 | 1 | 13 | 11440 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 430 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.04 | 6 | 0
1980-09-29 | 1900-09-28 | 12:00 | 12 | 995 | 1363 | 348 | 1 | 9 | 1 | 1 | 9 | 348 | 1 | 13 | 40000 | 1 | 9 | 100 | 1 | 9 | 39900 | 1 | 13 | 14430 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 460 | A | 7 | 2.3 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.04 | 6 | 0
1980-09-29 | 1900-09-28 | 13:00 | 13 | 1006 | 1363 | 353 | 1 | 9 | 1 | 1 | 9 | 352 | 1 | 13 | 40500 | 1 | 9 | 100 | 1 | 9 | 40400 | 1 | 13 | 14630 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 460 | A | 7 | 2.4 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.02 | 6 | 0
1980-09-29 | 1900-09-28 | 14:00 | 14 | 945 | 1363 | 307 | 1 | 9 | 0 | 1 | 9 | 307 | 1 | 13 | 35300 | 1 | 9 | 0 | 1 | 9 | 35300 | 1 | 13 | 12920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 520 | A | 7 | 2.5 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.52 | 6 | 0
1980-09-29 | 1900-09-28 | 15:00 | 15 | 817 | 1363 | 509 | 1 | 9 | 492 | 1 | 9 | 212 | 1 | 13 | 53800 | 1 | 9 | 50400 | 1 | 9 | 23500 | 1 | 13 | 5030 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 977 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 6 | 0
1980-09-29 | 1900-09-28 | 16:00 | 16 | 631 | 1363 | 154 | 1 | 9 | 39 | 1 | 9 | 135 | 1 | 13 | 16900 | 1 | 9 | 3800 | 1 | 9 | 15100 | 1 | 13 | 4210 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 20.6 | 69.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 490 | A | 7 | 2.5 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.92 | 6 | 0
1980-09-29 | 1900-09-28 | 17:00 | 17 | 399 | 1363 | 87 | 1 | 9 | 5 | 1 | 9 | 86 | 1 | 13 | 10000 | 1 | 9 | 300 | 1 | 9 | 9900 | 1 | 13 | 3300 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 2.4 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.52 | 6 | 0
1980-09-29 | 1900-09-28 | 18:00 | 18 | 140 | 1363 | 27 | 1 | 13 | 1 | 1 | 9 | 27 | 1 | 13 | 3100 | 1 | 13 | 0 | 1 | 9 | 3100 | 1 | 13 | 950 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.75 | A | 7 | 978 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 340 | A | 7 | 2.4 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.42 | 6 | 0
1980-09-29 | 1900-09-28 | 19:00 | 19 | 0 | 57 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.9 | 57.02 | A | 7 | 0.75 | A | 7 | 979 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 340 | A | 7 | 2.4 | E | 8 | 0.215 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.42 | 6 | 0
1980-09-29 | 1900-09-28 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 16.7 | 62.06 | A | 7 | 13.3 | 55.94 | A | 7 | 0.81 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12900 | A | 7 | 310 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.54 | 6 | 0
1980-09-29 | 1900-09-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 16.1 | 60.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.87 | A | 7 | 979 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 340 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.62 | 6 | 0
1980-09-29 | 1900-09-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.64 | 6 | 0
1980-09-29 | 1900-09-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 460 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.14 | 6 | 0
1980-09-29 | 1900-09-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 13.9 | 57.02 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 120 | A | 7 | 2.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.22 | 6 | 0
1980-09-30 | 1900-09-29 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 7 | 0
1980-09-30 | 1900-09-29 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 12.2 | 53.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 1300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.78 | 7 | 0
1980-09-30 | 1900-09-29 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 800 | A | 7 | 0 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 7 | 0
1980-09-30 | 1900-09-29 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 3200 | A | 7 | 60 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 7 | 0
1980-09-30 | 1900-09-29 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 2400 | A | 7 | 60 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.24 | 7 | 0
1980-09-30 | 1900-09-29 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 400 | A | 7 | 0 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.24 | 7 | 0
1980-09-30 | 1900-09-29 | 7:00 | 7 | 69 | 1011 | 22 | 1 | 13 | 3 | 1 | 9 | 22 | 1 | 13 | 2500 | 1 | 13 | 0 | 1 | 9 | 2500 | 1 | 13 | 740 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 400 | A | 7 | 0 | A | 7 | 2.3 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.24 | 7 | 0
1980-09-30 | 1900-09-29 | 8:00 | 8 | 321 | 1364 | 106 | 1 | 13 | 1 | 1 | 9 | 106 | 1 | 13 | 11700 | 1 | 13 | 100 | 1 | 9 | 11600 | 1 | 13 | 3380 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 800 | A | 7 | 30 | A | 7 | 2.3 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.84 | 7 | 0
1980-09-30 | 1900-09-29 | 9:00 | 9 | 563 | 1364 | 156 | 1 | 9 | 0 | 1 | 9 | 156 | 1 | 13 | 17700 | 1 | 9 | 0 | 1 | 9 | 17700 | 1 | 13 | 6000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 2000 | A | 7 | 30 | A | 7 | 2.3 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.64 | 7 | 0
1980-09-30 | 1900-09-29 | 10:00 | 10 | 764 | 1364 | 228 | 1 | 9 | 3 | 1 | 9 | 226 | 1 | 13 | 26000 | 1 | 9 | 300 | 1 | 9 | 25900 | 1 | 13 | 9240 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 2.3 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.14 | 7 | 0
1980-09-30 | 1900-09-29 | 11:00 | 11 | 909 | 1364 | 651 | 1 | 13 | 723 | 1 | 13 | 166 | 1 | 13 | 68500 | 1 | 13 | 73100 | 1 | 13 | 19600 | 1 | 13 | 4350 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 18.9 | 66.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.76 | A | 7 | 980 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.42 | 7 | 0
1980-09-30 | 1900-09-29 | 12:00 | 12 | 990 | 1364 | 709 | 1 | 9 | 868 | 1 | 9 | 76 | 1 | 13 | 74000 | 1 | 9 | 86800 | 1 | 9 | 10800 | 1 | 13 | 2260 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.64 | A | 7 | 979 | A | 7 | 270 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.12 | 7 | 0
1980-09-30 | 1900-09-29 | 13:00 | 13 | 1000 | 1364 | 755 | 1 | 9 | 920 | 1 | 9 | 76 | 1 | 13 | 78700 | 1 | 9 | 92000 | 1 | 9 | 11000 | 1 | 13 | 2290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.12 | 7 | 0
1980-09-30 | 1900-09-29 | 14:00 | 14 | 939 | 1364 | 704 | 1 | 9 | 910 | 1 | 9 | 73 | 1 | 13 | 73400 | 1 | 9 | 90800 | 1 | 9 | 10700 | 1 | 13 | 2060 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 26.1 | 78.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.49 | A | 7 | 977 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.02 | 7 | 0
1980-09-30 | 1900-09-29 | 15:00 | 15 | 811 | 1364 | 598 | 1 | 9 | 889 | 1 | 9 | 66 | 1 | 13 | 62500 | 1 | 9 | 88000 | 1 | 9 | 10100 | 1 | 13 | 1710 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 27.8 | 82.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.4 | A | 7 | 977 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.84 | 7 | 0
1980-09-30 | 1900-09-29 | 16:00 | 16 | 624 | 1364 | 440 | 1 | 9 | 836 | 1 | 9 | 54 | 1 | 13 | 46100 | 1 | 9 | 80700 | 1 | 9 | 9000 | 1 | 13 | 1340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.34 | A | 7 | 976 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.28 | 7 | 0
1980-09-30 | 1900-09-29 | 17:00 | 17 | 392 | 1364 | 246 | 1 | 9 | 709 | 1 | 9 | 39 | 1 | 13 | 25700 | 1 | 9 | 63200 | 1 | 9 | 7500 | 1 | 13 | 940 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 28.3 | 82.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.34 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.28 | 7 | 0
1980-09-30 | 1900-09-29 | 18:00 | 18 | 133 | 1364 | 63 | 1 | 13 | 388 | 1 | 9 | 22 | 1 | 13 | 6000 | 1 | 13 | 23700 | 1 | 9 | 3700 | 1 | 13 | 410 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.41 | A | 7 | 976 | A | 7 | 180 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.04 | 7 | 0
1980-09-30 | 1900-09-29 | 19:00 | 19 | 0 | 34 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | 21.7 | 71.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.57 | A | 7 | 976 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.24 | 7 | 0
1980-09-30 | 1900-09-29 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.61 | A | 7 | 975 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.04 | 7 | 0
1980-09-30 | 1900-09-29 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 975 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.96 | 7 | 0
1980-09-30 | 1900-09-29 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 16.3 | 61.34 | A | 7 | 11.5 | 52.7 | A | 7 | 0.68 | A | 7 | 975 | A | 7 | 180 | A | 7 | 3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.2 | 7 | 0
1980-09-30 | 1900-09-29 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 15.5 | 59.9 | A | 7 | 11.2 | 52.16 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 190 | A | 7 | 3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.96 | 7 | 0
1980-09-30 | 1900-09-29 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 14.6 | 58.28 | A | 7 | 11 | 51.8 | A | 7 | 0.75 | A | 7 | 974 | A | 7 | 190 | A | 7 | 2.9 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.6 | 7 | 0
2001-10-01 | 1900-09-30 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 13.7 | 56.66 | A | 7 | 10.7 | 51.26 | A | 7 | 0.96 | A | 7 | 988 | A | 7 | 170 | A | 7 | 2.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.56 | 1 | 0
2001-10-01 | 1900-09-30 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 10.5 | 50.9 | A | 7 | 0.9 | A | 7 | 988 | A | 7 | 210 | A | 7 | 2.7 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.3 | 1 | 0
2001-10-01 | 1900-09-30 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 12 | 53.6 | A | 7 | 10.2 | 50.36 | A | 7 | 0.86 | A | 7 | 987 | A | 7 | 210 | A | 7 | 2.7 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.06 | 1 | 0
2001-10-01 | 1900-09-30 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 10 | 50 | A | 7 | 0.93 | A | 7 | 987 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.9 | 1 | 0
2001-10-01 | 1900-09-30 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.97 | A | 7 | 987 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.52 | 1 | 0
2001-10-01 | 1900-09-30 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 986 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.92 | 1 | 0
2001-10-01 | 1900-09-30 | 7:00 | 7 | 67 | 989 | 11 | 2 | 8 | 169 | 2 | 15 | 4 | 2 | 8 | 1800 | 2 | 8 | 10400 | 2 | 15 | 1000 | 2 | 8 | 150 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.97 | A | 7 | 988 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.52 | 1 | 0
2001-10-01 | 1900-09-30 | 8:00 | 8 | 317 | 1364 | 195 | 2 | 8 | 507 | 2 | 15 | 77 | 2 | 8 | 19700 | 2 | 8 | 40300 | 2 | 15 | 10300 | 2 | 8 | 1320 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.9 | A | 7 | 988 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.36 | 1 | 0
2001-10-01 | 1900-09-30 | 9:00 | 9 | 558 | 1364 | 382 | 2 | 8 | 705 | 2 | 15 | 93 | 2 | 8 | 40000 | 2 | 8 | 67300 | 2 | 15 | 12300 | 2 | 8 | 1860 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 988 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.14 | 1 | 0
2001-10-01 | 1900-09-30 | 10:00 | 10 | 759 | 1364 | 546 | 2 | 8 | 800 | 2 | 15 | 99 | 2 | 8 | 57100 | 2 | 8 | 79200 | 2 | 15 | 12900 | 2 | 8 | 2180 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.68 | A | 7 | 988 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.14 | 1 | 0
2001-10-01 | 1900-09-30 | 11:00 | 11 | 904 | 1364 | 664 | 2 | 8 | 811 | 2 | 15 | 125 | 2 | 8 | 69400 | 2 | 8 | 81100 | 2 | 15 | 15500 | 2 | 8 | 3070 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 22.2 | 71.96 | A | 7 | 13.3 | 55.94 | A | 7 | 0.57 | A | 7 | 988 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.04 | 1 | 0
2001-10-01 | 1900-09-30 | 12:00 | 12 | 985 | 1364 | 732 | 2 | 8 | 867 | 2 | 15 | 105 | 2 | 8 | 75800 | 2 | 8 | 86500 | 2 | 15 | 13200 | 2 | 8 | 2590 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.52 | A | 7 | 985 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.92 | 1 | 0
2001-10-01 | 1900-09-30 | 13:00 | 13 | 994 | 1364 | 740 | 2 | 8 | 869 | 2 | 15 | 104 | 2 | 8 | 76600 | 2 | 8 | 86700 | 2 | 15 | 13100 | 2 | 8 | 2630 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 25 | 77 | A | 7 | 12.2 | 53.96 | A | 7 | 0.45 | A | 7 | 987 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.96 | 1 | 0
2001-10-01 | 1900-09-30 | 14:00 | 14 | 933 | 1364 | 688 | 2 | 8 | 835 | 2 | 15 | 115 | 2 | 8 | 72900 | 2 | 8 | 84000 | 2 | 15 | 15200 | 2 | 8 | 3040 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.47 | A | 7 | 986 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.04 | 1 | 0
2001-10-01 | 1900-09-30 | 15:00 | 15 | 804 | 1364 | 577 | 2 | 8 | 800 | 2 | 15 | 104 | 2 | 8 | 60600 | 2 | 8 | 79600 | 2 | 15 | 13500 | 2 | 8 | 2380 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 25 | 77 | A | 7 | 12.8 | 55.04 | A | 7 | 0.47 | A | 7 | 985 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.24 | 1 | 0
2001-10-01 | 1900-09-30 | 16:00 | 16 | 618 | 1364 | 421 | 2 | 8 | 749 | 2 | 15 | 81 | 2 | 8 | 43900 | 2 | 8 | 72400 | 2 | 15 | 11000 | 2 | 8 | 1670 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.44 | 1 | 0
2001-10-01 | 1900-09-30 | 17:00 | 17 | 386 | 1364 | 228 | 2 | 8 | 558 | 2 | 15 | 70 | 2 | 8 | 23600 | 2 | 8 | 48300 | 2 | 15 | 9800 | 2 | 8 | 1300 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 22.8 | 73.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.64 | 1 | 0
2001-10-01 | 1900-09-30 | 18:00 | 18 | 127 | 1352 | 48 | 2 | 8 | 278 | 2 | 15 | 22 | 2 | 8 | 5100 | 2 | 8 | 15600 | 2 | 15 | 3500 | 2 | 8 | 400 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.59 | A | 7 | 982 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.66 | 1 | 0
2001-10-01 | 1900-09-30 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 983 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.96 | 1 | 0
2001-10-01 | 1900-09-30 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 11.7 | 53.06 | A | 7 | 0.78 | A | 7 | 983 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.36 | 1 | 0
2001-10-01 | 1900-09-30 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 11.1 | 51.98 | A | 7 | 0.81 | A | 7 | 983 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.78 | 1 | 0
2001-10-01 | 1900-09-30 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.8 | A | 7 | 983 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.78 | 1 | 0
2001-10-01 | 1900-09-30 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 15 | 59 | A | 7 | 10.6 | 51.08 | A | 7 | 0.75 | A | 7 | 983 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.98 | 1 | 0
2001-10-01 | 1900-09-30 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.106 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.18 | 1 | 0
2001-10-02 | 1900-10-01 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 10 | 50 | A | 7 | 0.8 | A | 7 | 981 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.8 | 2 | 0
2001-10-02 | 1900-10-01 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 10 | 50 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.3 | 2 | 0
2001-10-02 | 1900-10-01 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.22 | 2 | 0
2001-10-02 | 1900-10-01 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.83 | A | 7 | 981 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.42 | 2 | 0
2001-10-02 | 1900-10-01 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.89 | A | 7 | 981 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.32 | 2 | 0
2001-10-02 | 1900-10-01 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.32 | 2 | 0
2001-10-02 | 1900-10-01 | 7:00 | 7 | 64 | 967 | 10 | 2 | 8 | 154 | 2 | 15 | 4 | 2 | 8 | 1600 | 2 | 8 | 9400 | 2 | 15 | 1000 | 2 | 8 | 150 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 10 | 50 | A | 7 | 0.93 | A | 7 | 981 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.9 | 2 | 0
2001-10-02 | 1900-10-01 | 8:00 | 8 | 313 | 1365 | 188 | 2 | 8 | 482 | 2 | 15 | 77 | 2 | 8 | 19500 | 2 | 8 | 38400 | 2 | 15 | 10700 | 2 | 8 | 1420 | 2 | 19 | 9 | E | 9 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 11.1 | 51.98 | A | 7 | 0.75 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.78 | 2 | 0
2001-10-02 | 1900-10-01 | 9:00 | 9 | 554 | 1365 | 390 | 2 | 8 | 718 | 2 | 15 | 97 | 2 | 8 | 40500 | 2 | 8 | 68300 | 2 | 15 | 12700 | 2 | 8 | 1920 | 2 | 19 | 9 | E | 9 | 3 | A | 7 | 18.3 | 64.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.06 | 2 | 0
2001-10-02 | 1900-10-01 | 10:00 | 10 | 754 | 1365 | 533 | 2 | 8 | 751 | 2 | 15 | 116 | 2 | 8 | 56400 | 2 | 8 | 75300 | 2 | 15 | 14700 | 2 | 8 | 2640 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.57 | A | 7 | 982 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.36 | 2 | 0
2001-10-02 | 1900-10-01 | 11:00 | 11 | 899 | 1365 | 639 | 2 | 8 | 750 | 2 | 15 | 143 | 2 | 8 | 67900 | 2 | 8 | 76200 | 2 | 15 | 17600 | 2 | 8 | 3760 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.24 | 2 | 0
2001-10-02 | 1900-10-01 | 12:00 | 12 | 979 | 1365 | 726 | 2 | 8 | 813 | 2 | 15 | 141 | 2 | 8 | 75700 | 2 | 8 | 81400 | 2 | 15 | 17100 | 2 | 8 | 3760 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 25.6 | 78.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.45 | A | 7 | 979 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.84 | 2 | 0
2001-10-02 | 1900-10-01 | 13:00 | 13 | 989 | 1365 | 734 | 2 | 8 | 821 | 2 | 15 | 137 | 2 | 8 | 76800 | 2 | 8 | 82400 | 2 | 15 | 17000 | 2 | 8 | 3760 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 26.7 | 80.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.41 | A | 7 | 980 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.16 | 2 | 0
2001-10-02 | 1900-10-01 | 14:00 | 14 | 927 | 1365 | 676 | 2 | 8 | 806 | 2 | 15 | 127 | 2 | 8 | 70800 | 2 | 8 | 80700 | 2 | 15 | 15800 | 2 | 8 | 3210 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.41 | A | 7 | 979 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.04 | 2 | 0
2001-10-02 | 1900-10-01 | 15:00 | 15 | 798 | 1365 | 566 | 2 | 8 | 747 | 2 | 15 | 128 | 2 | 8 | 59900 | 2 | 8 | 75200 | 2 | 15 | 15800 | 2 | 8 | 3010 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 27.2 | 80.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.39 | A | 7 | 979 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.76 | 2 | 0
2001-10-02 | 1900-10-01 | 16:00 | 16 | 611 | 1365 | 415 | 2 | 8 | 708 | 2 | 15 | 97 | 2 | 8 | 43600 | 2 | 8 | 68900 | 2 | 15 | 12700 | 2 | 8 | 2000 | 2 | 19 | 0 | B | 8 | 0 | B | 8 | 26.7 | 80.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.39 | A | 7 | 978 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.06 | 2 | 0
2001-10-02 | 1900-10-01 | 17:00 | 17 | 379 | 1365 | 223 | 2 | 8 | 591 | 2 | 15 | 58 | 2 | 8 | 23200 | 2 | 8 | 51300 | 2 | 15 | 9000 | 2 | 8 | 1100 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 25 | 77 | A | 7 | 11.7 | 53.06 | A | 7 | 0.43 | A | 7 | 978 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.86 | 2 | 0
2001-10-02 | 1900-10-01 | 18:00 | 18 | 120 | 1331 | 43 | 2 | 8 | 270 | 2 | 15 | 20 | 2 | 8 | 4700 | 2 | 8 | 15000 | 2 | 15 | 3300 | 2 | 8 | 370 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.68 | A | 7 | 976 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.36 | 2 | 0
2001-10-02 | 1900-10-01 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.08 | 2 | 0
2001-10-02 | 1900-10-01 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.59 | A | 7 | 978 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.18 | 2 | 0
2001-10-02 | 1900-10-01 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 19.4 | 66.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.88 | 2 | 0
2001-10-02 | 1900-10-01 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.38 | 2 | 0
2001-10-02 | 1900-10-01 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 18.3 | 64.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.68 | 2 | 0
2001-10-02 | 1900-10-01 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.105 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.38 | 2 | 0
2001-10-03 | 1900-10-02 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.96 | 3 | 0
2001-10-03 | 1900-10-02 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.96 | 3 | 0
2001-10-03 | 1900-10-02 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.26 | 3 | 0
2001-10-03 | 1900-10-02 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.26 | 3 | 0
2001-10-03 | 1900-10-02 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.28 | 3 | 0
2001-10-03 | 1900-10-02 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 976 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.28 | 3 | 0
2001-10-03 | 1900-10-02 | 7:00 | 7 | 61 | 944 | 8 | 2 | 8 | 138 | 2 | 15 | 4 | 2 | 8 | 1500 | 2 | 8 | 8400 | 2 | 15 | 900 | 2 | 8 | 150 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 11.7 | 53.06 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.36 | 3 | 0
2001-10-03 | 1900-10-02 | 8:00 | 8 | 308 | 1365 | 181 | 2 | 8 | 449 | 2 | 15 | 79 | 2 | 8 | 18700 | 2 | 8 | 35500 | 2 | 15 | 10700 | 2 | 8 | 1460 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 17.2 | 62.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.06 | 3 | 0
2001-10-03 | 1900-10-02 | 9:00 | 9 | 549 | 1365 | 376 | 2 | 8 | 693 | 2 | 15 | 97 | 2 | 8 | 39200 | 2 | 8 | 65800 | 2 | 15 | 12700 | 2 | 8 | 1910 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 18.3 | 64.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.74 | 3 | 0
2001-10-03 | 1900-10-02 | 10:00 | 10 | 749 | 1365 | 514 | 2 | 8 | 721 | 2 | 15 | 117 | 2 | 8 | 54400 | 2 | 8 | 72200 | 2 | 15 | 14700 | 2 | 8 | 2650 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 20.6 | 69.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.14 | 3 | 0
2001-10-03 | 1900-10-02 | 11:00 | 11 | 894 | 1365 | 670 | 2 | 8 | 853 | 2 | 15 | 110 | 2 | 8 | 70900 | 2 | 8 | 85700 | 2 | 15 | 14600 | 2 | 8 | 2780 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 22.2 | 71.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.52 | 3 | 0
2001-10-03 | 1900-10-02 | 12:00 | 12 | 974 | 1365 | 732 | 2 | 8 | 855 | 2 | 15 | 121 | 2 | 8 | 77600 | 2 | 8 | 86200 | 2 | 15 | 16000 | 2 | 8 | 3360 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 23.3 | 73.94 | A | 7 | 14.4 | 57.92 | A | 7 | 0.57 | A | 7 | 977 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.72 | 3 | 0
2001-10-03 | 1900-10-02 | 13:00 | 13 | 983 | 1365 | 740 | 2 | 8 | 857 | 2 | 15 | 121 | 2 | 8 | 78500 | 2 | 8 | 86400 | 2 | 15 | 16100 | 2 | 8 | 3420 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 23.9 | 75.02 | A | 7 | 14.4 | 57.92 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.32 | 3 | 0
2001-10-03 | 1900-10-02 | 14:00 | 14 | 921 | 1365 | 682 | 2 | 8 | 847 | 2 | 15 | 109 | 2 | 8 | 72500 | 2 | 8 | 85300 | 2 | 15 | 14800 | 2 | 8 | 2870 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 24.4 | 75.92 | A | 7 | 15 | 59 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.4 | 3 | 0
2001-10-03 | 1900-10-02 | 15:00 | 15 | 791 | 1365 | 565 | 2 | 8 | 676 | 2 | 15 | 173 | 2 | 8 | 58600 | 2 | 8 | 66900 | 2 | 15 | 19700 | 2 | 8 | 3850 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 15 | 59 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 250 | B | 8 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.7 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.4 | 3 | 0
2001-10-03 | 1900-10-02 | 16:00 | 16 | 604 | 1365 | 302 | 2 | 8 | 205 | 2 | 15 | 211 | 2 | 8 | 32600 | 2 | 8 | 20500 | 2 | 15 | 23500 | 2 | 8 | 5070 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 24.4 | 75.92 | A | 7 | 15 | 59 | A | 7 | 0.56 | A | 7 | 978 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.4 | 3 | 0
2001-10-03 | 1900-10-02 | 17:00 | 17 | 372 | 1365 | 164 | 2 | 8 | 135 | 2 | 15 | 127 | 2 | 8 | 17600 | 2 | 8 | 11900 | 2 | 15 | 14400 | 2 | 8 | 2810 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 23.9 | 75.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.38 | 3 | 0
2001-10-03 | 1900-10-02 | 18:00 | 18 | 113 | 1286 | 31 | 2 | 8 | 66 | 2 | 15 | 25 | 2 | 8 | 3300 | 2 | 8 | 3000 | 2 | 15 | 3100 | 2 | 8 | 440 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.8 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.48 | 3 | 0
2001-10-03 | 1900-10-02 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 19.4 | 66.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.73 | A | 7 | 978 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.92 | 3 | 0
2001-10-03 | 1900-10-02 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | A | 7 | 19.4 | 66.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.92 | 3 | 0
2001-10-03 | 1900-10-02 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 17.8 | 64.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.9 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.02 | 3 | 0
2001-10-03 | 1900-10-02 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | A | 7 | 17.2 | 62.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 3 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.52 | 3 | 0
2001-10-03 | 1900-10-02 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 980 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 2286 | A | 7 | 3 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.44 | 3 | 0
2001-10-03 | 1900-10-02 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 978 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 3 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.44 | 3 | 0
2001-10-04 | 1900-10-03 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 3 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.14 | 4 | 0
2001-10-04 | 1900-10-03 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 2.9 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.74 | 4 | 0
2001-10-04 | 1900-10-03 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 12.2 | 53.96 | A | 7 | 0.75 | A | 7 | 979 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1433 | A | 7 | 2.9 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.66 | 4 | 0
2001-10-04 | 1900-10-03 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1372 | A | 7 | 2.8 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.58 | 4 | 0
2001-10-04 | 1900-10-03 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1280 | A | 7 | 2.8 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.08 | 4 | 0
2001-10-04 | 1900-10-03 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 7 | A | 7 | 15.6 | 60.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 2896 | A | 7 | 2.7 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.72 | 4 | 0
2001-10-04 | 1900-10-03 | 7:00 | 7 | 58 | 922 | 6 | 2 | 8 | 42 | 2 | 15 | 5 | 2 | 8 | 900 | 2 | 8 | 2100 | 2 | 15 | 700 | 2 | 8 | 100 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1189 | A | 7 | 2.7 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45 | 4 | 0
2001-10-04 | 1900-10-03 | 8:00 | 8 | 304 | 1366 | 147 | 2 | 8 | 143 | 2 | 15 | 115 | 2 | 8 | 15700 | 2 | 8 | 11600 | 2 | 15 | 13100 | 2 | 8 | 2500 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 2743 | A | 7 | 2.6 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.48 | 4 | 0
2001-10-04 | 1900-10-03 | 9:00 | 9 | 545 | 1366 | 300 | 2 | 8 | 344 | 2 | 15 | 163 | 2 | 8 | 31900 | 2 | 8 | 34000 | 2 | 15 | 18300 | 2 | 8 | 3450 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 11.7 | 53.06 | A | 7 | 0.72 | A | 7 | 980 | A | 7 | 80 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 1219 | A | 7 | 2.5 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.26 | 4 | 0
2001-10-04 | 1900-10-03 | 10:00 | 10 | 744 | 1366 | 397 | 2 | 8 | 183 | 2 | 15 | 297 | 2 | 8 | 42700 | 2 | 8 | 18800 | 2 | 15 | 32400 | 2 | 8 | 7660 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 13.3 | 55.94 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 1097 | A | 7 | 2.5 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.44 | 4 | 0
2001-10-04 | 1900-10-03 | 11:00 | 11 | 889 | 1366 | 482 | 2 | 8 | 224 | 2 | 15 | 336 | 2 | 8 | 52300 | 2 | 8 | 23500 | 2 | 15 | 36900 | 2 | 8 | 9580 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.92 | 4 | 0
2001-10-04 | 1900-10-03 | 12:00 | 12 | 968 | 1366 | 519 | 2 | 8 | 247 | 2 | 15 | 343 | 2 | 8 | 56600 | 2 | 8 | 26100 | 2 | 15 | 38000 | 2 | 8 | 10530 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 13.3 | 55.94 | A | 7 | 0.73 | A | 7 | 978 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 884 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.04 | 4 | 0
2001-10-04 | 1900-10-03 | 13:00 | 13 | 977 | 1366 | 113 | 2 | 8 | 0 | 2 | 15 | 113 | 2 | 8 | 14100 | 2 | 8 | 0 | 2 | 15 | 14100 | 2 | 8 | 5860 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 30 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 884 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.24 | 4 | 0
2001-10-04 | 1900-10-03 | 14:00 | 14 | 914 | 1366 | 379 | 2 | 8 | 95 | 2 | 15 | 315 | 2 | 8 | 41700 | 2 | 8 | 9700 | 2 | 15 | 35100 | 2 | 8 | 10700 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 12.2 | 53.96 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 20 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 884 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.06 | 4 | 0
2001-10-04 | 1900-10-03 | 15:00 | 15 | 785 | 1366 | 322 | 2 | 8 | 89 | 2 | 15 | 271 | 2 | 8 | 35400 | 2 | 8 | 9000 | 2 | 15 | 30200 | 2 | 8 | 8430 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 977 | A | 7 | 30 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 884 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.28 | 4 | 0
2001-10-04 | 1900-10-03 | 16:00 | 16 | 597 | 1366 | 102 | 2 | 8 | 0 | 2 | 15 | 102 | 2 | 8 | 12000 | 2 | 8 | 0 | 2 | 15 | 12000 | 2 | 8 | 4470 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 977 | A | 7 | 30 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 884 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.48 | 4 | 0
2001-10-04 | 1900-10-03 | 17:00 | 17 | 365 | 1366 | 34 | 2 | 8 | 0 | 2 | 15 | 34 | 2 | 8 | 4100 | 2 | 8 | 0 | 2 | 15 | 4100 | 2 | 8 | 1470 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 20 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 975 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.3 | 4 | 0
2001-10-04 | 1900-10-03 | 18:00 | 18 | 107 | 1241 | 27 | 2 | 8 | 87 | 2 | 15 | 20 | 2 | 8 | 3000 | 2 | 8 | 4200 | 2 | 15 | 2600 | 2 | 8 | 350 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.83 | A | 7 | 977 | A | 7 | 20 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 6645 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.22 | 4 | 0
2001-10-04 | 1900-10-03 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 30 | A | 7 | 11.8 | A | 7 | 16000 | A | 7 | 579 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.84 | 4 | 0
2001-10-04 | 1900-10-03 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 30 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 1128 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.92 | 4 | 0
2001-10-04 | 1900-10-03 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 40 | A | 7 | 8.2 | A | 7 | 11200 | A | 7 | 274 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 6 | 1 | A | 7 | 47.52 | 4 | 0
2001-10-04 | 1900-10-03 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 30 | A | 7 | 5.7 | A | 7 | 9600 | A | 7 | 274 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 2 | 1 | A | 7 | 47.52 | 4 | 0
2001-10-04 | 1900-10-03 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 8.9 | 48.02 | A | 7 | 1 | A | 7 | 981 | A | 7 | 10 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 274 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 3 | 1 | A | 7 | 48.02 | 4 | 0
2001-10-04 | 1900-10-03 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 8.9 | 48.02 | A | 7 | 1 | A | 7 | 981 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 11200 | A | 7 | 183 | A | 7 | 2.4 | E | 8 | 0.104 | F | 8 | 0.18 | F | 8 | 7 | 1 | A | 7 | 48.02 | 4 | 0
2001-10-05 | 1900-10-04 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 981 | A | 7 | 40 | A | 7 | 7.2 | A | 7 | 12800 | A | 7 | 1250 | A | 7 | 2.4 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 2 | 1 | A | 7 | 46.84 | 5 | 0
2001-10-05 | 1900-10-04 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 40 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 1981 | A | 7 | 2.3 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.94 | 5 | 0
2001-10-05 | 1900-10-04 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 40 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 2134 | A | 7 | 2.2 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.54 | 5 | 0
2001-10-05 | 1900-10-04 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.97 | A | 7 | 981 | A | 7 | 10 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 1676 | A | 7 | 2.1 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 3 | 1 | A | 7 | 45.54 | 5 | 0
2001-10-05 | 1900-10-04 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.97 | A | 7 | 983 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 1829 | A | 7 | 2 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 2 | 1 | A | 7 | 45.54 | 5 | 0
2001-10-05 | 1900-10-04 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.97 | A | 7 | 982 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 1219 | A | 7 | 2 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 1 | 1 | A | 7 | 45.54 | 5 | 0
2001-10-05 | 1900-10-04 | 7:00 | 7 | 55 | 900 | 4 | 2 | 8 | 38 | 2 | 15 | 3 | 2 | 8 | 600 | 2 | 8 | 1900 | 2 | 15 | 500 | 2 | 8 | 60 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.93 | A | 7 | 983 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.9 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.98 | 5 | 0
2001-10-05 | 1900-10-04 | 8:00 | 8 | 299 | 1367 | 122 | 2 | 8 | 137 | 2 | 15 | 92 | 2 | 8 | 13200 | 2 | 8 | 11100 | 2 | 15 | 10800 | 2 | 8 | 1990 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1158 | A | 7 | 1.8 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 1 | 1 | A | 7 | 41.08 | 5 | 0
2001-10-05 | 1900-10-04 | 9:00 | 9 | 540 | 1367 | 70 | 2 | 8 | 0 | 2 | 15 | 70 | 2 | 8 | 8400 | 2 | 8 | 0 | 2 | 15 | 8400 | 2 | 8 | 3130 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.93 | A | 7 | 984 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.7 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.98 | 5 | 0
2001-10-05 | 1900-10-04 | 10:00 | 10 | 739 | 1367 | 91 | 2 | 8 | 0 | 2 | 15 | 91 | 2 | 8 | 11100 | 2 | 8 | 0 | 2 | 15 | 11100 | 2 | 8 | 4400 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.86 | A | 7 | 985 | A | 7 | 350 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 2134 | A | 7 | 1.6 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.08 | 5 | 0
2001-10-05 | 1900-10-04 | 11:00 | 11 | 884 | 1367 | 119 | 2 | 8 | 0 | 2 | 15 | 119 | 2 | 8 | 14600 | 2 | 8 | 0 | 2 | 15 | 14600 | 2 | 8 | 5940 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.93 | A | 7 | 986 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.6 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.94 | 5 | 0
2001-10-05 | 1900-10-04 | 12:00 | 12 | 963 | 1367 | 299 | 2 | 8 | 30 | 2 | 15 | 278 | 2 | 8 | 33000 | 2 | 8 | 3100 | 2 | 15 | 30800 | 2 | 8 | 10120 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.77 | A | 7 | 984 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.64 | 5 | 0
2001-10-05 | 1900-10-04 | 13:00 | 13 | 971 | 1367 | 561 | 2 | 8 | 282 | 2 | 15 | 360 | 2 | 8 | 60000 | 2 | 8 | 30300 | 2 | 15 | 38400 | 2 | 8 | 10840 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.62 | A | 7 | 985 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.68 | 5 | 0
2001-10-05 | 1900-10-04 | 14:00 | 14 | 908 | 1367 | 658 | 2 | 8 | 704 | 2 | 15 | 189 | 2 | 8 | 68700 | 2 | 8 | 70700 | 2 | 15 | 21600 | 2 | 8 | 4840 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 13.3 | 55.94 | A | 7 | 3.3 | 37.94 | A | 7 | 0.51 | A | 7 | 985 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 2743 | A | 7 | 1.4 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.44 | 5 | 0
2001-10-05 | 1900-10-04 | 15:00 | 15 | 778 | 1367 | 559 | 2 | 8 | 788 | 2 | 15 | 109 | 2 | 8 | 58100 | 2 | 8 | 77900 | 2 | 15 | 13600 | 2 | 8 | 2360 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 13.9 | 57.02 | A | 7 | 3.3 | 37.94 | A | 7 | 0.49 | A | 7 | 985 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.14 | 5 | 0
2001-10-05 | 1900-10-04 | 16:00 | 16 | 590 | 1367 | 397 | 2 | 8 | 683 | 2 | 15 | 101 | 2 | 8 | 41500 | 2 | 8 | 65800 | 2 | 15 | 13000 | 2 | 8 | 2040 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 13.9 | 57.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.51 | A | 7 | 986 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.72 | 5 | 0
2001-10-05 | 1900-10-04 | 17:00 | 17 | 357 | 1367 | 210 | 2 | 8 | 587 | 2 | 15 | 56 | 2 | 8 | 21900 | 2 | 8 | 50000 | 2 | 15 | 8800 | 2 | 8 | 1060 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 11.1 | 51.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.59 | A | 7 | 986 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.84 | 5 | 0
2001-10-05 | 1900-10-04 | 18:00 | 18 | 101 | 1219 | 38 | 2 | 8 | 272 | 2 | 15 | 19 | 2 | 8 | 4400 | 2 | 8 | 14500 | 2 | 15 | 3200 | 2 | 8 | 350 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 11.1 | 51.98 | A | 7 | 2.8 | 37.04 | A | 7 | 0.57 | A | 7 | 984 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.44 | 5 | 0
2001-10-05 | 1900-10-04 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 9.4 | 48.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.66 | A | 7 | 986 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.74 | 5 | 0
2001-10-05 | 1900-10-04 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | A | 7 | 10 | 50 | A | 7 | 3.3 | 37.94 | A | 7 | 0.63 | A | 7 | 986 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.34 | 5 | 0
2001-10-05 | 1900-10-04 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 3.3 | 37.94 | A | 7 | 0.68 | A | 7 | 986 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.94 | 5 | 0
2001-10-05 | 1900-10-04 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.32 | 5 | 0
2001-10-05 | 1900-10-04 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | 3.9 | 39.02 | A | 7 | 0.89 | A | 7 | 987 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.62 | 5 | 0
2001-10-05 | 1900-10-04 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | 3.9 | 39.02 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.103 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.62 | 5 | 0
2001-10-06 | 1900-10-05 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 987 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.54 | 6 | 0
2001-10-06 | 1900-10-05 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.04 | 6 | 0
2001-10-06 | 1900-10-05 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.16 | 6 | 0
2001-10-06 | 1900-10-05 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.93 | A | 7 | 987 | A | 7 | 240 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.04 | 6 | 0
2001-10-06 | 1900-10-05 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | 2.2 | 35.96 | A | 7 | 0.96 | A | 7 | 987 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.46 | 6 | 0
2001-10-06 | 1900-10-05 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 2 | A | 7 | 1.7 | 35.06 | A | 7 | 1.7 | 35.06 | A | 7 | 1 | A | 7 | 987 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.96 | 6 | 0
2001-10-06 | 1900-10-05 | 7:00 | 7 | 52 | 878 | 6 | 2 | 8 | 141 | 2 | 15 | 2 | 2 | 8 | 1200 | 2 | 8 | 8400 | 2 | 15 | 700 | 2 | 8 | 80 | 2 | 19 | 8 | E | 9 | 3 | A | 7 | 2.2 | 35.96 | A | 7 | 2.2 | 35.96 | A | 7 | 1 | A | 7 | 988 | A | 7 | 220 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.86 | 6 | 0
2001-10-06 | 1900-10-05 | 8:00 | 8 | 295 | 1368 | 185 | 2 | 8 | 529 | 2 | 15 | 70 | 2 | 8 | 18600 | 2 | 8 | 40900 | 2 | 15 | 9700 | 2 | 8 | 1200 | 2 | 19 | 7 | E | 9 | 2 | A | 7 | 7.2 | 44.96 | A | 7 | 5 | 41 | A | 7 | 0.86 | A | 7 | 989 | A | 7 | 200 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.1 | 6 | 0
2001-10-06 | 1900-10-05 | 9:00 | 9 | 535 | 1368 | 378 | 2 | 8 | 751 | 2 | 15 | 83 | 2 | 8 | 39700 | 2 | 8 | 71300 | 2 | 15 | 11700 | 2 | 8 | 1660 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 10 | 50 | A | 7 | 6.1 | 42.98 | A | 7 | 0.77 | A | 7 | 989 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.78 | 6 | 0
2001-10-06 | 1900-10-05 | 10:00 | 10 | 734 | 1368 | 527 | 2 | 8 | 795 | 2 | 15 | 99 | 2 | 8 | 54900 | 2 | 8 | 78300 | 2 | 15 | 12700 | 2 | 8 | 2120 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.64 | A | 7 | 989 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.88 | 6 | 0
2001-10-06 | 1900-10-05 | 11:00 | 11 | 878 | 1368 | 627 | 2 | 8 | 757 | 2 | 15 | 139 | 2 | 8 | 66600 | 2 | 8 | 76800 | 2 | 15 | 17100 | 2 | 8 | 3560 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.51 | A | 7 | 989 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.28 | 6 | 0
2001-10-06 | 1900-10-05 | 12:00 | 12 | 957 | 1368 | 720 | 2 | 8 | 837 | 2 | 15 | 133 | 2 | 8 | 75300 | 2 | 8 | 83900 | 2 | 15 | 16500 | 2 | 8 | 3470 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.51 | A | 7 | 987 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.98 | 6 | 0
2001-10-06 | 1900-10-05 | 13:00 | 13 | 965 | 1368 | 728 | 2 | 8 | 875 | 2 | 15 | 108 | 2 | 8 | 75200 | 2 | 8 | 87100 | 2 | 15 | 13500 | 2 | 8 | 2500 | 2 | 19 | 8 | E | 9 | 3 | A | 7 | 16.7 | 62.06 | A | 7 | 5 | 41 | A | 7 | 0.46 | A | 7 | 988 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.6 | 6 | 0
2001-10-06 | 1900-10-05 | 14:00 | 14 | 902 | 1368 | 669 | 2 | 8 | 853 | 2 | 15 | 105 | 2 | 8 | 71200 | 2 | 8 | 85900 | 2 | 15 | 14400 | 2 | 8 | 2710 | 2 | 19 | 7 | E | 9 | 2 | A | 7 | 17.2 | 62.96 | A | 7 | 5 | 41 | A | 7 | 0.44 | A | 7 | 987 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.3 | 6 | 0
2001-10-06 | 1900-10-05 | 15:00 | 15 | 772 | 1368 | 564 | 2 | 8 | 835 | 2 | 15 | 92 | 2 | 8 | 59600 | 2 | 8 | 83100 | 2 | 15 | 12600 | 2 | 8 | 2110 | 2 | 19 | 8 | E | 9 | 3 | A | 7 | 16.7 | 62.06 | A | 7 | 5 | 41 | A | 7 | 0.46 | A | 7 | 986 | A | 7 | 220 | B | 8 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.6 | 6 | 0
2001-10-06 | 1900-10-05 | 16:00 | 16 | 583 | 1368 | 397 | 2 | 8 | 706 | 2 | 15 | 94 | 2 | 8 | 41500 | 2 | 8 | 68000 | 2 | 15 | 12400 | 2 | 8 | 1910 | 2 | 19 | 7 | E | 9 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | 5 | 41 | A | 7 | 0.46 | A | 7 | 986 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.6 | 6 | 0
2001-10-06 | 1900-10-05 | 17:00 | 17 | 350 | 1368 | 214 | 2 | 8 | 625 | 2 | 15 | 53 | 2 | 8 | 21700 | 2 | 8 | 53200 | 2 | 15 | 8000 | 2 | 8 | 980 | 2 | 19 | 8 | E | 9 | 3 | A | 7 | 15.6 | 60.08 | A | 7 | 5 | 41 | A | 7 | 0.49 | A | 7 | 986 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.1 | 6 | 0
2001-10-06 | 1900-10-05 | 18:00 | 18 | 95 | 1174 | 31 | 2 | 8 | 229 | 2 | 15 | 16 | 2 | 8 | 3700 | 2 | 8 | 12100 | 2 | 15 | 2700 | 2 | 8 | 300 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 5 | 41 | A | 7 | 0.59 | A | 7 | 984 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.5 | 6 | 0
2001-10-06 | 1900-10-05 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 4.4 | 39.92 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.12 | 6 | 0
2001-10-06 | 1900-10-05 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 5 | 41 | A | 7 | 0.74 | A | 7 | 986 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.5 | 6 | 0
2001-10-06 | 1900-10-05 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 4.4 | 39.92 | A | 7 | 0.76 | A | 7 | 986 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.82 | 6 | 0
2001-10-06 | 1900-10-05 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.52 | 6 | 0
2001-10-06 | 1900-10-05 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.52 | 6 | 0
2001-10-06 | 1900-10-05 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | 3.9 | 39.02 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.62 | 6 | 0
2001-10-07 | 1900-10-06 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | 3.9 | 39.02 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.62 | 7 | 0
2001-10-07 | 1900-10-06 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.54 | 7 | 0
2001-10-07 | 1900-10-06 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.54 | 7 | 0
2001-10-07 | 1900-10-06 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5 | 41 | A | 7 | 3.3 | 37.94 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.54 | 7 | 0
2001-10-07 | 1900-10-06 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.74 | 7 | 0
2001-10-07 | 1900-10-06 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | 3.9 | 39.02 | A | 7 | 0.82 | A | 7 | 986 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.72 | 7 | 0
2001-10-07 | 1900-10-06 | 7:00 | 7 | 50 | 855 | 5 | 2 | 8 | 120 | 2 | 15 | 2 | 2 | 8 | 1100 | 2 | 8 | 7100 | 2 | 15 | 600 | 2 | 8 | 80 | 2 | 19 | 5 | E | 9 | 2 | A | 7 | 7.8 | 46.04 | A | 7 | 5 | 41 | A | 7 | 0.82 | A | 7 | 988 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.6 | 7 | 0
2001-10-07 | 1900-10-06 | 8:00 | 8 | 290 | 1369 | 177 | 2 | 8 | 475 | 2 | 15 | 76 | 2 | 8 | 18300 | 2 | 8 | 36500 | 2 | 15 | 10500 | 2 | 8 | 1400 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 11.1 | 51.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.74 | A | 7 | 988 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.36 | 7 | 0
2001-10-07 | 1900-10-06 | 9:00 | 9 | 530 | 1369 | 365 | 2 | 8 | 701 | 2 | 15 | 92 | 2 | 8 | 38000 | 2 | 8 | 66100 | 2 | 15 | 12300 | 2 | 8 | 1800 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 13.9 | 57.02 | A | 7 | 6.7 | 44.06 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.56 | 7 | 0
2001-10-07 | 1900-10-06 | 10:00 | 10 | 729 | 1369 | 528 | 2 | 8 | 801 | 2 | 15 | 100 | 2 | 8 | 54900 | 2 | 8 | 78800 | 2 | 15 | 12800 | 2 | 8 | 2120 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 16.1 | 60.98 | A | 7 | 7.2 | 44.96 | A | 7 | 0.56 | A | 7 | 989 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.46 | 7 | 0
2001-10-07 | 1900-10-06 | 11:00 | 11 | 873 | 1369 | 621 | 2 | 8 | 739 | 2 | 15 | 148 | 2 | 8 | 65700 | 2 | 8 | 74700 | 2 | 15 | 17800 | 2 | 8 | 3730 | 2 | 19 | 5 | E | 9 | 2 | A | 7 | 17.8 | 64.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.46 | A | 7 | 989 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.28 | 7 | 0
2001-10-07 | 1900-10-06 | 12:00 | 12 | 951 | 1369 | 708 | 2 | 8 | 807 | 2 | 15 | 146 | 2 | 8 | 73300 | 2 | 8 | 80400 | 2 | 15 | 17200 | 2 | 8 | 3620 | 2 | 19 | 5 | E | 9 | 3 | A | 7 | 18.3 | 64.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.48 | A | 7 | 986 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.16 | 7 | 0
2001-10-07 | 1900-10-06 | 13:00 | 13 | 959 | 1369 | 722 | 2 | 8 | 863 | 2 | 15 | 115 | 2 | 8 | 76700 | 2 | 8 | 87000 | 2 | 15 | 15500 | 2 | 8 | 3150 | 2 | 19 | 5 | E | 9 | 2 | A | 7 | 19.4 | 66.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.47 | A | 7 | 987 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.94 | 7 | 0
2001-10-07 | 1900-10-06 | 14:00 | 14 | 895 | 1369 | 663 | 2 | 8 | 853 | 2 | 15 | 104 | 2 | 8 | 70600 | 2 | 8 | 85800 | 2 | 15 | 14300 | 2 | 8 | 2670 | 2 | 19 | 5 | E | 9 | 3 | A | 7 | 19.4 | 66.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.45 | A | 7 | 986 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.76 | 7 | 0
2001-10-07 | 1900-10-06 | 15:00 | 15 | 765 | 1369 | 547 | 2 | 8 | 764 | 2 | 15 | 119 | 2 | 8 | 58000 | 2 | 8 | 76700 | 2 | 15 | 15000 | 2 | 8 | 2720 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 18.9 | 66.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.48 | A | 7 | 986 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.14 | 7 | 0
2001-10-07 | 1900-10-06 | 16:00 | 16 | 577 | 1369 | 375 | 2 | 8 | 630 | 2 | 15 | 108 | 2 | 8 | 38800 | 2 | 8 | 60100 | 2 | 15 | 13400 | 2 | 8 | 2130 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 18.3 | 64.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.16 | 7 | 0
2001-10-07 | 1900-10-06 | 17:00 | 17 | 343 | 1369 | 179 | 2 | 8 | 406 | 2 | 15 | 77 | 2 | 8 | 18800 | 2 | 8 | 33600 | 2 | 15 | 10400 | 2 | 8 | 1410 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 16.7 | 62.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.58 | A | 7 | 985 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.44 | 7 | 0
2001-10-07 | 1900-10-06 | 18:00 | 18 | 89 | 1152 | 25 | 2 | 8 | 171 | 2 | 15 | 15 | 2 | 8 | 3000 | 2 | 8 | 9000 | 2 | 15 | 2300 | 2 | 8 | 280 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 12.2 | 53.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.76 | 7 | 0
2001-10-07 | 1900-10-06 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 2 | A | 7 | 11.1 | 51.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.74 | A | 7 | 984 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.36 | 7 | 0
2001-10-07 | 1900-10-06 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 3 | A | 7 | 10 | 50 | A | 7 | 6.7 | 44.06 | A | 7 | 0.8 | A | 7 | 984 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.26 | 7 | 0
2001-10-07 | 1900-10-06 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 10.6 | 51.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.79 | A | 7 | 984 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.96 | 7 | 0
2001-10-07 | 1900-10-06 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 10.6 | 51.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.79 | A | 7 | 984 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.96 | 7 | 0
2001-10-07 | 1900-10-06 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 11.1 | 51.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.8 | A | 7 | 984 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.04 | 7 | 0
2001-10-07 | 1900-10-06 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 5 | A | 7 | 11.7 | 53.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.102 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.64 | 7 | 0
2001-10-08 | 1900-10-07 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.69 | A | 7 | 983 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.46 | 1 | 0
2001-10-08 | 1900-10-07 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | B | 8 | 0 | B | 8 | 12.2 | 53.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.76 | 1 | 0
2001-10-08 | 1900-10-07 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | B | 8 | 0 | B | 8 | 12.2 | 53.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.76 | 1 | 0
2001-10-08 | 1900-10-07 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.36 | 1 | 0
2001-10-08 | 1900-10-07 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | A | 7 | 10.6 | 51.08 | A | 7 | 6.7 | 44.06 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.76 | 1 | 0
2001-10-08 | 1900-10-07 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 7 | A | 7 | 11.1 | 51.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.1 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.36 | 1 | 0
2001-10-08 | 1900-10-07 | 7:00 | 7 | 47 | 833 | 3 | 2 | 8 | 45 | 2 | 15 | 2 | 2 | 8 | 600 | 2 | 8 | 2500 | 2 | 15 | 400 | 2 | 8 | 60 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 10 | 50 | A | 7 | 7.8 | 46.04 | A | 7 | 0.86 | A | 7 | 983 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 2.2 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.94 | 1 | 0
2001-10-08 | 1900-10-07 | 8:00 | 8 | 286 | 1369 | 125 | 2 | 8 | 187 | 2 | 15 | 86 | 2 | 8 | 13100 | 2 | 8 | 14300 | 2 | 15 | 10100 | 2 | 8 | 1690 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.89 | A | 7 | 983 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 2134 | A | 7 | 2.3 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.24 | 1 | 0
2001-10-08 | 1900-10-07 | 9:00 | 9 | 526 | 1369 | 56 | 2 | 8 | 0 | 2 | 15 | 56 | 2 | 8 | 6800 | 2 | 8 | 0 | 2 | 15 | 6800 | 2 | 8 | 2550 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 160 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 2.3 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.84 | 1 | 0
2001-10-08 | 1900-10-07 | 10:00 | 10 | 724 | 1369 | 287 | 2 | 8 | 79 | 2 | 15 | 245 | 2 | 8 | 31500 | 2 | 8 | 7900 | 2 | 15 | 27300 | 2 | 8 | 7360 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 12.8 | 55.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 170 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 2.4 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.42 | 1 | 0
2001-10-08 | 1900-10-07 | 11:00 | 11 | 868 | 1369 | 615 | 2 | 8 | 617 | 2 | 15 | 222 | 2 | 8 | 65200 | 2 | 8 | 63500 | 2 | 15 | 24800 | 2 | 8 | 5530 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 160 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.5 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.58 | 1 | 0
2001-10-08 | 1900-10-07 | 12:00 | 12 | 946 | 1369 | 720 | 2 | 8 | 867 | 2 | 15 | 120 | 2 | 8 | 76100 | 2 | 8 | 87200 | 2 | 15 | 15700 | 2 | 8 | 3170 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 18.9 | 66.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 160 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.6 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.66 | 1 | 0
2001-10-08 | 1900-10-07 | 13:00 | 13 | 953 | 1369 | 704 | 2 | 8 | 791 | 2 | 15 | 151 | 2 | 8 | 75000 | 2 | 8 | 80700 | 2 | 15 | 18700 | 2 | 8 | 4250 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 20.6 | 69.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 160 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.66 | 1 | 0
2001-10-08 | 1900-10-07 | 14:00 | 14 | 889 | 1369 | 634 | 2 | 8 | 757 | 2 | 15 | 141 | 2 | 8 | 67400 | 2 | 8 | 76900 | 2 | 15 | 17300 | 2 | 8 | 3650 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 21.7 | 71.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 160 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.24 | 1 | 0
2001-10-08 | 1900-10-07 | 15:00 | 15 | 758 | 1369 | 535 | 2 | 8 | 746 | 2 | 15 | 121 | 2 | 8 | 56600 | 2 | 8 | 74700 | 2 | 15 | 15100 | 2 | 8 | 2750 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 22.8 | 73.04 | A | 7 | 13.9 | 57.02 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.92 | 1 | 0
2001-10-08 | 1900-10-07 | 16:00 | 16 | 570 | 1369 | 369 | 2 | 8 | 612 | 2 | 15 | 113 | 2 | 8 | 38000 | 2 | 8 | 58100 | 2 | 15 | 13800 | 2 | 8 | 2190 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 22.2 | 71.96 | A | 7 | 13.9 | 57.02 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 170 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.32 | 1 | 0
2001-10-08 | 1900-10-07 | 17:00 | 17 | 336 | 1369 | 192 | 2 | 8 | 494 | 2 | 15 | 71 | 2 | 8 | 19600 | 2 | 8 | 40500 | 2 | 15 | 9700 | 2 | 8 | 1260 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 21.1 | 69.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.12 | 1 | 0
2001-10-08 | 1900-10-07 | 18:00 | 18 | 84 | 1107 | 24 | 2 | 8 | 219 | 2 | 15 | 11 | 2 | 8 | 3000 | 2 | 8 | 12900 | 2 | 15 | 2000 | 2 | 8 | 250 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 20 | 68 | A | 7 | 13.3 | 55.94 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.54 | 1 | 0
2001-10-08 | 1900-10-07 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.24 | 1 | 0
2001-10-08 | 1900-10-07 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 12.8 | 55.04 | A | 7 | 0.75 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.64 | 1 | 0
2001-10-08 | 1900-10-07 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.76 | 1 | 0
2001-10-08 | 1900-10-07 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | A | 7 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.08 | 1 | 0
2001-10-08 | 1900-10-07 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 11.1 | 51.98 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.38 | 1 | 0
2001-10-08 | 1900-10-07 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 10.6 | 51.08 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.101 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.28 | 1 | 0
2001-10-09 | 1900-10-08 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 1097 | A | 7 | 2.2 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.08 | 2 | 0
2001-10-09 | 1900-10-08 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 980 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 1097 | A | 7 | 2.2 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.08 | 2 | 0
2001-10-09 | 1900-10-08 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 5 | A | 7 | 16.7 | 62.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.58 | 2 | 0
2001-10-09 | 1900-10-08 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 5 | A | 7 | 16.1 | 60.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.08 | 2 | 0
2001-10-09 | 1900-10-08 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 16.7 | 62.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 1189 | A | 7 | 2.5 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.58 | 2 | 0
2001-10-09 | 1900-10-08 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 2.6 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.28 | 2 | 0
2001-10-09 | 1900-10-08 | 7:00 | 7 | 44 | 811 | 2 | 2 | 8 | 0 | 2 | 15 | 2 | 2 | 8 | 300 | 2 | 8 | 0 | 2 | 15 | 300 | 2 | 8 | 80 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 1676 | A | 7 | 2.7 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.98 | 2 | 0
2001-10-09 | 1900-10-08 | 8:00 | 8 | 281 | 1370 | 90 | 2 | 8 | 0 | 2 | 15 | 90 | 2 | 8 | 9900 | 2 | 8 | 0 | 2 | 15 | 9900 | 2 | 8 | 2840 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 17.2 | 62.96 | A | 7 | 11.7 | 53.06 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 1158 | A | 7 | 2.8 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.96 | 2 | 0
2001-10-09 | 1900-10-08 | 9:00 | 9 | 521 | 1370 | 246 | 2 | 8 | 132 | 2 | 15 | 196 | 2 | 8 | 26400 | 2 | 8 | 12800 | 2 | 15 | 21600 | 2 | 8 | 4550 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 12.8 | 55.04 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 2.9 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.24 | 2 | 0
2001-10-09 | 1900-10-08 | 10:00 | 10 | 719 | 1370 | 346 | 2 | 8 | 177 | 2 | 15 | 252 | 2 | 8 | 37400 | 2 | 8 | 18200 | 2 | 15 | 27800 | 2 | 8 | 6400 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 13.9 | 57.02 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 3 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.02 | 2 | 0
2001-10-09 | 1900-10-08 | 11:00 | 11 | 862 | 1370 | 113 | 2 | 8 | 0 | 2 | 15 | 113 | 2 | 8 | 13800 | 2 | 8 | 0 | 2 | 15 | 13800 | 2 | 8 | 5620 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 20 | 68 | A | 7 | 15 | 59 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 160 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 2134 | A | 7 | 3.1 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.9 | 2 | 0
2001-10-09 | 1900-10-08 | 12:00 | 12 | 940 | 1370 | 281 | 2 | 8 | 18 | 2 | 15 | 268 | 2 | 8 | 32500 | 2 | 8 | 1600 | 2 | 15 | 31400 | 2 | 8 | 11710 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 21.7 | 71.06 | A | 7 | 16.1 | 60.98 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 1981 | A | 7 | 3.1 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.08 | 2 | 0
2001-10-09 | 1900-10-08 | 13:00 | 13 | 947 | 1370 | 185 | 2 | 8 | 0 | 2 | 15 | 185 | 2 | 8 | 22100 | 2 | 8 | 0 | 2 | 15 | 22100 | 2 | 8 | 8850 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 3 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.66 | 2 | 0
2001-10-09 | 1900-10-08 | 14:00 | 14 | 883 | 1370 | 110 | 2 | 8 | 0 | 2 | 15 | 110 | 2 | 8 | 13500 | 2 | 8 | 0 | 2 | 15 | 13500 | 2 | 8 | 5530 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 976 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 2.9 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.16 | 2 | 0
2001-10-09 | 1900-10-08 | 15:00 | 15 | 752 | 1370 | 186 | 2 | 8 | 6 | 2 | 15 | 182 | 2 | 8 | 21500 | 2 | 8 | 500 | 2 | 15 | 21200 | 2 | 8 | 7830 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 22.8 | 73.04 | A | 7 | 17.2 | 62.96 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 170 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 2.8 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.06 | 2 | 0
2001-10-09 | 1900-10-08 | 16:00 | 16 | 563 | 1370 | 69 | 2 | 8 | 0 | 2 | 15 | 69 | 2 | 8 | 8300 | 2 | 8 | 0 | 2 | 15 | 8300 | 2 | 8 | 3130 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 20 | 68 | A | 7 | 17.2 | 62.96 | A | 7 | 0.84 | A | 7 | 977 | A | 7 | 170 | A | 7 | 9.8 | A | 7 | 12800 | A | 7 | 1128 | A | 7 | 2.7 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 59.76 | 2 | 0
2001-10-09 | 1900-10-08 | 17:00 | 17 | 330 | 1370 | 42 | 2 | 8 | 0 | 2 | 15 | 42 | 2 | 8 | 5000 | 2 | 8 | 0 | 2 | 15 | 5000 | 2 | 8 | 1720 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.81 | A | 7 | 976 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 2.5 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 59.16 | 2 | 0
2001-10-09 | 1900-10-08 | 18:00 | 18 | 78 | 1085 | 6 | 2 | 8 | 0 | 2 | 15 | 6 | 2 | 8 | 700 | 2 | 8 | 0 | 2 | 15 | 700 | 2 | 8 | 240 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 20 | 68 | A | 7 | 16.7 | 62.06 | A | 7 | 0.81 | A | 7 | 973 | A | 7 | 150 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 914 | A | 7 | 2.4 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.36 | 2 | 0
2001-10-09 | 1900-10-08 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 17.2 | 62.96 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 180 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 671 | A | 7 | 2.3 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 60.36 | 2 | 0
2001-10-09 | 1900-10-08 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 976 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 59.46 | 2 | 0
2001-10-09 | 1900-10-08 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 18.3 | 64.94 | A | 7 | 16.7 | 62.06 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.1 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 60.06 | 2 | 0
2001-10-09 | 1900-10-08 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 17.2 | 62.96 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 610 | A | 7 | 1.9 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 60.96 | 2 | 0
2001-10-09 | 1900-10-08 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 5 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 59.46 | 2 | 0
2001-10-09 | 1900-10-08 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | A | 7 | 18.9 | 66.02 | A | 7 | 16.7 | 62.06 | A | 7 | 0.87 | A | 7 | 973 | A | 7 | 160 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 12802 | A | 7 | 1.7 | E | 8 | 0.1 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 59.46 | 2 | 0
2001-10-10 | 1900-10-09 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 16.1 | 60.98 | A | 7 | 0.87 | A | 7 | 974 | A | 7 | 160 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 671 | A | 7 | 1.8 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.48 | 3 | 0
2001-10-10 | 1900-10-09 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 610 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 61.56 | 3 | 0
2001-10-10 | 1900-10-09 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 457 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 63.54 | 3 | 0
2001-10-10 | 1900-10-09 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 20 | 68 | A | 7 | 18.9 | 66.02 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 457 | A | 7 | 2 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 64.52 | 3 | 0
2001-10-10 | 1900-10-09 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 19 | 66.2 | A | 7 | 19 | 66.2 | A | 7 | 1 | A | 7 | 974 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 720 | A | 7 | 2.1 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 66.1 | 3 | 0
2001-10-10 | 1900-10-09 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 19.4 | 66.92 | A | 7 | 18.9 | 66.02 | A | 7 | 0.97 | A | 7 | 972 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 65.42 | 3 | 0
2001-10-10 | 1900-10-09 | 7:00 | 7 | 42 | 788 | 1 | 2 | 8 | 0 | 2 | 15 | 1 | 2 | 8 | 100 | 2 | 8 | 0 | 2 | 15 | 100 | 2 | 8 | 40 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 20 | 68 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 11200 | A | 7 | 2438 | A | 7 | 2.2 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 66.5 | 3 | 0
2001-10-10 | 1900-10-09 | 8:00 | 8 | 276 | 1371 | 36 | 2 | 8 | 0 | 2 | 15 | 36 | 2 | 8 | 4200 | 2 | 8 | 0 | 2 | 15 | 4200 | 2 | 8 | 1440 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 16 | 60.8 | A | 7 | 15 | 59 | A | 7 | 0.94 | A | 7 | 975 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 300 | A | 7 | 2.3 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.9 | 3 | 0
2001-10-10 | 1900-10-09 | 9:00 | 9 | 516 | 1371 | 169 | 2 | 8 | 13 | 2 | 15 | 164 | 2 | 8 | 18800 | 2 | 8 | 1000 | 2 | 15 | 18500 | 2 | 8 | 5850 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 4389 | A | 7 | 2.4 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.06 | 3 | 0
2001-10-10 | 1900-10-09 | 10:00 | 10 | 714 | 1371 | 242 | 2 | 8 | 18 | 2 | 15 | 232 | 2 | 8 | 27300 | 2 | 8 | 1600 | 2 | 15 | 26400 | 2 | 8 | 8970 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 427 | A | 7 | 2.5 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.36 | 3 | 0
2001-10-10 | 1900-10-09 | 11:00 | 11 | 857 | 1371 | 314 | 2 | 8 | 42 | 2 | 15 | 287 | 2 | 8 | 34500 | 2 | 8 | 4300 | 2 | 15 | 31800 | 2 | 8 | 9390 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 15 | 59 | A | 7 | 11.7 | 53.06 | A | 7 | 0.81 | A | 7 | 979 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 610 | A | 7 | 2.6 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.86 | 3 | 0
2001-10-10 | 1900-10-09 | 12:00 | 12 | 934 | 1371 | 482 | 2 | 8 | 217 | 2 | 15 | 334 | 2 | 8 | 52500 | 2 | 8 | 22900 | 2 | 15 | 36900 | 2 | 8 | 9880 | 2 | 19 | 7 | E | 9 | 7 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.98 | 3 | 0
2001-10-10 | 1900-10-09 | 13:00 | 13 | 941 | 1371 | 507 | 2 | 8 | 246 | 2 | 15 | 338 | 2 | 8 | 55200 | 2 | 8 | 25900 | 2 | 15 | 37400 | 2 | 8 | 10060 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 17.8 | 64.04 | A | 7 | 11.1 | 51.98 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.6 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.08 | 3 | 0
2001-10-10 | 1900-10-09 | 14:00 | 14 | 876 | 1371 | 604 | 2 | 8 | 638 | 2 | 15 | 195 | 2 | 8 | 62600 | 2 | 8 | 63600 | 2 | 15 | 21800 | 2 | 8 | 4720 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.38 | 3 | 0
2001-10-10 | 1900-10-09 | 15:00 | 15 | 745 | 1371 | 467 | 2 | 8 | 438 | 2 | 15 | 228 | 2 | 8 | 50000 | 2 | 8 | 46000 | 2 | 15 | 24900 | 2 | 8 | 5380 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 11.1 | 51.98 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.38 | 3 | 0
2001-10-10 | 1900-10-09 | 16:00 | 16 | 556 | 1371 | 160 | 2 | 8 | 12 | 2 | 15 | 155 | 2 | 8 | 18100 | 2 | 8 | 900 | 2 | 15 | 17700 | 2 | 8 | 5910 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 17.8 | 64.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 5486 | A | 7 | 2.4 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.88 | 3 | 0
2001-10-10 | 1900-10-09 | 17:00 | 17 | 323 | 1371 | 42 | 2 | 8 | 0 | 2 | 15 | 42 | 2 | 8 | 5000 | 2 | 8 | 0 | 2 | 15 | 5000 | 2 | 8 | 1710 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.3 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.98 | 3 | 0
2001-10-10 | 1900-10-09 | 18:00 | 18 | 73 | 1040 | 9 | 2 | 8 | 0 | 2 | 15 | 9 | 2 | 8 | 1100 | 2 | 8 | 0 | 2 | 15 | 1100 | 2 | 8 | 350 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 11.1 | 51.98 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 20 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 2.3 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.98 | 3 | 0
2001-10-10 | 1900-10-09 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 2.2 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.58 | 3 | 0
2001-10-10 | 1900-10-09 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 982 | A | 7 | 10 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 2.2 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.48 | 3 | 0
2001-10-10 | 1900-10-09 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 15 | 59 | A | 7 | 10 | 50 | A | 7 | 0.72 | A | 7 | 983 | A | 7 | 350 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.1 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.5 | 3 | 0
2001-10-10 | 1900-10-09 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 10 | 50 | A | 7 | 0.8 | A | 7 | 983 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.8 | 3 | 0
2001-10-10 | 1900-10-09 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 13.3 | 55.94 | A | 7 | 9.4 | 48.92 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 350 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.32 | 3 | 0
2001-10-10 | 1900-10-09 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 11.7 | 53.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.86 | A | 7 | 981 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.72 | 3 | 0
2001-10-11 | 1900-10-10 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 2 | A | 7 | 11.1 | 51.98 | A | 7 | 8.9 | 48.02 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.82 | 4 | 0
2001-10-11 | 1900-10-10 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 3 | A | 7 | 11.1 | 51.98 | A | 7 | 8.9 | 48.02 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.82 | 4 | 0
2001-10-11 | 1900-10-10 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | A | 7 | 10 | 50 | A | 7 | 7.2 | 44.96 | A | 7 | 0.83 | A | 7 | 982 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.46 | 4 | 0
2001-10-11 | 1900-10-10 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | A | 7 | 10 | 50 | A | 7 | 7.2 | 44.96 | A | 7 | 0.83 | A | 7 | 983 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.46 | 4 | 0
2001-10-11 | 1900-10-10 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 9.4 | 48.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.86 | A | 7 | 983 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.96 | 4 | 0
2001-10-11 | 1900-10-10 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 5 | A | 7 | 10.6 | 51.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.96 | 4 | 0
2001-10-11 | 1900-10-10 | 7:00 | 7 | 39 | 766 | 1 | 2 | 8 | 7 | 2 | 15 | 1 | 2 | 8 | 200 | 2 | 8 | 300 | 2 | 15 | 200 | 2 | 8 | 20 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 10.6 | 51.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.83 | A | 7 | 983 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.54 | 4 | 0
2001-10-11 | 1900-10-10 | 8:00 | 8 | 272 | 1372 | 101 | 2 | 8 | 35 | 2 | 15 | 94 | 2 | 8 | 11000 | 2 | 8 | 2900 | 2 | 15 | 10500 | 2 | 8 | 2190 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.83 | A | 7 | 983 | A | 7 | 50 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.42 | 4 | 0
2001-10-11 | 1900-10-10 | 9:00 | 9 | 511 | 1372 | 205 | 2 | 8 | 50 | 2 | 15 | 186 | 2 | 8 | 22400 | 2 | 8 | 4800 | 2 | 15 | 20600 | 2 | 8 | 4850 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.3 | 4 | 0
2001-10-11 | 1900-10-10 | 10:00 | 10 | 709 | 1372 | 281 | 2 | 8 | 86 | 2 | 15 | 236 | 2 | 8 | 30800 | 2 | 8 | 8600 | 2 | 15 | 26300 | 2 | 8 | 7050 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 15 | 59 | A | 7 | 10 | 50 | A | 7 | 0.72 | A | 7 | 982 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.5 | 4 | 0
2001-10-11 | 1900-10-10 | 11:00 | 11 | 851 | 1372 | 615 | 2 | 8 | 654 | 2 | 15 | 208 | 2 | 8 | 65600 | 2 | 8 | 67300 | 2 | 15 | 23700 | 2 | 8 | 5060 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.64 | A | 7 | 982 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.22 | 4 | 0
2001-10-11 | 1900-10-10 | 12:00 | 12 | 928 | 1372 | 684 | 2 | 8 | 807 | 2 | 15 | 136 | 2 | 8 | 71000 | 2 | 8 | 80500 | 2 | 15 | 16300 | 2 | 8 | 3330 | 2 | 19 | 10 | E | 9 | 5 | A | 7 | 18.3 | 64.94 | A | 7 | 9.4 | 48.92 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 110 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.82 | 4 | 0
2001-10-11 | 1900-10-10 | 13:00 | 13 | 935 | 1372 | 679 | 2 | 8 | 779 | 2 | 15 | 147 | 2 | 8 | 72400 | 2 | 8 | 79400 | 2 | 15 | 18200 | 2 | 8 | 4020 | 2 | 19 | 10 | E | 9 | 5 | A | 7 | 18.3 | 64.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 110 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.54 | 4 | 0
2001-10-11 | 1900-10-10 | 14:00 | 14 | 870 | 1372 | 622 | 2 | 8 | 769 | 2 | 15 | 132 | 2 | 8 | 66200 | 2 | 8 | 78100 | 2 | 15 | 16500 | 2 | 8 | 3350 | 2 | 19 | 10 | E | 9 | 5 | A | 7 | 18.9 | 66.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.52 | A | 7 | 979 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.42 | 4 | 0
2001-10-11 | 1900-10-10 | 15:00 | 15 | 738 | 1372 | 528 | 2 | 8 | 787 | 2 | 15 | 103 | 2 | 8 | 54800 | 2 | 8 | 77400 | 2 | 15 | 13000 | 2 | 8 | 2170 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 18.9 | 66.02 | A | 7 | 9.4 | 48.92 | A | 7 | 0.54 | A | 7 | 979 | A | 7 | 60 | B | 8 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.52 | 4 | 0
2001-10-11 | 1900-10-10 | 16:00 | 16 | 549 | 1372 | 367 | 2 | 8 | 710 | 2 | 15 | 82 | 2 | 8 | 38700 | 2 | 8 | 67800 | 2 | 15 | 11400 | 2 | 8 | 1650 | 2 | 19 | 8 | E | 9 | 3 | A | 7 | 18.3 | 64.94 | A | 7 | 8.3 | 46.94 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.54 | 4 | 0
2001-10-11 | 1900-10-10 | 17:00 | 17 | 316 | 1372 | 185 | 2 | 8 | 469 | 2 | 15 | 76 | 2 | 8 | 19200 | 2 | 8 | 37500 | 2 | 15 | 10500 | 2 | 8 | 1390 | 2 | 19 | 7 | E | 9 | 2 | A | 7 | 17.8 | 64.04 | A | 7 | 7.8 | 46.04 | A | 7 | 0.52 | A | 7 | 977 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.74 | 4 | 0
2001-10-11 | 1900-10-10 | 18:00 | 18 | 68 | 1017 | 14 | 2 | 8 | 73 | 2 | 15 | 11 | 2 | 8 | 1800 | 2 | 8 | 3100 | 2 | 15 | 1600 | 2 | 8 | 180 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | A | 7 | 975 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.84 | 4 | 0
2001-10-11 | 1900-10-10 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.32 | 4 | 0
2001-10-11 | 1900-10-10 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.75 | A | 7 | 976 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.12 | 4 | 0
2001-10-11 | 1900-10-10 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 8.9 | 48.02 | A | 7 | 0.77 | A | 7 | 976 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.42 | 4 | 0
2001-10-11 | 1900-10-10 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 8.9 | 48.02 | A | 7 | 0.8 | A | 7 | 976 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.92 | 4 | 0
2001-10-11 | 1900-10-10 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.83 | A | 7 | 976 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.42 | 4 | 0
2001-10-11 | 1900-10-10 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.099 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.32 | 4 | 0
2001-10-12 | 1900-10-11 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.92 | 5 | 0
2001-10-12 | 1900-10-11 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.52 | 5 | 0
2001-10-12 | 1900-10-11 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.97 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.52 | 5 | 0
2001-10-12 | 1900-10-11 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 8 | 46.4 | A | 7 | 8 | 46.4 | A | 7 | 1 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 450 | A | 7 | 1.6 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.3 | 5 | 0
2001-10-12 | 1900-10-11 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 9 | 48.2 | A | 7 | 9 | 48.2 | A | 7 | 1 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 4800 | A | 7 | 450 | A | 7 | 1.7 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.1 | 5 | 0
2001-10-12 | 1900-10-11 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9600 | A | 7 | 518 | A | 7 | 1.7 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.22 | 5 | 0
2001-10-12 | 1900-10-11 | 7:00 | 7 | 37 | 744 | 1 | 2 | 8 | 8 | 2 | 15 | 1 | 2 | 8 | 200 | 2 | 8 | 300 | 2 | 15 | 200 | 2 | 8 | 20 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 9.4 | 48.92 | A | 7 | 9.4 | 48.92 | A | 7 | 1 | A | 7 | 975 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 4800 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.82 | 5 | 0
2001-10-12 | 1900-10-11 | 8:00 | 8 | 267 | 1373 | 102 | 2 | 8 | 42 | 2 | 15 | 93 | 2 | 8 | 11000 | 2 | 8 | 3400 | 2 | 15 | 10400 | 2 | 8 | 2160 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 9.4 | 48.92 | A | 7 | 9.4 | 48.92 | A | 7 | 1 | A | 7 | 976 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 4800 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.82 | 5 | 0
2001-10-12 | 1900-10-11 | 9:00 | 9 | 506 | 1373 | 226 | 2 | 8 | 94 | 2 | 15 | 191 | 2 | 8 | 24700 | 2 | 8 | 9000 | 2 | 15 | 21300 | 2 | 8 | 4910 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 12.8 | 55.04 | A | 7 | 11.7 | 53.06 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 9600 | A | 7 | 518 | A | 7 | 1.7 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.86 | 5 | 0
2001-10-12 | 1900-10-11 | 10:00 | 10 | 704 | 1373 | 320 | 2 | 8 | 129 | 2 | 15 | 254 | 2 | 8 | 34600 | 2 | 8 | 13200 | 2 | 15 | 27800 | 2 | 8 | 6390 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 579 | A | 7 | 1.8 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.06 | 5 | 0
2001-10-12 | 1900-10-11 | 11:00 | 11 | 846 | 1373 | 144 | 2 | 8 | 0 | 2 | 15 | 144 | 2 | 8 | 17300 | 2 | 8 | 0 | 2 | 15 | 17300 | 2 | 8 | 6870 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 977 | A | 7 | 100 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 488 | A | 7 | 1.8 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.86 | 5 | 0
2001-10-12 | 1900-10-11 | 12:00 | 12 | 923 | 1373 | 159 | 2 | 8 | 0 | 2 | 15 | 159 | 2 | 8 | 19200 | 2 | 8 | 0 | 2 | 15 | 19200 | 2 | 8 | 7730 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 975 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 549 | A | 7 | 1.8 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.86 | 5 | 0
2001-10-12 | 1900-10-11 | 13:00 | 13 | 929 | 1373 | 113 | 2 | 8 | 0 | 2 | 15 | 113 | 2 | 8 | 14000 | 2 | 8 | 0 | 2 | 15 | 14000 | 2 | 8 | 5760 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.2 | 53.96 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 396 | A | 7 | 1.9 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.06 | 5 | 0
2001-10-12 | 1900-10-11 | 14:00 | 14 | 864 | 1373 | 105 | 2 | 8 | 0 | 2 | 15 | 105 | 2 | 8 | 12900 | 2 | 8 | 0 | 2 | 15 | 12900 | 2 | 8 | 5270 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 12.2 | 53.96 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 335 | A | 7 | 2 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.76 | 5 | 0
2001-10-12 | 1900-10-11 | 15:00 | 15 | 732 | 1373 | 146 | 2 | 8 | 0 | 2 | 15 | 146 | 2 | 8 | 17200 | 2 | 8 | 0 | 2 | 15 | 17200 | 2 | 8 | 6520 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 274 | A | 7 | 2 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.84 | 5 | 0
2001-10-12 | 1900-10-11 | 16:00 | 16 | 543 | 1373 | 101 | 2 | 8 | 0 | 2 | 15 | 101 | 2 | 8 | 11800 | 2 | 8 | 0 | 2 | 15 | 11800 | 2 | 8 | 4250 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 335 | A | 7 | 2.1 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.84 | 5 | 0
2001-10-12 | 1900-10-11 | 17:00 | 17 | 309 | 1373 | 46 | 2 | 8 | 0 | 2 | 15 | 46 | 2 | 8 | 5400 | 2 | 8 | 0 | 2 | 15 | 5400 | 2 | 8 | 1830 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 974 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 12800 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.24 | 5 | 0
2001-10-12 | 1900-10-11 | 18:00 | 18 | 63 | 972 | 11 | 2 | 8 | 70 | 2 | 15 | 8 | 2 | 8 | 1400 | 2 | 8 | 3500 | 2 | 15 | 1200 | 2 | 8 | 160 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 972 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.84 | 5 | 0
2001-10-12 | 1900-10-11 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 7 | E | 9 | 12.8 | 55.04 | A | 7 | 12.8 | 55.04 | A | 7 | 1 | A | 7 | 973 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.94 | 5 | 0
2001-10-12 | 1900-10-11 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 12.8 | 55.04 | A | 7 | 12.8 | 55.04 | A | 7 | 1 | A | 7 | 973 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 11200 | A | 7 | 183 | A | 7 | 2.4 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.94 | 5 | 0
2001-10-12 | 1900-10-11 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | E | 9 | 13.3 | 55.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.97 | A | 7 | 972 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 2743 | A | 7 | 2.5 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.44 | 5 | 0
2001-10-12 | 1900-10-11 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | A | 7 | 12.8 | 55.04 | A | 7 | 12.8 | 55.04 | A | 7 | 1 | A | 7 | 971 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 11200 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.94 | 5 | 0
2001-10-12 | 1900-10-11 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 12.8 | 55.04 | A | 7 | 12.8 | 55.04 | A | 7 | 1 | A | 7 | 970 | A | 7 | 110 | A | 7 | 5.2 | A | 7 | 2400 | A | 7 | 91 | A | 7 | 2.6 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.94 | 5 | 0
2001-10-12 | 1900-10-11 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 967 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 91 | A | 7 | 2.7 | E | 8 | 0.098 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.84 | 5 | 0
2001-10-13 | 1900-10-12 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 6 | E | 9 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 968 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 91 | A | 7 | 2.6 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.84 | 6 | 0
2001-10-13 | 1900-10-12 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 967 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 2.5 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.84 | 6 | 0
2001-10-13 | 1900-10-12 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 4 | E | 9 | 12.8 | 55.04 | A | 7 | 12.8 | 55.04 | A | 7 | 1 | A | 7 | 966 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.5 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.94 | 6 | 0
2001-10-13 | 1900-10-12 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 6 | E | 9 | 13.3 | 55.94 | A | 7 | 12.8 | 55.04 | A | 7 | 0.97 | A | 7 | 966 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.44 | 6 | 0
2001-10-13 | 1900-10-12 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 966 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 2.3 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.84 | 6 | 0
2001-10-13 | 1900-10-12 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 13.9 | 57.02 | A | 7 | 13.3 | 55.94 | A | 7 | 0.96 | A | 7 | 964 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 2.2 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.24 | 6 | 0
2001-10-13 | 1900-10-12 | 7:00 | 7 | 35 | 721 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 13.9 | 57.02 | A | 7 | 13.9 | 57.02 | A | 7 | 1 | A | 7 | 965 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 11200 | A | 7 | 366 | A | 7 | 2.2 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.02 | 6 | 0
2001-10-13 | 1900-10-12 | 8:00 | 8 | 262 | 1373 | 37 | 2 | 8 | 0 | 2 | 15 | 37 | 2 | 8 | 4300 | 2 | 8 | 0 | 2 | 15 | 4300 | 2 | 8 | 1450 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 12.8 | 55.04 | A | 7 | 12.8 | 55.04 | A | 7 | 1 | A | 7 | 966 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 213 | A | 7 | 2.1 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.94 | 6 | 0
2001-10-13 | 1900-10-12 | 9:00 | 9 | 501 | 1373 | 106 | 2 | 8 | 0 | 2 | 15 | 106 | 2 | 8 | 12200 | 2 | 8 | 0 | 2 | 15 | 12200 | 2 | 8 | 4260 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 12.8 | 55.04 | A | 7 | 12.2 | 53.96 | A | 7 | 0.96 | A | 7 | 966 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 11200 | A | 7 | 213 | A | 7 | 2 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.26 | 6 | 0
2001-10-13 | 1900-10-12 | 10:00 | 10 | 699 | 1373 | 131 | 2 | 8 | 0 | 2 | 15 | 131 | 2 | 8 | 15400 | 2 | 8 | 0 | 2 | 15 | 15400 | 2 | 8 | 5850 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 13.9 | 57.02 | A | 7 | 11.7 | 53.06 | A | 7 | 0.87 | A | 7 | 966 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 335 | A | 7 | 1.9 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.86 | 6 | 0
2001-10-13 | 1900-10-12 | 11:00 | 11 | 840 | 1373 | 100 | 2 | 8 | 0 | 2 | 15 | 100 | 2 | 8 | 12300 | 2 | 8 | 0 | 2 | 15 | 12300 | 2 | 8 | 4990 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.84 | A | 7 | 966 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 488 | A | 7 | 1.9 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 48.48 | 6 | 0
2001-10-13 | 1900-10-12 | 12:00 | 12 | 917 | 1373 | 201 | 2 | 8 | 6 | 2 | 15 | 197 | 2 | 8 | 23800 | 2 | 8 | 500 | 2 | 15 | 23500 | 2 | 8 | 9170 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 14.4 | 57.92 | A | 7 | 10.6 | 51.08 | A | 7 | 0.78 | A | 7 | 964 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 549 | A | 7 | 1.8 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.48 | 6 | 0
2001-10-13 | 1900-10-12 | 13:00 | 13 | 922 | 1373 | 655 | 2 | 8 | 599 | 2 | 15 | 252 | 2 | 8 | 69300 | 2 | 8 | 61900 | 2 | 15 | 27600 | 2 | 8 | 6740 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 15.6 | 60.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.67 | A | 7 | 966 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.72 | 6 | 0
2001-10-13 | 1900-10-12 | 14:00 | 14 | 857 | 1373 | 633 | 2 | 8 | 834 | 2 | 15 | 110 | 2 | 8 | 66400 | 2 | 8 | 83300 | 2 | 15 | 14200 | 2 | 8 | 2620 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 16.7 | 62.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.58 | A | 7 | 965 | A | 7 | 310 | B | 8 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.44 | 6 | 0
2001-10-13 | 1900-10-12 | 15:00 | 15 | 725 | 1373 | 516 | 2 | 8 | 680 | 2 | 15 | 156 | 2 | 8 | 53300 | 2 | 8 | 66700 | 2 | 15 | 18000 | 2 | 8 | 3280 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.48 | A | 7 | 965 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.46 | 6 | 0
2001-10-13 | 1900-10-12 | 16:00 | 16 | 536 | 1373 | 275 | 2 | 8 | 267 | 2 | 15 | 171 | 2 | 8 | 29100 | 2 | 8 | 26200 | 2 | 15 | 18800 | 2 | 8 | 3660 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.8 | 64.04 | A | 7 | 5.6 | 42.08 | A | 7 | 0.45 | A | 7 | 965 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.38 | 6 | 0
2001-10-13 | 1900-10-12 | 17:00 | 17 | 302 | 1373 | 159 | 2 | 8 | 433 | 2 | 15 | 64 | 2 | 8 | 16200 | 2 | 8 | 34100 | 2 | 15 | 8700 | 2 | 8 | 1130 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 16.7 | 62.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.5 | A | 7 | 966 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.88 | 6 | 0
2001-10-13 | 1900-10-12 | 18:00 | 18 | 59 | 950 | 11 | 2 | 8 | 129 | 2 | 15 | 7 | 2 | 8 | 1700 | 2 | 8 | 7300 | 2 | 15 | 1200 | 2 | 8 | 170 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 15 | 59 | A | 7 | 6.1 | 42.98 | A | 7 | 0.55 | A | 7 | 964 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.58 | 6 | 0
2001-10-13 | 1900-10-12 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.62 | A | 7 | 967 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.68 | 6 | 0
2001-10-13 | 1900-10-12 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 11.7 | 53.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.66 | A | 7 | 968 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.38 | 6 | 0
2001-10-13 | 1900-10-12 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.66 | A | 7 | 968 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.38 | 6 | 0
2001-10-13 | 1900-10-12 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 5.6 | 42.08 | A | 7 | 0.74 | A | 7 | 968 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.58 | 6 | 0
2001-10-13 | 1900-10-12 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.8 | A | 7 | 969 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.38 | 6 | 0
2001-10-13 | 1900-10-12 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.8 | A | 7 | 967 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.38 | 6 | 0
2001-10-14 | 1900-10-13 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 5 | 41 | A | 7 | 0.8 | A | 7 | 969 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.3 | 7 | 0
2001-10-14 | 1900-10-13 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 5 | 41 | A | 7 | 0.86 | A | 7 | 970 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.1 | 7 | 0
2001-10-14 | 1900-10-13 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.85 | A | 7 | 970 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.02 | 7 | 0
2001-10-14 | 1900-10-13 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 970 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.4 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.78 | 7 | 0
2001-10-14 | 1900-10-13 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 7.8 | 46.04 | A | 7 | 5 | 41 | A | 7 | 0.82 | A | 7 | 971 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 1.3 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.6 | 7 | 0
2001-10-14 | 1900-10-13 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | E | 9 | 7.8 | 46.04 | A | 7 | 5 | 41 | A | 7 | 0.82 | A | 7 | 971 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.6 | 7 | 0
2001-10-14 | 1900-10-13 | 7:00 | 7 | 32 | 699 | 0 | 2 | 8 | 50 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 7.8 | 46.04 | A | 7 | 5 | 41 | A | 7 | 0.82 | A | 7 | 973 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.6 | 7 | 0
2001-10-14 | 1900-10-13 | 8:00 | 8 | 257 | 1374 | 132 | 2 | 8 | 312 | 2 | 15 | 73 | 2 | 8 | 13400 | 2 | 8 | 22600 | 2 | 15 | 9200 | 2 | 8 | 1360 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 9.4 | 48.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.8 | A | 7 | 974 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.18 | 7 | 0
2001-10-14 | 1900-10-13 | 9:00 | 9 | 496 | 1374 | 312 | 2 | 8 | 573 | 2 | 15 | 105 | 2 | 8 | 32000 | 2 | 8 | 52600 | 2 | 15 | 13000 | 2 | 8 | 1950 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 11.1 | 51.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.88 | 7 | 0
2001-10-14 | 1900-10-13 | 10:00 | 10 | 693 | 1374 | 497 | 2 | 8 | 765 | 2 | 15 | 110 | 2 | 8 | 52400 | 2 | 8 | 75800 | 2 | 15 | 14100 | 2 | 8 | 2370 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 13.3 | 55.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.62 | A | 7 | 977 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.68 | 7 | 0
2001-10-14 | 1900-10-13 | 11:00 | 11 | 835 | 1374 | 603 | 2 | 8 | 812 | 2 | 15 | 108 | 2 | 8 | 63200 | 2 | 8 | 80900 | 2 | 15 | 13900 | 2 | 8 | 2510 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 14.4 | 57.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.49 | A | 7 | 977 | A | 7 | 280 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.42 | 7 | 0
2001-10-14 | 1900-10-13 | 12:00 | 12 | 911 | 1374 | 671 | 2 | 8 | 795 | 2 | 15 | 143 | 2 | 8 | 71500 | 2 | 8 | 80900 | 2 | 15 | 17700 | 2 | 8 | 3790 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 15.6 | 60.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.42 | A | 7 | 975 | A | 7 | 300 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.54 | 7 | 0
2001-10-14 | 1900-10-13 | 13:00 | 13 | 916 | 1374 | 637 | 2 | 8 | 683 | 2 | 15 | 180 | 2 | 8 | 66700 | 2 | 8 | 68800 | 2 | 15 | 20700 | 2 | 8 | 4660 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 16.1 | 60.98 | A | 7 | 2.2 | 35.96 | A | 7 | 0.39 | A | 7 | 977 | A | 7 | 270 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 28.26 | 7 | 0
2001-10-14 | 1900-10-13 | 14:00 | 14 | 851 | 1374 | 575 | 2 | 8 | 656 | 2 | 15 | 167 | 2 | 8 | 60000 | 2 | 8 | 65700 | 2 | 15 | 19200 | 2 | 8 | 4000 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 16.1 | 60.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.38 | A | 7 | 977 | A | 7 | 260 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 27.46 | 7 | 0
2001-10-14 | 1900-10-13 | 15:00 | 15 | 719 | 1374 | 477 | 2 | 8 | 656 | 2 | 15 | 132 | 2 | 8 | 49700 | 2 | 8 | 64800 | 2 | 15 | 15700 | 2 | 8 | 2840 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 17.2 | 62.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.33 | A | 7 | 977 | A | 7 | 290 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.38 | 7 | 0
2001-10-14 | 1900-10-13 | 16:00 | 16 | 529 | 1374 | 349 | 2 | 8 | 644 | 2 | 15 | 100 | 2 | 8 | 36100 | 2 | 8 | 60300 | 2 | 15 | 12800 | 2 | 8 | 1920 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 17.2 | 62.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.33 | A | 7 | 977 | A | 7 | 250 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.38 | 7 | 0
2001-10-14 | 1900-10-13 | 17:00 | 17 | 295 | 1374 | 145 | 2 | 8 | 350 | 2 | 15 | 69 | 2 | 8 | 15100 | 2 | 8 | 27200 | 2 | 15 | 9200 | 2 | 8 | 1260 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.35 | A | 7 | 977 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.58 | 7 | 0
2001-10-14 | 1900-10-13 | 18:00 | 18 | 55 | 905 | 9 | 2 | 8 | 98 | 2 | 15 | 6 | 2 | 8 | 1400 | 2 | 8 | 5500 | 2 | 15 | 1000 | 2 | 8 | 150 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.43 | A | 7 | 976 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 27.28 | 7 | 0
2001-10-14 | 1900-10-13 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.54 | A | 7 | 979 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.46 | 7 | 0
2001-10-14 | 1900-10-13 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | E | 9 | 10 | 50 | A | 7 | 1.7 | 35.06 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.76 | 7 | 0
2001-10-14 | 1900-10-13 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 7 | E | 9 | 9.4 | 48.92 | A | 7 | 2.8 | 37.04 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.54 | 7 | 0
2001-10-14 | 1900-10-13 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 3 | E | 9 | 9.4 | 48.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.66 | A | 7 | 980 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 1.6 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.74 | 7 | 0
2001-10-14 | 1900-10-13 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 5 | A | 7 | 10 | 50 | A | 7 | 3.3 | 37.94 | A | 7 | 0.63 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.34 | 7 | 0
2001-10-14 | 1900-10-13 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 3.9 | 39.02 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 1.7 | E | 8 | 0.097 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.72 | 7 | 0
2001-10-15 | 1900-10-14 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | E | 9 | 8.9 | 48.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 1.7 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.42 | 1 | 0
2001-10-15 | 1900-10-14 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 10 | 50 | A | 7 | 4.4 | 39.92 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 1.7 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.72 | 1 | 0
2001-10-15 | 1900-10-14 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 10 | 50 | A | 7 | 6.1 | 42.98 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 1829 | A | 7 | 1.6 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.78 | 1 | 0
2001-10-15 | 1900-10-14 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 8.9 | 48.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.83 | A | 7 | 982 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 2286 | A | 7 | 1.6 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.58 | 1 | 0
2001-10-15 | 1900-10-14 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 9.4 | 48.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.6 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.98 | 1 | 0
2001-10-15 | 1900-10-14 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 8.3 | 46.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.9 | A | 7 | 983 | A | 7 | 360 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 1433 | A | 7 | 1.5 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.66 | 1 | 0
2001-10-15 | 1900-10-14 | 7:00 | 7 | 30 | 676 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 7.2 | 44.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.97 | A | 7 | 984 | A | 7 | 20 | A | 7 | 7.7 | A | 7 | 6400 | A | 7 | 1006 | A | 7 | 1.5 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.56 | 1 | 0
2001-10-15 | 1900-10-14 | 8:00 | 8 | 253 | 1375 | 29 | 2 | 8 | 0 | 2 | 15 | 29 | 2 | 8 | 3400 | 2 | 8 | 0 | 2 | 15 | 3400 | 2 | 8 | 1170 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 985 | A | 7 | 10 | A | 7 | 6.7 | A | 7 | 4800 | A | 7 | 1128 | A | 7 | 1.4 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 3 | 1 | A | 7 | 44.06 | 1 | 0
2001-10-15 | 1900-10-14 | 9:00 | 9 | 491 | 1375 | 71 | 2 | 8 | 0 | 2 | 15 | 71 | 2 | 8 | 8400 | 2 | 8 | 0 | 2 | 15 | 8400 | 2 | 8 | 3060 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6.7 | 44.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.96 | A | 7 | 987 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 4000 | A | 7 | 213 | A | 7 | 1.4 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 6 | 1 | A | 7 | 42.38 | 1 | 0
2001-10-15 | 1900-10-14 | 10:00 | 10 | 688 | 1375 | 79 | 2 | 8 | 0 | 2 | 15 | 79 | 2 | 8 | 9700 | 2 | 8 | 0 | 2 | 15 | 9700 | 2 | 8 | 3770 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 5.6 | 42.08 | A | 7 | 5 | 41 | A | 7 | 0.96 | A | 7 | 988 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 457 | A | 7 | 1.4 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 5 | 1 | A | 7 | 40.4 | 1 | 0
2001-10-15 | 1900-10-14 | 11:00 | 11 | 829 | 1375 | 94 | 2 | 8 | 0 | 2 | 15 | 94 | 2 | 8 | 11600 | 2 | 8 | 0 | 2 | 15 | 11600 | 2 | 8 | 4700 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 4 | 39.2 | A | 7 | 4 | 39.2 | A | 7 | 1 | A | 7 | 987 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 300 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 4 | 1 | A | 7 | 39.1 | 1 | 0
2001-10-15 | 1900-10-14 | 12:00 | 12 | 905 | 1375 | 134 | 2 | 8 | 0 | 2 | 15 | 134 | 2 | 8 | 16300 | 2 | 8 | 0 | 2 | 15 | 16300 | 2 | 8 | 6630 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 3.9 | 39.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.93 | A | 7 | 986 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 640 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 4 | 1 | A | 7 | 36.14 | 1 | 0
2001-10-15 | 1900-10-14 | 13:00 | 13 | 910 | 1375 | 107 | 2 | 8 | 0 | 2 | 15 | 107 | 2 | 8 | 13300 | 2 | 8 | 0 | 2 | 15 | 13300 | 2 | 8 | 5450 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 4.4 | 39.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.97 | A | 7 | 987 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 9600 | A | 7 | 366 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 2 | 1 | A | 7 | 38.62 | 1 | 0
2001-10-15 | 1900-10-14 | 14:00 | 14 | 844 | 1375 | 186 | 2 | 8 | 0 | 2 | 15 | 186 | 2 | 8 | 21900 | 2 | 8 | 0 | 2 | 15 | 21900 | 2 | 8 | 8430 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 6 | 42.8 | A | 7 | 4 | 39.2 | A | 7 | 0.87 | A | 7 | 987 | A | 7 | 360 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 1470 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.5 | 1 | 0
2001-10-15 | 1900-10-14 | 15:00 | 15 | 712 | 1375 | 151 | 2 | 8 | 0 | 2 | 15 | 151 | 2 | 8 | 17600 | 2 | 8 | 0 | 2 | 15 | 17600 | 2 | 8 | 6600 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 7.2 | 44.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.9 | A | 7 | 987 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 488 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.68 | 1 | 0
2001-10-15 | 1900-10-14 | 16:00 | 16 | 522 | 1375 | 338 | 2 | 8 | 493 | 2 | 15 | 150 | 2 | 8 | 34900 | 2 | 8 | 46600 | 2 | 15 | 17100 | 2 | 8 | 2970 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 987 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.78 | 1 | 0
2001-10-15 | 1900-10-14 | 17:00 | 17 | 289 | 1375 | 148 | 2 | 8 | 447 | 2 | 15 | 54 | 2 | 8 | 15200 | 2 | 8 | 34800 | 2 | 15 | 7900 | 2 | 8 | 970 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 987 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 1433 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.78 | 1 | 0
2001-10-15 | 1900-10-14 | 18:00 | 18 | 51 | 882 | 1 | 2 | 8 | 0 | 2 | 15 | 1 | 2 | 8 | 100 | 2 | 8 | 0 | 2 | 15 | 100 | 2 | 8 | 40 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.02 | 1 | 0
2001-10-15 | 1900-10-14 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 5.6 | 42.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.79 | A | 7 | 989 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.46 | 1 | 0
2001-10-15 | 1900-10-14 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | A | 7 | 5.6 | 42.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.79 | A | 7 | 989 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2896 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.46 | 1 | 0
2001-10-15 | 1900-10-14 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | A | 7 | 4.4 | 39.92 | A | 7 | 1.7 | 35.06 | A | 7 | 0.83 | A | 7 | 989 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2743 | A | 7 | 1.3 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.06 | 1 | 0
2001-10-15 | 1900-10-14 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 1.7 | 35.06 | A | 7 | 0.83 | A | 7 | 990 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.06 | 1 | 0
2001-10-15 | 1900-10-14 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.82 | A | 7 | 990 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.88 | 1 | 0
2001-10-15 | 1900-10-14 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.8 | 37.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.85 | A | 7 | 989 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.096 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.38 | 1 | 0
2001-10-16 | 1900-10-15 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 990 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.1 | 2 | 0
2001-10-16 | 1900-10-15 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.2 | 35.96 | A | 7 | 0 | 32 | A | 7 | 0.85 | A | 7 | 991 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.4 | 2 | 0
2001-10-16 | 1900-10-15 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 991 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.1 | 2 | 0
2001-10-16 | 1900-10-15 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.78 | A | 7 | 991 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 28.62 | 2 | 0
2001-10-16 | 1900-10-15 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.88 | A | 7 | 991 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.62 | 2 | 0
2001-10-16 | 1900-10-15 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.84 | A | 7 | 991 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.22 | 2 | 0
2001-10-16 | 1900-10-15 | 7:00 | 7 | 28 | 654 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.88 | A | 7 | 992 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.62 | 2 | 0
2001-10-16 | 1900-10-15 | 8:00 | 8 | 248 | 1376 | 116 | 2 | 8 | 172 | 2 | 15 | 85 | 2 | 8 | 12000 | 2 | 8 | 12100 | 2 | 15 | 9800 | 2 | 8 | 1710 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 993 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.7 | 2 | 0
2001-10-16 | 1900-10-15 | 9:00 | 9 | 486 | 1376 | 335 | 2 | 8 | 574 | 2 | 15 | 132 | 2 | 8 | 34700 | 2 | 8 | 53300 | 2 | 15 | 15900 | 2 | 8 | 2560 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 994 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.76 | 2 | 0
2001-10-16 | 1900-10-15 | 10:00 | 10 | 683 | 1376 | 491 | 2 | 8 | 815 | 2 | 15 | 86 | 2 | 8 | 51500 | 2 | 8 | 79800 | 2 | 15 | 11700 | 2 | 8 | 1840 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.63 | A | 7 | 994 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.56 | 2 | 0
2001-10-16 | 1900-10-15 | 11:00 | 11 | 824 | 1376 | 603 | 2 | 8 | 842 | 2 | 15 | 97 | 2 | 8 | 63800 | 2 | 8 | 84200 | 2 | 15 | 13300 | 2 | 8 | 2310 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 10 | 50 | A | 7 | -0.6 | 30.92 | A | 7 | 0.47 | A | 7 | 994 | A | 7 | 320 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.22 | 2 | 0
2001-10-16 | 1900-10-15 | 12:00 | 12 | 899 | 1376 | 665 | 2 | 8 | 825 | 2 | 15 | 125 | 2 | 8 | 69400 | 2 | 8 | 82400 | 2 | 15 | 15400 | 2 | 8 | 3000 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 10.6 | 51.08 | A | 7 | 0 | 32 | A | 7 | 0.48 | A | 7 | 992 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.3 | 2 | 0
2001-10-16 | 1900-10-15 | 13:00 | 13 | 904 | 1376 | 649 | 2 | 8 | 737 | 2 | 15 | 163 | 2 | 8 | 68400 | 2 | 8 | 74500 | 2 | 15 | 19300 | 2 | 8 | 4200 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 11.7 | 53.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.42 | A | 7 | 994 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 24.72 | 2 | 0
2001-10-16 | 1900-10-15 | 14:00 | 14 | 838 | 1376 | 621 | 2 | 8 | 846 | 2 | 15 | 103 | 2 | 8 | 65400 | 2 | 8 | 84500 | 2 | 15 | 13700 | 2 | 8 | 2450 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 12.2 | 53.96 | A | 7 | 0 | 32 | A | 7 | 0.43 | A | 7 | 993 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.7 | 2 | 0
2001-10-16 | 1900-10-15 | 15:00 | 15 | 706 | 1376 | 504 | 2 | 8 | 780 | 2 | 15 | 103 | 2 | 8 | 52000 | 2 | 8 | 76100 | 2 | 15 | 12800 | 2 | 8 | 2080 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.45 | A | 7 | 993 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.78 | 2 | 0
2001-10-16 | 1900-10-15 | 16:00 | 16 | 516 | 1376 | 332 | 2 | 8 | 632 | 2 | 15 | 94 | 2 | 8 | 34400 | 2 | 8 | 59000 | 2 | 15 | 12200 | 2 | 8 | 1810 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 0 | 32 | A | 7 | 0.43 | A | 7 | 992 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.7 | 2 | 0
2001-10-16 | 1900-10-15 | 17:00 | 17 | 282 | 1376 | 152 | 2 | 8 | 505 | 2 | 15 | 48 | 2 | 8 | 15700 | 2 | 8 | 39200 | 2 | 15 | 7600 | 2 | 8 | 880 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.42 | A | 7 | 992 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 24.72 | 2 | 0
2001-10-16 | 1900-10-15 | 18:00 | 18 | 47 | 837 | 4 | 2 | 8 | 9 | 2 | 15 | 3 | 2 | 8 | 400 | 2 | 8 | 300 | 2 | 15 | 400 | 2 | 8 | 40 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 10.6 | 51.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.42 | A | 7 | 990 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.04 | 2 | 0
2001-10-16 | 1900-10-15 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.53 | A | 7 | 991 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.92 | 2 | 0
2001-10-16 | 1900-10-15 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.65 | A | 7 | 991 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.88 | 2 | 0
2001-10-16 | 1900-10-15 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.59 | A | 7 | 991 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.62 | 2 | 0
2001-10-16 | 1900-10-15 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | 0 | 32 | A | 7 | 0.67 | A | 7 | 991 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 28.4 | 2 | 0
2001-10-16 | 1900-10-15 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.7 | A | 7 | 991 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 27.72 | 2 | 0
2001-10-16 | 1900-10-15 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | 0 | 32 | A | 7 | 0.76 | A | 7 | 990 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.095 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.4 | 2 | 0
2001-10-17 | 1900-10-16 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 990 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.7 | 3 | 0
2001-10-17 | 1900-10-16 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 990 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.1 | 3 | 0
2001-10-17 | 1900-10-16 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 1.7 | 35.06 | A | 7 | 0 | 32 | A | 7 | 0.88 | A | 7 | 990 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.7 | 3 | 0
2001-10-17 | 1900-10-16 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 989 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.7 | 3 | 0
2001-10-17 | 1900-10-16 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 989 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.98 | 3 | 0
2001-10-17 | 1900-10-16 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 988 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.98 | 3 | 0
2001-10-17 | 1900-10-16 | 7:00 | 7 | 26 | 631 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 3.9 | 39.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.79 | A | 7 | 989 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.68 | 3 | 0
2001-10-17 | 1900-10-16 | 8:00 | 8 | 243 | 1377 | 127 | 2 | 8 | 302 | 2 | 15 | 73 | 2 | 8 | 12800 | 2 | 8 | 21200 | 2 | 15 | 9100 | 2 | 8 | 1360 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 2.2 | 35.96 | A | 7 | 0.7 | A | 7 | 989 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.36 | 3 | 0
2001-10-17 | 1900-10-16 | 9:00 | 9 | 481 | 1377 | 321 | 2 | 8 | 694 | 2 | 15 | 78 | 2 | 8 | 33500 | 2 | 8 | 64100 | 2 | 15 | 11100 | 2 | 8 | 1510 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.61 | A | 7 | 989 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.04 | 3 | 0
2001-10-17 | 1900-10-16 | 10:00 | 10 | 677 | 1377 | 452 | 2 | 8 | 619 | 2 | 15 | 147 | 2 | 8 | 46600 | 2 | 8 | 60100 | 2 | 15 | 16900 | 2 | 8 | 2970 | 2 | 19 | 2 | E | 9 | 1 | E | 9 | 13.9 | 57.02 | A | 7 | 5 | 41 | A | 7 | 0.55 | A | 7 | 989 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.9 | 3 | 0
2001-10-17 | 1900-10-16 | 11:00 | 11 | 818 | 1377 | 553 | 2 | 8 | 666 | 2 | 15 | 156 | 2 | 8 | 57800 | 2 | 8 | 66600 | 2 | 15 | 18100 | 2 | 8 | 3620 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.5 | A | 7 | 988 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.08 | 3 | 0
2001-10-17 | 1900-10-16 | 12:00 | 12 | 893 | 1377 | 659 | 2 | 8 | 801 | 2 | 15 | 138 | 2 | 8 | 70200 | 2 | 8 | 81400 | 2 | 15 | 17200 | 2 | 8 | 3580 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.7 | 62.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.5 | A | 7 | 985 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.88 | 3 | 0
2001-10-17 | 1900-10-16 | 13:00 | 13 | 898 | 1377 | 667 | 2 | 8 | 845 | 2 | 15 | 114 | 2 | 8 | 70200 | 2 | 8 | 84700 | 2 | 15 | 14800 | 2 | 8 | 2830 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.47 | A | 7 | 986 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.26 | 3 | 0
2001-10-17 | 1900-10-16 | 14:00 | 14 | 832 | 1377 | 591 | 2 | 8 | 786 | 2 | 15 | 115 | 2 | 8 | 61600 | 2 | 8 | 78100 | 2 | 15 | 14200 | 2 | 8 | 2590 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.9 | 66.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.43 | A | 7 | 985 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.78 | 3 | 0
2001-10-17 | 1900-10-16 | 15:00 | 15 | 699 | 1377 | 498 | 2 | 8 | 732 | 2 | 15 | 125 | 2 | 8 | 52100 | 2 | 8 | 72100 | 2 | 15 | 15300 | 2 | 8 | 2660 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 17.8 | 64.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.46 | A | 7 | 984 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.28 | 3 | 0
2001-10-17 | 1900-10-16 | 16:00 | 16 | 509 | 1377 | 310 | 2 | 8 | 469 | 2 | 15 | 136 | 2 | 8 | 32200 | 2 | 8 | 44100 | 2 | 15 | 15800 | 2 | 8 | 2650 | 2 | 19 | 2 | E | 9 | 1 | E | 9 | 17.2 | 62.96 | A | 7 | 3.9 | 39.02 | A | 7 | 0.41 | A | 7 | 983 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.92 | 3 | 0
2001-10-17 | 1900-10-16 | 17:00 | 17 | 276 | 1377 | 120 | 2 | 8 | 227 | 2 | 15 | 74 | 2 | 8 | 12600 | 2 | 8 | 17000 | 2 | 15 | 9200 | 2 | 8 | 1420 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 4.4 | 39.92 | A | 7 | 0.46 | A | 7 | 983 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.72 | 3 | 0
2001-10-17 | 1900-10-16 | 18:00 | 18 | 43 | 815 | 2 | 2 | 8 | 0 | 2 | 15 | 2 | 2 | 8 | 300 | 2 | 8 | 0 | 2 | 15 | 300 | 2 | 8 | 80 | 2 | 19 | 4 | E | 9 | 3 | A | 7 | 13.9 | 57.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.72 | 3 | 0
2001-10-17 | 1900-10-16 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.56 | A | 7 | 982 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.44 | 3 | 0
2001-10-17 | 1900-10-16 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.84 | 3 | 0
2001-10-17 | 1900-10-16 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.49 | A | 7 | 982 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.44 | 3 | 0
2001-10-17 | 1900-10-16 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 3.3 | 37.94 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.44 | 3 | 0
2001-10-17 | 1900-10-16 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 1 | E | 9 | 12.8 | 55.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.52 | A | 7 | 981 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.54 | 3 | 0
2001-10-17 | 1900-10-16 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 1 | E | 9 | 11.7 | 53.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.61 | A | 7 | 979 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.82 | 3 | 0
2001-10-18 | 1900-10-17 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.82 | 4 | 0
2001-10-18 | 1900-10-17 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | E | 9 | 11.1 | 51.98 | A | 7 | 5 | 41 | A | 7 | 0.66 | A | 7 | 979 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.4 | 4 | 0
2001-10-18 | 1900-10-17 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 11.1 | 51.98 | A | 7 | 5 | 41 | A | 7 | 0.66 | A | 7 | 979 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.4 | 4 | 0
2001-10-18 | 1900-10-17 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.08 | 4 | 0
2001-10-18 | 1900-10-17 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 1 | E | 9 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.08 | 4 | 0
2001-10-18 | 1900-10-17 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 1 | E | 9 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 976 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.08 | 4 | 0
2001-10-18 | 1900-10-17 | 7:00 | 7 | 24 | 608 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 3 | E | 9 | 2 | E | 9 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.08 | 4 | 0
2001-10-18 | 1900-10-17 | 8:00 | 8 | 238 | 1377 | 138 | 2 | 8 | 311 | 2 | 15 | 84 | 2 | 8 | 13800 | 2 | 8 | 21500 | 2 | 15 | 10000 | 2 | 8 | 1610 | 2 | 19 | 6 | E | 9 | 3 | E | 9 | 11.7 | 53.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.68 | A | 7 | 978 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.4 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.48 | 4 | 0
2001-10-18 | 1900-10-17 | 9:00 | 9 | 476 | 1377 | 215 | 2 | 8 | 152 | 2 | 15 | 162 | 2 | 8 | 23100 | 2 | 8 | 14400 | 2 | 15 | 18200 | 2 | 8 | 3700 | 2 | 19 | 7 | E | 9 | 3 | E | 9 | 12.8 | 55.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.69 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.3 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.46 | 4 | 0
2001-10-18 | 1900-10-17 | 10:00 | 10 | 672 | 1377 | 367 | 2 | 8 | 294 | 2 | 15 | 223 | 2 | 8 | 38900 | 2 | 8 | 30300 | 2 | 15 | 24100 | 2 | 8 | 5120 | 2 | 19 | 7 | E | 9 | 3 | E | 9 | 14.4 | 57.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.94 | 4 | 0
2001-10-18 | 1900-10-17 | 11:00 | 11 | 812 | 1377 | 547 | 2 | 8 | 630 | 2 | 15 | 174 | 2 | 8 | 56700 | 2 | 8 | 62500 | 2 | 15 | 19700 | 2 | 8 | 3940 | 2 | 19 | 8 | E | 9 | 4 | E | 9 | 15 | 59 | A | 7 | 8.3 | 46.94 | A | 7 | 0.64 | A | 7 | 978 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.44 | 4 | 0
2001-10-18 | 1900-10-17 | 12:00 | 12 | 887 | 1377 | 604 | 2 | 8 | 638 | 2 | 15 | 192 | 2 | 8 | 62800 | 2 | 8 | 63700 | 2 | 15 | 21600 | 2 | 8 | 4710 | 2 | 19 | 7 | E | 9 | 5 | E | 9 | 16.7 | 62.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.82 | 4 | 0
2001-10-18 | 1900-10-17 | 13:00 | 13 | 892 | 1377 | 524 | 2 | 8 | 359 | 2 | 15 | 290 | 2 | 8 | 56200 | 2 | 8 | 38400 | 2 | 15 | 31300 | 2 | 8 | 7770 | 2 | 19 | 7 | E | 9 | 6 | E | 9 | 17.2 | 62.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.52 | 4 | 0
2001-10-18 | 1900-10-17 | 14:00 | 14 | 825 | 1377 | 475 | 2 | 8 | 357 | 2 | 15 | 260 | 2 | 8 | 50900 | 2 | 8 | 37900 | 2 | 15 | 28100 | 2 | 8 | 6530 | 2 | 19 | 4 | E | 9 | 3 | E | 9 | 17.8 | 64.04 | A | 7 | 9.4 | 48.92 | A | 7 | 0.58 | A | 7 | 977 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.2 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.22 | 4 | 0
2001-10-18 | 1900-10-17 | 15:00 | 15 | 693 | 1377 | 458 | 2 | 8 | 531 | 2 | 15 | 190 | 2 | 8 | 47800 | 2 | 8 | 53100 | 2 | 15 | 21000 | 2 | 8 | 4070 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 17.8 | 64.04 | A | 7 | 9.4 | 48.92 | A | 7 | 0.58 | A | 7 | 978 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 1463 | A | 7 | 1.3 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.22 | 4 | 0
2001-10-18 | 1900-10-17 | 16:00 | 16 | 503 | 1377 | 142 | 2 | 8 | 17 | 2 | 15 | 135 | 2 | 8 | 15900 | 2 | 8 | 1200 | 2 | 15 | 15500 | 2 | 8 | 5080 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 16.7 | 62.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.6 | A | 7 | 978 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 1.4 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.72 | 4 | 0
2001-10-18 | 1900-10-17 | 17:00 | 17 | 269 | 1377 | 79 | 2 | 8 | 32 | 2 | 15 | 73 | 2 | 8 | 8700 | 2 | 8 | 2600 | 2 | 15 | 8200 | 2 | 8 | 1810 | 2 | 19 | 6 | E | 9 | 4 | E | 9 | 14.4 | 57.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.67 | A | 7 | 978 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.5 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.94 | 4 | 0
2001-10-18 | 1900-10-17 | 18:00 | 18 | 40 | 769 | 2 | 2 | 8 | 30 | 2 | 15 | 2 | 2 | 8 | 400 | 2 | 8 | 1400 | 2 | 15 | 400 | 2 | 8 | 40 | 2 | 19 | 7 | E | 9 | 7 | A | 7 | 12.2 | 53.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.44 | 4 | 0
2001-10-18 | 1900-10-17 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 1 | E | 9 | 11.7 | 53.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.77 | A | 7 | 980 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.7 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.64 | 4 | 0
2001-10-18 | 1900-10-17 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.14 | 4 | 0
2001-10-18 | 1900-10-17 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | 7.2 | 44.96 | A | 7 | 0.83 | A | 7 | 980 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.46 | 4 | 0
2001-10-18 | 1900-10-17 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 6.7 | 44.06 | A | 7 | 0.86 | A | 7 | 980 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.06 | 4 | 0
2001-10-18 | 1900-10-17 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.66 | 4 | 0
2001-10-18 | 1900-10-17 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.83 | A | 7 | 979 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.094 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.78 | 4 | 0
2001-10-19 | 1900-10-18 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.97 | A | 7 | 980 | A | 7 | 10 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.68 | 5 | 0
2001-10-19 | 1900-10-18 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | 4.4 | 39.92 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.82 | 5 | 0
2001-10-19 | 1900-10-18 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40 | 5 | 0
2001-10-19 | 1900-10-18 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 140 | A | 7 | 1.5 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40 | 5 | 0
2001-10-19 | 1900-10-18 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 4.4 | 39.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.93 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.04 | 5 | 0
2001-10-19 | 1900-10-18 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.9 | 39.02 | A | 7 | 3.3 | 37.94 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.44 | 5 | 0
2001-10-19 | 1900-10-18 | 7:00 | 7 | 22 | 586 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 4.4 | 39.92 | A | 7 | 4.4 | 39.92 | A | 7 | 1 | A | 7 | 980 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.92 | 5 | 0
2001-10-19 | 1900-10-18 | 8:00 | 8 | 233 | 1378 | 140 | 2 | 8 | 451 | 2 | 15 | 63 | 2 | 8 | 13900 | 2 | 8 | 31200 | 2 | 15 | 8600 | 2 | 8 | 1030 | 2 | 19 | 4 | E | 9 | 3 | E | 9 | 7.8 | 46.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11200 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.36 | 5 | 0
2001-10-19 | 1900-10-18 | 9:00 | 9 | 471 | 1378 | 301 | 2 | 8 | 544 | 2 | 15 | 115 | 2 | 8 | 31500 | 2 | 8 | 50100 | 2 | 15 | 14400 | 2 | 8 | 2190 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.89 | A | 7 | 982 | A | 7 | 210 | A | 7 | 1.5 | A | 7 | 11200 | A | 7 | 3962 | A | 7 | 1.7 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.32 | 5 | 0
2001-10-19 | 1900-10-18 | 10:00 | 10 | 667 | 1378 | 335 | 2 | 8 | 190 | 2 | 15 | 243 | 2 | 8 | 36200 | 2 | 8 | 19300 | 2 | 15 | 26800 | 2 | 8 | 5990 | 2 | 19 | 8 | E | 9 | 7 | E | 9 | 13.3 | 55.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.75 | A | 7 | 982 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 12800 | A | 7 | 3962 | A | 7 | 1.7 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.12 | 5 | 0
2001-10-19 | 1900-10-18 | 11:00 | 11 | 807 | 1378 | 516 | 2 | 8 | 455 | 2 | 15 | 249 | 2 | 8 | 53500 | 2 | 8 | 46300 | 2 | 15 | 26300 | 2 | 8 | 5920 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 15 | 59 | A | 7 | 7.2 | 44.96 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 1.6 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.06 | 5 | 0
2001-10-19 | 1900-10-18 | 12:00 | 12 | 881 | 1378 | 275 | 2 | 8 | 30 | 2 | 15 | 255 | 2 | 8 | 30200 | 2 | 8 | 3000 | 2 | 15 | 28300 | 2 | 8 | 8700 | 2 | 19 | 5 | E | 9 | 4 | E | 9 | 16.1 | 60.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.84 | 5 | 0
2001-10-19 | 1900-10-18 | 13:00 | 13 | 886 | 1378 | 446 | 2 | 8 | 216 | 2 | 15 | 307 | 2 | 8 | 48600 | 2 | 8 | 22700 | 2 | 15 | 34000 | 2 | 8 | 8680 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 16.1 | 60.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.36 | 5 | 0
2001-10-19 | 1900-10-18 | 14:00 | 14 | 819 | 1378 | 284 | 2 | 8 | 66 | 2 | 15 | 245 | 2 | 8 | 31300 | 2 | 8 | 6700 | 2 | 15 | 27300 | 2 | 8 | 7980 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 16.7 | 62.06 | A | 7 | 6.7 | 44.06 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 1.6 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.06 | 5 | 0
2001-10-19 | 1900-10-18 | 15:00 | 15 | 686 | 1378 | 458 | 2 | 8 | 555 | 2 | 15 | 181 | 2 | 8 | 48000 | 2 | 8 | 55500 | 2 | 15 | 20300 | 2 | 8 | 3850 | 2 | 19 | 4 | E | 9 | 3 | E | 9 | 17.2 | 62.96 | A | 7 | 7.2 | 44.96 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.6 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.86 | 5 | 0
2001-10-19 | 1900-10-18 | 16:00 | 16 | 496 | 1378 | 283 | 2 | 8 | 440 | 2 | 15 | 124 | 2 | 8 | 29600 | 2 | 8 | 41100 | 2 | 15 | 14700 | 2 | 8 | 2390 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 17.2 | 62.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.46 | A | 7 | 980 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.48 | 5 | 0
2001-10-19 | 1900-10-18 | 17:00 | 17 | 263 | 1378 | 135 | 2 | 8 | 457 | 2 | 15 | 48 | 2 | 8 | 13900 | 2 | 8 | 34300 | 2 | 15 | 7300 | 2 | 8 | 870 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.51 | A | 7 | 980 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.98 | 5 | 0
2001-10-19 | 1900-10-18 | 18:00 | 18 | 36 | 747 | 1 | 2 | 8 | 69 | 2 | 15 | 1 | 2 | 8 | 500 | 2 | 8 | 3900 | 2 | 15 | 300 | 2 | 8 | 40 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 14.4 | 57.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.88 | 5 | 0
2001-10-19 | 1900-10-18 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 5 | 41 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 170 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36 | 5 | 0
2001-10-19 | 1900-10-18 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 9.4 | 48.92 | A | 7 | 5 | 41 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.5 | 5 | 0
2001-10-19 | 1900-10-18 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.8 | 46.04 | A | 7 | 4.4 | 39.92 | A | 7 | 0.79 | A | 7 | 979 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.22 | 5 | 0
2001-10-19 | 1900-10-18 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.9 | 5 | 0
2001-10-19 | 1900-10-18 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.42 | 5 | 0
2001-10-19 | 1900-10-18 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 9.4 | 48.92 | A | 7 | 5 | 41 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.093 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.5 | 5 | 0
2001-10-20 | 1900-10-19 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.8 | 46.04 | A | 7 | 4.4 | 39.92 | A | 7 | 0.79 | A | 7 | 979 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.22 | 6 | 0
2001-10-20 | 1900-10-19 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.9 | 6 | 0
2001-10-20 | 1900-10-19 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 5 | 41 | A | 7 | 0.86 | A | 7 | 978 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.1 | 6 | 0
2001-10-20 | 1900-10-19 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.8 | A | 7 | 979 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.38 | 6 | 0
2001-10-20 | 1900-10-19 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 979 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.5 | 6 | 0
2001-10-20 | 1900-10-19 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | 5 | 41 | A | 7 | 0.89 | A | 7 | 978 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.5 | 6 | 0
2001-10-20 | 1900-10-19 | 7:00 | 7 | 20 | 563 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.98 | 6 | 0
2001-10-20 | 1900-10-19 | 8:00 | 8 | 228 | 1379 | 112 | 2 | 8 | 212 | 2 | 15 | 76 | 2 | 8 | 11500 | 2 | 8 | 14200 | 2 | 15 | 9100 | 2 | 8 | 1510 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 9.4 | 48.92 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.22 | 6 | 0
2001-10-20 | 1900-10-19 | 9:00 | 9 | 466 | 1379 | 295 | 2 | 8 | 576 | 2 | 15 | 100 | 2 | 8 | 30100 | 2 | 8 | 51900 | 2 | 15 | 12600 | 2 | 8 | 1830 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 11.1 | 51.98 | A | 7 | 0.87 | A | 7 | 980 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.78 | 6 | 0
2001-10-20 | 1900-10-19 | 10:00 | 10 | 661 | 1379 | 447 | 2 | 8 | 656 | 2 | 15 | 131 | 2 | 8 | 46200 | 2 | 8 | 63800 | 2 | 15 | 15600 | 2 | 8 | 2670 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 16.7 | 62.06 | A | 7 | 12.8 | 55.04 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.14 | 6 | 0
2001-10-20 | 1900-10-19 | 11:00 | 11 | 801 | 1379 | 591 | 2 | 8 | 855 | 2 | 15 | 93 | 2 | 8 | 62600 | 2 | 8 | 85300 | 2 | 15 | 12900 | 2 | 8 | 2180 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 19.4 | 66.92 | A | 7 | 14.4 | 57.92 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.92 | 6 | 0
2001-10-20 | 1900-10-19 | 12:00 | 12 | 875 | 1379 | 653 | 2 | 8 | 855 | 2 | 15 | 109 | 2 | 8 | 68900 | 2 | 8 | 85600 | 2 | 15 | 14400 | 2 | 8 | 2660 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 21.1 | 69.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.66 | A | 7 | 979 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.52 | 6 | 0
2001-10-20 | 1900-10-19 | 13:00 | 13 | 879 | 1379 | 649 | 2 | 8 | 833 | 2 | 15 | 116 | 2 | 8 | 68000 | 2 | 8 | 83200 | 2 | 15 | 14700 | 2 | 8 | 2780 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 21.7 | 71.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 49.72 | 6 | 0
2001-10-20 | 1900-10-19 | 14:00 | 14 | 813 | 1379 | 573 | 2 | 8 | 774 | 2 | 15 | 115 | 2 | 8 | 59400 | 2 | 8 | 76700 | 2 | 15 | 14100 | 2 | 8 | 2520 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 21.7 | 71.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.92 | 6 | 0
2001-10-20 | 1900-10-19 | 15:00 | 15 | 680 | 1379 | 469 | 2 | 8 | 738 | 2 | 15 | 104 | 2 | 8 | 49500 | 2 | 8 | 72900 | 2 | 15 | 13400 | 2 | 8 | 2230 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 22.2 | 71.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.61 | A | 7 | 978 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.52 | 6 | 0
2001-10-20 | 1900-10-19 | 16:00 | 16 | 490 | 1379 | 319 | 2 | 8 | 636 | 2 | 15 | 92 | 2 | 8 | 32900 | 2 | 8 | 58500 | 2 | 15 | 12000 | 2 | 8 | 1740 | 2 | 19 | 3 | E | 9 | 1 | E | 9 | 21.7 | 71.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.92 | 6 | 0
2001-10-20 | 1900-10-19 | 17:00 | 17 | 256 | 1379 | 121 | 2 | 8 | 316 | 2 | 15 | 62 | 2 | 8 | 12600 | 2 | 8 | 22900 | 2 | 15 | 8300 | 2 | 8 | 1130 | 2 | 19 | 6 | E | 9 | 3 | E | 9 | 20 | 68 | A | 7 | 14.4 | 57.92 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.32 | 6 | 0
2001-10-20 | 1900-10-19 | 18:00 | 18 | 33 | 724 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 9 | E | 9 | 7 | A | 7 | 16.1 | 60.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.83 | A | 7 | 975 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.8 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.94 | 6 | 0
2001-10-20 | 1900-10-19 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 3 | E | 9 | 15.6 | 60.08 | A | 7 | 13.3 | 55.94 | A | 7 | 0.86 | A | 7 | 977 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 1.7 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.44 | 6 | 0
2001-10-20 | 1900-10-19 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 3 | E | 9 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 1.7 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.14 | 6 | 0
2001-10-20 | 1900-10-19 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | E | 9 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.86 | A | 7 | 978 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 1.6 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.32 | 6 | 0
2001-10-20 | 1900-10-19 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 3 | E | 9 | 16.7 | 62.06 | A | 7 | 13.9 | 57.02 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 4200 | A | 7 | 1.5 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.12 | 6 | 0
2001-10-20 | 1900-10-19 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 5 | E | 9 | 16.1 | 60.98 | A | 7 | 13.9 | 57.02 | A | 7 | 0.87 | A | 7 | 978 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 4267 | A | 7 | 1.5 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.62 | 6 | 0
2001-10-20 | 1900-10-19 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 3 | E | 9 | 16.1 | 60.98 | A | 7 | 13.3 | 55.94 | A | 7 | 0.83 | A | 7 | 977 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.092 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.94 | 6 | 0
2001-10-21 | 1900-10-20 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 5 | E | 9 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 250 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.14 | 7 | 0
2001-10-21 | 1900-10-20 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 3 | E | 9 | 13.9 | 57.02 | A | 7 | 12.8 | 55.04 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 170 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.84 | 7 | 0
2001-10-21 | 1900-10-20 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 15 | 59 | A | 7 | 13.3 | 55.94 | A | 7 | 0.9 | A | 7 | 979 | A | 7 | 150 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 1097 | A | 7 | 1.5 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.14 | 7 | 0
2001-10-21 | 1900-10-20 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 9 | E | 9 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 1372 | A | 7 | 1.5 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.72 | 7 | 0
2001-10-21 | 1900-10-20 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 6 | E | 9 | 15 | 59 | A | 7 | 13.9 | 57.02 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.72 | 7 | 0
2001-10-21 | 1900-10-20 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 6 | E | 9 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.97 | A | 7 | 978 | A | 7 | 150 | A | 7 | 1.5 | A | 7 | 12800 | A | 7 | 4572 | A | 7 | 1.6 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.42 | 7 | 0
2001-10-21 | 1900-10-20 | 7:00 | 7 | 18 | 540 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 15 | 59 | A | 7 | 14.4 | 57.92 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 12800 | A | 7 | 1829 | A | 7 | 1.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.12 | 7 | 0
2001-10-21 | 1900-10-20 | 8:00 | 8 | 224 | 1380 | 144 | 2 | 8 | 295 | 2 | 15 | 96 | 2 | 8 | 14600 | 2 | 8 | 19400 | 2 | 15 | 11400 | 2 | 8 | 2050 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 15.6 | 60.08 | A | 7 | 15 | 59 | A | 7 | 0.96 | A | 7 | 982 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 4800 | A | 7 | 640 | A | 7 | 1.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.2 | 7 | 0
2001-10-21 | 1900-10-20 | 9:00 | 9 | 460 | 1380 | 123 | 2 | 8 | 0 | 2 | 15 | 123 | 2 | 8 | 13800 | 2 | 8 | 0 | 2 | 15 | 13800 | 2 | 8 | 4540 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 15 | 59 | A | 7 | 14.4 | 57.92 | A | 7 | 0.96 | A | 7 | 982 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 579 | A | 7 | 1.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.12 | 7 | 0
2001-10-21 | 1900-10-20 | 10:00 | 10 | 656 | 1380 | 99 | 2 | 8 | 0 | 2 | 15 | 99 | 2 | 8 | 11800 | 2 | 8 | 0 | 2 | 15 | 11800 | 2 | 8 | 4510 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 20 | 68 | A | 7 | 17 | 62.6 | A | 7 | 0.83 | A | 7 | 982 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 1500 | A | 7 | 1.8 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 59.2 | 7 | 0
2001-10-21 | 1900-10-20 | 11:00 | 11 | 795 | 1380 | 283 | 2 | 8 | 42 | 2 | 15 | 259 | 2 | 8 | 31100 | 2 | 8 | 4200 | 2 | 15 | 28700 | 2 | 8 | 8160 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 762 | A | 7 | 1.8 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.68 | 7 | 0
2001-10-21 | 1900-10-20 | 12:00 | 12 | 870 | 1380 | 488 | 2 | 8 | 283 | 2 | 15 | 310 | 2 | 8 | 52100 | 2 | 8 | 30200 | 2 | 15 | 33000 | 2 | 8 | 8280 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 979 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 640 | A | 7 | 1.9 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.68 | 7 | 0
2001-10-21 | 1900-10-20 | 13:00 | 13 | 873 | 1380 | 411 | 2 | 8 | 156 | 2 | 15 | 312 | 2 | 8 | 44700 | 2 | 8 | 16400 | 2 | 15 | 34300 | 2 | 8 | 8730 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 20.6 | 69.08 | A | 7 | 16.1 | 60.98 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 701 | A | 7 | 1.8 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.08 | 7 | 0
2001-10-21 | 1900-10-20 | 14:00 | 14 | 806 | 1380 | 243 | 2 | 8 | 18 | 2 | 15 | 233 | 2 | 8 | 27900 | 2 | 8 | 1600 | 2 | 15 | 27000 | 2 | 8 | 9680 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 12800 | A | 7 | 884 | A | 7 | 1.8 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.66 | 7 | 0
2001-10-21 | 1900-10-20 | 15:00 | 15 | 673 | 1380 | 201 | 2 | 8 | 18 | 2 | 15 | 192 | 2 | 8 | 22800 | 2 | 8 | 1500 | 2 | 15 | 22100 | 2 | 8 | 7620 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.7 | 71.06 | A | 7 | 16.7 | 62.06 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 120 | A | 7 | 1.5 | A | 7 | 14400 | A | 7 | 1006 | A | 7 | 1.8 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.66 | 7 | 0
2001-10-21 | 1900-10-20 | 16:00 | 16 | 483 | 1380 | 287 | 2 | 8 | 323 | 2 | 15 | 173 | 2 | 8 | 29900 | 2 | 8 | 30600 | 2 | 15 | 19100 | 2 | 8 | 3740 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 22.2 | 71.96 | A | 7 | 17.2 | 62.96 | A | 7 | 0.73 | A | 7 | 979 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.46 | 7 | 0
2001-10-21 | 1900-10-20 | 17:00 | 17 | 250 | 1380 | 60 | 2 | 8 | 0 | 2 | 15 | 60 | 2 | 8 | 6700 | 2 | 8 | 0 | 2 | 15 | 6700 | 2 | 8 | 2070 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 20.6 | 69.08 | A | 7 | 17.2 | 62.96 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 12800 | A | 7 | 1463 | A | 7 | 1.8 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 59.16 | 7 | 0
2001-10-21 | 1900-10-20 | 18:00 | 18 | 30 | 678 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 16.1 | 60.98 | A | 7 | 0.84 | A | 7 | 978 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 1311 | A | 7 | 1.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.88 | 7 | 0
2001-10-21 | 1900-10-20 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 14400 | A | 7 | 1250 | A | 7 | 1.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56 | 7 | 0
2001-10-21 | 1900-10-20 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 17.2 | 62.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.84 | A | 7 | 980 | A | 7 | 40 | A | 7 | 6.2 | A | 7 | 14400 | A | 7 | 1372 | A | 7 | 1.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.02 | 7 | 0
2001-10-21 | 1900-10-20 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.16 | 7 | 0
2001-10-21 | 1900-10-20 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 15.6 | 60.08 | A | 7 | 12.2 | 53.96 | A | 7 | 0.8 | A | 7 | 980 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.56 | 7 | 0
2001-10-21 | 1900-10-20 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 15 | 59 | A | 7 | 12.2 | 53.96 | A | 7 | 0.83 | A | 7 | 980 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.6 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.06 | 7 | 0
2001-10-21 | 1900-10-20 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 15 | 59 | A | 7 | 12.2 | 53.96 | A | 7 | 0.83 | A | 7 | 978 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.6 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.06 | 7 | 0
2001-10-22 | 1900-10-21 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 15 | 59 | A | 7 | 12.2 | 53.96 | A | 7 | 0.83 | A | 7 | 979 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.8 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.06 | 1 | 0
2001-10-22 | 1900-10-21 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | E | 9 | 14.4 | 57.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.9 | A | 7 | 978 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.9 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.24 | 1 | 0
2001-10-22 | 1900-10-21 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | E | 9 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 2.1 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.64 | 1 | 0
2001-10-22 | 1900-10-21 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 2 | E | 9 | 14.4 | 57.92 | A | 7 | 13.3 | 55.94 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.64 | 1 | 0
2001-10-22 | 1900-10-21 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 8 | E | 9 | 14.4 | 57.92 | A | 7 | 13.9 | 57.02 | A | 7 | 0.97 | A | 7 | 977 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 12800 | A | 7 | 2438 | A | 7 | 2.4 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.42 | 1 | 0
2001-10-22 | 1900-10-21 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 15.6 | 60.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 1676 | A | 7 | 2.6 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.62 | 1 | 0
2001-10-22 | 1900-10-21 | 7:00 | 7 | 17 | 518 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 16.1 | 60.98 | A | 7 | 14.4 | 57.92 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.12 | 1 | 0
2001-10-22 | 1900-10-21 | 8:00 | 8 | 219 | 1381 | 52 | 2 | 8 | 0 | 2 | 15 | 52 | 2 | 8 | 5800 | 2 | 8 | 0 | 2 | 15 | 5800 | 2 | 8 | 1780 | 2 | 19 | 10 | E | 9 | 7 | E | 9 | 16.7 | 62.06 | A | 7 | 14.4 | 57.92 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.9 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.32 | 1 | 0
2001-10-22 | 1900-10-21 | 9:00 | 9 | 455 | 1381 | 79 | 2 | 8 | 0 | 2 | 15 | 79 | 2 | 8 | 9200 | 2 | 8 | 0 | 2 | 15 | 9200 | 2 | 8 | 3240 | 2 | 19 | 10 | E | 9 | 6 | E | 9 | 17.2 | 62.96 | A | 7 | 14.4 | 57.92 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 3.1 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.02 | 1 | 0
2001-10-22 | 1900-10-21 | 10:00 | 10 | 650 | 1381 | 145 | 2 | 8 | 0 | 2 | 15 | 145 | 2 | 8 | 16800 | 2 | 8 | 0 | 2 | 15 | 16800 | 2 | 8 | 6110 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 1524 | A | 7 | 3.2 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56 | 1 | 0
2001-10-22 | 1900-10-21 | 11:00 | 11 | 790 | 1381 | 183 | 2 | 8 | 0 | 2 | 15 | 183 | 2 | 8 | 21300 | 2 | 8 | 0 | 2 | 15 | 21300 | 2 | 8 | 8040 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 17.8 | 64.04 | A | 7 | 15 | 59 | A | 7 | 0.84 | A | 7 | 973 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 9600 | A | 7 | 4572 | A | 7 | 3.4 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56 | 1 | 0
2001-10-22 | 1900-10-21 | 12:00 | 12 | 864 | 1381 | 348 | 2 | 8 | 90 | 2 | 15 | 291 | 2 | 8 | 38200 | 2 | 8 | 9200 | 2 | 15 | 32500 | 2 | 8 | 9500 | 2 | 19 | 8 | E | 9 | 7 | E | 9 | 20 | 68 | A | 7 | 16.1 | 60.98 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 9600 | A | 7 | 4572 | A | 7 | 3.5 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.68 | 1 | 0
2001-10-22 | 1900-10-21 | 13:00 | 13 | 867 | 1381 | 208 | 2 | 8 | 6 | 2 | 15 | 204 | 2 | 8 | 24300 | 2 | 8 | 500 | 2 | 15 | 24000 | 2 | 8 | 9150 | 2 | 19 | 9 | E | 9 | 8 | E | 9 | 20.6 | 69.08 | A | 7 | 16.7 | 62.06 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 11200 | A | 7 | 610 | A | 7 | 3.4 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.66 | 1 | 0
2001-10-22 | 1900-10-21 | 14:00 | 14 | 800 | 1381 | 191 | 2 | 8 | 6 | 2 | 15 | 188 | 2 | 8 | 22300 | 2 | 8 | 500 | 2 | 15 | 22000 | 2 | 8 | 8260 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 11200 | A | 7 | 732 | A | 7 | 3.2 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.56 | 1 | 0
2001-10-22 | 1900-10-21 | 15:00 | 15 | 667 | 1381 | 189 | 2 | 8 | 6 | 2 | 15 | 187 | 2 | 8 | 21600 | 2 | 8 | 500 | 2 | 15 | 21400 | 2 | 8 | 7440 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 969 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 14400 | A | 7 | 945 | A | 7 | 3 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.16 | 1 | 0
2001-10-22 | 1900-10-21 | 16:00 | 16 | 477 | 1381 | 114 | 2 | 8 | 0 | 2 | 15 | 114 | 2 | 8 | 13000 | 2 | 8 | 0 | 2 | 15 | 13000 | 2 | 8 | 4390 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 21.7 | 71.06 | A | 7 | 17.2 | 62.96 | A | 7 | 0.76 | A | 7 | 969 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 1433 | A | 7 | 2.9 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.16 | 1 | 0
2001-10-22 | 1900-10-21 | 17:00 | 17 | 244 | 1381 | 76 | 2 | 8 | 69 | 2 | 15 | 64 | 2 | 8 | 8300 | 2 | 8 | 5100 | 2 | 15 | 7400 | 2 | 8 | 1370 | 2 | 19 | 8 | E | 9 | 6 | E | 9 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.78 | A | 7 | 969 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 14400 | A | 7 | 3962 | A | 7 | 2.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.56 | 1 | 0
2001-10-22 | 1900-10-21 | 18:00 | 18 | 27 | 656 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 21.1 | 69.98 | A | 7 | 17.2 | 62.96 | A | 7 | 0.78 | A | 7 | 966 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 4572 | A | 7 | 2.5 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.56 | 1 | 0
2001-10-22 | 1900-10-21 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 17.8 | 64.04 | A | 7 | 0.84 | A | 7 | 968 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 1463 | A | 7 | 2.4 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 60.84 | 1 | 0
2001-10-22 | 1900-10-21 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 18.3 | 64.94 | A | 7 | 0.93 | A | 7 | 968 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 12800 | A | 7 | 1250 | A | 7 | 2.2 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 63.54 | 1 | 0
2001-10-22 | 1900-10-21 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 968 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 14400 | A | 7 | 1250 | A | 7 | 2 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 62.04 | 1 | 0
2001-10-22 | 1900-10-21 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 17.8 | 64.04 | A | 7 | 0.9 | A | 7 | 968 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 14400 | A | 7 | 1250 | A | 7 | 1.9 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 62.04 | 1 | 0
2001-10-22 | 1900-10-21 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 17.8 | 64.04 | A | 7 | 0.93 | A | 7 | 968 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 12800 | A | 7 | 1463 | A | 7 | 1.7 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 62.64 | 1 | 0
2001-10-22 | 1900-10-21 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 7 | A | 7 | 17.8 | 64.04 | A | 7 | 16.7 | 62.06 | A | 7 | 0.93 | A | 7 | 966 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 12800 | A | 7 | 3658 | A | 7 | 1.5 | E | 8 | 0.091 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 60.66 | 1 | 0
2001-10-23 | 1900-10-22 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | A | 7 | 16.1 | 60.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.97 | A | 7 | 967 | A | 7 | 250 | A | 7 | 1.5 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 59.48 | 2 | 0
2001-10-23 | 1900-10-22 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | A | 7 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 967 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 9600 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.9 | 2 | 0
2001-10-23 | 1900-10-22 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | A | 7 | 12.2 | 53.96 | A | 7 | 12.2 | 53.96 | A | 7 | 1 | A | 7 | 966 | A | 7 | 200 | A | 7 | 1.5 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 53.86 | 2 | 0
2001-10-23 | 1900-10-22 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | A | 7 | 11.7 | 53.06 | A | 7 | 11.7 | 53.06 | A | 7 | 1 | A | 7 | 966 | A | 7 | 0 | A | 7 | 0 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.96 | 2 | 0
2001-10-23 | 1900-10-22 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 10.6 | 51.08 | A | 7 | 1 | A | 7 | 966 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 800 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 50.98 | 2 | 0
2001-10-23 | 1900-10-22 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 8 | A | 7 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 965 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 400 | A | 7 | 152 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.84 | 2 | 0
2001-10-23 | 1900-10-22 | 7:00 | 7 | 15 | 495 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 13.3 | 55.94 | A | 7 | 1 | A | 7 | 966 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 300 | A | 7 | 30 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.84 | 2 | 0
2001-10-23 | 1900-10-22 | 8:00 | 8 | 214 | 1381 | 74 | 2 | 8 | 37 | 2 | 15 | 69 | 2 | 8 | 8200 | 2 | 8 | 2800 | 2 | 15 | 7700 | 2 | 8 | 1590 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 14.4 | 57.92 | A | 7 | 1 | A | 7 | 967 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 300 | A | 7 | 30 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.82 | 2 | 0
2001-10-23 | 1900-10-22 | 9:00 | 9 | 450 | 1381 | 188 | 2 | 8 | 89 | 2 | 15 | 159 | 2 | 8 | 20600 | 2 | 8 | 8300 | 2 | 15 | 17800 | 2 | 8 | 4030 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 15 | 59 | A | 7 | 15 | 59 | A | 7 | 1 | A | 7 | 966 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 400 | A | 7 | 30 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.9 | 2 | 0
2001-10-23 | 1900-10-22 | 10:00 | 10 | 645 | 1381 | 329 | 2 | 8 | 215 | 2 | 15 | 229 | 2 | 8 | 35600 | 2 | 8 | 21700 | 2 | 15 | 25400 | 2 | 8 | 5580 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 17.2 | 62.96 | A | 7 | 17.2 | 62.96 | A | 7 | 1 | A | 7 | 966 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 62.86 | 2 | 0
2001-10-23 | 1900-10-22 | 11:00 | 11 | 784 | 1381 | 516 | 2 | 8 | 564 | 2 | 15 | 195 | 2 | 8 | 54700 | 2 | 8 | 57500 | 2 | 15 | 22000 | 2 | 8 | 4430 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 16.7 | 62.06 | A | 7 | 0.76 | A | 7 | 966 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 12800 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.26 | 2 | 0
2001-10-23 | 1900-10-22 | 12:00 | 12 | 858 | 1381 | 592 | 2 | 8 | 699 | 2 | 15 | 157 | 2 | 8 | 62200 | 2 | 8 | 70300 | 2 | 15 | 18400 | 2 | 8 | 3810 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 23.3 | 73.94 | A | 7 | 17.2 | 62.96 | A | 7 | 0.69 | A | 7 | 963 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.66 | 2 | 0
2001-10-23 | 1900-10-22 | 13:00 | 13 | 861 | 1381 | 607 | 2 | 8 | 731 | 2 | 15 | 150 | 2 | 8 | 64000 | 2 | 8 | 73700 | 2 | 15 | 17900 | 2 | 8 | 3680 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.6 | A | 7 | 965 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.98 | 2 | 0
2001-10-23 | 1900-10-22 | 14:00 | 14 | 794 | 1381 | 561 | 2 | 8 | 774 | 2 | 15 | 115 | 2 | 8 | 58000 | 2 | 8 | 76400 | 2 | 15 | 14000 | 2 | 8 | 2450 | 2 | 19 | 3 | E | 9 | 3 | A | 7 | 24.4 | 75.92 | A | 7 | 15.6 | 60.08 | A | 7 | 0.58 | A | 7 | 964 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.78 | 2 | 0
2001-10-23 | 1900-10-22 | 15:00 | 15 | 661 | 1381 | 451 | 2 | 8 | 713 | 2 | 15 | 108 | 2 | 8 | 47300 | 2 | 8 | 70000 | 2 | 15 | 13700 | 2 | 8 | 2270 | 2 | 19 | 2 | E | 9 | 2 | A | 7 | 24.4 | 75.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.6 | A | 7 | 964 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.98 | 2 | 0
2001-10-23 | 1900-10-22 | 16:00 | 16 | 471 | 1381 | 285 | 2 | 8 | 571 | 2 | 15 | 90 | 2 | 8 | 29400 | 2 | 8 | 51900 | 2 | 15 | 11600 | 2 | 8 | 1690 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 24.4 | 75.92 | A | 7 | 16.1 | 60.98 | A | 7 | 0.6 | A | 7 | 964 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 52.98 | 2 | 0
2001-10-23 | 1900-10-22 | 17:00 | 17 | 238 | 1381 | 118 | 2 | 8 | 371 | 2 | 15 | 54 | 2 | 8 | 12300 | 2 | 8 | 25900 | 2 | 15 | 7900 | 2 | 8 | 970 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 22.2 | 71.96 | A | 7 | 16.1 | 60.98 | A | 7 | 0.68 | A | 7 | 963 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.68 | 2 | 0
2001-10-23 | 1900-10-22 | 18:00 | 18 | 25 | 633 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 21.1 | 69.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.71 | A | 7 | 961 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 54.48 | 2 | 0
2001-10-23 | 1900-10-22 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 15 | 59 | A | 7 | 0.81 | A | 7 | 963 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 55.4 | 2 | 0
2001-10-23 | 1900-10-22 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 18.3 | 64.94 | A | 7 | 15.6 | 60.08 | A | 7 | 0.84 | A | 7 | 963 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.98 | 2 | 0
2001-10-23 | 1900-10-22 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15.6 | 60.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.93 | A | 7 | 963 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.62 | 2 | 0
2001-10-23 | 1900-10-22 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 15.6 | 60.08 | A | 7 | 0.97 | A | 7 | 962 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 59.48 | 2 | 0
2001-10-23 | 1900-10-22 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15.6 | 60.08 | A | 7 | 15 | 59 | A | 7 | 0.96 | A | 7 | 962 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 58.2 | 2 | 0
2001-10-23 | 1900-10-22 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 0 | E | 9 | 15.6 | 60.08 | A | 7 | 14.4 | 57.92 | A | 7 | 0.93 | A | 7 | 960 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 14400 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.09 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.62 | 2 | 0
2001-10-24 | 1900-10-23 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 17.2 | 62.96 | A | 7 | 15 | 59 | A | 7 | 0.87 | A | 7 | 961 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 56.6 | 3 | 0
2001-10-24 | 1900-10-23 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 3 | E | 9 | 17.8 | 64.04 | A | 7 | 15.6 | 60.08 | A | 7 | 0.87 | A | 7 | 963 | A | 7 | 270 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 57.58 | 3 | 0
2001-10-24 | 1900-10-23 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 12.8 | 55.04 | A | 7 | 0.81 | A | 7 | 963 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 51.74 | 3 | 0
2001-10-24 | 1900-10-23 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13.3 | 55.94 | A | 7 | 10 | 50 | A | 7 | 0.8 | A | 7 | 963 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 46.8 | 3 | 0
2001-10-24 | 1900-10-23 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 4 | E | 9 | 11.7 | 53.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.66 | A | 7 | 964 | A | 7 | 10 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.38 | 3 | 0
2001-10-24 | 1900-10-23 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 3 | E | 9 | 11.7 | 53.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.66 | A | 7 | 964 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.38 | 3 | 0
2001-10-24 | 1900-10-23 | 7:00 | 7 | 14 | 472 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 10.6 | 51.08 | A | 7 | 6.1 | 42.98 | A | 7 | 0.74 | A | 7 | 965 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.3 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.38 | 3 | 0
2001-10-24 | 1900-10-23 | 8:00 | 8 | 209 | 1382 | 22 | 2 | 8 | 0 | 2 | 15 | 22 | 2 | 8 | 2600 | 2 | 8 | 0 | 2 | 15 | 2600 | 2 | 8 | 880 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10.6 | 51.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.79 | A | 7 | 967 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.2 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.96 | 3 | 0
2001-10-24 | 1900-10-23 | 9:00 | 9 | 445 | 1382 | 44 | 2 | 8 | 0 | 2 | 15 | 44 | 2 | 8 | 5300 | 2 | 8 | 0 | 2 | 15 | 5300 | 2 | 8 | 1950 | 2 | 19 | 10 | E | 9 | 10 | E | 9 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.89 | A | 7 | 968 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 1036 | A | 7 | 1.1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 1 | 1 | A | 7 | 45.24 | 3 | 0
2001-10-24 | 1900-10-23 | 10:00 | 10 | 639 | 1382 | 73 | 2 | 8 | 0 | 2 | 15 | 73 | 2 | 8 | 8900 | 2 | 8 | 0 | 2 | 15 | 8900 | 2 | 8 | 3430 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 10.6 | 51.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.92 | A | 7 | 969 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 2591 | A | 7 | 1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 47.62 | 3 | 0
2001-10-24 | 1900-10-23 | 11:00 | 11 | 778 | 1382 | 88 | 2 | 8 | 0 | 2 | 15 | 88 | 2 | 8 | 10800 | 2 | 8 | 0 | 2 | 15 | 10800 | 2 | 8 | 4330 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 11.7 | 53.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.83 | A | 7 | 970 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 45.42 | 3 | 0
2001-10-24 | 1900-10-23 | 12:00 | 12 | 852 | 1382 | 318 | 2 | 8 | 132 | 2 | 15 | 236 | 2 | 8 | 35000 | 2 | 8 | 13900 | 2 | 15 | 26400 | 2 | 8 | 6480 | 2 | 19 | 3 | E | 9 | 2 | E | 9 | 13.3 | 55.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.69 | A | 7 | 968 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 0.8 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.44 | 3 | 0
2001-10-24 | 1900-10-23 | 13:00 | 13 | 855 | 1382 | 613 | 2 | 8 | 647 | 2 | 15 | 211 | 2 | 8 | 65200 | 2 | 8 | 66500 | 2 | 15 | 23900 | 2 | 8 | 5130 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 16.1 | 60.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.5 | A | 7 | 970 | A | 7 | 270 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.08 | 3 | 0
2001-10-24 | 1900-10-23 | 14:00 | 14 | 788 | 1382 | 555 | 2 | 8 | 780 | 2 | 15 | 109 | 2 | 8 | 57700 | 2 | 8 | 77100 | 2 | 15 | 13600 | 2 | 8 | 2360 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 17.2 | 62.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.38 | A | 7 | 970 | A | 7 | 290 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.04 | 3 | 0
2001-10-24 | 1900-10-23 | 15:00 | 15 | 655 | 1382 | 445 | 2 | 8 | 707 | 2 | 15 | 109 | 2 | 8 | 46700 | 2 | 8 | 69200 | 2 | 15 | 13800 | 2 | 8 | 2270 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 17.2 | 62.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.34 | A | 7 | 971 | A | 7 | 270 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.18 | 3 | 0
2001-10-24 | 1900-10-23 | 16:00 | 16 | 465 | 1382 | 280 | 2 | 8 | 553 | 2 | 15 | 93 | 2 | 8 | 28700 | 2 | 8 | 50000 | 2 | 15 | 11800 | 2 | 8 | 1720 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 15.6 | 60.08 | A | 7 | 0 | 32 | A | 7 | 0.34 | A | 7 | 972 | A | 7 | 290 | A | 7 | 11.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 24.7 | 3 | 0
2001-10-24 | 1900-10-23 | 17:00 | 17 | 232 | 1382 | 117 | 2 | 8 | 438 | 2 | 15 | 43 | 2 | 8 | 12000 | 2 | 8 | 31200 | 2 | 15 | 6700 | 2 | 8 | 770 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 13.9 | 57.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.37 | A | 7 | 973 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 24.12 | 3 | 0
2001-10-24 | 1900-10-23 | 18:00 | 18 | 22 | 587 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.41 | A | 7 | 973 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.82 | 3 | 0
2001-10-24 | 1900-10-23 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.46 | A | 7 | 976 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.12 | 3 | 0
2001-10-24 | 1900-10-23 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.9 | 48.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.51 | A | 7 | 976 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.72 | 3 | 0
2001-10-24 | 1900-10-23 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.8 | 46.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.55 | A | 7 | 977 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.12 | 3 | 0
2001-10-24 | 1900-10-23 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.8 | 46.04 | A | 7 | 0 | 32 | A | 7 | 0.58 | A | 7 | 977 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 27.4 | 3 | 0
2001-10-24 | 1900-10-23 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.53 | A | 7 | 978 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.92 | 3 | 0
2001-10-24 | 1900-10-23 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.8 | 46.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.12 | 3 | 0
2001-10-25 | 1900-10-24 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.62 | 4 | 0
2001-10-25 | 1900-10-24 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.62 | A | 7 | 980 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.92 | 4 | 0
2001-10-25 | 1900-10-24 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.62 | 4 | 0
2001-10-25 | 1900-10-24 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.92 | 4 | 0
2001-10-25 | 1900-10-24 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.59 | A | 7 | 983 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.82 | 4 | 0
2001-10-25 | 1900-10-24 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.02 | 4 | 0
2001-10-25 | 1900-10-24 | 7:00 | 7 | 12 | 449 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 5 | 41 | A | 7 | -0.6 | 30.92 | A | 7 | 0.67 | A | 7 | 985 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 27.42 | 4 | 0
2001-10-25 | 1900-10-24 | 8:00 | 8 | 204 | 1383 | 121 | 2 | 8 | 418 | 2 | 15 | 59 | 2 | 8 | 12300 | 2 | 8 | 26800 | 2 | 15 | 8300 | 2 | 8 | 1090 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 6.1 | 42.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.62 | A | 7 | 986 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 26.92 | 4 | 0
2001-10-25 | 1900-10-24 | 9:00 | 9 | 439 | 1383 | 277 | 2 | 8 | 553 | 2 | 15 | 100 | 2 | 8 | 28100 | 2 | 8 | 48800 | 2 | 15 | 12500 | 2 | 8 | 1780 | 2 | 19 | 4 | E | 9 | 4 | E | 9 | 7.2 | 44.96 | A | 7 | 0 | 32 | A | 7 | 0.6 | A | 7 | 986 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 27.6 | 4 | 0
2001-10-25 | 1900-10-24 | 10:00 | 10 | 634 | 1383 | 403 | 2 | 8 | 584 | 2 | 15 | 134 | 2 | 8 | 41400 | 2 | 8 | 56200 | 2 | 15 | 15600 | 2 | 8 | 2640 | 2 | 19 | 5 | E | 9 | 5 | E | 9 | 8.9 | 48.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.51 | A | 7 | 987 | A | 7 | 290 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.72 | 4 | 0
2001-10-25 | 1900-10-24 | 11:00 | 11 | 772 | 1383 | 548 | 2 | 8 | 764 | 2 | 15 | 120 | 2 | 8 | 58000 | 2 | 8 | 76600 | 2 | 15 | 15100 | 2 | 8 | 2740 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 9.4 | 48.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.47 | A | 7 | 988 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 24.52 | 4 | 0
2001-10-25 | 1900-10-24 | 12:00 | 12 | 846 | 1383 | 605 | 2 | 8 | 771 | 2 | 15 | 132 | 2 | 8 | 64200 | 2 | 8 | 78000 | 2 | 15 | 16400 | 2 | 8 | 3230 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 11.1 | 51.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.39 | A | 7 | 986 | A | 7 | 290 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 22.04 | 4 | 0
2001-10-25 | 1900-10-24 | 13:00 | 13 | 849 | 1383 | 613 | 2 | 8 | 803 | 2 | 15 | 118 | 2 | 8 | 63700 | 2 | 8 | 79800 | 2 | 15 | 14600 | 2 | 8 | 2680 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 11.7 | 53.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.35 | A | 7 | 987 | A | 7 | 290 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 20.76 | 4 | 0
2001-10-25 | 1900-10-24 | 14:00 | 14 | 782 | 1383 | 538 | 2 | 8 | 726 | 2 | 15 | 126 | 2 | 8 | 56800 | 2 | 8 | 72800 | 2 | 15 | 15500 | 2 | 8 | 2890 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.36 | A | 7 | 987 | A | 7 | 280 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 21.74 | 4 | 0
2001-10-25 | 1900-10-24 | 15:00 | 15 | 649 | 1383 | 439 | 2 | 8 | 707 | 2 | 15 | 106 | 2 | 8 | 46000 | 2 | 8 | 69200 | 2 | 15 | 13500 | 2 | 8 | 2210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.36 | A | 7 | 988 | A | 7 | 290 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 22.44 | 4 | 0
2001-10-25 | 1900-10-24 | 16:00 | 16 | 459 | 1383 | 295 | 2 | 8 | 685 | 2 | 15 | 67 | 2 | 8 | 31000 | 2 | 8 | 62700 | 2 | 15 | 10100 | 2 | 8 | 1310 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.2 | 53.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.34 | A | 7 | 988 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 20.66 | 4 | 0
2001-10-25 | 1900-10-24 | 17:00 | 17 | 226 | 1383 | 112 | 2 | 8 | 410 | 2 | 15 | 44 | 2 | 8 | 11300 | 2 | 8 | 28800 | 2 | 15 | 6600 | 2 | 8 | 780 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.32 | A | 7 | 988 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 18.18 | 4 | 0
2001-10-25 | 1900-10-24 | 18:00 | 18 | 20 | 565 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.37 | A | 7 | 986 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19.38 | 4 | 0
2001-10-25 | 1900-10-24 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.8 | 46.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.4 | A | 7 | 988 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 18.88 | 4 | 0
2001-10-25 | 1900-10-24 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.43 | A | 7 | 989 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19.18 | 4 | 0
2001-10-25 | 1900-10-24 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.43 | A | 7 | 989 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19.18 | 4 | 0
2001-10-25 | 1900-10-24 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 5 | 41 | A | 7 | -3.9 | 24.98 | A | 7 | 0.51 | A | 7 | 989 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 20.58 | 4 | 0
2001-10-25 | 1900-10-24 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 5 | 41 | A | 7 | -4.4 | 24.08 | A | 7 | 0.48 | A | 7 | 990 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19.58 | 4 | 0
2001-10-25 | 1900-10-24 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 4.4 | 39.92 | A | 7 | -5 | 23 | A | 7 | 0.48 | A | 7 | 990 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.089 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 18.7 | 4 | 0
2001-10-26 | 1900-10-25 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 4.4 | 39.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.51 | A | 7 | 991 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19.88 | 5 | 0
2001-10-26 | 1900-10-25 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 4 | E | 9 | 4.4 | 39.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.53 | A | 7 | 991 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 20.78 | 5 | 0
2001-10-26 | 1900-10-25 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 2 | E | 9 | 3.3 | 37.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.6 | A | 7 | 992 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 22.36 | 5 | 0
2001-10-26 | 1900-10-25 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 10 | E | 9 | 10 | E | 9 | 2.8 | 37.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.59 | A | 7 | 993 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 21.38 | 5 | 0
2001-10-26 | 1900-10-25 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 9 | E | 9 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.6 | A | 7 | 994 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.16 | 5 | 0
2001-10-26 | 1900-10-25 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 5 | E | 9 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.68 | A | 7 | 994 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.96 | 5 | 0
2001-10-26 | 1900-10-25 | 7:00 | 7 | 11 | 427 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 7 | E | 9 | 7 | E | 9 | 2.8 | 37.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 995 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.66 | 5 | 0
2001-10-26 | 1900-10-25 | 8:00 | 8 | 199 | 1384 | 101 | 2 | 8 | 207 | 2 | 15 | 71 | 2 | 8 | 10400 | 2 | 8 | 12700 | 2 | 15 | 8500 | 2 | 8 | 1430 | 2 | 19 | 9 | E | 9 | 9 | E | 9 | 4.4 | 39.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.63 | A | 7 | 996 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 3048 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.24 | 5 | 0
2001-10-26 | 1900-10-25 | 9:00 | 9 | 434 | 1384 | 248 | 2 | 8 | 395 | 2 | 15 | 124 | 2 | 8 | 25500 | 2 | 8 | 35300 | 2 | 15 | 14400 | 2 | 8 | 2380 | 2 | 19 | 10 | E | 9 | 9 | E | 9 | 6.1 | 42.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.59 | A | 7 | 997 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 3353 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.82 | 5 | 0
2001-10-26 | 1900-10-25 | 10:00 | 10 | 628 | 1384 | 244 | 2 | 8 | 80 | 2 | 15 | 208 | 2 | 8 | 26800 | 2 | 8 | 7900 | 2 | 15 | 23200 | 2 | 8 | 5910 | 2 | 19 | 6 | E | 9 | 6 | E | 9 | 6.7 | 44.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.52 | A | 7 | 998 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.34 | 5 | 0
2001-10-26 | 1900-10-25 | 11:00 | 11 | 767 | 1384 | 529 | 2 | 8 | 570 | 2 | 15 | 212 | 2 | 8 | 55400 | 2 | 8 | 57800 | 2 | 15 | 23200 | 2 | 8 | 4790 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 8.9 | 48.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.42 | A | 7 | 998 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 21.46 | 5 | 0
2001-10-26 | 1900-10-25 | 12:00 | 12 | 840 | 1384 | 580 | 2 | 8 | 705 | 2 | 15 | 151 | 2 | 8 | 61000 | 2 | 8 | 70800 | 2 | 15 | 17800 | 2 | 8 | 3600 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 9.4 | 48.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.41 | A | 7 | 996 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 21.36 | 5 | 0
2001-10-26 | 1900-10-25 | 13:00 | 13 | 843 | 1384 | 607 | 2 | 8 | 785 | 2 | 15 | 127 | 2 | 8 | 64600 | 2 | 8 | 79500 | 2 | 15 | 16000 | 2 | 8 | 3110 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.38 | A | 7 | 997 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 21.06 | 5 | 0
2001-10-26 | 1900-10-25 | 14:00 | 14 | 776 | 1384 | 549 | 2 | 8 | 798 | 2 | 15 | 100 | 2 | 8 | 57400 | 2 | 8 | 79000 | 2 | 15 | 13000 | 2 | 8 | 2210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.39 | A | 7 | 996 | A | 7 | 330 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 22.04 | 5 | 0
2001-10-26 | 1900-10-25 | 15:00 | 15 | 642 | 1384 | 433 | 2 | 8 | 701 | 2 | 15 | 107 | 2 | 8 | 45400 | 2 | 8 | 68400 | 2 | 15 | 13500 | 2 | 8 | 2210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.33 | A | 7 | 996 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 18.98 | 5 | 0
2001-10-26 | 1900-10-25 | 16:00 | 16 | 453 | 1384 | 284 | 2 | 8 | 633 | 2 | 15 | 76 | 2 | 8 | 29500 | 2 | 8 | 57400 | 2 | 15 | 10700 | 2 | 8 | 1450 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.35 | A | 7 | 996 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19.18 | 5 | 0
2001-10-26 | 1900-10-25 | 17:00 | 17 | 220 | 1384 | 115 | 2 | 8 | 486 | 2 | 15 | 37 | 2 | 8 | 11800 | 2 | 8 | 34000 | 2 | 15 | 6400 | 2 | 8 | 680 | 2 | 19 | 0 | B | 8 | 0 | B | 8 | 8.3 | 46.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.4 | A | 7 | 996 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19.58 | 5 | 0
2001-10-26 | 1900-10-25 | 18:00 | 18 | 18 | 542 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.46 | A | 7 | 994 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19.38 | 5 | 0
2001-10-26 | 1900-10-25 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 4.4 | 39.92 | A | 7 | -5 | 23 | A | 7 | 0.48 | A | 7 | 996 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 18.7 | 5 | 0
2001-10-26 | 1900-10-25 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | -5 | 23 | A | 7 | 0.52 | A | 7 | 996 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19 | 5 | 0
2001-10-26 | 1900-10-25 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | -5 | 23 | A | 7 | 0.52 | A | 7 | 996 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19 | 5 | 0
2001-10-26 | 1900-10-25 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 2.8 | 37.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.51 | A | 7 | 997 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 18.02 | 5 | 0
2001-10-26 | 1900-10-25 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 1.1 | 33.98 | A | 7 | -5 | 23 | A | 7 | 0.61 | A | 7 | 997 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 19.8 | 5 | 0
2001-10-26 | 1900-10-25 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 0.6 | 33.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.57 | A | 7 | 997 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.088 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 17.62 | 5 | 0
2001-10-27 | 1900-10-26 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 1.1 | 33.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.55 | A | 7 | 997 | A | 7 | 350 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 17.52 | 6 | 0
2001-10-27 | 1900-10-26 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 0 | 32 | A | 7 | -6.1 | 21.02 | A | 7 | 0.6 | A | 7 | 997 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 17.92 | 6 | 0
2001-10-27 | 1900-10-26 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.65 | A | 7 | 997 | A | 7 | 350 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 17.34 | 6 | 0
2001-10-27 | 1900-10-26 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.62 | A | 7 | 997 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 17.04 | 6 | 0
2001-10-27 | 1900-10-26 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 0 | 32 | A | 7 | -6.7 | 19.94 | A | 7 | 0.57 | A | 7 | 997 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 16.74 | 6 | 0
2001-10-27 | 1900-10-26 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 0 | 32 | A | 7 | -7.2 | 19.04 | A | 7 | 0.54 | A | 7 | 997 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 15.64 | 6 | 0
2001-10-27 | 1900-10-26 | 7:00 | 7 | 9 | 404 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | -1.1 | 30.02 | A | 7 | -5 | 23 | A | 7 | 0.72 | A | 7 | 998 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 20.7 | 6 | 0
2001-10-27 | 1900-10-26 | 8:00 | 8 | 194 | 1385 | 80 | 2 | 8 | 131 | 2 | 15 | 62 | 2 | 8 | 8300 | 2 | 8 | 7900 | 2 | 15 | 7200 | 2 | 8 | 1210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 998 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 24.66 | 6 | 0
2001-10-27 | 1900-10-26 | 9:00 | 9 | 429 | 1385 | 278 | 2 | 8 | 555 | 2 | 15 | 106 | 2 | 8 | 29000 | 2 | 8 | 49600 | 2 | 15 | 13600 | 2 | 8 | 2000 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.63 | A | 7 | 998 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.46 | 6 | 0
2001-10-27 | 1900-10-26 | 10:00 | 10 | 623 | 1385 | 436 | 2 | 8 | 725 | 2 | 15 | 109 | 2 | 8 | 45500 | 2 | 8 | 70200 | 2 | 15 | 13800 | 2 | 8 | 2210 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.49 | A | 7 | 999 | A | 7 | 140 | B | 8 | 1.5 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 20.48 | 6 | 0
2001-10-27 | 1900-10-26 | 11:00 | 11 | 761 | 1385 | 511 | 2 | 8 | 685 | 2 | 15 | 133 | 2 | 8 | 53600 | 2 | 8 | 68200 | 2 | 15 | 16000 | 2 | 8 | 2960 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -3.3 | 26.06 | A | 7 | 0.47 | A | 7 | 998 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 21.16 | 6 | 0
2001-10-27 | 1900-10-26 | 12:00 | 12 | 834 | 1385 | 586 | 2 | 8 | 723 | 2 | 15 | 150 | 2 | 8 | 61600 | 2 | 8 | 72600 | 2 | 15 | 17800 | 2 | 8 | 3550 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 8.3 | 46.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.46 | A | 7 | 996 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 22.74 | 6 | 0
2001-10-27 | 1900-10-26 | 13:00 | 13 | 837 | 1385 | 607 | 2 | 8 | 803 | 2 | 15 | 120 | 2 | 8 | 62900 | 2 | 8 | 79600 | 2 | 15 | 14600 | 2 | 8 | 2660 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | -2.2 | 28.04 | A | 7 | 0.41 | A | 7 | 996 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 22.24 | 6 | 0
2001-10-27 | 1900-10-26 | 14:00 | 14 | 770 | 1385 | 549 | 2 | 8 | 815 | 2 | 15 | 94 | 2 | 8 | 57700 | 2 | 8 | 80900 | 2 | 15 | 12600 | 2 | 8 | 2120 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10.6 | 51.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.38 | A | 7 | 995 | A | 7 | 160 | B | 8 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 21.06 | 6 | 0
2001-10-27 | 1900-10-26 | 15:00 | 15 | 636 | 1385 | 444 | 2 | 8 | 777 | 2 | 15 | 85 | 2 | 8 | 46000 | 2 | 8 | 75200 | 2 | 15 | 11300 | 2 | 8 | 1730 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.37 | A | 7 | 995 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 21.84 | 6 | 0
2001-10-27 | 1900-10-26 | 16:00 | 16 | 447 | 1385 | 288 | 2 | 8 | 701 | 2 | 15 | 61 | 2 | 8 | 29600 | 2 | 8 | 63500 | 2 | 15 | 9000 | 2 | 8 | 1190 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.39 | A | 7 | 994 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 22.04 | 6 | 0
2001-10-27 | 1900-10-26 | 17:00 | 17 | 214 | 1385 | 109 | 2 | 8 | 458 | 2 | 15 | 38 | 2 | 8 | 11200 | 2 | 8 | 31600 | 2 | 15 | 6300 | 2 | 8 | 690 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 10 | 50 | A | 7 | -2.2 | 28.04 | A | 7 | 0.41 | A | 7 | 993 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 22.24 | 6 | 0
2001-10-27 | 1900-10-26 | 18:00 | 18 | 16 | 496 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 0 | E | 9 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.48 | A | 7 | 990 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 22.94 | 6 | 0
2001-10-27 | 1900-10-26 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.5 | A | 7 | 992 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.14 | 6 | 0
2001-10-27 | 1900-10-26 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | B | 8 | 0 | B | 8 | 7.1 | 44.78 | B | 8 | -2.1 | 28.22 | B | 8 | 0.51 | A | 7 | 992 | B | 8 | 150 | B | 8 | 4.6 | B | 8 | -9900 | ? | 0 | 77777 | B | 8 | 1.8 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | -9900 | -9900 | ? | 0 | 23.42 | 6 | 0
2001-10-27 | 1900-10-26 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.5 | A | 7 | 991 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.14 | 6 | 0
2001-10-27 | 1900-10-26 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.5 | A | 7 | 991 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.14 | 6 | 0
2001-10-27 | 1900-10-26 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 5.6 | 42.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.56 | A | 7 | 991 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.74 | 6 | 0
2001-10-27 | 1900-10-26 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.1 | 42.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.54 | A | 7 | 991 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.087 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.54 | 6 | 0
2001-10-28 | 1900-10-27 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.5 | A | 7 | 990 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.14 | 7 | 0
2001-10-28 | 1900-10-27 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.52 | A | 7 | 990 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.34 | 7 | 0
2001-10-28 | 1900-10-27 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.8 | 46.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.5 | A | 7 | 989 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 23.94 | 7 | 0
2001-10-28 | 1900-10-27 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 6.7 | 44.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.57 | A | 7 | 989 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.62 | 7 | 0
2001-10-28 | 1900-10-27 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.2 | 44.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.55 | A | 7 | 989 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.42 | 7 | 0
2001-10-28 | 1900-10-27 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 7.8 | 46.04 | A | 7 | -1.1 | 30.02 | A | 7 | 0.53 | A | 7 | 988 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.12 | 7 | 0
2001-10-28 | 1900-10-27 | 7:00 | 7 | 8 | 358 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 8 | E | 9 | 8 | E | 9 | 9.4 | 48.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.49 | A | 7 | 989 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 2438 | A | 7 | 1.7 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 25.52 | 7 | 0
2001-10-28 | 1900-10-27 | 8:00 | 8 | 189 | 1385 | 70 | 2 | 8 | 62 | 2 | 15 | 62 | 2 | 8 | 7600 | 2 | 8 | 4000 | 2 | 15 | 7000 | 2 | 8 | 1310 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 11.1 | 51.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.48 | A | 7 | 989 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 27.18 | 7 | 0
2001-10-28 | 1900-10-27 | 9:00 | 9 | 424 | 1385 | 264 | 2 | 8 | 530 | 2 | 15 | 102 | 2 | 8 | 27700 | 2 | 8 | 47200 | 2 | 15 | 13200 | 2 | 8 | 1910 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 12.8 | 55.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.45 | A | 7 | 989 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 27.48 | 7 | 0
2001-10-28 | 1900-10-27 | 10:00 | 10 | 617 | 1385 | 397 | 2 | 8 | 578 | 2 | 15 | 139 | 2 | 8 | 42200 | 2 | 8 | 56800 | 2 | 15 | 16800 | 2 | 8 | 2790 | 2 | 19 | 1 | E | 9 | 1 | E | 9 | 15 | 59 | A | 7 | 1.7 | 35.06 | A | 7 | 0.41 | A | 7 | 989 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 27.86 | 7 | 0
2001-10-28 | 1900-10-27 | 11:00 | 11 | 755 | 1385 | 498 | 2 | 8 | 643 | 2 | 15 | 146 | 2 | 8 | 51800 | 2 | 8 | 63700 | 2 | 15 | 17000 | 2 | 8 | 3180 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.39 | A | 7 | 989 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 29.84 | 7 | 0
2001-10-28 | 1900-10-27 | 12:00 | 12 | 828 | 1385 | 587 | 2 | 8 | 741 | 2 | 15 | 142 | 2 | 8 | 61800 | 2 | 8 | 74500 | 2 | 15 | 17100 | 2 | 8 | 3360 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 19.4 | 66.92 | A | 7 | 5 | 41 | A | 7 | 0.39 | A | 7 | 986 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.6 | 7 | 0
2001-10-28 | 1900-10-27 | 13:00 | 13 | 831 | 1385 | 589 | 2 | 8 | 767 | 2 | 15 | 127 | 2 | 8 | 62500 | 2 | 8 | 77500 | 2 | 15 | 15900 | 2 | 8 | 3060 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20 | 68 | A | 7 | 6.1 | 42.98 | A | 7 | 0.4 | A | 7 | 987 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.38 | 7 | 0
2001-10-28 | 1900-10-27 | 14:00 | 14 | 764 | 1385 | 514 | 2 | 8 | 678 | 2 | 15 | 139 | 2 | 8 | 53800 | 2 | 8 | 67400 | 2 | 15 | 16500 | 2 | 8 | 3080 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.39 | A | 7 | 987 | A | 7 | 200 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.06 | 7 | 0
2001-10-28 | 1900-10-27 | 15:00 | 15 | 630 | 1385 | 427 | 2 | 8 | 712 | 2 | 15 | 102 | 2 | 8 | 44800 | 2 | 8 | 69400 | 2 | 15 | 13100 | 2 | 8 | 2100 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 21.1 | 69.98 | A | 7 | 7.2 | 44.96 | A | 7 | 0.41 | A | 7 | 987 | A | 7 | 170 | A | 7 | 9.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.06 | 7 | 0
2001-10-28 | 1900-10-27 | 16:00 | 16 | 441 | 1385 | 272 | 2 | 8 | 608 | 2 | 15 | 78 | 2 | 8 | 28200 | 2 | 8 | 54500 | 2 | 15 | 10700 | 2 | 8 | 1470 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 20.6 | 69.08 | A | 7 | 7.2 | 44.96 | A | 7 | 0.42 | A | 7 | 986 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.26 | 7 | 0
2001-10-28 | 1900-10-27 | 17:00 | 17 | 209 | 1385 | 100 | 2 | 8 | 378 | 2 | 15 | 43 | 2 | 8 | 10200 | 2 | 8 | 25500 | 2 | 15 | 6300 | 2 | 8 | 750 | 2 | 19 | 0 | E | 9 | 0 | E | 9 | 18.9 | 66.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.43 | A | 7 | 986 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.78 | 7 | 0
2001-10-28 | 1900-10-27 | 18:00 | 18 | 14 | 473 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 6 | E | 9 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.78 | 7 | 0
2001-10-28 | 1900-10-27 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 5.6 | 42.08 | A | 7 | 0.53 | A | 7 | 988 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.58 | 7 | 0
2001-10-28 | 1900-10-27 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | 3.9 | 39.02 | A | 7 | 0.46 | A | 7 | 988 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.02 | 7 | 0
2001-10-28 | 1900-10-27 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 3 | A | 7 | 15 | 59 | A | 7 | 3.3 | 37.94 | A | 7 | 0.45 | A | 7 | 988 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.64 | 7 | 0
2001-10-28 | 1900-10-27 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | A | 7 | 15 | 59 | A | 7 | 3.3 | 37.94 | A | 7 | 0.45 | A | 7 | 988 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.64 | 7 | 0
2001-10-28 | 1900-10-27 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 5 | A | 7 | 14.4 | 57.92 | A | 7 | 3.3 | 37.94 | A | 7 | 0.47 | A | 7 | 988 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 30.94 | 7 | 0
2001-10-28 | 1900-10-27 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 5 | A | 7 | 13.3 | 55.94 | A | 7 | 3.3 | 37.94 | A | 7 | 0.51 | A | 7 | 986 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.44 | 7 | 0
2001-10-29 | 1900-10-28 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 5 | A | 7 | 12.8 | 55.04 | A | 7 | 3.3 | 37.94 | A | 7 | 0.52 | A | 7 | 988 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.54 | 1 | 0
2001-10-29 | 1900-10-28 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 3 | A | 7 | 12.2 | 53.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.54 | A | 7 | 989 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 31.84 | 1 | 0
2001-10-29 | 1900-10-28 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.56 | A | 7 | 989 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.44 | 1 | 0
2001-10-29 | 1900-10-28 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.56 | A | 7 | 989 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.44 | 1 | 0
2001-10-29 | 1900-10-28 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.59 | A | 7 | 989 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.84 | 1 | 0
2001-10-29 | 1900-10-28 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.61 | A | 7 | 988 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.04 | 1 | 0
2001-10-29 | 1900-10-28 | 7:00 | 7 | 7 | 335 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 4 | E | 9 | 2 | A | 7 | 10 | 50 | A | 7 | 3.3 | 37.94 | A | 7 | 0.63 | A | 7 | 990 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.34 | 1 | 0
2001-10-29 | 1900-10-28 | 8:00 | 8 | 184 | 1386 | 108 | 2 | 8 | 284 | 2 | 15 | 70 | 2 | 8 | 10600 | 2 | 8 | 17000 | 2 | 15 | 8400 | 2 | 8 | 1350 | 2 | 19 | 4 | E | 9 | 3 | A | 7 | 11.1 | 51.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.61 | A | 7 | 991 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.02 | 1 | 0
2001-10-29 | 1900-10-28 | 9:00 | 9 | 418 | 1386 | 265 | 2 | 8 | 550 | 2 | 15 | 99 | 2 | 8 | 27800 | 2 | 8 | 48700 | 2 | 15 | 13000 | 2 | 8 | 1850 | 2 | 19 | 4 | E | 9 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | 4.4 | 39.92 | A | 7 | 0.57 | A | 7 | 992 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.22 | 1 | 0
2001-10-29 | 1900-10-28 | 10:00 | 10 | 612 | 1386 | 391 | 2 | 8 | 566 | 2 | 15 | 140 | 2 | 8 | 41400 | 2 | 8 | 55500 | 2 | 15 | 16800 | 2 | 8 | 2800 | 2 | 19 | 4 | E | 9 | 3 | A | 7 | 15 | 59 | A | 7 | 5.6 | 42.08 | A | 7 | 0.53 | A | 7 | 993 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.58 | 1 | 0
2001-10-29 | 1900-10-28 | 11:00 | 11 | 749 | 1386 | 492 | 2 | 8 | 631 | 2 | 15 | 150 | 2 | 8 | 51100 | 2 | 8 | 62300 | 2 | 15 | 17300 | 2 | 8 | 3230 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 16.1 | 60.98 | A | 7 | 6.1 | 42.98 | A | 7 | 0.51 | A | 7 | 993 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.98 | 1 | 0
2001-10-29 | 1900-10-28 | 12:00 | 12 | 822 | 1386 | 574 | 2 | 8 | 711 | 2 | 15 | 151 | 2 | 8 | 60200 | 2 | 8 | 71200 | 2 | 15 | 17800 | 2 | 8 | 3520 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 17.2 | 62.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.54 | A | 7 | 991 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.04 | 1 | 0
2001-10-29 | 1900-10-28 | 13:00 | 13 | 825 | 1386 | 583 | 2 | 8 | 761 | 2 | 15 | 128 | 2 | 8 | 61800 | 2 | 8 | 76800 | 2 | 15 | 15900 | 2 | 8 | 3060 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 18.9 | 66.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.48 | A | 7 | 992 | A | 7 | 250 | B | 8 | 3.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.14 | 1 | 0
2001-10-29 | 1900-10-28 | 14:00 | 14 | 758 | 1386 | 514 | 2 | 8 | 690 | 2 | 15 | 135 | 2 | 8 | 53800 | 2 | 8 | 68600 | 2 | 15 | 16100 | 2 | 8 | 2990 | 2 | 19 | 6 | E | 9 | 5 | A | 7 | 19.4 | 66.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.49 | A | 7 | 992 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.04 | 1 | 0
2001-10-29 | 1900-10-28 | 15:00 | 15 | 625 | 1386 | 399 | 2 | 8 | 583 | 2 | 15 | 135 | 2 | 8 | 40900 | 2 | 8 | 55800 | 2 | 15 | 15700 | 2 | 8 | 2630 | 2 | 19 | 10 | E | 9 | 9 | A | 7 | 19.4 | 66.92 | A | 7 | 9.4 | 48.92 | A | 7 | 0.52 | A | 7 | 992 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.12 | 1 | 0
2001-10-29 | 1900-10-28 | 16:00 | 16 | 435 | 1386 | 251 | 2 | 8 | 482 | 2 | 15 | 99 | 2 | 8 | 26400 | 2 | 8 | 43300 | 2 | 15 | 12700 | 2 | 8 | 1850 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 18.9 | 66.02 | A | 7 | 9.4 | 48.92 | A | 7 | 0.54 | A | 7 | 992 | A | 7 | 130 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.52 | 1 | 0
2001-10-29 | 1900-10-28 | 17:00 | 17 | 203 | 1386 | 75 | 2 | 8 | 155 | 2 | 15 | 53 | 2 | 8 | 8000 | 2 | 8 | 9700 | 2 | 15 | 6600 | 2 | 8 | 990 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.62 | A | 7 | 992 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.82 | 1 | 0
2001-10-29 | 1900-10-28 | 18:00 | 18 | 12 | 450 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.58 | A | 7 | 990 | A | 7 | 130 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.44 | 1 | 0
2001-10-29 | 1900-10-28 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 2 | E | 9 | 16.1 | 60.98 | A | 7 | 8.9 | 48.02 | A | 7 | 0.62 | A | 7 | 992 | A | 7 | 70 | A | 7 | 1.5 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.02 | 1 | 0
2001-10-29 | 1900-10-28 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 2 | E | 9 | 15.6 | 60.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.64 | A | 7 | 992 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.42 | 1 | 0
2001-10-29 | 1900-10-28 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 2 | E | 9 | 15 | 59 | A | 7 | 8.3 | 46.94 | A | 7 | 0.64 | A | 7 | 992 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.44 | 1 | 0
2001-10-29 | 1900-10-28 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 5 | E | 9 | 12.8 | 55.04 | A | 7 | 8.3 | 46.94 | A | 7 | 0.74 | A | 7 | 992 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.04 | 1 | 0
2001-10-29 | 1900-10-28 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 4 | E | 9 | 12.2 | 53.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.77 | A | 7 | 992 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.44 | 1 | 0
2001-10-29 | 1900-10-28 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.1 | 51.98 | A | 7 | 7.8 | 46.04 | A | 7 | 0.8 | A | 7 | 990 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.086 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.04 | 1 | 0
2001-10-30 | 1900-10-29 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.8 | A | 7 | 991 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.94 | 2 | 0
2001-10-30 | 1900-10-29 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 0 | E | 9 | 11.7 | 53.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.77 | A | 7 | 991 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.64 | 2 | 0
2001-10-30 | 1900-10-29 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | E | 9 | 2 | E | 9 | 13.3 | 55.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.69 | A | 7 | 991 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.44 | 2 | 0
2001-10-30 | 1900-10-29 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 6 | E | 9 | 13.3 | 55.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.69 | A | 7 | 990 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.44 | 2 | 0
2001-10-30 | 1900-10-29 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 6 | E | 9 | 12.8 | 55.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.69 | A | 7 | 990 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.46 | 2 | 0
2001-10-30 | 1900-10-29 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 7 | E | 9 | 12.8 | 55.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.69 | A | 7 | 989 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.2 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.46 | 2 | 0
2001-10-30 | 1900-10-29 | 7:00 | 7 | 6 | 312 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 9 | E | 9 | 5 | E | 9 | 12.8 | 55.04 | A | 7 | 7.2 | 44.96 | A | 7 | 0.69 | A | 7 | 991 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 2.2 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.46 | 2 | 0
2001-10-30 | 1900-10-29 | 8:00 | 8 | 179 | 1387 | 37 | 2 | 8 | 0 | 2 | 15 | 37 | 2 | 8 | 4200 | 2 | 8 | 0 | 2 | 15 | 4200 | 2 | 8 | 1290 | 2 | 19 | 5 | E | 9 | 2 | E | 9 | 13.3 | 55.94 | A | 7 | 7.8 | 46.04 | A | 7 | 0.69 | A | 7 | 992 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.3 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.44 | 2 | 0
2001-10-30 | 1900-10-29 | 9:00 | 9 | 413 | 1387 | 237 | 2 | 8 | 384 | 2 | 15 | 122 | 2 | 8 | 24200 | 2 | 8 | 33700 | 2 | 15 | 14100 | 2 | 8 | 2340 | 2 | 19 | 5 | E | 9 | 3 | E | 9 | 15.6 | 60.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.6 | A | 7 | 992 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.04 | 2 | 0
2001-10-30 | 1900-10-29 | 10:00 | 10 | 606 | 1387 | 358 | 2 | 8 | 443 | 2 | 15 | 164 | 2 | 8 | 37300 | 2 | 8 | 43300 | 2 | 15 | 18300 | 2 | 8 | 3340 | 2 | 19 | 3 | E | 9 | 3 | E | 9 | 17.2 | 62.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.56 | A | 7 | 991 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.14 | 2 | 0
2001-10-30 | 1900-10-29 | 11:00 | 11 | 744 | 1387 | 511 | 2 | 8 | 686 | 2 | 15 | 142 | 2 | 8 | 53200 | 2 | 8 | 67800 | 2 | 15 | 16700 | 2 | 8 | 3070 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 18.9 | 66.02 | A | 7 | 8.9 | 48.02 | A | 7 | 0.52 | A | 7 | 991 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.42 | 2 | 0
2001-10-30 | 1900-10-29 | 12:00 | 12 | 816 | 1387 | 568 | 2 | 8 | 717 | 2 | 15 | 145 | 2 | 8 | 59700 | 2 | 8 | 71800 | 2 | 15 | 17300 | 2 | 8 | 3380 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 20.6 | 69.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.49 | A | 7 | 988 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.4 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.62 | 2 | 0
2001-10-30 | 1900-10-29 | 13:00 | 13 | 819 | 1387 | 571 | 2 | 8 | 731 | 2 | 15 | 138 | 2 | 8 | 60200 | 2 | 8 | 73400 | 2 | 15 | 16700 | 2 | 8 | 3250 | 2 | 19 | 5 | E | 9 | 5 | A | 7 | 21.7 | 71.06 | A | 7 | 9.4 | 48.92 | A | 7 | 0.45 | A | 7 | 989 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2.3 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.92 | 2 | 0
2001-10-30 | 1900-10-29 | 14:00 | 14 | 752 | 1387 | 502 | 2 | 8 | 642 | 2 | 15 | 153 | 2 | 8 | 52100 | 2 | 8 | 63300 | 2 | 15 | 17600 | 2 | 8 | 3290 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 22.2 | 71.96 | A | 7 | 9.4 | 48.92 | A | 7 | 0.44 | A | 7 | 988 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.72 | 2 | 0
2001-10-30 | 1900-10-29 | 15:00 | 15 | 619 | 1387 | 404 | 2 | 8 | 647 | 2 | 15 | 114 | 2 | 8 | 41900 | 2 | 8 | 62400 | 2 | 15 | 14000 | 2 | 8 | 2290 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 21.7 | 71.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.44 | A | 7 | 987 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 39.02 | 2 | 0
2001-10-30 | 1900-10-29 | 16:00 | 16 | 429 | 1387 | 245 | 2 | 8 | 464 | 2 | 15 | 101 | 2 | 8 | 25700 | 2 | 8 | 41500 | 2 | 15 | 12800 | 2 | 8 | 1890 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 20.6 | 69.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.45 | A | 7 | 986 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.34 | 2 | 0
2001-10-30 | 1900-10-29 | 17:00 | 17 | 198 | 1387 | 98 | 2 | 8 | 328 | 2 | 15 | 51 | 2 | 8 | 10100 | 2 | 8 | 20700 | 2 | 15 | 7100 | 2 | 8 | 930 | 2 | 19 | 9 | E | 9 | 9 | A | 7 | 18.9 | 66.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.1 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.14 | 2 | 0
2001-10-30 | 1900-10-29 | 18:00 | 18 | 11 | 428 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 7 | E | 9 | 7 | A | 7 | 16.1 | 60.98 | A | 7 | 6.7 | 44.06 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.36 | 2 | 0
2001-10-30 | 1900-10-29 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | E | 9 | 1 | E | 9 | 16.1 | 60.98 | A | 7 | 5 | 41 | A | 7 | 0.48 | A | 7 | 985 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 2 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.9 | 2 | 0
2001-10-30 | 1900-10-29 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 16.1 | 60.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.5 | A | 7 | 984 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.08 | 2 | 0
2001-10-30 | 1900-10-29 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 0 | E | 9 | 17.2 | 62.96 | A | 7 | 5 | 41 | A | 7 | 0.44 | A | 7 | 984 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.9 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.3 | 2 | 0
2001-10-30 | 1900-10-29 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 1 | E | 9 | 1 | E | 9 | 16.1 | 60.98 | A | 7 | 5 | 41 | A | 7 | 0.48 | A | 7 | 984 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.9 | 2 | 0
2001-10-30 | 1900-10-29 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15.6 | 60.08 | A | 7 | 3.9 | 39.02 | A | 7 | 0.46 | A | 7 | 983 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 32.02 | 2 | 0
2001-10-30 | 1900-10-29 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 15 | 59 | A | 7 | 4.4 | 39.92 | A | 7 | 0.49 | A | 7 | 981 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.085 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.12 | 2 | 0
2001-10-31 | 1900-10-30 | 1:00 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | B | 8 | 2 | B | 8 | 15 | 59 | A | 7 | 4.4 | 39.92 | A | 7 | 0.49 | A | 7 | 982 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 33.12 | 3 | 0
2001-10-31 | 1900-10-30 | 2:00 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 4 | E | 9 | 14.4 | 57.92 | A | 7 | 5 | 41 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 34.6 | 3 | 0
2001-10-31 | 1900-10-30 | 3:00 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 8 | E | 9 | 4 | E | 9 | 15 | 59 | A | 7 | 5.6 | 42.08 | A | 7 | 0.53 | A | 7 | 981 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1.8 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 35.58 | 3 | 0
2001-10-31 | 1900-10-30 | 4:00 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 3 | E | 9 | 14.4 | 57.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.57 | A | 7 | 980 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1.8 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.88 | 3 | 0
2001-10-31 | 1900-10-30 | 5:00 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 3 | E | 9 | 15 | 59 | A | 7 | 6.1 | 42.98 | A | 7 | 0.55 | A | 7 | 980 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 3658 | A | 7 | 1.8 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.58 | 3 | 0
2001-10-31 | 1900-10-30 | 6:00 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 6 | E | 9 | 14.4 | 57.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 3962 | A | 7 | 1.9 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 36.88 | 3 | 0
2001-10-31 | 1900-10-30 | 7:00 | 7 | 5 | 289 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 5 | E | 9 | 2 | E | 9 | 13.9 | 57.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.59 | A | 7 | 979 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 1.9 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.18 | 3 | 0
2001-10-31 | 1900-10-30 | 8:00 | 8 | 174 | 1388 | 50 | 2 | 8 | 0 | 2 | 15 | 50 | 2 | 8 | 5500 | 2 | 8 | 0 | 2 | 15 | 5500 | 2 | 8 | 1560 | 2 | 19 | 7 | E | 9 | 4 | E | 9 | 14.4 | 57.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.6 | A | 7 | 978 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 1.9 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 38.26 | 3 | 0
2001-10-31 | 1900-10-30 | 9:00 | 9 | 408 | 1388 | 126 | 2 | 8 | 6 | 2 | 15 | 124 | 2 | 8 | 14000 | 2 | 8 | 400 | 2 | 15 | 13800 | 2 | 8 | 4240 | 2 | 19 | 8 | E | 9 | 4 | E | 9 | 15 | 59 | A | 7 | 7.8 | 46.04 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.34 | 3 | 0
2001-10-31 | 1900-10-30 | 10:00 | 10 | 600 | 1388 | 206 | 2 | 8 | 31 | 2 | 15 | 192 | 2 | 8 | 22500 | 2 | 8 | 3000 | 2 | 15 | 21200 | 2 | 8 | 5410 | 2 | 19 | 9 | E | 9 | 4 | E | 9 | 16.1 | 60.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 7010 | A | 7 | 2 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.84 | 3 | 0
2001-10-31 | 1900-10-30 | 11:00 | 11 | 738 | 1388 | 177 | 2 | 8 | 0 | 2 | 15 | 177 | 2 | 8 | 20500 | 2 | 8 | 0 | 2 | 15 | 20500 | 2 | 8 | 7550 | 2 | 19 | 10 | E | 9 | 4 | E | 9 | 16.7 | 62.06 | A | 7 | 8.9 | 48.02 | A | 7 | 0.6 | A | 7 | 977 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 41.72 | 3 | 0
2001-10-31 | 1900-10-30 | 12:00 | 12 | 811 | 1388 | 446 | 2 | 8 | 271 | 2 | 15 | 287 | 2 | 8 | 47300 | 2 | 8 | 28700 | 2 | 15 | 30500 | 2 | 8 | 7280 | 2 | 19 | 8 | E | 9 | 4 | E | 9 | 17.8 | 64.04 | A | 7 | 10 | 50 | A | 7 | 0.6 | A | 7 | 973 | A | 7 | 180 | A | 7 | 12.4 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.5 | 3 | 0
2001-10-31 | 1900-10-30 | 13:00 | 13 | 813 | 1388 | 446 | 2 | 8 | 299 | 2 | 15 | 270 | 2 | 8 | 47600 | 2 | 8 | 31700 | 2 | 15 | 29000 | 2 | 8 | 6770 | 2 | 19 | 7 | E | 9 | 3 | E | 9 | 20 | 68 | A | 7 | 11.1 | 51.98 | A | 7 | 0.57 | A | 7 | 974 | A | 7 | 180 | A | 7 | 12.9 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.1 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.58 | 3 | 0
2001-10-31 | 1900-10-30 | 14:00 | 14 | 746 | 1388 | 277 | 2 | 8 | 48 | 2 | 15 | 251 | 2 | 8 | 30400 | 2 | 8 | 4800 | 2 | 15 | 27800 | 2 | 8 | 7590 | 2 | 19 | 8 | E | 9 | 4 | E | 9 | 20.6 | 69.08 | A | 7 | 11.1 | 51.98 | A | 7 | 0.54 | A | 7 | 973 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.1 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.08 | 3 | 0
2001-10-31 | 1900-10-30 | 15:00 | 15 | 613 | 1388 | 243 | 2 | 8 | 71 | 2 | 15 | 212 | 2 | 8 | 26700 | 2 | 8 | 7000 | 2 | 15 | 23600 | 2 | 8 | 5890 | 2 | 19 | 7 | E | 9 | 3 | E | 9 | 20.6 | 69.08 | A | 7 | 11.1 | 51.98 | A | 7 | 0.54 | A | 7 | 972 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.08 | 3 | 0
2001-10-31 | 1900-10-30 | 16:00 | 16 | 424 | 1388 | 128 | 2 | 8 | 17 | 2 | 15 | 122 | 2 | 8 | 14200 | 2 | 8 | 1100 | 2 | 15 | 13900 | 2 | 8 | 4300 | 2 | 19 | 7 | E | 9 | 3 | E | 9 | 20 | 68 | A | 7 | 10.6 | 51.08 | A | 7 | 0.55 | A | 7 | 971 | A | 7 | 180 | A | 7 | 12.9 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.2 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.48 | 3 | 0
2001-10-31 | 1900-10-30 | 17:00 | 17 | 192 | 1388 | 27 | 2 | 8 | 0 | 2 | 15 | 27 | 2 | 8 | 3100 | 2 | 8 | 0 | 2 | 15 | 3100 | 2 | 8 | 1030 | 2 | 19 | 8 | E | 9 | 4 | E | 9 | 18.9 | 66.02 | A | 7 | 10.6 | 51.08 | A | 7 | 0.59 | A | 7 | 971 | A | 7 | 180 | A | 7 | 10.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.18 | 3 | 0
2001-10-31 | 1900-10-30 | 18:00 | 18 | 10 | 405 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 8 | 0 | 2 | 15 | 0 | 2 | 8 | 0 | 2 | 19 | 10 | E | 9 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.61 | A | 7 | 969 | A | 7 | 180 | A | 7 | 11.8 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.3 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.58 | 3 | 0
2001-10-31 | 1900-10-30 | 19:00 | 19 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 7 | E | 9 | 3 | E | 9 | 18.3 | 64.94 | A | 7 | 10 | 50 | A | 7 | 0.58 | A | 7 | 971 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 43.1 | 3 | 0
2001-10-31 | 1900-10-30 | 20:00 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 9 | E | 9 | 4 | E | 9 | 17.8 | 64.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.63 | A | 7 | 971 | A | 7 | 190 | A | 7 | 11.3 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.88 | 3 | 0
2001-10-31 | 1900-10-30 | 21:00 | 21 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 6 | E | 9 | 3 | E | 9 | 17.8 | 64.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.63 | A | 7 | 971 | A | 7 | 190 | A | 7 | 14.4 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.4 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 44.88 | 3 | 0
2001-10-31 | 1900-10-30 | 22:00 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 5 | E | 9 | 2 | E | 9 | 16.2 | 61.16 | A | 7 | 8.8 | 47.84 | A | 7 | 0.67 | A | 7 | 971 | A | 7 | 190 | A | 7 | 13.7 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 42.74 | 3 | 0
2001-10-31 | 1900-10-30 | 23:00 | 23 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 4 | E | 9 | 2 | E | 9 | 14.6 | 58.28 | A | 7 | 6.9 | 44.42 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 190 | A | 7 | 12.9 | A | 7 | 16000 | A | 7 | 7620 | A | 7 | 2.5 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 40.12 | 3 | 0
2001-10-31 | 1900-10-30 | 24:00 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | E | 9 | 0 | E | 9 | 13 | 55.4 | A | 7 | 5.1 | 41.18 | A | 7 | 0.72 | A | 7 | 970 | A | 7 | 200 | A | 7 | 12.2 | A | 7 | 16000 | A | 7 | 6096 | A | 7 | 2.6 | E | 8 | 0.084 | F | 8 | 0.18 | F | 8 | 0 | 1 | A | 7 | 37.38 | 3 | 0
1979-11-01 | 1900-10-31 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.5 | 52.7 | A | 7 | 3.3 | 37.94 | A | 7 | 0.54 | A | 7 | 974 | A | 7 | 260 | A | 7 | 11.5 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.84 | 4 | 0
1979-11-01 | 1900-10-31 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.9 | 49.82 | A | 7 | 1.5 | 34.7 | A | 7 | 0.56 | A | 7 | 975 | A | 7 | 260 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 1340 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.4 | 4 | 0
1979-11-01 | 1900-10-31 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | -0.3 | 31.46 | A | 7 | 0.49 | A | 7 | 975 | A | 7 | 290 | A | 7 | 10 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.96 | 4 | 0
1979-11-01 | 1900-10-31 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.53 | A | 7 | 976 | A | 7 | 260 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 1340 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.44 | 4 | 0
1979-11-01 | 1900-10-31 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 6.1 | 42.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.53 | A | 7 | 977 | A | 7 | 260 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 1280 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.56 | 4 | 0
1979-11-01 | 1900-10-31 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 5.6 | 42.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.76 | 4 | 0
1979-11-01 | 1900-10-31 | 7:00 | 7 | 5 | 289 | 8 | 1 | 13 | 35 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 979 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 4 | 0
1979-11-01 | 1900-10-31 | 8:00 | 8 | 172 | 1388 | 85 | 1 | 13 | 477 | 1 | 9 | 25 | 1 | 13 | 8600 | 1 | 13 | 32100 | 1 | 9 | 4600 | 1 | 13 | 490 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 4 | 0
1979-11-01 | 1900-10-31 | 9:00 | 9 | 406 | 1388 | 263 | 1 | 9 | 752 | 1 | 9 | 40 | 1 | 13 | 27500 | 1 | 9 | 67300 | 1 | 9 | 7800 | 1 | 13 | 950 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 270 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.74 | 4 | 0
1979-11-01 | 1900-10-31 | 10:00 | 10 | 599 | 1388 | 427 | 1 | 9 | 860 | 1 | 9 | 52 | 1 | 13 | 44700 | 1 | 9 | 82400 | 1 | 9 | 9000 | 1 | 13 | 1280 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.5 | A | 7 | 981 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.14 | 4 | 0
1979-11-01 | 1900-10-31 | 11:00 | 11 | 736 | 1388 | 405 | 1 | 13 | 505 | 1 | 13 | 135 | 1 | 13 | 42200 | 1 | 13 | 50000 | 1 | 13 | 15600 | 1 | 13 | 2920 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 8.9 | 48.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.5 | A | 7 | 981 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.82 | 4 | 0
1979-11-01 | 1900-10-31 | 12:00 | 12 | 809 | 1388 | 549 | 1 | 13 | 719 | 1 | 13 | 127 | 1 | 13 | 58000 | 1 | 13 | 72400 | 1 | 13 | 15700 | 1 | 13 | 2980 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | 10 | 50 | A | 7 | -3.3 | 26.06 | A | 7 | 0.39 | A | 7 | 981 | A | 7 | 260 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.36 | 4 | 0
1979-11-01 | 1900-10-31 | 13:00 | 13 | 812 | 1388 | 320 | 1 | 13 | 142 | 1 | 13 | 236 | 1 | 13 | 35100 | 1 | 13 | 14900 | 1 | 13 | 26300 | 1 | 13 | 6290 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 11.1 | 51.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.4 | A | 7 | 981 | A | 7 | 260 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 760 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.14 | 4 | 0
1979-11-01 | 1900-10-31 | 14:00 | 14 | 744 | 1388 | 300 | 1 | 9 | 190 | 1 | 9 | 197 | 1 | 13 | 33000 | 1 | 9 | 19700 | 1 | 9 | 22400 | 1 | 13 | 5040 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 10 | 50 | A | 7 | -3.3 | 26.06 | A | 7 | 0.39 | A | 7 | 981 | A | 7 | 260 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1370 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.36 | 4 | 0
1979-11-01 | 1900-10-31 | 15:00 | 15 | 611 | 1388 | 377 | 1 | 13 | 647 | 1 | 13 | 88 | 1 | 13 | 39500 | 1 | 13 | 63000 | 1 | 13 | 11700 | 1 | 13 | 1830 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 10.6 | 51.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.38 | A | 7 | 981 | A | 7 | 260 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 1370 | A | 7 | 0.9 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.36 | 4 | 0
1979-11-01 | 1900-10-31 | 16:00 | 16 | 422 | 1388 | 253 | 1 | 13 | 540 | 1 | 13 | 86 | 1 | 13 | 25700 | 1 | 13 | 47400 | 1 | 13 | 11200 | 1 | 13 | 1560 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 10.6 | 51.08 | A | 7 | -5 | 23 | A | 7 | 0.33 | A | 7 | 981 | A | 7 | 270 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.4 | 4 | 0
1979-11-01 | 1900-10-31 | 17:00 | 17 | 191 | 1388 | 101 | 1 | 13 | 525 | 1 | 9 | 27 | 1 | 13 | 10100 | 1 | 13 | 36700 | 1 | 9 | 5100 | 1 | 13 | 530 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.33 | A | 7 | 981 | A | 7 | 260 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.72 | 4 | 0
1979-11-01 | 1900-10-31 | 18:00 | 18 | 9 | 382 | 13 | 1 | 13 | 55 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -5 | 23 | A | 7 | 0.45 | A | 7 | 982 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.045 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.4 | 4 | 0
1979-11-01 | 1900-10-31 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.45 | A | 7 | 982 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.52 | 4 | 0
1979-11-01 | 1900-10-31 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -5 | 23 | A | 7 | 0.53 | A | 7 | 983 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.1 | 4 | 0
1979-11-01 | 1900-10-31 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -5 | 23 | A | 7 | 0.59 | A | 7 | 983 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.6 | 4 | 0
1979-11-01 | 1900-10-31 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.57 | A | 7 | 984 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.42 | 4 | 0
1979-11-01 | 1900-10-31 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.59 | A | 7 | 984 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 4 | 0
1979-11-01 | 1900-10-31 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 4 | 0
1979-11-02 | 1900-11-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 984 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.22 | 5 | 0
1979-11-02 | 1900-11-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 984 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.22 | 5 | 0
1979-11-02 | 1900-11-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 984 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 5 | 0
1979-11-02 | 1900-11-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.72 | A | 7 | 984 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.84 | 5 | 0
1979-11-02 | 1900-11-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 984 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 5 | 0
1979-11-02 | 1900-11-01 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 984 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 5 | 0
1979-11-02 | 1900-11-01 | 7:00 | 7 | 4 | 266 | 4 | 1 | 13 | 17 | 1 | 13 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 984 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 5 | 0
1979-11-02 | 1900-11-01 | 8:00 | 8 | 167 | 1389 | 72 | 1 | 13 | 281 | 1 | 9 | 38 | 1 | 13 | 7500 | 1 | 13 | 16200 | 1 | 9 | 5600 | 1 | 13 | 680 | 1 | 21 | 7 | A | 7 | 2 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.75 | A | 7 | 985 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 5 | 0
1979-11-02 | 1900-11-01 | 9:00 | 9 | 401 | 1389 | 231 | 1 | 9 | 621 | 1 | 9 | 50 | 1 | 13 | 23800 | 1 | 9 | 55100 | 1 | 9 | 7900 | 1 | 13 | 1010 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 986 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 5 | 0
1979-11-02 | 1900-11-01 | 10:00 | 10 | 593 | 1389 | 376 | 1 | 9 | 692 | 1 | 9 | 77 | 1 | 13 | 38800 | 1 | 9 | 66300 | 1 | 9 | 10400 | 1 | 13 | 1560 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 6.7 | 44.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.51 | A | 7 | 986 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 5 | 0
1979-11-02 | 1900-11-01 | 11:00 | 11 | 731 | 1389 | 510 | 1 | 9 | 833 | 1 | 9 | 67 | 1 | 13 | 53100 | 1 | 9 | 81600 | 1 | 9 | 10000 | 1 | 13 | 1580 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 8.9 | 48.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.42 | A | 7 | 985 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.66 | 5 | 0
1979-11-02 | 1900-11-01 | 12:00 | 12 | 803 | 1389 | 576 | 1 | 9 | 856 | 1 | 9 | 77 | 1 | 13 | 59900 | 1 | 9 | 84400 | 1 | 9 | 10900 | 1 | 13 | 1780 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 10.6 | 51.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.38 | A | 7 | 985 | A | 7 | 230 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.36 | 5 | 0
1979-11-02 | 1900-11-01 | 13:00 | 13 | 806 | 1389 | 596 | 1 | 9 | 890 | 1 | 9 | 75 | 1 | 13 | 62000 | 1 | 9 | 87800 | 1 | 9 | 10800 | 1 | 13 | 1770 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.37 | A | 7 | 984 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.26 | 5 | 0
1979-11-02 | 1900-11-01 | 14:00 | 14 | 738 | 1389 | 522 | 1 | 9 | 765 | 1 | 9 | 111 | 1 | 13 | 55000 | 1 | 9 | 76400 | 1 | 9 | 14200 | 1 | 13 | 2470 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 12.2 | 53.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.31 | A | 7 | 983 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.08 | 5 | 0
1979-11-02 | 1900-11-01 | 15:00 | 15 | 606 | 1389 | 277 | 1 | 13 | 261 | 1 | 13 | 162 | 1 | 13 | 29600 | 1 | 13 | 26400 | 1 | 13 | 18100 | 1 | 13 | 3440 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 12.2 | 53.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.34 | A | 7 | 982 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.96 | 5 | 0
1979-11-02 | 1900-11-01 | 16:00 | 16 | 417 | 1389 | 225 | 1 | 13 | 470 | 1 | 13 | 82 | 1 | 13 | 22900 | 1 | 13 | 41200 | 1 | 13 | 10500 | 1 | 13 | 1500 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 12.8 | 55.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.31 | A | 7 | 982 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.78 | 5 | 0
1979-11-02 | 1900-11-01 | 17:00 | 17 | 185 | 1389 | 59 | 1 | 13 | 73 | 1 | 13 | 49 | 1 | 13 | 6400 | 1 | 13 | 4700 | 1 | 13 | 5800 | 1 | 13 | 1030 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 11.1 | 51.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.35 | A | 7 | 982 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 0.8 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.18 | 5 | 0
1979-11-02 | 1900-11-01 | 18:00 | 18 | 8 | 359 | 6 | 1 | 13 | 4 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | 10.6 | 51.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.39 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 0.9 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.16 | 5 | 0
1979-11-02 | 1900-11-01 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 8.9 | 48.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.46 | A | 7 | 982 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1400 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.74 | 5 | 0
1979-11-02 | 1900-11-01 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 2.2 | 35.96 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.56 | 5 | 0
1979-11-02 | 1900-11-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 982 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 5 | 0
1979-11-02 | 1900-11-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | 1.1 | 33.98 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.18 | 5 | 0
1979-11-02 | 1900-11-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 5 | 0
1979-11-02 | 1900-11-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 983 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 5 | 0
1979-11-03 | 1900-11-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 983 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.1 | 6 | 0
1979-11-03 | 1900-11-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.22 | 6 | 0
1979-11-03 | 1900-11-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.76 | A | 7 | 984 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.74 | 6 | 0
1979-11-03 | 1900-11-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.73 | A | 7 | 985 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.56 | 6 | 0
1979-11-03 | 1900-11-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -3.9 | 24.98 | A | 7 | 0.75 | A | 7 | 985 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 6 | 0
1979-11-03 | 1900-11-02 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.78 | A | 7 | 986 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.18 | 6 | 0
1979-11-03 | 1900-11-02 | 7:00 | 7 | 3 | 243 | 5 | 1 | 13 | 18 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 6 | 0
1979-11-03 | 1900-11-02 | 8:00 | 8 | 162 | 1390 | 77 | 1 | 13 | 425 | 1 | 9 | 27 | 1 | 13 | 7700 | 1 | 13 | 27700 | 1 | 9 | 4400 | 1 | 13 | 490 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 6 | 0
1979-11-03 | 1900-11-02 | 9:00 | 9 | 395 | 1390 | 250 | 1 | 9 | 715 | 1 | 9 | 44 | 1 | 13 | 26100 | 1 | 9 | 63500 | 1 | 9 | 7900 | 1 | 13 | 930 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -1.1 | 30.02 | A | 7 | 0.73 | A | 7 | 988 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.22 | 6 | 0
1979-11-03 | 1900-11-02 | 10:00 | 10 | 588 | 1390 | 414 | 1 | 9 | 836 | 1 | 9 | 57 | 1 | 13 | 43300 | 1 | 9 | 79900 | 1 | 9 | 9400 | 1 | 13 | 1310 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.6 | A | 7 | 988 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 6 | 0
1979-11-03 | 1900-11-02 | 11:00 | 11 | 725 | 1390 | 534 | 1 | 9 | 888 | 1 | 9 | 67 | 1 | 13 | 55700 | 1 | 9 | 86900 | 1 | 9 | 10200 | 1 | 13 | 1570 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.47 | A | 7 | 989 | A | 7 | 270 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.28 | 6 | 0
1979-11-03 | 1900-11-02 | 12:00 | 12 | 797 | 1390 | 600 | 1 | 9 | 907 | 1 | 9 | 75 | 1 | 13 | 62400 | 1 | 9 | 89400 | 1 | 9 | 10900 | 1 | 13 | 1760 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.45 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.28 | 6 | 0
1979-11-03 | 1900-11-02 | 13:00 | 13 | 800 | 1390 | 599 | 1 | 9 | 903 | 1 | 9 | 75 | 1 | 13 | 62400 | 1 | 9 | 89100 | 1 | 9 | 10900 | 1 | 13 | 1760 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -5 | 23 | A | 7 | 0.37 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.7 | 6 | 0
1979-11-03 | 1900-11-02 | 14:00 | 14 | 733 | 1390 | 544 | 1 | 9 | 894 | 1 | 9 | 68 | 1 | 13 | 56700 | 1 | 9 | 87600 | 1 | 9 | 10300 | 1 | 13 | 1590 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | -4.4 | 24.08 | A | 7 | 0.36 | A | 7 | 987 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.48 | 6 | 0
1979-11-03 | 1900-11-02 | 15:00 | 15 | 600 | 1390 | 428 | 1 | 9 | 846 | 1 | 9 | 58 | 1 | 13 | 44600 | 1 | 9 | 81000 | 1 | 9 | 9500 | 1 | 13 | 1330 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.34 | A | 7 | 986 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.28 | 6 | 0
1979-11-03 | 1900-11-02 | 16:00 | 16 | 411 | 1390 | 266 | 1 | 9 | 736 | 1 | 9 | 45 | 1 | 13 | 27800 | 1 | 9 | 66000 | 1 | 9 | 8200 | 1 | 13 | 990 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.34 | A | 7 | 986 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.28 | 6 | 0
1979-11-03 | 1900-11-02 | 17:00 | 17 | 180 | 1390 | 86 | 1 | 13 | 396 | 1 | 9 | 33 | 1 | 13 | 8700 | 1 | 13 | 25200 | 1 | 9 | 5400 | 1 | 13 | 590 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 10 | 50 | A | 7 | -3.3 | 26.06 | A | 7 | 0.39 | A | 7 | 986 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.36 | 6 | 0
1979-11-03 | 1900-11-02 | 18:00 | 18 | 7 | 336 | 8 | 1 | 13 | 30 | 1 | 9 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 6.1 | 42.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.53 | A | 7 | 986 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.56 | 6 | 0
1979-11-03 | 1900-11-02 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 6.7 | 44.06 | A | 7 | -3.3 | 26.06 | A | 7 | 0.49 | A | 7 | 985 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.36 | 6 | 0
1979-11-03 | 1900-11-02 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.51 | A | 7 | 985 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.56 | 6 | 0
1979-11-03 | 1900-11-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.55 | A | 7 | 985 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.76 | 6 | 0
1979-11-03 | 1900-11-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 6 | 0
1979-11-03 | 1900-11-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 6 | 0
1979-11-03 | 1900-11-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 6 | 0
1979-11-04 | 1900-11-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.74 | 7 | 0
1979-11-04 | 1900-11-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.55 | A | 7 | 985 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.76 | 7 | 0
1979-11-04 | 1900-11-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -3.3 | 26.06 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.96 | 7 | 0
1979-11-04 | 1900-11-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.57 | A | 7 | 984 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.18 | 7 | 0
1979-11-04 | 1900-11-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 984 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 7 | 0
1979-11-04 | 1900-11-03 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 984 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 7 | 0
1979-11-04 | 1900-11-03 | 7:00 | 7 | 3 | 197 | 1 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 3.3 | 37.94 | A | 7 | -5 | 23 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.2 | 7 | 0
1979-11-04 | 1900-11-03 | 8:00 | 8 | 157 | 1391 | 51 | 1 | 13 | 55 | 1 | 9 | 45 | 1 | 13 | 5500 | 1 | 13 | 3200 | 1 | 9 | 5200 | 1 | 13 | 940 | 1 | 21 | 8 | A | 7 | 2 | A | 7 | 5.6 | 42.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.51 | A | 7 | 985 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.58 | 7 | 0
1979-11-04 | 1900-11-03 | 9:00 | 9 | 390 | 1391 | 143 | 1 | 13 | 158 | 1 | 13 | 99 | 1 | 13 | 15700 | 1 | 13 | 14100 | 1 | 13 | 11700 | 1 | 13 | 2190 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 8.9 | 48.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.41 | A | 7 | 985 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.68 | 7 | 0
1979-11-04 | 1900-11-03 | 10:00 | 10 | 582 | 1391 | 337 | 1 | 13 | 502 | 1 | 13 | 125 | 1 | 13 | 35800 | 1 | 13 | 48800 | 1 | 13 | 15300 | 1 | 13 | 2450 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 11.1 | 51.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.37 | A | 7 | 985 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.26 | 7 | 0
1979-11-04 | 1900-11-03 | 11:00 | 11 | 719 | 1391 | 462 | 1 | 13 | 543 | 1 | 13 | 179 | 1 | 13 | 48600 | 1 | 13 | 54700 | 1 | 13 | 20300 | 1 | 13 | 3850 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 12.8 | 55.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.36 | A | 7 | 984 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.74 | 7 | 0
1979-11-04 | 1900-11-03 | 12:00 | 12 | 792 | 1391 | 379 | 1 | 13 | 294 | 1 | 13 | 210 | 1 | 13 | 41000 | 1 | 13 | 31100 | 1 | 13 | 23200 | 1 | 13 | 4950 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 15.6 | 60.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.3 | A | 7 | 983 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 9140 | A | 7 | 0.9 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.14 | 7 | 0
1979-11-04 | 1900-11-03 | 13:00 | 13 | 794 | 1391 | 455 | 1 | 13 | 391 | 1 | 13 | 230 | 1 | 13 | 48900 | 1 | 13 | 41300 | 1 | 13 | 25200 | 1 | 13 | 5530 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 16.1 | 60.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.31 | A | 7 | 982 | A | 7 | 160 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 9140 | A | 7 | 1 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.72 | 7 | 0
1979-11-04 | 1900-11-03 | 14:00 | 14 | 727 | 1391 | 335 | 1 | 13 | 280 | 1 | 13 | 187 | 1 | 13 | 36200 | 1 | 13 | 29300 | 1 | 13 | 20800 | 1 | 13 | 4200 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 16.1 | 60.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.32 | A | 7 | 981 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.62 | 7 | 0
1979-11-04 | 1900-11-03 | 15:00 | 15 | 595 | 1391 | 185 | 1 | 9 | 68 | 1 | 9 | 156 | 1 | 13 | 20400 | 1 | 9 | 6600 | 1 | 9 | 17500 | 1 | 13 | 4570 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 16.1 | 60.98 | A | 7 | 0 | 32 | A | 7 | 0.34 | A | 7 | 981 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.7 | 7 | 0
1979-11-04 | 1900-11-03 | 16:00 | 16 | 406 | 1391 | 139 | 1 | 9 | 89 | 1 | 9 | 113 | 1 | 13 | 15100 | 1 | 9 | 8100 | 1 | 9 | 12800 | 1 | 13 | 2520 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 16.1 | 60.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.32 | A | 7 | 981 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.62 | 7 | 0
1979-11-04 | 1900-11-03 | 17:00 | 17 | 175 | 1391 | 54 | 1 | 13 | 16 | 1 | 13 | 52 | 1 | 13 | 5900 | 1 | 13 | 1100 | 1 | 13 | 5800 | 1 | 13 | 1210 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 15 | 59 | A | 7 | -1.1 | 30.02 | A | 7 | 0.33 | A | 7 | 981 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.02 | 7 | 0
1979-11-04 | 1900-11-03 | 18:00 | 18 | 6 | 313 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 13.9 | 57.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.36 | A | 7 | 981 | A | 7 | 150 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.162 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.32 | 7 | 0
1979-11-04 | 1900-11-03 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.36 | A | 7 | 981 | A | 7 | 150 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.32 | 7 | 0
1979-11-04 | 1900-11-03 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 13.9 | 57.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.37 | A | 7 | 980 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.12 | 7 | 0
1979-11-04 | 1900-11-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 13.9 | 57.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.37 | A | 7 | 980 | A | 7 | 160 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.12 | 7 | 0
1979-11-04 | 1900-11-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 12.8 | 55.04 | A | 7 | -1.1 | 30.02 | A | 7 | 0.39 | A | 7 | 981 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.62 | 7 | 0
1979-11-04 | 1900-11-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 12.8 | 55.04 | A | 7 | -1.1 | 30.02 | A | 7 | 0.39 | A | 7 | 981 | A | 7 | 160 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.62 | 7 | 0
1979-11-04 | 1900-11-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 12.8 | 55.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.4 | A | 7 | 981 | A | 7 | 170 | A | 7 | 9.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.52 | 7 | 0
1979-11-05 | 1900-11-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 12.2 | 53.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.42 | A | 7 | 981 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.72 | 1 | 0
1979-11-05 | 1900-11-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 6 | A | 7 | 11.7 | 53.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.43 | A | 7 | 980 | A | 7 | 160 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.82 | 1 | 0
1979-11-05 | 1900-11-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 11.1 | 51.98 | A | 7 | 0 | 32 | A | 7 | 0.47 | A | 7 | 980 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.2 | 1 | 0
1979-11-05 | 1900-11-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 0 | 32 | A | 7 | 0.47 | A | 7 | 980 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1400 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.2 | 1 | 0
1979-11-05 | 1900-11-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 0 | 32 | A | 7 | 0.47 | A | 7 | 979 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1400 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.2 | 1 | 0
1979-11-05 | 1900-11-04 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 1.1 | 33.98 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1400 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.58 | 1 | 0
1979-11-05 | 1900-11-04 | 7:00 | 7 | 2 | 174 | 2 | 1 | 13 | 1 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 10.6 | 51.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 160 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 1340 | A | 7 | 1.1 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.38 | 1 | 0
1979-11-05 | 1900-11-04 | 8:00 | 8 | 152 | 1391 | 34 | 1 | 13 | 5 | 1 | 9 | 34 | 1 | 13 | 3900 | 1 | 13 | 0 | 1 | 9 | 3900 | 1 | 13 | 1150 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 1220 | A | 7 | 1.1 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.38 | 1 | 0
1979-11-05 | 1900-11-04 | 9:00 | 9 | 385 | 1391 | 143 | 1 | 9 | 12 | 1 | 9 | 140 | 1 | 13 | 15600 | 1 | 9 | 800 | 1 | 9 | 15400 | 1 | 13 | 4340 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 1.1 | 33.98 | A | 7 | 0.5 | A | 7 | 978 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 1.1 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.08 | 1 | 0
1979-11-05 | 1900-11-04 | 10:00 | 10 | 577 | 1391 | 187 | 1 | 9 | 12 | 1 | 9 | 182 | 1 | 13 | 20900 | 1 | 9 | 1000 | 1 | 9 | 20500 | 1 | 13 | 6640 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.49 | A | 7 | 978 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 1.2 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.86 | 1 | 0
1979-11-05 | 1900-11-04 | 11:00 | 11 | 714 | 1391 | 221 | 1 | 9 | 0 | 1 | 9 | 221 | 1 | 13 | 25000 | 1 | 9 | 0 | 1 | 9 | 25000 | 1 | 13 | 8620 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 3.9 | 39.02 | A | 7 | 0.51 | A | 7 | 978 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 1160 | A | 7 | 1.3 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.72 | 1 | 0
1979-11-05 | 1900-11-04 | 12:00 | 12 | 786 | 1391 | 214 | 1 | 9 | 2 | 1 | 9 | 213 | 1 | 13 | 24600 | 1 | 9 | 200 | 1 | 9 | 24500 | 1 | 13 | 8920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 5 | 41 | A | 7 | 0.5 | A | 7 | 978 | A | 7 | 220 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 1160 | A | 7 | 1.4 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.2 | 1 | 0
1979-11-05 | 1900-11-04 | 13:00 | 13 | 789 | 1391 | 234 | 1 | 9 | 4 | 1 | 9 | 231 | 1 | 13 | 26700 | 1 | 9 | 300 | 1 | 9 | 26500 | 1 | 13 | 9450 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 5 | 41 | A | 7 | 0.53 | A | 7 | 977 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 1.4 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.6 | 1 | 0
1979-11-05 | 1900-11-04 | 14:00 | 14 | 722 | 1391 | 225 | 1 | 9 | 3 | 1 | 9 | 223 | 1 | 13 | 25400 | 1 | 9 | 300 | 1 | 9 | 25300 | 1 | 13 | 8730 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.55 | A | 7 | 977 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 1010 | A | 7 | 1.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.88 | 1 | 0
1979-11-05 | 1900-11-04 | 15:00 | 15 | 589 | 1391 | 177 | 1 | 9 | 0 | 1 | 9 | 177 | 1 | 13 | 19900 | 1 | 9 | 0 | 1 | 9 | 19900 | 1 | 13 | 6620 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.6 | A | 7 | 978 | A | 7 | 230 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 1.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.58 | 1 | 0
1979-11-05 | 1900-11-04 | 16:00 | 16 | 401 | 1391 | 127 | 1 | 9 | 0 | 1 | 9 | 127 | 1 | 13 | 14000 | 1 | 9 | 0 | 1 | 9 | 14000 | 1 | 13 | 4250 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 520 | A | 7 | 1.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.38 | 1 | 0
1979-11-05 | 1900-11-04 | 17:00 | 17 | 171 | 1391 | 50 | 1 | 13 | 0 | 1 | 9 | 50 | 1 | 13 | 5500 | 1 | 13 | 0 | 1 | 9 | 5500 | 1 | 13 | 1550 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 460 | A | 7 | 1.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.38 | 1 | 0
1979-11-05 | 1900-11-04 | 18:00 | 18 | 5 | 290 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 310 | A | 7 | 9.8 | A | 7 | 11300 | A | 7 | 490 | A | 7 | 1.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.08 | 1 | 0
1979-11-05 | 1900-11-04 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 5 | 41 | A | 7 | 0.83 | A | 7 | 982 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 4000 | A | 7 | 150 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.7 | 1 | 0
1979-11-05 | 1900-11-04 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.83 | A | 7 | 984 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 8000 | A | 7 | 180 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.94 | 1 | 0
1979-11-05 | 1900-11-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 320 | A | 7 | 9.8 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 1 | 0
1979-11-05 | 1900-11-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.76 | A | 7 | 987 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.38 | 1 | 0
1979-11-05 | 1900-11-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 0 | 32 | A | 7 | 0.73 | A | 7 | 988 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.1 | 1 | 0
1979-11-05 | 1900-11-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.7 | A | 7 | 989 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.72 | 1 | 0
1979-11-06 | 1900-11-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.7 | A | 7 | 990 | A | 7 | 320 | A | 7 | 9.3 | A | 7 | 12900 | A | 7 | 310 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.72 | 2 | 0
1979-11-06 | 1900-11-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.68 | A | 7 | 991 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 12900 | A | 7 | 310 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.72 | 2 | 0
1979-11-06 | 1900-11-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.7 | A | 7 | 991 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.92 | 2 | 0
1979-11-06 | 1900-11-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.67 | A | 7 | 992 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 400 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 2 | 0
1979-11-06 | 1900-11-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 993 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 430 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 2 | 0
1979-11-06 | 1900-11-05 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 994 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 430 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 2 | 0
1979-11-06 | 1900-11-05 | 7:00 | 7 | 1 | 151 | 1 | 1 | 13 | 0 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.62 | A | 7 | 994 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 430 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.58 | 2 | 0
1979-11-06 | 1900-11-05 | 8:00 | 8 | 147 | 1392 | 35 | 1 | 13 | 0 | 1 | 9 | 35 | 1 | 13 | 3900 | 1 | 13 | 0 | 1 | 9 | 3900 | 1 | 13 | 1160 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 996 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.78 | 2 | 0
1979-11-06 | 1900-11-05 | 9:00 | 9 | 379 | 1392 | 121 | 1 | 9 | 66 | 1 | 9 | 103 | 1 | 13 | 13300 | 1 | 9 | 5900 | 1 | 9 | 11700 | 1 | 13 | 2680 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 3.3 | 37.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.6 | A | 7 | 996 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.48 | 2 | 0
1979-11-06 | 1900-11-05 | 10:00 | 10 | 571 | 1392 | 130 | 1 | 9 | 2 | 1 | 9 | 129 | 1 | 13 | 14900 | 1 | 9 | 100 | 1 | 9 | 14900 | 1 | 13 | 5230 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 997 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 2 | 0
1979-11-06 | 1900-11-05 | 11:00 | 11 | 708 | 1392 | 220 | 1 | 9 | 9 | 1 | 9 | 215 | 1 | 13 | 24900 | 1 | 9 | 800 | 1 | 9 | 24500 | 1 | 13 | 8420 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 997 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 2 | 0
1979-11-06 | 1900-11-05 | 12:00 | 12 | 780 | 1392 | 220 | 1 | 9 | 7 | 1 | 9 | 216 | 1 | 13 | 25200 | 1 | 9 | 600 | 1 | 9 | 24900 | 1 | 13 | 8970 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 997 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 2 | 0
1979-11-06 | 1900-11-05 | 13:00 | 13 | 783 | 1392 | 203 | 1 | 9 | 0 | 1 | 9 | 202 | 1 | 13 | 23300 | 1 | 9 | 0 | 1 | 9 | 23300 | 1 | 13 | 8570 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.55 | A | 7 | 996 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.18 | 2 | 0
1979-11-06 | 1900-11-05 | 14:00 | 14 | 716 | 1392 | 302 | 1 | 9 | 219 | 1 | 9 | 188 | 1 | 13 | 32500 | 1 | 9 | 22800 | 1 | 9 | 20700 | 1 | 13 | 4210 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 4.4 | 39.92 | A | 7 | -5 | 23 | A | 7 | 0.51 | A | 7 | 996 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.9 | 2 | 0
1979-11-06 | 1900-11-05 | 15:00 | 15 | 584 | 1392 | 293 | 1 | 13 | 373 | 1 | 13 | 134 | 1 | 13 | 30800 | 1 | 13 | 36200 | 1 | 13 | 15500 | 1 | 13 | 2640 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 5 | 41 | A | 7 | -5.6 | 21.92 | A | 7 | 0.47 | A | 7 | 995 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 2 | 0
1979-11-06 | 1900-11-05 | 16:00 | 16 | 396 | 1392 | 185 | 1 | 13 | 308 | 1 | 13 | 96 | 1 | 13 | 19200 | 1 | 13 | 26700 | 1 | 13 | 11500 | 1 | 13 | 1790 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 5 | 41 | A | 7 | -5.6 | 21.92 | A | 7 | 0.47 | A | 7 | 995 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 2 | 0
1979-11-06 | 1900-11-05 | 17:00 | 17 | 166 | 1392 | 66 | 1 | 13 | 256 | 1 | 9 | 35 | 1 | 13 | 6900 | 1 | 13 | 14700 | 1 | 9 | 5100 | 1 | 13 | 620 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 3.9 | 39.02 | A | 7 | -5 | 23 | A | 7 | 0.53 | A | 7 | 995 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.1 | 2 | 0
1979-11-06 | 1900-11-05 | 18:00 | 18 | 4 | 267 | 5 | 1 | 13 | 11 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 995 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 2 | 0
1979-11-06 | 1900-11-05 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 994 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.22 | 2 | 0
1979-11-06 | 1900-11-05 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 994 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.42 | 2 | 0
1979-11-06 | 1900-11-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 994 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.72 | 2 | 0
1979-11-06 | 1900-11-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 994 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 2 | 0
1979-11-06 | 1900-11-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.72 | A | 7 | 994 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 2 | 0
1979-11-06 | 1900-11-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 993 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 2 | 0
1979-11-07 | 1900-11-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 993 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 3 | 0
1979-11-07 | 1900-11-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 992 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 3 | 0
1979-11-07 | 1900-11-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.72 | A | 7 | 992 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.04 | 3 | 0
1979-11-07 | 1900-11-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.72 | A | 7 | 991 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 3 | 0
1979-11-07 | 1900-11-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.78 | A | 7 | 991 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 3 | 0
1979-11-07 | 1900-11-06 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 991 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 3 | 0
1979-11-07 | 1900-11-06 | 7:00 | 7 | 1 | 128 | 1 | 1 | 13 | 1 | 1 | 13 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.78 | A | 7 | 990 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 3 | 0
1979-11-07 | 1900-11-06 | 8:00 | 8 | 142 | 1393 | 50 | 1 | 13 | 70 | 1 | 13 | 43 | 1 | 13 | 5400 | 1 | 13 | 3900 | 1 | 13 | 5000 | 1 | 13 | 900 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | -1.1 | 30.02 | A | 7 | -5 | 23 | A | 7 | 0.75 | A | 7 | 990 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.9 | 3 | 0
1979-11-07 | 1900-11-06 | 9:00 | 9 | 374 | 1393 | 122 | 1 | 9 | 106 | 1 | 9 | 94 | 1 | 13 | 13400 | 1 | 9 | 9300 | 1 | 9 | 10900 | 1 | 13 | 2070 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -3.9 | 24.98 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 2440 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 3 | 0
1979-11-07 | 1900-11-06 | 10:00 | 10 | 566 | 1393 | 177 | 1 | 9 | 4 | 1 | 9 | 175 | 1 | 13 | 19800 | 1 | 9 | 300 | 1 | 9 | 19700 | 1 | 13 | 6400 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.7 | A | 7 | 987 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 4570 | A | 7 | 0.9 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.28 | 3 | 0
1979-11-07 | 1900-11-06 | 11:00 | 11 | 703 | 1393 | 191 | 1 | 9 | 7 | 1 | 9 | 188 | 1 | 13 | 21900 | 1 | 9 | 600 | 1 | 9 | 21600 | 1 | 13 | 7660 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 2130 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.78 | 3 | 0
1979-11-07 | 1900-11-06 | 12:00 | 12 | 775 | 1393 | 236 | 1 | 9 | 3 | 1 | 9 | 234 | 1 | 13 | 26800 | 1 | 9 | 300 | 1 | 9 | 26700 | 1 | 13 | 9420 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.65 | A | 7 | 985 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 2130 | A | 7 | 0.9 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.86 | 3 | 0
1979-11-07 | 1900-11-06 | 13:00 | 13 | 778 | 1393 | 212 | 1 | 9 | 9 | 1 | 9 | 207 | 1 | 13 | 24400 | 1 | 9 | 800 | 1 | 9 | 24000 | 1 | 13 | 8690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 984 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 2130 | A | 7 | 0.9 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 3 | 0
1979-11-07 | 1900-11-06 | 14:00 | 14 | 711 | 1393 | 193 | 1 | 9 | 1 | 1 | 9 | 193 | 1 | 13 | 22100 | 1 | 9 | 100 | 1 | 9 | 22100 | 1 | 13 | 7850 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 8000 | A | 7 | 2130 | A | 7 | 0.9 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 3 | 0
1979-11-07 | 1900-11-06 | 15:00 | 15 | 579 | 1393 | 114 | 1 | 9 | 3 | 1 | 9 | 113 | 1 | 13 | 13300 | 1 | 9 | 200 | 1 | 9 | 13200 | 1 | 13 | 4750 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 6400 | A | 7 | 700 | A | 7 | 1 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 3 | 0
1979-11-07 | 1900-11-06 | 16:00 | 16 | 391 | 1393 | 63 | 1 | 9 | 2 | 1 | 9 | 62 | 1 | 13 | 7300 | 1 | 9 | 100 | 1 | 9 | 7300 | 1 | 13 | 2510 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 6400 | A | 7 | 640 | A | 7 | 1 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.42 | 3 | 0
1979-11-07 | 1900-11-06 | 17:00 | 17 | 161 | 1393 | 45 | 1 | 13 | 1 | 1 | 9 | 45 | 1 | 13 | 5000 | 1 | 13 | 0 | 1 | 9 | 5000 | 1 | 13 | 1420 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 240 | A | 7 | 1.1 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.7 | 3 | 0
1979-11-07 | 1900-11-06 | 18:00 | 18 | 3 | 244 | 2 | 1 | 13 | 0 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 670 | A | 7 | 1.1 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 3 | 0
1979-11-07 | 1900-11-06 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 760 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 3 | 0
1979-11-07 | 1900-11-06 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 3 | 0
1979-11-07 | 1900-11-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.86 | A | 7 | 978 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.38 | 3 | 0
1979-11-07 | 1900-11-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 3 | 0
1979-11-07 | 1900-11-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 3 | 0
1979-11-07 | 1900-11-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 580 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 3 | 0
1979-11-08 | 1900-11-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 700 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 4 | 0
1979-11-08 | 1900-11-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 6 | A | 7 | 3.9 | 39.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 700 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 4 | 0
1979-11-08 | 1900-11-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 4 | A | 7 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.7 | 4 | 0
1979-11-08 | 1900-11-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 700 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.38 | 4 | 0
1979-11-08 | 1900-11-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 760 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.38 | 4 | 0
1979-11-08 | 1900-11-07 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 820 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.38 | 4 | 0
1979-11-08 | 1900-11-07 | 7:00 | 7 | 1 | 105 | 3 | 1 | 13 | 1 | 1 | 13 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 2400 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.1 | 4 | 0
1979-11-08 | 1900-11-07 | 8:00 | 8 | 137 | 1393 | 21 | 1 | 13 | 2 | 1 | 9 | 21 | 1 | 13 | 2500 | 1 | 13 | 0 | 1 | 9 | 2500 | 1 | 13 | 770 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 2400 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.38 | 4 | 0
1979-11-08 | 1900-11-07 | 9:00 | 9 | 369 | 1393 | 109 | 1 | 9 | 7 | 1 | 9 | 107 | 1 | 13 | 12100 | 1 | 9 | 400 | 1 | 9 | 12000 | 1 | 13 | 3650 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 3200 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.38 | 4 | 0
1979-11-08 | 1900-11-07 | 10:00 | 10 | 560 | 1393 | 146 | 1 | 9 | 9 | 1 | 9 | 142 | 1 | 13 | 16600 | 1 | 9 | 600 | 1 | 9 | 16300 | 1 | 13 | 5550 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 4800 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 4 | 0
1979-11-08 | 1900-11-07 | 11:00 | 11 | 697 | 1393 | 223 | 1 | 9 | 8 | 1 | 9 | 219 | 1 | 13 | 25200 | 1 | 9 | 700 | 1 | 9 | 24800 | 1 | 13 | 8430 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 240 | A | 7 | 1.1 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 4 | 0
1979-11-08 | 1900-11-07 | 12:00 | 12 | 769 | 1393 | 259 | 1 | 9 | 2 | 1 | 9 | 258 | 1 | 13 | 29300 | 1 | 9 | 200 | 1 | 9 | 29100 | 1 | 13 | 9960 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 1.1 | 33.98 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.18 | 4 | 0
1979-11-08 | 1900-11-07 | 13:00 | 13 | 772 | 1393 | 260 | 1 | 9 | 9 | 1 | 9 | 255 | 1 | 13 | 29400 | 1 | 9 | 800 | 1 | 9 | 28900 | 1 | 13 | 9920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.73 | A | 7 | 974 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 370 | A | 7 | 1.1 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.78 | 4 | 0
1979-11-08 | 1900-11-07 | 14:00 | 14 | 705 | 1393 | 278 | 1 | 9 | 1 | 1 | 9 | 277 | 1 | 13 | 30800 | 1 | 9 | 100 | 1 | 9 | 30700 | 1 | 13 | 9690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.76 | A | 7 | 973 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 520 | A | 7 | 1.2 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.26 | 4 | 0
1979-11-08 | 1900-11-07 | 15:00 | 15 | 574 | 1393 | 186 | 1 | 9 | 1 | 1 | 9 | 185 | 1 | 13 | 20700 | 1 | 9 | 100 | 1 | 9 | 20700 | 1 | 13 | 6670 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.76 | A | 7 | 972 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 370 | A | 7 | 1.2 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.26 | 4 | 0
1979-11-08 | 1900-11-07 | 16:00 | 16 | 386 | 1393 | 129 | 1 | 9 | 1 | 1 | 9 | 128 | 1 | 13 | 14100 | 1 | 9 | 100 | 1 | 9 | 14100 | 1 | 13 | 4160 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 972 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 460 | A | 7 | 1.2 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 4 | 0
1979-11-08 | 1900-11-07 | 17:00 | 17 | 157 | 1393 | 52 | 1 | 13 | 0 | 1 | 9 | 52 | 1 | 13 | 5600 | 1 | 13 | 0 | 1 | 9 | 5600 | 1 | 13 | 1510 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 971 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 490 | A | 7 | 1.2 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 4 | 0
1979-11-08 | 1900-11-07 | 18:00 | 18 | 3 | 221 | 4 | 1 | 13 | 0 | 1 | 9 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 970 | A | 7 | 80 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 550 | A | 7 | 1.2 | E | 8 | 0.037 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 4 | 0
1979-11-08 | 1900-11-07 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 970 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 400 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 4 | 0
1979-11-08 | 1900-11-07 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.76 | A | 7 | 970 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 370 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.26 | 4 | 0
1979-11-08 | 1900-11-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.76 | A | 7 | 970 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 310 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.26 | 4 | 0
1979-11-08 | 1900-11-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 969 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 270 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 4 | 0
1979-11-08 | 1900-11-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.83 | A | 7 | 969 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.94 | 4 | 0
1979-11-08 | 1900-11-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.86 | A | 7 | 968 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.24 | 4 | 0
1979-11-09 | 1900-11-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.83 | A | 7 | 968 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.84 | 5 | 0
1979-11-09 | 1900-11-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 3.3 | 37.94 | A | 7 | 0.83 | A | 7 | 967 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 150 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.84 | 5 | 0
1979-11-09 | 1900-11-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 2.8 | 37.04 | A | 7 | 0.83 | A | 7 | 967 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 3200 | A | 7 | 120 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.94 | 5 | 0
1979-11-09 | 1900-11-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.86 | A | 7 | 967 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 2800 | A | 7 | 60 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.24 | 5 | 0
1979-11-09 | 1900-11-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 3.3 | 37.94 | A | 7 | 0.86 | A | 7 | 968 | A | 7 | 360 | A | 7 | 5.7 | A | 7 | 2800 | A | 7 | 60 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.24 | 5 | 0
1979-11-09 | 1900-11-08 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 2.8 | 37.04 | A | 7 | 0.86 | A | 7 | 968 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 2800 | A | 7 | 60 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.34 | 5 | 0
1979-11-09 | 1900-11-08 | 7:00 | 7 | 0 | 81 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 2.2 | 35.96 | A | 7 | 0.86 | A | 7 | 969 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 2800 | A | 7 | 120 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.26 | 5 | 0
1979-11-09 | 1900-11-08 | 8:00 | 8 | 132 | 1394 | 39 | 1 | 13 | 0 | 1 | 9 | 39 | 1 | 13 | 4300 | 1 | 13 | 0 | 1 | 9 | 4300 | 1 | 13 | 1190 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 2.2 | 35.96 | A | 7 | 0.86 | A | 7 | 969 | A | 7 | 340 | A | 7 | 6.7 | A | 7 | 4000 | A | 7 | 210 | A | 7 | 1.2 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.26 | 5 | 0
1979-11-09 | 1900-11-08 | 9:00 | 9 | 363 | 1394 | 129 | 1 | 9 | 0 | 1 | 9 | 129 | 1 | 13 | 14100 | 1 | 9 | 0 | 1 | 9 | 14100 | 1 | 13 | 4000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.7 | 35.06 | A | 7 | 0.82 | A | 7 | 970 | A | 7 | 340 | A | 7 | 8.2 | A | 7 | 4000 | A | 7 | 340 | A | 7 | 1.1 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.96 | 5 | 0
1979-11-09 | 1900-11-08 | 10:00 | 10 | 555 | 1394 | 193 | 1 | 9 | 1 | 1 | 9 | 193 | 1 | 13 | 21400 | 1 | 9 | 100 | 1 | 9 | 21400 | 1 | 13 | 6680 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.76 | A | 7 | 970 | A | 7 | 320 | A | 7 | 6.7 | A | 7 | 4000 | A | 7 | 400 | A | 7 | 1.1 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.38 | 5 | 0
1979-11-09 | 1900-11-08 | 11:00 | 11 | 692 | 1394 | 493 | 1 | 9 | 845 | 1 | 9 | 70 | 1 | 13 | 51300 | 1 | 9 | 82200 | 1 | 9 | 10400 | 1 | 13 | 1540 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 971 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 5 | 0
1979-11-09 | 1900-11-08 | 12:00 | 12 | 764 | 1394 | 566 | 1 | 9 | 887 | 1 | 9 | 76 | 1 | 13 | 58900 | 1 | 9 | 87100 | 1 | 9 | 11000 | 1 | 13 | 1700 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.49 | A | 7 | 971 | A | 7 | 340 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.48 | 5 | 0
1979-11-09 | 1900-11-08 | 13:00 | 13 | 767 | 1394 | 568 | 1 | 9 | 875 | 1 | 9 | 82 | 1 | 13 | 58900 | 1 | 9 | 85900 | 1 | 9 | 11400 | 1 | 13 | 1730 | 1 | 18 | 3 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.49 | A | 7 | 971 | A | 7 | 310 | A | 7 | 10.3 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.68 | 5 | 0
1979-11-09 | 1900-11-08 | 14:00 | 14 | 700 | 1394 | 513 | 1 | 9 | 871 | 1 | 9 | 71 | 1 | 13 | 53300 | 1 | 9 | 84900 | 1 | 9 | 10600 | 1 | 13 | 1560 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.43 | A | 7 | 972 | A | 7 | 320 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.52 | 5 | 0
1979-11-09 | 1900-11-08 | 15:00 | 15 | 569 | 1394 | 401 | 1 | 9 | 839 | 1 | 9 | 55 | 1 | 13 | 41900 | 1 | 9 | 79700 | 1 | 9 | 9300 | 1 | 13 | 1270 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -6.7 | 19.94 | A | 7 | 0.43 | A | 7 | 973 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.64 | 5 | 0
1979-11-09 | 1900-11-08 | 16:00 | 16 | 381 | 1394 | 207 | 1 | 9 | 496 | 1 | 9 | 69 | 1 | 13 | 21100 | 1 | 9 | 42500 | 1 | 9 | 9500 | 1 | 13 | 1270 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 3.3 | 37.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.44 | A | 7 | 973 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.96 | 5 | 0
1979-11-09 | 1900-11-08 | 17:00 | 17 | 152 | 1394 | 70 | 1 | 13 | 371 | 1 | 9 | 28 | 1 | 13 | 7000 | 1 | 13 | 21800 | 1 | 9 | 4600 | 1 | 13 | 500 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 2.2 | 35.96 | A | 7 | -8.3 | 17.06 | A | 7 | 0.46 | A | 7 | 975 | A | 7 | 330 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.36 | 5 | 0
1979-11-09 | 1900-11-08 | 18:00 | 18 | 2 | 197 | 3 | 1 | 13 | 5 | 1 | 13 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 0.6 | 33.08 | A | 7 | -9.4 | 15.08 | A | 7 | 0.48 | A | 7 | 976 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 0.6 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.78 | 5 | 0
1979-11-09 | 1900-11-08 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.52 | A | 7 | 976 | A | 7 | 340 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.76 | 5 | 0
1979-11-09 | 1900-11-08 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -9.4 | 15.08 | A | 7 | 0.48 | A | 7 | 977 | A | 7 | 320 | A | 7 | 9.8 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.78 | 5 | 0
1979-11-09 | 1900-11-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -8.9 | 15.98 | A | 7 | 0.52 | A | 7 | 978 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.78 | 5 | 0
1979-11-09 | 1900-11-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.54 | A | 7 | 978 | A | 7 | 320 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.98 | 5 | 0
1979-11-09 | 1900-11-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.08 | 5 | 0
1979-11-09 | 1900-11-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.58 | A | 7 | 979 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.16 | 5 | 0
1979-11-10 | 1900-11-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 1040 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.06 | 6 | 0
1979-11-10 | 1900-11-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.56 | A | 7 | 980 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 1040 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.08 | 6 | 0
1979-11-10 | 1900-11-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -1.7 | 28.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 1070 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.18 | 6 | 0
1979-11-10 | 1900-11-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -8.3 | 17.06 | A | 7 | 0.66 | A | 7 | 981 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 1010 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.76 | 6 | 0
1979-11-10 | 1900-11-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.63 | A | 7 | 982 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 1040 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.56 | 6 | 0
1979-11-10 | 1900-11-09 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.63 | A | 7 | 982 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 1220 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.56 | 6 | 0
1979-11-10 | 1900-11-09 | 7:00 | 7 | 0 | 58 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.66 | A | 7 | 982 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 1040 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 6 | 0
1979-11-10 | 1900-11-09 | 8:00 | 8 | 128 | 1395 | 52 | 1 | 13 | 275 | 1 | 9 | 26 | 1 | 13 | 5200 | 1 | 13 | 14700 | 1 | 9 | 3900 | 1 | 13 | 460 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | -3.3 | 26.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.66 | A | 7 | 983 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 40200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 6 | 0
1979-11-10 | 1900-11-09 | 9:00 | 9 | 358 | 1395 | 192 | 1 | 9 | 527 | 1 | 9 | 55 | 1 | 13 | 19900 | 1 | 9 | 44600 | 1 | 9 | 8400 | 1 | 13 | 1040 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -2.8 | 26.96 | A | 7 | -7.8 | 17.96 | A | 7 | 0.69 | A | 7 | 984 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 6 | 0
1979-11-10 | 1900-11-09 | 10:00 | 10 | 550 | 1395 | 306 | 1 | 13 | 444 | 1 | 13 | 130 | 1 | 13 | 32200 | 1 | 13 | 42500 | 1 | 13 | 15400 | 1 | 13 | 2540 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 6 | 0
1979-11-10 | 1900-11-09 | 11:00 | 11 | 686 | 1395 | 452 | 1 | 13 | 620 | 1 | 13 | 145 | 1 | 13 | 46500 | 1 | 13 | 60300 | 1 | 13 | 16700 | 1 | 13 | 2940 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 0 | 32 | A | 7 | -11.7 | 10.94 | A | 7 | 0.42 | A | 7 | 985 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.74 | 6 | 0
1979-11-10 | 1900-11-09 | 12:00 | 12 | 758 | 1395 | 380 | 1 | 13 | 309 | 1 | 13 | 210 | 1 | 13 | 40800 | 1 | 13 | 32500 | 1 | 13 | 23100 | 1 | 13 | 4870 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 0.6 | 33.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.4 | A | 7 | 984 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.64 | 6 | 0
1979-11-10 | 1900-11-09 | 13:00 | 13 | 762 | 1395 | 488 | 1 | 13 | 665 | 1 | 13 | 122 | 1 | 13 | 51300 | 1 | 13 | 66400 | 1 | 13 | 14900 | 1 | 13 | 2740 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 1.1 | 33.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.4 | A | 7 | 984 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.62 | 6 | 0
1979-11-10 | 1900-11-09 | 14:00 | 14 | 695 | 1395 | 482 | 1 | 9 | 846 | 1 | 9 | 56 | 1 | 13 | 50500 | 1 | 9 | 82500 | 1 | 9 | 9200 | 1 | 13 | 1420 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 1.7 | 35.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.35 | A | 7 | 984 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.64 | 6 | 0
1979-11-10 | 1900-11-09 | 15:00 | 15 | 564 | 1395 | 381 | 1 | 9 | 798 | 1 | 9 | 55 | 1 | 13 | 39800 | 1 | 9 | 75700 | 1 | 9 | 9100 | 1 | 13 | 1260 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 2.2 | 35.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.35 | A | 7 | 984 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.44 | 6 | 0
1979-11-10 | 1900-11-09 | 16:00 | 16 | 377 | 1395 | 243 | 1 | 9 | 746 | 1 | 9 | 38 | 1 | 13 | 25400 | 1 | 9 | 65600 | 1 | 9 | 7600 | 1 | 13 | 900 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.34 | A | 7 | 984 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.54 | 6 | 0
1979-11-10 | 1900-11-09 | 17:00 | 17 | 148 | 1395 | 73 | 1 | 13 | 460 | 1 | 9 | 23 | 1 | 13 | 7300 | 1 | 13 | 29100 | 1 | 9 | 4200 | 1 | 13 | 440 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.4 | A | 7 | 984 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.62 | 6 | 0
1979-11-10 | 1900-11-09 | 18:00 | 18 | 2 | 174 | 5 | 1 | 13 | 17 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -1.7 | 28.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.49 | A | 7 | 984 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.12 | 6 | 0
1979-11-10 | 1900-11-09 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -10.6 | 12.92 | A | 7 | 0.55 | A | 7 | 985 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 6 | 0
1979-11-10 | 1900-11-09 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -10 | 14 | A | 7 | 0.47 | A | 7 | 985 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.8 | 6 | 0
1979-11-10 | 1900-11-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 6 | 0
1979-11-10 | 1900-11-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.54 | A | 7 | 985 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.18 | 6 | 0
1979-11-10 | 1900-11-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.54 | A | 7 | 985 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.18 | 6 | 0
1979-11-10 | 1900-11-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.54 | A | 7 | 985 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.18 | 6 | 0
1979-11-11 | 1900-11-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -10 | 14 | A | 7 | 0.53 | A | 7 | 985 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.1 | 7 | 0
1979-11-11 | 1900-11-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 7 | 0
1979-11-11 | 1900-11-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 7 | 0
1979-11-11 | 1900-11-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 7 | 0
1979-11-11 | 1900-11-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 7 | 0
1979-11-11 | 1900-11-10 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.58 | A | 7 | 985 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.18 | 7 | 0
1979-11-11 | 1900-11-10 | 7:00 | 7 | 0 | 35 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.58 | A | 7 | 985 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.18 | 7 | 0
1979-11-11 | 1900-11-10 | 8:00 | 8 | 123 | 1395 | 44 | 1 | 13 | 148 | 1 | 9 | 30 | 1 | 13 | 4500 | 1 | 13 | 7000 | 1 | 9 | 3800 | 1 | 13 | 540 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.58 | A | 7 | 986 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.16 | 7 | 0
1979-11-11 | 1900-11-10 | 9:00 | 9 | 353 | 1395 | 192 | 1 | 13 | 507 | 1 | 9 | 63 | 1 | 13 | 19800 | 1 | 13 | 42400 | 1 | 9 | 9000 | 1 | 13 | 1160 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.52 | A | 7 | 987 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.76 | 7 | 0
1979-11-11 | 1900-11-10 | 10:00 | 10 | 544 | 1395 | 355 | 1 | 9 | 674 | 1 | 9 | 90 | 1 | 13 | 36900 | 1 | 9 | 63700 | 1 | 9 | 12000 | 1 | 13 | 1770 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 2.8 | 37.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.44 | A | 7 | 987 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.26 | 7 | 0
1979-11-11 | 1900-11-10 | 11:00 | 11 | 681 | 1395 | 455 | 1 | 9 | 705 | 1 | 9 | 109 | 1 | 13 | 47800 | 1 | 9 | 69400 | 1 | 9 | 13800 | 1 | 13 | 2310 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 4.4 | 39.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.39 | A | 7 | 987 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.86 | 7 | 0
1979-11-11 | 1900-11-10 | 12:00 | 12 | 753 | 1395 | 480 | 1 | 9 | 612 | 1 | 9 | 147 | 1 | 13 | 49800 | 1 | 9 | 60500 | 1 | 9 | 17000 | 1 | 13 | 3180 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 6.1 | 42.98 | A | 7 | -7.8 | 17.96 | A | 7 | 0.37 | A | 7 | 986 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.46 | 7 | 0
1979-11-11 | 1900-11-10 | 13:00 | 13 | 756 | 1395 | 490 | 1 | 9 | 630 | 1 | 9 | 145 | 1 | 13 | 50800 | 1 | 9 | 62300 | 1 | 9 | 16900 | 1 | 13 | 3150 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 7.2 | 44.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.35 | A | 7 | 985 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.24 | 7 | 0
1979-11-11 | 1900-11-10 | 14:00 | 14 | 690 | 1395 | 446 | 1 | 9 | 559 | 1 | 9 | 167 | 1 | 13 | 47000 | 1 | 9 | 55900 | 1 | 9 | 19200 | 1 | 13 | 3510 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 8.3 | 46.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.36 | A | 7 | 984 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.02 | 7 | 0
1979-11-11 | 1900-11-10 | 15:00 | 15 | 559 | 1395 | 333 | 1 | 9 | 515 | 1 | 9 | 124 | 1 | 13 | 35100 | 1 | 9 | 49500 | 1 | 9 | 15200 | 1 | 13 | 2410 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | 8.3 | 46.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.34 | A | 7 | 984 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.94 | 7 | 0
1979-11-11 | 1900-11-10 | 16:00 | 16 | 372 | 1395 | 176 | 1 | 13 | 305 | 1 | 13 | 93 | 1 | 13 | 18100 | 1 | 13 | 25800 | 1 | 13 | 11200 | 1 | 13 | 1730 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 8.3 | 46.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.34 | A | 7 | 984 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.94 | 7 | 0
1979-11-11 | 1900-11-10 | 17:00 | 17 | 144 | 1395 | 53 | 1 | 13 | 86 | 1 | 13 | 44 | 1 | 13 | 5700 | 1 | 13 | 4800 | 1 | 13 | 5200 | 1 | 13 | 920 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 7.2 | 44.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.37 | A | 7 | 984 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.14 | 7 | 0
1979-11-11 | 1900-11-10 | 18:00 | 18 | 1 | 151 | 1 | 1 | 13 | 0 | 1 | 13 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 3.9 | 39.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.46 | A | 7 | 985 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.84 | 7 | 0
1979-11-11 | 1900-11-10 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 3.9 | 39.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.46 | A | 7 | 985 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.84 | 7 | 0
1979-11-11 | 1900-11-10 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 2.8 | 37.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.5 | A | 7 | 985 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.14 | 7 | 0
1979-11-11 | 1900-11-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 4 | A | 7 | 2.8 | 37.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.55 | A | 7 | 985 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.32 | 7 | 0
1979-11-11 | 1900-11-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 3.9 | 39.02 | A | 7 | -5 | 23 | A | 7 | 0.53 | A | 7 | 985 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.1 | 7 | 0
1979-11-11 | 1900-11-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -5 | 23 | A | 7 | 0.53 | A | 7 | 985 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.1 | 7 | 0
1979-11-11 | 1900-11-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.51 | A | 7 | 985 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 7 | 0
1979-11-12 | 1900-11-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.55 | A | 7 | 987 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.18 | 1 | 0
1979-11-12 | 1900-11-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 987 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.38 | 1 | 0
1979-11-12 | 1900-11-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.59 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.58 | 1 | 0
1979-11-12 | 1900-11-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 2.8 | 37.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.62 | A | 7 | 987 | A | 7 | 30 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.58 | 1 | 0
1979-11-12 | 1900-11-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.65 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 400 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.86 | 1 | 0
1979-11-12 | 1900-11-11 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.79 | A | 7 | 987 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 270 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.72 | 1 | 0
1979-11-12 | 1900-11-11 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.79 | A | 7 | 987 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.72 | 1 | 0
1979-11-12 | 1900-11-11 | 8:00 | 8 | 118 | 1384 | 11 | 1 | 13 | 1 | 1 | 9 | 11 | 1 | 13 | 1300 | 1 | 13 | 0 | 1 | 9 | 1300 | 1 | 13 | 430 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.82 | A | 7 | 987 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 310 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.02 | 1 | 0
1979-11-12 | 1900-11-11 | 9:00 | 9 | 348 | 1396 | 41 | 1 | 13 | 7 | 1 | 9 | 39 | 1 | 13 | 4900 | 1 | 13 | 200 | 1 | 9 | 4800 | 1 | 13 | 1630 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 987 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 180 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.1 | 1 | 0
1979-11-12 | 1900-11-11 | 10:00 | 10 | 539 | 1396 | 99 | 1 | 9 | 4 | 1 | 9 | 97 | 1 | 13 | 11500 | 1 | 9 | 200 | 1 | 9 | 11400 | 1 | 13 | 4080 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 987 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 4000 | A | 7 | 180 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.1 | 1 | 0
1979-11-12 | 1900-11-11 | 11:00 | 11 | 675 | 1396 | 183 | 1 | 9 | 8 | 1 | 9 | 179 | 1 | 13 | 20900 | 1 | 9 | 600 | 1 | 9 | 20600 | 1 | 13 | 7230 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 987 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 4000 | A | 7 | 240 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 1 | 0
1979-11-12 | 1900-11-11 | 12:00 | 12 | 748 | 1396 | 198 | 1 | 9 | 1 | 1 | 9 | 198 | 1 | 13 | 22800 | 1 | 9 | 100 | 1 | 9 | 22800 | 1 | 13 | 8220 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 987 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 240 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 1 | 0
1979-11-12 | 1900-11-11 | 13:00 | 13 | 751 | 1396 | 224 | 1 | 9 | 8 | 1 | 9 | 220 | 1 | 13 | 25600 | 1 | 9 | 700 | 1 | 9 | 25200 | 1 | 13 | 8860 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 610 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 1 | 0
1979-11-12 | 1900-11-11 | 14:00 | 14 | 685 | 1396 | 201 | 1 | 9 | 26 | 1 | 9 | 188 | 1 | 13 | 22900 | 1 | 9 | 2100 | 1 | 9 | 21900 | 1 | 13 | 7540 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 5 | 41 | A | 7 | 1.7 | 35.06 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 460 | A | 7 | 1.2 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.66 | 1 | 0
1979-11-12 | 1900-11-11 | 15:00 | 15 | 554 | 1396 | 235 | 1 | 13 | 247 | 1 | 13 | 135 | 1 | 13 | 25100 | 1 | 13 | 24400 | 1 | 13 | 15400 | 1 | 13 | 2750 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 6.1 | 42.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.68 | A | 7 | 986 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 760 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.48 | 1 | 0
1979-11-12 | 1900-11-11 | 16:00 | 16 | 368 | 1396 | 85 | 1 | 9 | 33 | 1 | 9 | 76 | 1 | 13 | 9300 | 1 | 9 | 2900 | 1 | 9 | 8500 | 1 | 13 | 2070 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 5.6 | 42.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.65 | A | 7 | 986 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 700 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.22 | 1 | 0
1979-11-12 | 1900-11-11 | 17:00 | 17 | 140 | 1396 | 41 | 1 | 13 | 76 | 1 | 9 | 33 | 1 | 13 | 4300 | 1 | 13 | 3700 | 1 | 9 | 3900 | 1 | 13 | 600 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 5 | 41 | A | 7 | 0 | 32 | A | 7 | 0.7 | A | 7 | 986 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 1680 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.8 | 1 | 0
1979-11-12 | 1900-11-11 | 18:00 | 18 | 1 | 128 | 2 | 1 | 13 | 0 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 4.4 | 39.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.7 | A | 7 | 987 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1160 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.72 | 1 | 0
1979-11-12 | 1900-11-11 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.7 | A | 7 | 988 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 1160 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.92 | 1 | 0
1979-11-12 | 1900-11-11 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 3.3 | 37.94 | A | 7 | -1.1 | 30.02 | A | 7 | 0.73 | A | 7 | 988 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 1160 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.22 | 1 | 0
1979-11-12 | 1900-11-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 1.7 | 35.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.76 | A | 7 | 988 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.74 | 1 | 0
1979-11-12 | 1900-11-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 1.1 | 33.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.79 | A | 7 | 989 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.04 | 1 | 0
1979-11-12 | 1900-11-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | 1.7 | 35.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.76 | A | 7 | 989 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 340 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.74 | 1 | 0
1979-11-12 | 1900-11-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 989 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 340 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 1 | 0
1979-11-13 | 1900-11-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 240 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 2 | 0
1979-11-13 | 1900-11-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 240 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 2 | 0
1979-11-13 | 1900-11-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 2 | 0
1979-11-13 | 1900-11-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -3.9 | 24.98 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 180 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 2 | 0
1979-11-13 | 1900-11-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -3.9 | 24.98 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 180 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 2 | 0
1979-11-13 | 1900-11-12 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 180 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 2 | 0
1979-11-13 | 1900-11-12 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 180 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 2 | 0
1979-11-13 | 1900-11-12 | 8:00 | 8 | 113 | 1362 | 42 | 1 | 13 | 18 | 1 | 9 | 40 | 1 | 13 | 4500 | 1 | 13 | 1100 | 1 | 9 | 4400 | 1 | 13 | 890 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.78 | A | 7 | 989 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 2 | 0
1979-11-13 | 1900-11-12 | 9:00 | 9 | 343 | 1397 | 115 | 1 | 13 | 74 | 1 | 9 | 96 | 1 | 13 | 12500 | 1 | 13 | 6400 | 1 | 9 | 10900 | 1 | 13 | 2430 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 990 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.38 | 2 | 0
1979-11-13 | 1900-11-12 | 10:00 | 10 | 534 | 1397 | 164 | 1 | 9 | 58 | 1 | 9 | 141 | 1 | 13 | 17900 | 1 | 9 | 5500 | 1 | 9 | 15800 | 1 | 13 | 3990 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.78 | A | 7 | 990 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 2 | 0
1979-11-13 | 1900-11-12 | 11:00 | 11 | 670 | 1397 | 378 | 1 | 13 | 410 | 1 | 13 | 180 | 1 | 13 | 39400 | 1 | 13 | 40700 | 1 | 13 | 19800 | 1 | 13 | 3780 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 1.1 | 33.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 990 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 2 | 0
1979-11-13 | 1900-11-12 | 12:00 | 12 | 743 | 1397 | 548 | 1 | 9 | 906 | 1 | 9 | 63 | 1 | 13 | 57400 | 1 | 9 | 88900 | 1 | 9 | 9900 | 1 | 13 | 1560 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 2 | 0
1979-11-13 | 1900-11-12 | 13:00 | 13 | 746 | 1397 | 554 | 1 | 9 | 911 | 1 | 9 | 63 | 1 | 13 | 57900 | 1 | 9 | 89400 | 1 | 9 | 10000 | 1 | 13 | 1560 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.51 | A | 7 | 989 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 2 | 0
1979-11-13 | 1900-11-12 | 14:00 | 14 | 680 | 1397 | 495 | 1 | 9 | 886 | 1 | 9 | 59 | 1 | 13 | 51700 | 1 | 9 | 86200 | 1 | 9 | 9600 | 1 | 13 | 1440 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.46 | A | 7 | 988 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.06 | 2 | 0
1979-11-13 | 1900-11-12 | 15:00 | 15 | 550 | 1397 | 384 | 1 | 9 | 836 | 1 | 9 | 50 | 1 | 13 | 40100 | 1 | 9 | 79100 | 1 | 9 | 8800 | 1 | 13 | 1200 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.44 | A | 7 | 988 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.66 | 2 | 0
1979-11-13 | 1900-11-12 | 16:00 | 16 | 363 | 1397 | 229 | 1 | 9 | 720 | 1 | 9 | 38 | 1 | 13 | 23900 | 1 | 9 | 62800 | 1 | 9 | 7500 | 1 | 13 | 880 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.46 | A | 7 | 987 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.74 | 2 | 0
1979-11-13 | 1900-11-12 | 17:00 | 17 | 136 | 1397 | 64 | 1 | 13 | 416 | 1 | 9 | 22 | 1 | 13 | 6300 | 1 | 13 | 25500 | 1 | 9 | 3800 | 1 | 13 | 410 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.49 | A | 7 | 987 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 2 | 0
1979-11-13 | 1900-11-12 | 18:00 | 18 | 1 | 105 | 4 | 1 | 13 | 11 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.57 | A | 7 | 988 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 2 | 0
1979-11-13 | 1900-11-12 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 988 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 2 | 0
1979-11-13 | 1900-11-12 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 988 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 2 | 0
1979-11-13 | 1900-11-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 988 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.78 | 2 | 0
1979-11-13 | 1900-11-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.56 | 2 | 0
1979-11-13 | 1900-11-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 989 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.08 | 2 | 0
1979-11-13 | 1900-11-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 989 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.08 | 2 | 0
1979-11-14 | 1900-11-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -4.4 | 24.08 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.68 | 3 | 0
1979-11-14 | 1900-11-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 989 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.42 | 3 | 0
1979-11-14 | 1900-11-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5 | 23 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.7 | 3 | 0
1979-11-14 | 1900-11-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -3.9 | 24.98 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 3 | 0
1979-11-14 | 1900-11-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 3 | 0
1979-11-14 | 1900-11-13 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 3 | 0
1979-11-14 | 1900-11-13 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -4.4 | 24.08 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.68 | 3 | 0
1979-11-14 | 1900-11-13 | 8:00 | 8 | 109 | 1339 | 39 | 1 | 13 | 126 | 1 | 9 | 27 | 1 | 13 | 4000 | 1 | 13 | 5900 | 1 | 9 | 3400 | 1 | 13 | 480 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.72 | A | 7 | 990 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 3 | 0
1979-11-14 | 1900-11-13 | 9:00 | 9 | 338 | 1397 | 180 | 1 | 13 | 481 | 1 | 9 | 62 | 1 | 13 | 18400 | 1 | 13 | 39500 | 1 | 9 | 8800 | 1 | 13 | 1130 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 991 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 3 | 0
1979-11-14 | 1900-11-13 | 10:00 | 10 | 528 | 1397 | 336 | 1 | 9 | 655 | 1 | 9 | 86 | 1 | 13 | 34900 | 1 | 9 | 61500 | 1 | 9 | 11600 | 1 | 13 | 1690 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.58 | A | 7 | 991 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.94 | 3 | 0
1979-11-14 | 1900-11-13 | 11:00 | 11 | 665 | 1397 | 454 | 1 | 9 | 735 | 1 | 9 | 102 | 1 | 13 | 47800 | 1 | 9 | 72200 | 1 | 9 | 13200 | 1 | 13 | 2150 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.56 | A | 7 | 991 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.52 | 3 | 0
1979-11-14 | 1900-11-13 | 12:00 | 12 | 738 | 1397 | 520 | 1 | 9 | 769 | 1 | 9 | 110 | 1 | 13 | 54800 | 1 | 9 | 76700 | 1 | 9 | 14100 | 1 | 13 | 2440 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.5 | A | 7 | 990 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.82 | 3 | 0
1979-11-14 | 1900-11-13 | 13:00 | 13 | 741 | 1397 | 524 | 1 | 9 | 771 | 1 | 9 | 111 | 1 | 13 | 55200 | 1 | 9 | 77000 | 1 | 9 | 14200 | 1 | 13 | 2470 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.45 | A | 7 | 989 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.32 | 3 | 0
1979-11-14 | 1900-11-13 | 14:00 | 14 | 676 | 1397 | 465 | 1 | 9 | 742 | 1 | 9 | 103 | 1 | 13 | 48900 | 1 | 9 | 73100 | 1 | 9 | 13400 | 1 | 13 | 2190 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.4 | A | 7 | 989 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.72 | 3 | 0
1979-11-14 | 1900-11-13 | 15:00 | 15 | 545 | 1397 | 351 | 1 | 9 | 665 | 1 | 9 | 88 | 1 | 13 | 36400 | 1 | 9 | 62900 | 1 | 9 | 11800 | 1 | 13 | 1740 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.4 | A | 7 | 988 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.72 | 3 | 0
1979-11-14 | 1900-11-13 | 16:00 | 16 | 359 | 1397 | 198 | 1 | 9 | 509 | 1 | 9 | 65 | 1 | 13 | 20200 | 1 | 9 | 42700 | 1 | 9 | 9200 | 1 | 13 | 1190 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.42 | A | 7 | 988 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.72 | 3 | 0
1979-11-14 | 1900-11-13 | 17:00 | 17 | 133 | 1397 | 50 | 1 | 13 | 162 | 1 | 9 | 34 | 1 | 13 | 5100 | 1 | 13 | 8100 | 1 | 9 | 4300 | 1 | 13 | 610 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.46 | A | 7 | 988 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.12 | 3 | 0
1979-11-14 | 1900-11-13 | 18:00 | 18 | 0 | 82 | 1 | 1 | 13 | 0 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.52 | A | 7 | 987 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 3 | 0
1979-11-14 | 1900-11-13 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 3 | 0
1979-11-14 | 1900-11-13 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.58 | A | 7 | 987 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.72 | 3 | 0
1979-11-14 | 1900-11-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.94 | 3 | 0
1979-11-14 | 1900-11-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.56 | A | 7 | 987 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.74 | 3 | 0
1979-11-14 | 1900-11-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 986 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 3 | 0
1979-11-14 | 1900-11-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -2.8 | 26.96 | A | 7 | 0.58 | A | 7 | 985 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.96 | 3 | 0
1979-11-15 | 1900-11-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.16 | 4 | 0
1979-11-15 | 1900-11-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.16 | 4 | 0
1979-11-15 | 1900-11-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.56 | 4 | 0
1979-11-15 | 1900-11-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 4 | 0
1979-11-15 | 1900-11-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 4 | 0
1979-11-15 | 1900-11-14 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 4 | 0
1979-11-15 | 1900-11-14 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 4 | 0
1979-11-15 | 1900-11-14 | 8:00 | 8 | 104 | 1316 | 38 | 1 | 13 | 57 | 1 | 13 | 32 | 1 | 13 | 4000 | 1 | 13 | 2900 | 1 | 13 | 3800 | 1 | 13 | 660 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 4 | 0
1979-11-15 | 1900-11-14 | 9:00 | 9 | 332 | 1398 | 179 | 1 | 13 | 512 | 1 | 9 | 57 | 1 | 13 | 18500 | 1 | 13 | 42000 | 1 | 9 | 8500 | 1 | 13 | 1050 | 1 | 21 | 9 | A | 7 | 1 | A | 7 | 7.2 | 44.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 4 | 0
1979-11-15 | 1900-11-14 | 10:00 | 10 | 523 | 1398 | 336 | 1 | 9 | 595 | 1 | 9 | 112 | 1 | 13 | 34300 | 1 | 9 | 55000 | 1 | 9 | 13700 | 1 | 13 | 2080 | 1 | 18 | 9 | A | 7 | 1 | A | 7 | 10.6 | 51.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.45 | A | 7 | 982 | A | 7 | 240 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.32 | 4 | 0
1979-11-15 | 1900-11-14 | 11:00 | 11 | 660 | 1398 | 383 | 1 | 9 | 501 | 1 | 9 | 145 | 1 | 13 | 40700 | 1 | 9 | 49800 | 1 | 9 | 17100 | 1 | 13 | 2960 | 1 | 18 | 10 | A | 7 | 2 | A | 7 | 13.3 | 55.94 | A | 7 | -1.1 | 30.02 | A | 7 | 0.37 | A | 7 | 982 | A | 7 | 240 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.42 | 4 | 0
1979-11-15 | 1900-11-14 | 12:00 | 12 | 732 | 1398 | 484 | 1 | 9 | 651 | 1 | 9 | 140 | 1 | 13 | 50200 | 1 | 9 | 64200 | 1 | 9 | 16400 | 1 | 13 | 2980 | 1 | 18 | 10 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.32 | A | 7 | 982 | A | 7 | 250 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.82 | 4 | 0
1979-11-15 | 1900-11-14 | 13:00 | 13 | 736 | 1398 | 476 | 1 | 9 | 641 | 1 | 9 | 136 | 1 | 13 | 49500 | 1 | 9 | 63300 | 1 | 9 | 16000 | 1 | 13 | 2920 | 1 | 18 | 10 | A | 7 | 2 | A | 7 | 16.7 | 62.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.29 | A | 7 | 981 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.74 | 4 | 0
1979-11-15 | 1900-11-14 | 14:00 | 14 | 671 | 1398 | 430 | 1 | 9 | 603 | 1 | 9 | 138 | 1 | 13 | 44200 | 1 | 9 | 58500 | 1 | 9 | 16000 | 1 | 13 | 2780 | 1 | 18 | 10 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.27 | A | 7 | 981 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.44 | 4 | 0
1979-11-15 | 1900-11-14 | 15:00 | 15 | 541 | 1398 | 332 | 1 | 9 | 630 | 1 | 9 | 85 | 1 | 13 | 34500 | 1 | 9 | 59600 | 1 | 9 | 11400 | 1 | 13 | 1680 | 1 | 18 | 10 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.26 | A | 7 | 981 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.34 | 4 | 0
1979-11-15 | 1900-11-14 | 16:00 | 16 | 355 | 1398 | 199 | 1 | 9 | 567 | 1 | 9 | 52 | 1 | 13 | 20600 | 1 | 9 | 47900 | 1 | 9 | 8300 | 1 | 13 | 990 | 1 | 18 | 8 | A | 7 | 1 | A | 7 | 18.3 | 64.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.26 | A | 7 | 981 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.34 | 4 | 0
1979-11-15 | 1900-11-14 | 17:00 | 17 | 129 | 1398 | 53 | 1 | 13 | 221 | 1 | 9 | 32 | 1 | 13 | 5400 | 1 | 13 | 10800 | 1 | 9 | 4400 | 1 | 13 | 580 | 1 | 21 | 8 | A | 7 | 2 | A | 7 | 15.6 | 60.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.32 | A | 7 | 982 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.82 | 4 | 0
1979-11-15 | 1900-11-14 | 18:00 | 18 | 0 | 82 | 5 | 1 | 13 | 4 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 7 | A | 7 | 1 | A | 7 | 11.1 | 51.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.43 | A | 7 | 982 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.12 | 4 | 0
1979-11-15 | 1900-11-14 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.43 | A | 7 | 983 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.12 | 4 | 0
1979-11-15 | 1900-11-14 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.45 | A | 7 | 984 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.32 | 4 | 0
1979-11-15 | 1900-11-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.48 | A | 7 | 984 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.74 | 4 | 0
1979-11-15 | 1900-11-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.56 | A | 7 | 984 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.52 | 4 | 0
1979-11-15 | 1900-11-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.58 | A | 7 | 985 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.74 | 4 | 0
1979-11-15 | 1900-11-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -1.7 | 28.94 | A | 7 | 0.62 | A | 7 | 985 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 4 | 0
1979-11-16 | 1900-11-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.62 | A | 7 | 985 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 5 | 0
1979-11-16 | 1900-11-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 985 | A | 7 | 70 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 5 | 0
1979-11-16 | 1900-11-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 986 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 5 | 0
1979-11-16 | 1900-11-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.73 | A | 7 | 986 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.56 | 5 | 0
1979-11-16 | 1900-11-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -3.3 | 26.06 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 5 | 0
1979-11-16 | 1900-11-15 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -3.3 | 26.06 | A | 7 | 0.79 | A | 7 | 987 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 5 | 0
1979-11-16 | 1900-11-15 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.78 | A | 7 | 987 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 5 | 0
1979-11-16 | 1900-11-15 | 8:00 | 8 | 100 | 1294 | 42 | 1 | 13 | 190 | 1 | 9 | 24 | 1 | 13 | 4200 | 1 | 13 | 8700 | 1 | 9 | 3500 | 1 | 13 | 420 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.79 | A | 7 | 987 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.96 | 5 | 0
1979-11-16 | 1900-11-15 | 9:00 | 9 | 327 | 1399 | 180 | 1 | 13 | 553 | 1 | 9 | 49 | 1 | 13 | 18700 | 1 | 13 | 45400 | 1 | 9 | 8000 | 1 | 13 | 920 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.76 | A | 7 | 987 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.38 | 5 | 0
1979-11-16 | 1900-11-15 | 10:00 | 10 | 518 | 1399 | 335 | 1 | 9 | 719 | 1 | 9 | 67 | 1 | 13 | 34700 | 1 | 9 | 67200 | 1 | 9 | 9600 | 1 | 13 | 1340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.59 | A | 7 | 987 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.18 | 5 | 0
1979-11-16 | 1900-11-15 | 11:00 | 11 | 655 | 1399 | 453 | 1 | 9 | 792 | 1 | 9 | 80 | 1 | 13 | 47300 | 1 | 9 | 77100 | 1 | 9 | 11100 | 1 | 13 | 1690 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.47 | A | 7 | 987 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.08 | 5 | 0
1979-11-16 | 1900-11-15 | 12:00 | 12 | 727 | 1399 | 520 | 1 | 9 | 829 | 1 | 9 | 86 | 1 | 13 | 54600 | 1 | 9 | 81800 | 1 | 9 | 11900 | 1 | 13 | 1900 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.44 | A | 7 | 987 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.38 | 5 | 0
1979-11-16 | 1900-11-15 | 13:00 | 13 | 731 | 1399 | 528 | 1 | 9 | 837 | 1 | 9 | 86 | 1 | 13 | 55400 | 1 | 9 | 82600 | 1 | 9 | 12000 | 1 | 13 | 1910 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 0.6 | 33.08 | A | 7 | 0.36 | A | 7 | 985 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.68 | 5 | 0
1979-11-16 | 1900-11-15 | 14:00 | 14 | 666 | 1399 | 470 | 1 | 9 | 809 | 1 | 9 | 81 | 1 | 13 | 49000 | 1 | 9 | 78900 | 1 | 9 | 11300 | 1 | 13 | 1720 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.33 | A | 7 | 984 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.38 | 5 | 0
1979-11-16 | 1900-11-15 | 15:00 | 15 | 537 | 1399 | 357 | 1 | 9 | 742 | 1 | 9 | 69 | 1 | 13 | 36800 | 1 | 9 | 69800 | 1 | 9 | 9900 | 1 | 13 | 1390 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 0 | 32 | A | 7 | 0.3 | A | 7 | 984 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.2 | 5 | 0
1979-11-16 | 1900-11-15 | 16:00 | 16 | 352 | 1399 | 204 | 1 | 13 | 595 | 1 | 9 | 52 | 1 | 13 | 21100 | 1 | 13 | 50100 | 1 | 9 | 8500 | 1 | 13 | 980 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 0 | 32 | A | 7 | 0.3 | A | 7 | 984 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.2 | 5 | 0
1979-11-16 | 1900-11-15 | 17:00 | 17 | 126 | 1399 | 51 | 1 | 13 | 254 | 1 | 9 | 27 | 1 | 13 | 5000 | 1 | 13 | 13400 | 1 | 9 | 3800 | 1 | 13 | 470 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 13.9 | 57.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.42 | A | 7 | 983 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.09 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.18 | 5 | 0
1979-11-16 | 1900-11-15 | 18:00 | 18 | 0 | 58 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 0 | 32 | A | 7 | 0.47 | A | 7 | 983 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.2 | 5 | 0
1979-11-16 | 1900-11-15 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 0 | 32 | A | 7 | 0.5 | A | 7 | 983 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.5 | 5 | 0
1979-11-16 | 1900-11-15 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 0.6 | 33.08 | A | 7 | 0.5 | A | 7 | 983 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.38 | 5 | 0
1979-11-16 | 1900-11-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.88 | 5 | 0
1979-11-16 | 1900-11-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 1.1 | 33.98 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.58 | 5 | 0
1979-11-16 | 1900-11-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.88 | 5 | 0
1979-11-16 | 1900-11-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.52 | 5 | 0
1979-11-17 | 1900-11-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.92 | 6 | 0
1979-11-17 | 1900-11-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -1.1 | 30.02 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.42 | 6 | 0
1979-11-17 | 1900-11-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 6 | 0
1979-11-17 | 1900-11-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 6 | 0
1979-11-17 | 1900-11-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 6 | 0
1979-11-17 | 1900-11-16 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 6 | 0
1979-11-17 | 1900-11-16 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.84 | 6 | 0
1979-11-17 | 1900-11-16 | 8:00 | 8 | 95 | 1271 | 42 | 1 | 13 | 223 | 1 | 9 | 22 | 1 | 13 | 4100 | 1 | 13 | 11300 | 1 | 9 | 3200 | 1 | 13 | 390 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -0.6 | 30.92 | A | 7 | 0.68 | A | 7 | 980 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.52 | 6 | 0
1979-11-17 | 1900-11-16 | 9:00 | 9 | 322 | 1399 | 185 | 1 | 13 | 607 | 1 | 9 | 44 | 1 | 13 | 18900 | 1 | 13 | 50400 | 1 | 9 | 7200 | 1 | 13 | 850 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 0 | 32 | A | 7 | 0.52 | A | 7 | 980 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.7 | 6 | 0
1979-11-17 | 1900-11-16 | 10:00 | 10 | 513 | 1399 | 340 | 1 | 9 | 761 | 1 | 9 | 59 | 1 | 13 | 35600 | 1 | 9 | 71400 | 1 | 9 | 9300 | 1 | 13 | 1240 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.42 | A | 7 | 980 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.48 | 6 | 0
1979-11-17 | 1900-11-16 | 11:00 | 11 | 650 | 1399 | 460 | 1 | 9 | 832 | 1 | 9 | 70 | 1 | 13 | 48600 | 1 | 9 | 81300 | 1 | 9 | 10700 | 1 | 13 | 1550 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 0 | 32 | A | 7 | 0.34 | A | 7 | 980 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.7 | 6 | 0
1979-11-17 | 1900-11-16 | 12:00 | 12 | 723 | 1399 | 525 | 1 | 9 | 863 | 1 | 9 | 76 | 1 | 13 | 54600 | 1 | 9 | 84300 | 1 | 9 | 10900 | 1 | 13 | 1610 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.33 | A | 7 | 979 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.08 | 6 | 0
1979-11-17 | 1900-11-16 | 13:00 | 13 | 727 | 1399 | 528 | 1 | 9 | 862 | 1 | 9 | 76 | 1 | 13 | 54900 | 1 | 9 | 84200 | 1 | 9 | 10900 | 1 | 13 | 1620 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 1.7 | 35.06 | A | 7 | 0.3 | A | 7 | 978 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.46 | 6 | 0
1979-11-17 | 1900-11-16 | 14:00 | 14 | 662 | 1399 | 470 | 1 | 9 | 835 | 1 | 9 | 71 | 1 | 13 | 49700 | 1 | 9 | 81800 | 1 | 9 | 10800 | 1 | 13 | 1580 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.29 | A | 7 | 977 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.36 | 6 | 0
1979-11-17 | 1900-11-16 | 15:00 | 15 | 533 | 1399 | 358 | 1 | 9 | 772 | 1 | 9 | 61 | 1 | 13 | 37400 | 1 | 9 | 72900 | 1 | 9 | 9500 | 1 | 13 | 1290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 20.6 | 69.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.3 | A | 7 | 977 | A | 7 | 200 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.16 | 6 | 0
1979-11-17 | 1900-11-16 | 16:00 | 16 | 348 | 1399 | 206 | 1 | 13 | 633 | 1 | 9 | 46 | 1 | 13 | 21000 | 1 | 13 | 53800 | 1 | 9 | 7600 | 1 | 13 | 910 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 20 | 68 | A | 7 | 3.3 | 37.94 | A | 7 | 0.33 | A | 7 | 976 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.04 | 6 | 0
1979-11-17 | 1900-11-16 | 17:00 | 17 | 123 | 1399 | 54 | 1 | 13 | 298 | 1 | 9 | 25 | 1 | 13 | 5200 | 1 | 13 | 15600 | 1 | 9 | 3800 | 1 | 13 | 440 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 17.2 | 62.96 | A | 7 | 4.4 | 39.92 | A | 7 | 0.43 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.072 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.32 | 6 | 0
1979-11-17 | 1900-11-16 | 18:00 | 18 | 0 | 35 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 5 | 41 | A | 7 | 0.48 | A | 7 | 976 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.9 | 6 | 0
1979-11-17 | 1900-11-16 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 5.6 | 42.08 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.68 | 6 | 0
1979-11-17 | 1900-11-16 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.52 | A | 7 | 976 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.38 | 6 | 0
1979-11-17 | 1900-11-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 14.4 | 57.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.55 | A | 7 | 976 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.88 | 6 | 0
1979-11-17 | 1900-11-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.6 | A | 7 | 976 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.58 | 6 | 0
1979-11-17 | 1900-11-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 5.6 | 42.08 | A | 7 | 0.6 | A | 7 | 976 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.58 | 6 | 0
1979-11-17 | 1900-11-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 6.1 | 42.98 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.68 | 6 | 0
1979-11-18 | 1900-11-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.64 | A | 7 | 976 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.88 | 7 | 0
1979-11-18 | 1900-11-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.64 | A | 7 | 975 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.88 | 7 | 0
1979-11-18 | 1900-11-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.67 | A | 7 | 975 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.38 | 7 | 0
1979-11-18 | 1900-11-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | 6.1 | 42.98 | A | 7 | 0.67 | A | 7 | 975 | A | 7 | 210 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.38 | 7 | 0
1979-11-18 | 1900-11-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.68 | 7 | 0
1979-11-18 | 1900-11-17 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.68 | 7 | 0
1979-11-18 | 1900-11-17 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 11.7 | 53.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.69 | A | 7 | 975 | A | 7 | 190 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.68 | 7 | 0
1979-11-18 | 1900-11-17 | 8:00 | 8 | 91 | 1248 | 20 | 1 | 13 | 4 | 1 | 9 | 19 | 1 | 13 | 2200 | 1 | 13 | 0 | 1 | 9 | 2200 | 1 | 13 | 670 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.77 | A | 7 | 975 | A | 7 | 200 | A | 7 | 9.8 | A | 7 | 12900 | A | 7 | 370 | A | 7 | 1.7 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.64 | 7 | 0
1979-11-18 | 1900-11-17 | 9:00 | 9 | 317 | 1400 | 108 | 1 | 13 | 8 | 1 | 9 | 107 | 1 | 13 | 11900 | 1 | 13 | 400 | 1 | 9 | 11800 | 1 | 13 | 3320 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 8.3 | 46.94 | A | 7 | 0.77 | A | 7 | 975 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 400 | A | 7 | 1.7 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.44 | 7 | 0
1979-11-18 | 1900-11-17 | 10:00 | 10 | 508 | 1400 | 168 | 1 | 9 | 11 | 1 | 9 | 164 | 1 | 13 | 18700 | 1 | 9 | 800 | 1 | 9 | 18400 | 1 | 13 | 5720 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 9.4 | 48.92 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.02 | 7 | 0
1979-11-18 | 1900-11-17 | 11:00 | 11 | 645 | 1400 | 199 | 1 | 9 | 12 | 1 | 9 | 193 | 1 | 13 | 22400 | 1 | 9 | 1000 | 1 | 9 | 21900 | 1 | 13 | 7380 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 14.4 | 57.92 | A | 7 | 9.4 | 48.92 | A | 7 | 0.72 | A | 7 | 975 | A | 7 | 180 | A | 7 | 10.3 | A | 7 | 11300 | A | 7 | 370 | A | 7 | 1.8 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.52 | 7 | 0
1979-11-18 | 1900-11-17 | 12:00 | 12 | 718 | 1400 | 198 | 1 | 9 | 3 | 1 | 9 | 196 | 1 | 13 | 22600 | 1 | 9 | 200 | 1 | 9 | 22400 | 1 | 13 | 7960 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 10 | 50 | A | 7 | 0.67 | A | 7 | 974 | A | 7 | 180 | A | 7 | 9.8 | A | 7 | 11300 | A | 7 | 520 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.6 | 7 | 0
1979-11-18 | 1900-11-17 | 13:00 | 13 | 722 | 1400 | 275 | 1 | 9 | 9 | 1 | 9 | 271 | 1 | 13 | 30700 | 1 | 9 | 900 | 1 | 9 | 30300 | 1 | 13 | 9730 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 10 | 50 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 170 | A | 7 | 10.8 | A | 7 | 11300 | A | 7 | 580 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.3 | 7 | 0
1979-11-18 | 1900-11-17 | 14:00 | 14 | 658 | 1400 | 189 | 1 | 9 | 5 | 1 | 9 | 186 | 1 | 13 | 21400 | 1 | 9 | 400 | 1 | 9 | 21200 | 1 | 13 | 7290 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 10 | 50 | A | 7 | 0.65 | A | 7 | 972 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 610 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.3 | 7 | 0
1979-11-18 | 1900-11-17 | 15:00 | 15 | 529 | 1400 | 187 | 1 | 9 | 2 | 1 | 9 | 186 | 1 | 13 | 20600 | 1 | 9 | 200 | 1 | 9 | 20600 | 1 | 13 | 6300 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 10 | 50 | A | 7 | 0.65 | A | 7 | 971 | A | 7 | 180 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 760 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.3 | 7 | 0
1979-11-18 | 1900-11-17 | 16:00 | 16 | 344 | 1400 | 98 | 1 | 13 | 1 | 1 | 9 | 98 | 1 | 13 | 10900 | 1 | 13 | 100 | 1 | 9 | 10900 | 1 | 13 | 3320 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 16.7 | 62.06 | A | 7 | 10 | 50 | A | 7 | 0.65 | A | 7 | 971 | A | 7 | 170 | A | 7 | 9.8 | A | 7 | 11300 | A | 7 | 700 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.3 | 7 | 0
1979-11-18 | 1900-11-17 | 17:00 | 17 | 120 | 1400 | 37 | 1 | 13 | 0 | 1 | 9 | 37 | 1 | 13 | 4000 | 1 | 13 | 0 | 1 | 9 | 4000 | 1 | 13 | 1100 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.7 | A | 7 | 970 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 700 | A | 7 | 1.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.1 | 7 | 0
1979-11-18 | 1900-11-17 | 18:00 | 18 | 0 | 12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10 | 50 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 160 | A | 7 | 10.3 | A | 7 | 12900 | A | 7 | 700 | A | 7 | 1.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.1 | 7 | 0
1979-11-18 | 1900-11-17 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 971 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 700 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.48 | 7 | 0
1979-11-18 | 1900-11-17 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15.6 | 60.08 | A | 7 | 10.6 | 51.08 | A | 7 | 0.72 | A | 7 | 971 | A | 7 | 160 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 820 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.48 | 7 | 0
1979-11-18 | 1900-11-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 10.6 | 51.08 | A | 7 | 0.75 | A | 7 | 971 | A | 7 | 160 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.98 | 7 | 0
1979-11-18 | 1900-11-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 970 | A | 7 | 160 | A | 7 | 11.3 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.28 | 7 | 0
1979-11-18 | 1900-11-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 970 | A | 7 | 180 | A | 7 | 11.3 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.28 | 7 | 0
1979-11-18 | 1900-11-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 16.1 | 60.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.75 | A | 7 | 970 | A | 7 | 180 | A | 7 | 9.8 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.76 | 7 | 0
1979-11-19 | 1900-11-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 970 | A | 7 | 200 | A | 7 | 11.8 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.16 | 1 | 0
1979-11-19 | 1900-11-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 16.1 | 60.98 | A | 7 | 12.2 | 53.96 | A | 7 | 0.78 | A | 7 | 970 | A | 7 | 200 | A | 7 | 11.8 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 2.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.16 | 1 | 0
1979-11-19 | 1900-11-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 16.1 | 60.98 | A | 7 | 11.7 | 53.06 | A | 7 | 0.75 | A | 7 | 970 | A | 7 | 210 | A | 7 | 9.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 2.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.76 | 1 | 0
1979-11-19 | 1900-11-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 15 | 59 | A | 7 | 11.1 | 51.98 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 230 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.28 | 1 | 0
1979-11-19 | 1900-11-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 8.9 | 48.02 | A | 7 | 0.75 | A | 7 | 972 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.12 | 1 | 0
1979-11-19 | 1900-11-18 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.77 | A | 7 | 973 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.64 | 1 | 0
1979-11-19 | 1900-11-18 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 5.6 | 42.08 | A | 7 | 0.71 | A | 7 | 975 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.08 | 1 | 0
1979-11-19 | 1900-11-18 | 8:00 | 8 | 87 | 1225 | 36 | 1 | 13 | 148 | 1 | 9 | 23 | 1 | 13 | 3600 | 1 | 13 | 6500 | 1 | 9 | 3100 | 1 | 13 | 410 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 4.4 | 39.92 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 240 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.92 | 1 | 0
1979-11-19 | 1900-11-18 | 9:00 | 9 | 312 | 1400 | 168 | 1 | 13 | 527 | 1 | 9 | 50 | 1 | 13 | 17400 | 1 | 13 | 42400 | 1 | 9 | 7900 | 1 | 13 | 930 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | 3.9 | 39.02 | A | 7 | 0.64 | A | 7 | 978 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.42 | 1 | 0
1979-11-19 | 1900-11-18 | 10:00 | 10 | 503 | 1400 | 320 | 1 | 9 | 697 | 1 | 9 | 68 | 1 | 13 | 32900 | 1 | 9 | 64600 | 1 | 9 | 9600 | 1 | 13 | 1330 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 2.2 | 35.96 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.06 | 1 | 0
1979-11-19 | 1900-11-18 | 11:00 | 11 | 640 | 1400 | 442 | 1 | 9 | 784 | 1 | 9 | 81 | 1 | 13 | 45900 | 1 | 9 | 75900 | 1 | 9 | 11100 | 1 | 13 | 1680 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 13.3 | 55.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.44 | A | 7 | 980 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.38 | 1 | 0
1979-11-19 | 1900-11-18 | 12:00 | 12 | 713 | 1400 | 504 | 1 | 9 | 811 | 1 | 9 | 88 | 1 | 13 | 52600 | 1 | 9 | 79700 | 1 | 9 | 11900 | 1 | 13 | 1900 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 15 | 59 | A | 7 | 1.1 | 33.98 | A | 7 | 0.39 | A | 7 | 980 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.78 | 1 | 0
1979-11-19 | 1900-11-18 | 13:00 | 13 | 718 | 1400 | 510 | 1 | 9 | 815 | 1 | 9 | 88 | 1 | 13 | 53200 | 1 | 9 | 80200 | 1 | 9 | 11900 | 1 | 13 | 1910 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 16.7 | 62.06 | A | 7 | 0 | 32 | A | 7 | 0.32 | A | 7 | 980 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.4 | 1 | 0
1979-11-19 | 1900-11-18 | 14:00 | 14 | 654 | 1400 | 453 | 1 | 9 | 787 | 1 | 9 | 83 | 1 | 13 | 47100 | 1 | 9 | 76400 | 1 | 9 | 11300 | 1 | 13 | 1730 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.32 | A | 7 | 980 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.28 | 1 | 0
1979-11-19 | 1900-11-18 | 15:00 | 15 | 525 | 1400 | 342 | 1 | 9 | 710 | 1 | 9 | 72 | 1 | 13 | 34900 | 1 | 9 | 66300 | 1 | 9 | 9900 | 1 | 13 | 1400 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.32 | A | 7 | 981 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.28 | 1 | 0
1979-11-19 | 1900-11-18 | 16:00 | 16 | 341 | 1400 | 184 | 1 | 13 | 513 | 1 | 9 | 56 | 1 | 13 | 18800 | 1 | 13 | 42500 | 1 | 9 | 8400 | 1 | 13 | 1040 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 17.8 | 64.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.32 | A | 7 | 981 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.28 | 1 | 0
1979-11-19 | 1900-11-18 | 17:00 | 17 | 117 | 1400 | 47 | 1 | 13 | 217 | 1 | 9 | 27 | 1 | 13 | 4500 | 1 | 13 | 11000 | 1 | 9 | 3600 | 1 | 13 | 460 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 16.1 | 60.98 | A | 7 | 0 | 32 | A | 7 | 0.34 | A | 7 | 982 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.7 | 1 | 0
1979-11-19 | 1900-11-18 | 18:00 | 18 | 0 | 12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 0 | 32 | A | 7 | 0.42 | A | 7 | 982 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.6 | 1 | 0
1979-11-19 | 1900-11-18 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 0 | 32 | A | 7 | 0.47 | A | 7 | 983 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.2 | 1 | 0
1979-11-19 | 1900-11-18 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 0 | 32 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27 | 1 | 0
1979-11-19 | 1900-11-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 0 | 32 | A | 7 | 0.56 | A | 7 | 984 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.2 | 1 | 0
1979-11-19 | 1900-11-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | 0 | 32 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.6 | 1 | 0
1979-11-19 | 1900-11-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | 0 | 32 | A | 7 | 0.65 | A | 7 | 985 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.2 | 1 | 0
1979-11-19 | 1900-11-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -0.6 | 30.92 | A | 7 | 0.68 | A | 7 | 985 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.52 | 1 | 0
1979-11-20 | 1900-11-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 4.4 | 39.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.7 | A | 7 | 985 | A | 7 | 60 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.72 | 2 | 0
1979-11-20 | 1900-11-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 5.6 | 42.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.65 | A | 7 | 985 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.22 | 2 | 0
1979-11-20 | 1900-11-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 6.1 | 42.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.63 | A | 7 | 985 | A | 7 | 50 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.02 | 2 | 0
1979-11-20 | 1900-11-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 6.7 | 44.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.6 | A | 7 | 984 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 2740 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.72 | 2 | 0
1979-11-20 | 1900-11-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 8.3 | 46.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 2740 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.02 | 2 | 0
1979-11-20 | 1900-11-19 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.63 | A | 7 | 985 | A | 7 | 40 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 980 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.56 | 2 | 0
1979-11-20 | 1900-11-19 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 2.8 | 37.04 | A | 7 | 0.74 | A | 7 | 984 | A | 7 | 50 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.84 | 2 | 0
1979-11-20 | 1900-11-19 | 8:00 | 8 | 83 | 1179 | 10 | 1 | 13 | 0 | 1 | 9 | 10 | 1 | 13 | 1200 | 1 | 13 | 0 | 1 | 9 | 1200 | 1 | 13 | 390 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 2.8 | 37.04 | A | 7 | 0.76 | A | 7 | 984 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 850 | A | 7 | 1.2 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.14 | 2 | 0
1979-11-20 | 1900-11-19 | 9:00 | 9 | 308 | 1401 | 40 | 1 | 13 | 6 | 1 | 9 | 39 | 1 | 13 | 4800 | 1 | 13 | 200 | 1 | 9 | 4700 | 1 | 13 | 1580 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.8 | A | 7 | 983 | A | 7 | 80 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 610 | A | 7 | 1.3 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.44 | 2 | 0
1979-11-20 | 1900-11-19 | 10:00 | 10 | 498 | 1401 | 77 | 1 | 9 | 3 | 1 | 9 | 76 | 1 | 13 | 9100 | 1 | 9 | 200 | 1 | 9 | 9000 | 1 | 13 | 3230 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 3.3 | 37.94 | A | 7 | 0.8 | A | 7 | 984 | A | 7 | 80 | A | 7 | 7.7 | A | 7 | 4000 | A | 7 | 490 | A | 7 | 1.3 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.44 | 2 | 0
1979-11-20 | 1900-11-19 | 11:00 | 11 | 635 | 1401 | 104 | 1 | 9 | 3 | 1 | 9 | 102 | 1 | 13 | 12200 | 1 | 9 | 200 | 1 | 9 | 12200 | 1 | 13 | 4540 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.86 | A | 7 | 984 | A | 7 | 70 | A | 7 | 6.7 | A | 7 | 4000 | A | 7 | 180 | A | 7 | 1.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.12 | 2 | 0
1979-11-20 | 1900-11-19 | 12:00 | 12 | 708 | 1401 | 127 | 1 | 9 | 5 | 1 | 9 | 124 | 1 | 13 | 15000 | 1 | 9 | 400 | 1 | 9 | 14800 | 1 | 13 | 5580 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 4.4 | 39.92 | A | 7 | 0.86 | A | 7 | 982 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 4000 | A | 7 | 180 | A | 7 | 1.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.12 | 2 | 0
1979-11-20 | 1900-11-19 | 13:00 | 13 | 713 | 1401 | 144 | 1 | 9 | 3 | 1 | 9 | 143 | 1 | 13 | 16900 | 1 | 9 | 200 | 1 | 9 | 16800 | 1 | 13 | 6280 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 5 | 41 | A | 7 | 0.86 | A | 7 | 981 | A | 7 | 70 | A | 7 | 7.7 | A | 7 | 4000 | A | 7 | 120 | A | 7 | 1.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.1 | 2 | 0
1979-11-20 | 1900-11-19 | 14:00 | 14 | 650 | 1401 | 125 | 1 | 9 | 6 | 1 | 9 | 122 | 1 | 13 | 14600 | 1 | 9 | 400 | 1 | 9 | 14400 | 1 | 13 | 5300 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 5 | 41 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 4000 | A | 7 | 120 | A | 7 | 1.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.1 | 2 | 0
1979-11-20 | 1900-11-19 | 15:00 | 15 | 521 | 1401 | 89 | 1 | 9 | 1 | 1 | 9 | 88 | 1 | 13 | 10300 | 1 | 9 | 100 | 1 | 9 | 10300 | 1 | 13 | 3710 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 5 | 41 | A | 7 | 0.86 | A | 7 | 979 | A | 7 | 70 | A | 7 | 7.2 | A | 7 | 2400 | A | 7 | 120 | A | 7 | 1.4 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.1 | 2 | 0
1979-11-20 | 1900-11-19 | 16:00 | 16 | 338 | 1401 | 53 | 1 | 13 | 2 | 1 | 9 | 53 | 1 | 13 | 6200 | 1 | 13 | 100 | 1 | 9 | 6200 | 1 | 13 | 2100 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.89 | A | 7 | 979 | A | 7 | 60 | A | 7 | 6.2 | A | 7 | 2400 | A | 7 | 120 | A | 7 | 1.5 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.58 | 2 | 0
1979-11-20 | 1900-11-19 | 17:00 | 17 | 114 | 1389 | 18 | 1 | 13 | 0 | 1 | 9 | 18 | 1 | 13 | 2100 | 1 | 13 | 0 | 1 | 9 | 2100 | 1 | 13 | 660 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.89 | A | 7 | 979 | A | 7 | 80 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 1.5 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.58 | 2 | 0
1979-11-20 | 1900-11-19 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 5.6 | 42.08 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 50 | A | 7 | 6.2 | A | 7 | 2400 | A | 7 | 90 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.58 | 2 | 0
1979-11-20 | 1900-11-19 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.89 | A | 7 | 978 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 120 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.48 | 2 | 0
1979-11-20 | 1900-11-19 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 6.1 | 42.98 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 110 | A | 7 | 7.7 | A | 7 | 4800 | A | 7 | 90 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.48 | 2 | 0
1979-11-20 | 1900-11-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 90 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.36 | 2 | 0
1979-11-20 | 1900-11-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.9 | A | 7 | 976 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 120 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.52 | 2 | 0
1979-11-20 | 1900-11-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 1520 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.24 | 2 | 0
1979-11-20 | 1900-11-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 800 | A | 7 | 0 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.44 | 2 | 0
1979-11-21 | 1900-11-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.86 | A | 7 | 976 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.96 | 3 | 0
1979-11-21 | 1900-11-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 20 | A | 7 | 2.1 | A | 7 | 800 | A | 7 | 700 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.44 | 3 | 0
1979-11-21 | 1900-11-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.89 | A | 7 | 976 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 1600 | A | 7 | 60 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.36 | 3 | 0
1979-11-21 | 1900-11-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 7.8 | 46.04 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 1600 | A | 7 | 400 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.94 | 3 | 0
1979-11-21 | 1900-11-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 3200 | A | 7 | 400 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.44 | 3 | 0
1979-11-21 | 1900-11-20 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 2400 | A | 7 | 270 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.84 | 3 | 0
1979-11-21 | 1900-11-20 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.9 | 48.02 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 80 | A | 7 | 2.6 | A | 7 | 1600 | A | 7 | 210 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.92 | 3 | 0
1979-11-21 | 1900-11-20 | 8:00 | 8 | 79 | 1156 | 25 | 1 | 13 | 0 | 1 | 9 | 25 | 1 | 13 | 2800 | 1 | 13 | 0 | 1 | 9 | 2800 | 1 | 13 | 810 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 9.4 | 48.92 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 2400 | A | 7 | 120 | A | 7 | 1.9 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.82 | 3 | 0
1979-11-21 | 1900-11-20 | 9:00 | 9 | 303 | 1402 | 79 | 1 | 13 | 1 | 1 | 9 | 79 | 1 | 13 | 8800 | 1 | 13 | 0 | 1 | 9 | 8800 | 1 | 13 | 2700 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 10 | 50 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 2400 | A | 7 | 210 | A | 7 | 1.9 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.9 | 3 | 0
1979-11-21 | 1900-11-20 | 10:00 | 10 | 493 | 1402 | 91 | 1 | 9 | 0 | 1 | 9 | 91 | 1 | 13 | 10600 | 1 | 9 | 0 | 1 | 9 | 10600 | 1 | 13 | 3730 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 11.7 | 53.06 | A | 7 | 10.6 | 51.08 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 1600 | A | 7 | 120 | A | 7 | 2 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.88 | 3 | 0
1979-11-21 | 1900-11-20 | 11:00 | 11 | 630 | 1402 | 132 | 1 | 9 | 0 | 1 | 9 | 132 | 1 | 13 | 15300 | 1 | 9 | 0 | 1 | 9 | 15300 | 1 | 13 | 5560 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.9 | A | 7 | 975 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 2800 | A | 7 | 120 | A | 7 | 1.8 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.52 | 3 | 0
1979-11-21 | 1900-11-20 | 12:00 | 12 | 704 | 1402 | 253 | 1 | 9 | 0 | 1 | 9 | 253 | 1 | 13 | 28200 | 1 | 9 | 0 | 1 | 9 | 28200 | 1 | 13 | 9190 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.86 | A | 7 | 974 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 90 | A | 7 | 1.7 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.84 | 3 | 0
1979-11-21 | 1900-11-20 | 13:00 | 13 | 709 | 1402 | 250 | 1 | 9 | 1 | 1 | 9 | 250 | 1 | 13 | 28000 | 1 | 9 | 100 | 1 | 9 | 28000 | 1 | 13 | 9180 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 8.3 | 46.94 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 260 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 180 | A | 7 | 1.7 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.24 | 3 | 0
1979-11-21 | 1900-11-20 | 14:00 | 14 | 646 | 1402 | 213 | 1 | 9 | 1 | 1 | 9 | 212 | 1 | 13 | 23800 | 1 | 9 | 100 | 1 | 9 | 23800 | 1 | 13 | 7810 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 7.8 | 46.04 | A | 7 | 0.86 | A | 7 | 974 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 210 | A | 7 | 1.7 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 3 | 0
1979-11-21 | 1900-11-20 | 15:00 | 15 | 518 | 1402 | 250 | 1 | 13 | 293 | 1 | 13 | 140 | 1 | 13 | 26500 | 1 | 13 | 28400 | 1 | 13 | 16000 | 1 | 13 | 2870 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 10.6 | 51.08 | A | 7 | 8.3 | 46.94 | A | 7 | 0.86 | A | 7 | 975 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 1.7 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.84 | 3 | 0
1979-11-21 | 1900-11-20 | 16:00 | 16 | 334 | 1402 | 181 | 1 | 13 | 473 | 1 | 9 | 66 | 1 | 13 | 18300 | 1 | 13 | 38500 | 1 | 9 | 9100 | 1 | 13 | 1180 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 11.1 | 51.98 | A | 7 | 7.2 | 44.96 | A | 7 | 0.77 | A | 7 | 976 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.66 | 3 | 0
1979-11-21 | 1900-11-20 | 17:00 | 17 | 111 | 1367 | 40 | 1 | 13 | 155 | 1 | 9 | 26 | 1 | 13 | 4100 | 1 | 13 | 7300 | 1 | 9 | 3500 | 1 | 13 | 460 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 9.4 | 48.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.77 | A | 7 | 976 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.113 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.98 | 3 | 0
1979-11-21 | 1900-11-20 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 9.4 | 48.92 | A | 7 | 5.6 | 42.08 | A | 7 | 0.77 | A | 7 | 977 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.98 | 3 | 0
1979-11-21 | 1900-11-20 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 3.9 | 39.02 | A | 7 | 0.74 | A | 7 | 977 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.72 | 3 | 0
1979-11-21 | 1900-11-20 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 2.8 | 37.04 | A | 7 | 0.71 | A | 7 | 977 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.54 | 3 | 0
1979-11-21 | 1900-11-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 6.1 | 42.98 | A | 7 | 2.2 | 35.96 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.16 | 3 | 0
1979-11-21 | 1900-11-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 5.6 | 42.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.46 | 3 | 0
1979-11-21 | 1900-11-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 5 | 41 | A | 7 | 1.7 | 35.06 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.66 | 3 | 0
1979-11-21 | 1900-11-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 3.9 | 39.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.12 | 3 | 0
1979-11-22 | 1900-11-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 3.3 | 37.94 | A | 7 | -1.1 | 30.02 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.22 | 4 | 0
1979-11-22 | 1900-11-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 2.8 | 37.04 | A | 7 | -1.1 | 30.02 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 880 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.52 | 4 | 0
1979-11-22 | 1900-11-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 940 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.72 | 4 | 0
1979-11-22 | 1900-11-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.72 | 4 | 0
1979-11-22 | 1900-11-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -1.1 | 30.02 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.52 | 4 | 0
1979-11-22 | 1900-11-21 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 240 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 4 | 0
1979-11-22 | 1900-11-21 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 4 | 0
1979-11-22 | 1900-11-21 | 8:00 | 8 | 76 | 1133 | 18 | 1 | 13 | 8 | 1 | 9 | 17 | 1 | 13 | 1900 | 1 | 13 | 500 | 1 | 9 | 1900 | 1 | 13 | 430 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 4 | 0
1979-11-22 | 1900-11-21 | 9:00 | 9 | 298 | 1402 | 81 | 1 | 13 | 33 | 1 | 9 | 74 | 1 | 13 | 8900 | 1 | 13 | 2700 | 1 | 9 | 8300 | 1 | 13 | 1880 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 430 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 4 | 0
1979-11-22 | 1900-11-21 | 10:00 | 10 | 488 | 1402 | 151 | 1 | 9 | 2 | 1 | 9 | 150 | 1 | 13 | 16800 | 1 | 9 | 100 | 1 | 9 | 16700 | 1 | 13 | 5280 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 1 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 4 | 0
1979-11-22 | 1900-11-21 | 11:00 | 11 | 626 | 1402 | 180 | 1 | 9 | 3 | 1 | 9 | 179 | 1 | 13 | 20400 | 1 | 9 | 200 | 1 | 9 | 20300 | 1 | 13 | 6890 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 550 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 4 | 0
1979-11-22 | 1900-11-21 | 12:00 | 12 | 699 | 1402 | 225 | 1 | 9 | 0 | 1 | 9 | 225 | 1 | 13 | 25300 | 1 | 9 | 0 | 1 | 9 | 25300 | 1 | 13 | 8550 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 4 | 0
1979-11-22 | 1900-11-21 | 13:00 | 13 | 705 | 1402 | 231 | 1 | 9 | 8 | 1 | 9 | 227 | 1 | 13 | 26000 | 1 | 9 | 700 | 1 | 9 | 25700 | 1 | 13 | 8640 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 400 | A | 7 | 1 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.24 | 4 | 0
1979-11-22 | 1900-11-21 | 14:00 | 14 | 642 | 1402 | 198 | 1 | 9 | 1 | 1 | 9 | 198 | 1 | 13 | 22300 | 1 | 9 | 100 | 1 | 9 | 22300 | 1 | 13 | 7470 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.73 | A | 7 | 978 | A | 7 | 250 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 400 | A | 7 | 1 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.24 | 4 | 0
1979-11-22 | 1900-11-21 | 15:00 | 15 | 514 | 1402 | 153 | 1 | 9 | 1 | 1 | 9 | 153 | 1 | 13 | 17200 | 1 | 9 | 100 | 1 | 9 | 17100 | 1 | 13 | 5520 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 12900 | A | 7 | 490 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 4 | 0
1979-11-22 | 1900-11-21 | 16:00 | 16 | 331 | 1402 | 105 | 1 | 13 | 2 | 1 | 9 | 104 | 1 | 13 | 11500 | 1 | 13 | 100 | 1 | 9 | 11500 | 1 | 13 | 3360 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 260 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 490 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.86 | 4 | 0
1979-11-22 | 1900-11-21 | 17:00 | 17 | 109 | 1367 | 32 | 1 | 13 | 0 | 1 | 9 | 32 | 1 | 13 | 3500 | 1 | 13 | 0 | 1 | 9 | 3500 | 1 | 13 | 1010 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 260 | A | 7 | 8.2 | A | 7 | 12900 | A | 7 | 520 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.06 | 4 | 0
1979-11-22 | 1900-11-21 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 979 | A | 7 | 260 | A | 7 | 6.7 | A | 7 | 12900 | A | 7 | 700 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.78 | 4 | 0
1979-11-22 | 1900-11-21 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -5 | 23 | A | 7 | 0.62 | A | 7 | 979 | A | 7 | 260 | A | 7 | 7.7 | A | 7 | 12900 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.8 | 4 | 0
1979-11-22 | 1900-11-21 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -5 | 23 | A | 7 | 0.62 | A | 7 | 979 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.8 | 4 | 0
1979-11-22 | 1900-11-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 1.1 | 33.98 | A | 7 | -5 | 23 | A | 7 | 0.64 | A | 7 | 979 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 880 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20 | 4 | 0
1979-11-22 | 1900-11-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 760 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 4 | 0
1979-11-22 | 1900-11-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 1.1 | 33.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 4 | 0
1979-11-22 | 1900-11-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.72 | 4 | 0
1979-11-23 | 1900-11-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 977 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.92 | 5 | 0
1979-11-23 | 1900-11-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 977 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.92 | 5 | 0
1979-11-23 | 1900-11-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 5 | 0
1979-11-23 | 1900-11-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 5 | 0
1979-11-23 | 1900-11-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.44 | 5 | 0
1979-11-23 | 1900-11-22 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 5 | 0
1979-11-23 | 1900-11-22 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -8.3 | 17.06 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.56 | 5 | 0
1979-11-23 | 1900-11-22 | 8:00 | 8 | 72 | 1111 | 40 | 1 | 13 | 247 | 1 | 9 | 17 | 1 | 13 | 3500 | 1 | 13 | 11800 | 1 | 9 | 2700 | 1 | 13 | 310 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.44 | 5 | 0
1979-11-23 | 1900-11-22 | 9:00 | 9 | 293 | 1403 | 171 | 1 | 13 | 657 | 1 | 9 | 33 | 1 | 13 | 18100 | 1 | 13 | 54200 | 1 | 9 | 6700 | 1 | 13 | 740 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 5 | 0
1979-11-23 | 1900-11-22 | 10:00 | 10 | 484 | 1403 | 322 | 1 | 9 | 798 | 1 | 9 | 45 | 1 | 13 | 33900 | 1 | 9 | 73800 | 1 | 9 | 8300 | 1 | 13 | 1080 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -5 | 23 | A | 7 | 0.75 | A | 7 | 977 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.9 | 5 | 0
1979-11-23 | 1900-11-22 | 11:00 | 11 | 621 | 1403 | 448 | 1 | 9 | 885 | 1 | 9 | 53 | 1 | 13 | 47000 | 1 | 9 | 85100 | 1 | 9 | 9200 | 1 | 13 | 1310 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -5 | 23 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.3 | 5 | 0
1979-11-23 | 1900-11-22 | 12:00 | 12 | 695 | 1403 | 511 | 1 | 9 | 908 | 1 | 9 | 58 | 1 | 13 | 53600 | 1 | 9 | 88500 | 1 | 9 | 9600 | 1 | 13 | 1440 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.55 | A | 7 | 976 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.32 | 5 | 0
1979-11-23 | 1900-11-22 | 13:00 | 13 | 701 | 1403 | 517 | 1 | 9 | 910 | 1 | 9 | 58 | 1 | 13 | 54100 | 1 | 9 | 88800 | 1 | 9 | 9600 | 1 | 13 | 1450 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.51 | A | 7 | 975 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 5 | 0
1979-11-23 | 1900-11-22 | 14:00 | 14 | 638 | 1403 | 467 | 1 | 9 | 898 | 1 | 9 | 55 | 1 | 13 | 49000 | 1 | 9 | 86700 | 1 | 9 | 9400 | 1 | 13 | 1340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -6.1 | 21.02 | A | 7 | 0.45 | A | 7 | 974 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.72 | 5 | 0
1979-11-23 | 1900-11-22 | 15:00 | 15 | 511 | 1403 | 355 | 1 | 9 | 836 | 1 | 9 | 46 | 1 | 13 | 37100 | 1 | 9 | 78100 | 1 | 9 | 8600 | 1 | 13 | 1120 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.38 | A | 7 | 974 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.44 | 5 | 0
1979-11-23 | 1900-11-22 | 16:00 | 16 | 329 | 1403 | 204 | 1 | 13 | 706 | 1 | 9 | 35 | 1 | 13 | 21300 | 1 | 13 | 60000 | 1 | 9 | 7100 | 1 | 13 | 810 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -7.8 | 17.96 | A | 7 | 0.37 | A | 7 | 974 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.46 | 5 | 0
1979-11-23 | 1900-11-22 | 17:00 | 17 | 106 | 1344 | 54 | 1 | 13 | 362 | 1 | 9 | 20 | 1 | 13 | 5000 | 1 | 13 | 20900 | 1 | 9 | 3300 | 1 | 13 | 370 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -7.2 | 19.04 | A | 7 | 0.45 | A | 7 | 974 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.04 | 5 | 0
1979-11-23 | 1900-11-22 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.52 | A | 7 | 974 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.34 | 5 | 0
1979-11-23 | 1900-11-22 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.5 | A | 7 | 975 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.46 | 5 | 0
1979-11-23 | 1900-11-22 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.54 | A | 7 | 975 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.44 | 5 | 0
1979-11-23 | 1900-11-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 5 | 0
1979-11-23 | 1900-11-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 5 | 0
1979-11-23 | 1900-11-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.24 | 5 | 0
1979-11-23 | 1900-11-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 976 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.24 | 5 | 0
1979-11-24 | 1900-11-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 6 | 0
1979-11-24 | 1900-11-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 976 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.42 | 6 | 0
1979-11-24 | 1900-11-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 976 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.22 | 6 | 0
1979-11-24 | 1900-11-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 976 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 6 | 0
1979-11-24 | 1900-11-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.66 | A | 7 | 977 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.32 | 6 | 0
1979-11-24 | 1900-11-23 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 977 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.22 | 6 | 0
1979-11-24 | 1900-11-23 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -6.1 | 21.02 | A | 7 | 0.64 | A | 7 | 977 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.22 | 6 | 0
1979-11-24 | 1900-11-23 | 8:00 | 8 | 69 | 1088 | 35 | 1 | 13 | 186 | 1 | 9 | 18 | 1 | 13 | 3100 | 1 | 13 | 8700 | 1 | 9 | 2500 | 1 | 13 | 320 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.64 | A | 7 | 978 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 6 | 0
1979-11-24 | 1900-11-23 | 9:00 | 9 | 289 | 1403 | 164 | 1 | 13 | 605 | 1 | 9 | 38 | 1 | 13 | 16800 | 1 | 13 | 48600 | 1 | 9 | 6700 | 1 | 13 | 750 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -5 | 23 | A | 7 | 0.57 | A | 7 | 978 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.4 | 6 | 0
1979-11-24 | 1900-11-23 | 10:00 | 10 | 479 | 1403 | 317 | 1 | 9 | 773 | 1 | 9 | 52 | 1 | 13 | 33400 | 1 | 9 | 71700 | 1 | 9 | 8900 | 1 | 13 | 1110 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -3.9 | 24.98 | A | 7 | 0.53 | A | 7 | 979 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.78 | 6 | 0
1979-11-24 | 1900-11-23 | 11:00 | 11 | 616 | 1403 | 436 | 1 | 9 | 846 | 1 | 9 | 62 | 1 | 13 | 45600 | 1 | 9 | 81200 | 1 | 9 | 9800 | 1 | 13 | 1370 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.49 | A | 7 | 979 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 6 | 0
1979-11-24 | 1900-11-23 | 12:00 | 12 | 691 | 1403 | 503 | 1 | 9 | 877 | 1 | 9 | 67 | 1 | 13 | 52400 | 1 | 9 | 85300 | 1 | 9 | 10300 | 1 | 13 | 1510 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.44 | A | 7 | 978 | A | 7 | 230 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.54 | 6 | 0
1979-11-24 | 1900-11-23 | 13:00 | 13 | 697 | 1403 | 507 | 1 | 9 | 876 | 1 | 9 | 68 | 1 | 13 | 52900 | 1 | 9 | 85300 | 1 | 9 | 10300 | 1 | 13 | 1530 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.43 | A | 7 | 978 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.14 | 6 | 0
1979-11-24 | 1900-11-23 | 14:00 | 14 | 635 | 1403 | 452 | 1 | 9 | 851 | 1 | 9 | 63 | 1 | 13 | 47100 | 1 | 9 | 82000 | 1 | 9 | 9900 | 1 | 13 | 1400 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.4 | A | 7 | 978 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.84 | 6 | 0
1979-11-24 | 1900-11-23 | 15:00 | 15 | 508 | 1403 | 342 | 1 | 9 | 786 | 1 | 9 | 54 | 1 | 13 | 35700 | 1 | 9 | 73200 | 1 | 9 | 9100 | 1 | 13 | 1170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.38 | A | 7 | 978 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.64 | 6 | 0
1979-11-24 | 1900-11-23 | 16:00 | 16 | 326 | 1403 | 194 | 1 | 13 | 645 | 1 | 9 | 41 | 1 | 13 | 19800 | 1 | 13 | 53900 | 1 | 9 | 7200 | 1 | 13 | 830 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.43 | A | 7 | 979 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.82 | 6 | 0
1979-11-24 | 1900-11-23 | 17:00 | 17 | 104 | 1345 | 49 | 1 | 13 | 291 | 1 | 9 | 22 | 1 | 13 | 4700 | 1 | 13 | 14900 | 1 | 9 | 3500 | 1 | 13 | 390 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | -0.6 | 30.92 | A | 7 | 0.5 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.62 | 6 | 0
1979-11-24 | 1900-11-23 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.56 | A | 7 | 979 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.52 | 6 | 0
1979-11-24 | 1900-11-23 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -1.7 | 28.94 | A | 7 | 0.62 | A | 7 | 979 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 6 | 0
1979-11-24 | 1900-11-23 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.62 | A | 7 | 978 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 6 | 0
1979-11-24 | 1900-11-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 979 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 6 | 0
1979-11-24 | 1900-11-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 3.3 | 37.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.67 | A | 7 | 979 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.84 | 6 | 0
1979-11-24 | 1900-11-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 3.3 | 37.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 6 | 0
1979-11-24 | 1900-11-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 978 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 6 | 0
1979-11-25 | 1900-11-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 7 | 0
1979-11-25 | 1900-11-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 978 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 7 | 0
1979-11-25 | 1900-11-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 977 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 7 | 0
1979-11-25 | 1900-11-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 7 | 0
1979-11-25 | 1900-11-24 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.6 | A | 7 | 976 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 7 | 0
1979-11-25 | 1900-11-24 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 3.9 | 39.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.6 | A | 7 | 975 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 7 | 0
1979-11-25 | 1900-11-24 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 3.3 | 37.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.6 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.48 | 7 | 0
1979-11-25 | 1900-11-24 | 8:00 | 8 | 65 | 1065 | 34 | 1 | 13 | 135 | 1 | 9 | 21 | 1 | 13 | 3100 | 1 | 13 | 5400 | 1 | 9 | 2800 | 1 | 13 | 370 | 1 | 21 | 8 | A | 7 | 2 | A | 7 | 3.9 | 39.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.57 | A | 7 | 973 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.18 | 7 | 0
1979-11-25 | 1900-11-24 | 9:00 | 9 | 284 | 1404 | 128 | 1 | 13 | 297 | 1 | 13 | 68 | 1 | 13 | 13300 | 1 | 13 | 22400 | 1 | 13 | 8800 | 1 | 13 | 1240 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 4.4 | 39.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.57 | A | 7 | 974 | A | 7 | 160 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 7 | 0
1979-11-25 | 1900-11-24 | 10:00 | 10 | 475 | 1404 | 293 | 1 | 9 | 666 | 1 | 9 | 66 | 1 | 13 | 30800 | 1 | 9 | 61400 | 1 | 9 | 9900 | 1 | 13 | 1300 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 7.2 | 44.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.47 | A | 7 | 973 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.16 | 7 | 0
1979-11-25 | 1900-11-24 | 11:00 | 11 | 612 | 1404 | 391 | 1 | 13 | 656 | 1 | 13 | 104 | 1 | 13 | 40800 | 1 | 13 | 63300 | 1 | 13 | 13100 | 1 | 13 | 2100 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 8.3 | 46.94 | A | 7 | -5 | 23 | A | 7 | 0.39 | A | 7 | 972 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.9 | 7 | 0
1979-11-25 | 1900-11-24 | 12:00 | 12 | 687 | 1404 | 442 | 1 | 9 | 713 | 1 | 9 | 90 | 1 | 13 | 45800 | 1 | 9 | 69500 | 1 | 9 | 11600 | 1 | 13 | 1870 | 1 | 18 | 6 | A | 7 | 2 | A | 7 | 10 | 50 | A | 7 | -3.9 | 24.98 | A | 7 | 0.38 | A | 7 | 971 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.38 | 7 | 0
1979-11-25 | 1900-11-24 | 13:00 | 13 | 693 | 1404 | 468 | 1 | 9 | 736 | 1 | 9 | 102 | 1 | 13 | 49400 | 1 | 9 | 72800 | 1 | 9 | 13300 | 1 | 13 | 2200 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.34 | A | 7 | 970 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.08 | 7 | 0
1979-11-25 | 1900-11-24 | 14:00 | 14 | 631 | 1404 | 414 | 1 | 13 | 677 | 1 | 13 | 107 | 1 | 13 | 43100 | 1 | 13 | 65600 | 1 | 13 | 13500 | 1 | 13 | 2180 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | 12.2 | 53.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.35 | A | 7 | 969 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.76 | 7 | 0
1979-11-25 | 1900-11-24 | 15:00 | 15 | 505 | 1404 | 302 | 1 | 9 | 579 | 1 | 9 | 91 | 1 | 13 | 31100 | 1 | 9 | 53500 | 1 | 9 | 11700 | 1 | 13 | 1730 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.31 | A | 7 | 967 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.78 | 7 | 0
1979-11-25 | 1900-11-24 | 16:00 | 16 | 323 | 1404 | 177 | 1 | 13 | 499 | 1 | 9 | 60 | 1 | 13 | 18000 | 1 | 13 | 40200 | 1 | 9 | 8700 | 1 | 13 | 1090 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | 11.7 | 53.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.34 | A | 7 | 967 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.08 | 7 | 0
1979-11-25 | 1900-11-24 | 17:00 | 17 | 102 | 1322 | 37 | 1 | 13 | 32 | 1 | 13 | 34 | 1 | 13 | 4000 | 1 | 13 | 2000 | 1 | 13 | 3800 | 1 | 13 | 770 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 10 | 50 | A | 7 | -3.3 | 26.06 | A | 7 | 0.39 | A | 7 | 966 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.36 | 7 | 0
1979-11-25 | 1900-11-24 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 7.2 | 44.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.47 | A | 7 | 967 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.16 | 7 | 0
1979-11-25 | 1900-11-24 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 6.1 | 42.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.51 | A | 7 | 967 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.56 | 7 | 0
1979-11-25 | 1900-11-24 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | 6.1 | 42.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.56 | A | 7 | 966 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.74 | 7 | 0
1979-11-25 | 1900-11-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 6.1 | 42.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.6 | A | 7 | 967 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.92 | 7 | 0
1979-11-25 | 1900-11-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 4.4 | 39.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.68 | A | 7 | 967 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.72 | 7 | 0
1979-11-25 | 1900-11-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 3.3 | 37.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.7 | A | 7 | 967 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 7 | 0
1979-11-25 | 1900-11-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 967 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 700 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 7 | 0
1979-11-26 | 1900-11-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 967 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 700 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 1 | 0
1979-11-26 | 1900-11-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.67 | A | 7 | 967 | A | 7 | 280 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.84 | 1 | 0
1979-11-26 | 1900-11-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.7 | A | 7 | 967 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 1 | 0
1979-11-26 | 1900-11-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.7 | A | 7 | 967 | A | 7 | 290 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 460 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.92 | 1 | 0
1979-11-26 | 1900-11-25 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.7 | A | 7 | 968 | A | 7 | 280 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 460 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.92 | 1 | 0
1979-11-26 | 1900-11-25 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.67 | A | 7 | 969 | A | 7 | 270 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 1 | 0
1979-11-26 | 1900-11-25 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.67 | A | 7 | 969 | A | 7 | 280 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 1 | 0
1979-11-26 | 1900-11-25 | 8:00 | 8 | 62 | 1042 | 11 | 1 | 13 | 2 | 1 | 9 | 11 | 1 | 13 | 1300 | 1 | 13 | 0 | 1 | 9 | 1300 | 1 | 13 | 410 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 970 | A | 7 | 280 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 1 | 0
1979-11-26 | 1900-11-25 | 9:00 | 9 | 279 | 1404 | 133 | 1 | 13 | 431 | 1 | 9 | 47 | 1 | 13 | 13700 | 1 | 13 | 33100 | 1 | 9 | 7100 | 1 | 13 | 860 | 1 | 21 | 5 | A | 7 | 1 | A | 7 | 3.3 | 37.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.67 | A | 7 | 971 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.84 | 1 | 0
1979-11-26 | 1900-11-25 | 10:00 | 10 | 470 | 1404 | 289 | 1 | 9 | 684 | 1 | 9 | 58 | 1 | 13 | 29900 | 1 | 9 | 62800 | 1 | 9 | 8800 | 1 | 13 | 1180 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 973 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 1 | 0
1979-11-26 | 1900-11-25 | 11:00 | 11 | 608 | 1404 | 404 | 1 | 9 | 769 | 1 | 9 | 69 | 1 | 13 | 42500 | 1 | 9 | 74200 | 1 | 9 | 10200 | 1 | 13 | 1480 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 6.1 | 42.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.56 | A | 7 | 973 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.74 | 1 | 0
1979-11-26 | 1900-11-25 | 12:00 | 12 | 683 | 1404 | 483 | 1 | 9 | 831 | 1 | 9 | 76 | 1 | 13 | 50900 | 1 | 9 | 81600 | 1 | 9 | 11100 | 1 | 13 | 1680 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.51 | A | 7 | 973 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.24 | 1 | 0
1979-11-26 | 1900-11-25 | 13:00 | 13 | 689 | 1404 | 407 | 1 | 13 | 508 | 1 | 13 | 155 | 1 | 13 | 43100 | 1 | 13 | 50800 | 1 | 13 | 18100 | 1 | 13 | 3220 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 8.3 | 46.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.48 | A | 7 | 973 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.94 | 1 | 0
1979-11-26 | 1900-11-25 | 14:00 | 14 | 628 | 1404 | 365 | 1 | 9 | 398 | 1 | 9 | 185 | 1 | 13 | 38700 | 1 | 9 | 40400 | 1 | 9 | 20600 | 1 | 13 | 4040 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 8.3 | 46.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.46 | A | 7 | 973 | A | 7 | 260 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.86 | 1 | 0
1979-11-26 | 1900-11-25 | 15:00 | 15 | 502 | 1404 | 295 | 1 | 13 | 504 | 1 | 13 | 113 | 1 | 13 | 31000 | 1 | 13 | 47100 | 1 | 13 | 14100 | 1 | 13 | 2150 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 8.9 | 48.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.42 | A | 7 | 974 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.66 | 1 | 0
1979-11-26 | 1900-11-25 | 16:00 | 16 | 321 | 1404 | 142 | 1 | 13 | 164 | 1 | 13 | 104 | 1 | 13 | 15200 | 1 | 13 | 13500 | 1 | 13 | 12100 | 1 | 13 | 2260 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | 7.8 | 46.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.44 | A | 7 | 974 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.98 | 1 | 0
1979-11-26 | 1900-11-25 | 17:00 | 17 | 101 | 1323 | 30 | 1 | 13 | 54 | 1 | 9 | 25 | 1 | 13 | 3200 | 1 | 13 | 2700 | 1 | 9 | 3000 | 1 | 13 | 520 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 7.8 | 46.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.44 | A | 7 | 974 | A | 7 | 220 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.98 | 1 | 0
1979-11-26 | 1900-11-25 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 5.6 | 42.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.53 | A | 7 | 974 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.76 | 1 | 0
1979-11-26 | 1900-11-25 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.51 | A | 7 | 974 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.56 | 1 | 0
1979-11-26 | 1900-11-25 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 6.1 | 42.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.51 | A | 7 | 975 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.56 | 1 | 0
1979-11-26 | 1900-11-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 5 | 41 | A | 7 | -3.3 | 26.06 | A | 7 | 0.55 | A | 7 | 975 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.96 | 1 | 0
1979-11-26 | 1900-11-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 5 | 41 | A | 7 | -3.3 | 26.06 | A | 7 | 0.55 | A | 7 | 976 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.96 | 1 | 0
1979-11-26 | 1900-11-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 1 | 0
1979-11-26 | 1900-11-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 1 | 0
1979-11-27 | 1900-11-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 975 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 2 | 0
1979-11-27 | 1900-11-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 975 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 2 | 0
1979-11-27 | 1900-11-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 975 | A | 7 | 50 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 2 | 0
1979-11-27 | 1900-11-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.62 | A | 7 | 975 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 2 | 0
1979-11-27 | 1900-11-26 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.68 | A | 7 | 975 | A | 7 | 30 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 580 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.72 | 2 | 0
1979-11-27 | 1900-11-26 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.73 | A | 7 | 976 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 460 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.12 | 2 | 0
1979-11-27 | 1900-11-26 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 30 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 1160 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.42 | 2 | 0
1979-11-27 | 1900-11-26 | 8:00 | 8 | 59 | 1019 | 7 | 1 | 13 | 2 | 1 | 9 | 6 | 1 | 13 | 700 | 1 | 13 | 100 | 1 | 9 | 700 | 1 | 13 | 160 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.7 | 2 | 0
1979-11-27 | 1900-11-26 | 9:00 | 9 | 275 | 1405 | 35 | 1 | 13 | 1 | 1 | 9 | 35 | 1 | 13 | 4100 | 1 | 13 | 0 | 1 | 9 | 4100 | 1 | 13 | 1390 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 979 | A | 7 | 20 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.7 | 2 | 0
1979-11-27 | 1900-11-26 | 10:00 | 10 | 466 | 1405 | 60 | 1 | 9 | 0 | 1 | 9 | 60 | 1 | 13 | 7100 | 1 | 9 | 0 | 1 | 9 | 7100 | 1 | 13 | 2580 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 979 | A | 7 | 10 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 270 | A | 7 | 1.1 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.7 | 2 | 0
1979-11-27 | 1900-11-26 | 11:00 | 11 | 604 | 1405 | 170 | 1 | 9 | 9 | 1 | 9 | 166 | 1 | 13 | 19200 | 1 | 9 | 700 | 1 | 9 | 18900 | 1 | 13 | 6410 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 1.1 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.7 | 2 | 0
1979-11-27 | 1900-11-26 | 12:00 | 12 | 679 | 1405 | 204 | 1 | 9 | 11 | 1 | 9 | 199 | 1 | 13 | 23100 | 1 | 9 | 900 | 1 | 9 | 22700 | 1 | 13 | 7750 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 340 | A | 7 | 1.1 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.68 | 2 | 0
1979-11-27 | 1900-11-26 | 13:00 | 13 | 686 | 1405 | 194 | 1 | 9 | 3 | 1 | 9 | 192 | 1 | 13 | 22000 | 1 | 9 | 200 | 1 | 9 | 21900 | 1 | 13 | 7620 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 0.6 | 33.08 | A | 7 | 0.73 | A | 7 | 980 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 270 | A | 7 | 1.1 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.08 | 2 | 0
1979-11-27 | 1900-11-26 | 14:00 | 14 | 625 | 1405 | 200 | 1 | 9 | 5 | 1 | 9 | 197 | 1 | 13 | 22300 | 1 | 9 | 400 | 1 | 9 | 22200 | 1 | 13 | 7300 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 0.6 | 33.08 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 580 | A | 7 | 1.1 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.78 | 2 | 0
1979-11-27 | 1900-11-26 | 15:00 | 15 | 499 | 1405 | 218 | 1 | 9 | 132 | 1 | 9 | 170 | 1 | 13 | 23400 | 1 | 9 | 12600 | 1 | 9 | 18900 | 1 | 13 | 3900 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 6.7 | 44.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 1 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.72 | 2 | 0
1979-11-27 | 1900-11-26 | 16:00 | 16 | 319 | 1405 | 142 | 1 | 13 | 235 | 1 | 13 | 88 | 1 | 13 | 14900 | 1 | 13 | 18800 | 1 | 13 | 10600 | 1 | 13 | 1720 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 6.7 | 44.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.44 | 2 | 0
1979-11-27 | 1900-11-26 | 17:00 | 17 | 99 | 1300 | 40 | 1 | 13 | 146 | 1 | 9 | 27 | 1 | 13 | 4000 | 1 | 13 | 6600 | 1 | 9 | 3500 | 1 | 13 | 480 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | 5 | 41 | A | 7 | -3.9 | 24.98 | A | 7 | 0.53 | A | 7 | 983 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.78 | 2 | 0
1979-11-27 | 1900-11-26 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 4.4 | 39.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 2 | 0
1979-11-27 | 1900-11-26 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.62 | A | 7 | 985 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.78 | 2 | 0
1979-11-27 | 1900-11-26 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 985 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 2 | 0
1979-11-27 | 1900-11-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.59 | A | 7 | 986 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.82 | 2 | 0
1979-11-27 | 1900-11-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.66 | A | 7 | 987 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.32 | 2 | 0
1979-11-27 | 1900-11-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 988 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.22 | 2 | 0
1979-11-27 | 1900-11-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 988 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.42 | 2 | 0
1979-11-28 | 1900-11-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 988 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.24 | 3 | 0
1979-11-28 | 1900-11-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -0.6 | 30.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.59 | A | 7 | 988 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 3 | 0
1979-11-28 | 1900-11-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | -1.1 | 30.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.58 | A | 7 | 989 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.16 | 3 | 0
1979-11-28 | 1900-11-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -11.1 | 12.02 | A | 7 | 0.47 | A | 7 | 988 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 2290 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.02 | 3 | 0
1979-11-28 | 1900-11-27 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.45 | A | 7 | 989 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.14 | 3 | 0
1979-11-28 | 1900-11-27 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -3.3 | 26.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.48 | A | 7 | 989 | A | 7 | 300 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.36 | 3 | 0
1979-11-28 | 1900-11-27 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | -4.4 | 24.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.55 | A | 7 | 990 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.64 | 3 | 0
1979-11-28 | 1900-11-27 | 8:00 | 8 | 56 | 996 | 11 | 1 | 13 | 1 | 1 | 9 | 10 | 1 | 13 | 1200 | 1 | 13 | 0 | 1 | 9 | 1200 | 1 | 13 | 380 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | -4.4 | 24.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.55 | A | 7 | 990 | A | 7 | 290 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 880 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.64 | 3 | 0
1979-11-28 | 1900-11-27 | 9:00 | 9 | 271 | 1405 | 92 | 1 | 13 | 80 | 1 | 9 | 76 | 1 | 13 | 9900 | 1 | 13 | 6200 | 1 | 9 | 8700 | 1 | 13 | 1630 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | -4.4 | 24.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.5 | A | 7 | 991 | A | 7 | 290 | A | 7 | 12.9 | A | 7 | 32200 | A | 7 | 880 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.66 | 3 | 0
1979-11-28 | 1900-11-27 | 10:00 | 10 | 461 | 1405 | 152 | 1 | 9 | 109 | 1 | 9 | 116 | 1 | 13 | 16700 | 1 | 9 | 10200 | 1 | 9 | 13300 | 1 | 13 | 2620 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | -4.4 | 24.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.5 | A | 7 | 991 | A | 7 | 280 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 850 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.66 | 3 | 0
1979-11-28 | 1900-11-27 | 11:00 | 11 | 599 | 1405 | 278 | 1 | 13 | 191 | 1 | 13 | 196 | 1 | 13 | 30100 | 1 | 13 | 19000 | 1 | 13 | 21900 | 1 | 13 | 4670 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -3.9 | 24.98 | A | 7 | -13.3 | 8.06 | A | 7 | 0.48 | A | 7 | 991 | A | 7 | 300 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 880 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.56 | 3 | 0
1979-11-28 | 1900-11-27 | 12:00 | 12 | 675 | 1405 | 321 | 1 | 9 | 157 | 1 | 9 | 245 | 1 | 13 | 34600 | 1 | 9 | 15900 | 1 | 9 | 26900 | 1 | 13 | 6030 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | -3.9 | 24.98 | A | 7 | -13.3 | 8.06 | A | 7 | 0.48 | A | 7 | 990 | A | 7 | 290 | A | 7 | 11.3 | A | 7 | 32200 | A | 7 | 940 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.56 | 3 | 0
1979-11-28 | 1900-11-27 | 13:00 | 13 | 683 | 1405 | 334 | 1 | 13 | 345 | 1 | 13 | 164 | 1 | 13 | 36000 | 1 | 13 | 35700 | 1 | 13 | 18700 | 1 | 13 | 3540 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -2.8 | 26.96 | A | 7 | -12.8 | 8.96 | A | 7 | 0.47 | A | 7 | 990 | A | 7 | 290 | A | 7 | 11.8 | A | 7 | 32200 | A | 7 | 1040 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.26 | 3 | 0
1979-11-28 | 1900-11-27 | 14:00 | 14 | 622 | 1405 | 161 | 1 | 9 | 5 | 1 | 9 | 158 | 1 | 13 | 18300 | 1 | 9 | 400 | 1 | 9 | 18100 | 1 | 13 | 6300 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.48 | A | 7 | 989 | A | 7 | 290 | A | 7 | 10.8 | A | 7 | 32200 | A | 7 | 1100 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.36 | 3 | 0
1979-11-28 | 1900-11-27 | 15:00 | 15 | 497 | 1405 | 178 | 1 | 9 | 11 | 1 | 9 | 174 | 1 | 13 | 19600 | 1 | 9 | 900 | 1 | 9 | 19300 | 1 | 13 | 5800 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.53 | A | 7 | 989 | A | 7 | 280 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 940 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.56 | 3 | 0
1979-11-28 | 1900-11-27 | 16:00 | 16 | 317 | 1405 | 80 | 1 | 13 | 5 | 1 | 9 | 79 | 1 | 13 | 9000 | 1 | 13 | 200 | 1 | 9 | 8900 | 1 | 13 | 2760 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.48 | A | 7 | 989 | A | 7 | 280 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 1340 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.36 | 3 | 0
1979-11-28 | 1900-11-27 | 17:00 | 17 | 97 | 1300 | 31 | 1 | 13 | 36 | 1 | 9 | 28 | 1 | 13 | 3400 | 1 | 13 | 1800 | 1 | 9 | 3200 | 1 | 13 | 580 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -3.3 | 26.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.51 | A | 7 | 989 | A | 7 | 280 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1040 | A | 7 | 0.5 | E | 8 | 0.048 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.44 | 3 | 0
1979-11-28 | 1900-11-27 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.53 | A | 7 | 989 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 3 | 0
1979-11-28 | 1900-11-27 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.55 | A | 7 | 989 | A | 7 | 300 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.44 | 3 | 0
1979-11-28 | 1900-11-27 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -4.4 | 24.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.53 | A | 7 | 989 | A | 7 | 280 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 1830 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.56 | 3 | 0
1979-11-28 | 1900-11-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.53 | A | 7 | 989 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 1490 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.54 | 3 | 0
1979-11-28 | 1900-11-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.58 | A | 7 | 989 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 1160 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.64 | 3 | 0
1979-11-28 | 1900-11-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.6 | A | 7 | 989 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 4800 | A | 7 | 850 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 3 | 0
1979-11-28 | 1900-11-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | -5 | 23 | A | 7 | -12.2 | 10.04 | A | 7 | 0.57 | A | 7 | 990 | A | 7 | 320 | A | 7 | 9.3 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.74 | 3 | 0
1979-11-29 | 1900-11-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.57 | A | 7 | 989 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 4 | 0
1979-11-29 | 1900-11-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -6.1 | 21.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.6 | A | 7 | 990 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.96 | 4 | 0
1979-11-29 | 1900-11-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 990 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.04 | 4 | 0
1979-11-29 | 1900-11-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.6 | A | 7 | 990 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.96 | 4 | 0
1979-11-29 | 1900-11-28 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.62 | A | 7 | 991 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.06 | 4 | 0
1979-11-29 | 1900-11-28 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 991 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.14 | 4 | 0
1979-11-29 | 1900-11-28 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 991 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.14 | 4 | 0
1979-11-29 | 1900-11-28 | 8:00 | 8 | 53 | 972 | 26 | 1 | 13 | 45 | 1 | 13 | 22 | 1 | 13 | 2700 | 1 | 13 | 1900 | 1 | 13 | 2600 | 1 | 13 | 450 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 992 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 520 | A | 7 | 0.6 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 4 | 0
1979-11-29 | 1900-11-28 | 9:00 | 9 | 266 | 1406 | 113 | 1 | 13 | 250 | 1 | 13 | 66 | 1 | 13 | 11700 | 1 | 13 | 18300 | 1 | 13 | 8300 | 1 | 13 | 1210 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | -6.1 | 21.02 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 993 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.22 | 4 | 0
1979-11-29 | 1900-11-28 | 10:00 | 10 | 457 | 1406 | 119 | 1 | 9 | 3 | 1 | 9 | 118 | 1 | 13 | 13400 | 1 | 9 | 200 | 1 | 9 | 13300 | 1 | 13 | 4360 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.58 | A | 7 | 993 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 700 | A | 7 | 0.6 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.62 | 4 | 0
1979-11-29 | 1900-11-28 | 11:00 | 11 | 595 | 1406 | 161 | 1 | 9 | 9 | 1 | 9 | 157 | 1 | 13 | 18300 | 1 | 9 | 700 | 1 | 9 | 18000 | 1 | 13 | 6120 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.55 | A | 7 | 993 | A | 7 | 310 | A | 7 | 9.8 | A | 7 | 4800 | A | 7 | 910 | A | 7 | 0.6 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.42 | 4 | 0
1979-11-29 | 1900-11-28 | 12:00 | 12 | 671 | 1406 | 187 | 1 | 9 | 4 | 1 | 9 | 185 | 1 | 13 | 21300 | 1 | 9 | 300 | 1 | 9 | 21100 | 1 | 13 | 7330 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.53 | A | 7 | 993 | A | 7 | 310 | A | 7 | 9.8 | A | 7 | 9700 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 4 | 0
1979-11-29 | 1900-11-28 | 13:00 | 13 | 679 | 1406 | 224 | 1 | 9 | 10 | 1 | 9 | 220 | 1 | 13 | 25300 | 1 | 9 | 900 | 1 | 9 | 24800 | 1 | 13 | 8250 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.51 | A | 7 | 993 | A | 7 | 320 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.5 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.44 | 4 | 0
1979-11-29 | 1900-11-28 | 14:00 | 14 | 619 | 1406 | 420 | 1 | 9 | 769 | 1 | 9 | 79 | 1 | 13 | 43600 | 1 | 9 | 74000 | 1 | 9 | 10800 | 1 | 13 | 1620 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -2.8 | 26.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.49 | A | 7 | 992 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.34 | 4 | 0
1979-11-29 | 1900-11-28 | 15:00 | 15 | 494 | 1406 | 347 | 1 | 9 | 862 | 1 | 9 | 40 | 1 | 13 | 36500 | 1 | 9 | 80100 | 1 | 9 | 8200 | 1 | 13 | 1040 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.45 | A | 7 | 991 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.14 | 4 | 0
1979-11-29 | 1900-11-28 | 16:00 | 16 | 315 | 1406 | 197 | 1 | 13 | 732 | 1 | 9 | 30 | 1 | 13 | 20600 | 1 | 13 | 61600 | 1 | 9 | 6800 | 1 | 13 | 750 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.43 | A | 7 | 991 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.06 | 4 | 0
1979-11-29 | 1900-11-28 | 17:00 | 17 | 96 | 1301 | 52 | 1 | 13 | 383 | 1 | 9 | 17 | 1 | 13 | 4800 | 1 | 13 | 21900 | 1 | 9 | 3100 | 1 | 13 | 330 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -12.8 | 8.96 | A | 7 | 0.45 | A | 7 | 990 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.032 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.16 | 4 | 0
1979-11-29 | 1900-11-28 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.5 | A | 7 | 990 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.46 | 4 | 0
1979-11-29 | 1900-11-28 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.53 | A | 7 | 990 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.56 | 4 | 0
1979-11-29 | 1900-11-28 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -12.2 | 10.04 | A | 7 | 0.57 | A | 7 | 990 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.74 | 4 | 0
1979-11-29 | 1900-11-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -11.7 | 10.94 | A | 7 | 0.6 | A | 7 | 989 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.74 | 4 | 0
1979-11-29 | 1900-11-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 4 | 0
1979-11-29 | 1900-11-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.6 | A | 7 | 989 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.94 | 4 | 0
1979-11-29 | 1900-11-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.6 | A | 7 | 989 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.94 | 4 | 0
1979-11-30 | 1900-11-29 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 988 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.04 | 5 | 0
1979-11-30 | 1900-11-29 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 987 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.14 | 5 | 0
1979-11-30 | 1900-11-29 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 987 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 5 | 0
1979-11-30 | 1900-11-29 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 987 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 5 | 0
1979-11-30 | 1900-11-29 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 987 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 5 | 0
1979-11-30 | 1900-11-29 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.54 | 5 | 0
1979-11-30 | 1900-11-29 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.54 | 5 | 0
1979-11-30 | 1900-11-29 | 8:00 | 8 | 51 | 949 | 28 | 1 | 13 | 82 | 1 | 13 | 20 | 1 | 13 | 2600 | 1 | 13 | 2600 | 1 | 13 | 2500 | 1 | 13 | 350 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 5 | 0
1979-11-30 | 1900-11-29 | 9:00 | 9 | 262 | 1406 | 94 | 1 | 13 | 104 | 1 | 9 | 74 | 1 | 13 | 10100 | 1 | 13 | 7900 | 1 | 9 | 8700 | 1 | 13 | 1590 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | -5 | 23 | A | 7 | -10.6 | 12.92 | A | 7 | 0.65 | A | 7 | 986 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 4270 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.82 | 5 | 0
1979-11-30 | 1900-11-29 | 10:00 | 10 | 453 | 1406 | 203 | 1 | 13 | 315 | 1 | 13 | 101 | 1 | 13 | 21400 | 1 | 13 | 28500 | 1 | 13 | 12100 | 1 | 13 | 1890 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | -4.4 | 24.08 | A | 7 | -10 | 14 | A | 7 | 0.66 | A | 7 | 986 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.9 | 5 | 0
1979-11-30 | 1900-11-29 | 11:00 | 11 | 592 | 1406 | 261 | 1 | 13 | 121 | 1 | 13 | 210 | 1 | 13 | 28600 | 1 | 13 | 11900 | 1 | 13 | 23600 | 1 | 13 | 5680 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | -2.2 | 28.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.61 | A | 7 | 985 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.38 | 5 | 0
1979-11-30 | 1900-11-29 | 12:00 | 12 | 668 | 1406 | 273 | 1 | 9 | 171 | 1 | 9 | 192 | 1 | 13 | 29900 | 1 | 9 | 17400 | 1 | 9 | 21600 | 1 | 13 | 4700 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 985 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 5 | 0
1979-11-30 | 1900-11-29 | 13:00 | 13 | 676 | 1406 | 336 | 1 | 9 | 249 | 1 | 9 | 215 | 1 | 13 | 35600 | 1 | 9 | 25600 | 1 | 9 | 23200 | 1 | 13 | 4890 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 0.6 | 33.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.5 | A | 7 | 984 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.68 | 5 | 0
1979-11-30 | 1900-11-29 | 14:00 | 14 | 616 | 1406 | 348 | 1 | 13 | 489 | 1 | 13 | 131 | 1 | 13 | 36900 | 1 | 13 | 47900 | 1 | 13 | 15800 | 1 | 13 | 2600 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | 2.2 | 35.96 | A | 7 | -10 | 14 | A | 7 | 0.4 | A | 7 | 982 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.3 | 5 | 0
1979-11-30 | 1900-11-29 | 15:00 | 15 | 492 | 1406 | 307 | 1 | 13 | 616 | 1 | 13 | 88 | 1 | 13 | 31500 | 1 | 13 | 56600 | 1 | 13 | 11600 | 1 | 13 | 1670 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 3.3 | 37.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.39 | A | 7 | 982 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.18 | 5 | 0
1979-11-30 | 1900-11-29 | 16:00 | 16 | 313 | 1406 | 134 | 1 | 13 | 306 | 1 | 13 | 65 | 1 | 13 | 14100 | 1 | 13 | 24200 | 1 | 13 | 8700 | 1 | 13 | 1170 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 2.2 | 35.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.42 | A | 7 | 982 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.38 | 5 | 0
1979-11-30 | 1900-11-29 | 17:00 | 17 | 95 | 1278 | 44 | 1 | 13 | 93 | 1 | 9 | 35 | 1 | 13 | 4400 | 1 | 13 | 3700 | 1 | 9 | 4100 | 1 | 13 | 670 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | 1.1 | 33.98 | A | 7 | -9.4 | 15.08 | A | 7 | 0.46 | A | 7 | 981 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | 0.034 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.68 | 5 | 0
1979-11-30 | 1900-11-29 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 0.6 | 33.08 | A | 7 | -10 | 14 | A | 7 | 0.45 | A | 7 | 982 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.6 | 5 | 0
1979-11-30 | 1900-11-29 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -1.1 | 30.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.49 | A | 7 | 981 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.92 | 5 | 0
1979-11-30 | 1900-11-29 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -1.1 | 30.02 | A | 7 | -10 | 14 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11 | 5 | 0
1979-11-30 | 1900-11-29 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -2.2 | 28.04 | A | 7 | -10 | 14 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.3 | 5 | 0
1979-11-30 | 1900-11-29 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -1.9 | 28.58 | A | 7 | -8.9 | 15.98 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 240 | A | 7 | 4.4 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.08 | 5 | 0
1979-11-30 | 1900-11-29 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -1.6 | 29.12 | A | 7 | -7.8 | 17.96 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 230 | A | 7 | 4.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.16 | 5 | 0
1979-11-30 | 1900-11-29 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | -1.4 | 29.48 | A | 7 | -6.8 | 19.76 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 250 | A | 7 | 4 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.76 | 5 | 0
1977-12-01 | 1900-11-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | -1.2 | 29.84 | A | 7 | -5.8 | 21.56 | A | 7 | 0.92 | A | 7 | 970 | A | 7 | 280 | A | 7 | 3.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.86 | 6 | 0
1977-12-01 | 1900-11-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | -1 | 30.2 | A | 7 | -4.8 | 23.36 | A | 7 | 0.85 | A | 7 | 970 | A | 7 | 270 | A | 7 | 3.5 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.06 | 6 | 0
1977-12-01 | 1900-11-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.7 | 30.74 | A | 7 | -3.7 | 25.34 | A | 7 | 0.85 | A | 7 | 970 | A | 7 | 270 | A | 7 | 3.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.94 | 6 | 0
1977-12-01 | 1900-11-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 970 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 6 | 0
1977-12-01 | 1900-11-30 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.82 | A | 7 | 970 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 6 | 0
1977-12-01 | 1900-11-30 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -0.6 | 30.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.82 | A | 7 | 970 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 6 | 0
1977-12-01 | 1900-11-30 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | 0 | 32 | A | 7 | -3.3 | 26.06 | A | 7 | 0.79 | A | 7 | 970 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 6 | 0
1977-12-01 | 1900-11-30 | 8:00 | 8 | 47 | 903 | 26 | 1 | 13 | 88 | 1 | 9 | 17 | 1 | 13 | 2300 | 1 | 13 | 3200 | 1 | 9 | 2100 | 1 | 13 | 300 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | 0 | 32 | A | 7 | -3.9 | 24.98 | A | 7 | 0.75 | A | 7 | 971 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 6 | 0
1977-12-01 | 1900-11-30 | 9:00 | 9 | 256 | 1407 | 135 | 1 | 13 | 496 | 1 | 9 | 44 | 1 | 13 | 13900 | 1 | 13 | 36700 | 1 | 9 | 7200 | 1 | 13 | 800 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.73 | A | 7 | 971 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.56 | 6 | 0
1977-12-01 | 1900-11-30 | 10:00 | 10 | 447 | 1407 | 270 | 1 | 9 | 679 | 1 | 9 | 51 | 1 | 13 | 28000 | 1 | 9 | 61800 | 1 | 9 | 8300 | 1 | 13 | 1070 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 2.8 | 37.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.67 | A | 7 | 972 | A | 7 | 250 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.86 | 6 | 0
1977-12-01 | 1900-11-30 | 11:00 | 11 | 586 | 1407 | 381 | 1 | 9 | 753 | 1 | 9 | 65 | 1 | 13 | 40100 | 1 | 9 | 72300 | 1 | 9 | 9800 | 1 | 13 | 1400 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 4.4 | 39.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.6 | A | 7 | 972 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.16 | 6 | 0
1977-12-01 | 1900-11-30 | 12:00 | 12 | 662 | 1407 | 205 | 1 | 9 | 125 | 1 | 9 | 145 | 1 | 13 | 22700 | 1 | 9 | 12800 | 1 | 9 | 16700 | 1 | 13 | 3540 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 972 | A | 7 | 290 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 980 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 6 | 0
1977-12-01 | 1900-11-30 | 13:00 | 13 | 672 | 1407 | 185 | 1 | 9 | 11 | 1 | 9 | 179 | 1 | 13 | 21000 | 1 | 9 | 900 | 1 | 9 | 20600 | 1 | 13 | 7170 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.57 | A | 7 | 973 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 980 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 6 | 0
1977-12-01 | 1900-11-30 | 14:00 | 14 | 612 | 1407 | 221 | 1 | 9 | 71 | 1 | 9 | 189 | 1 | 13 | 24100 | 1 | 9 | 7000 | 1 | 9 | 21100 | 1 | 13 | 5360 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 5 | 41 | A | 7 | -2.8 | 26.96 | A | 7 | 0.58 | A | 7 | 973 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 980 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.96 | 6 | 0
1977-12-01 | 1900-11-30 | 15:00 | 15 | 489 | 1407 | 251 | 1 | 13 | 384 | 1 | 13 | 115 | 1 | 13 | 26100 | 1 | 13 | 35600 | 1 | 13 | 13700 | 1 | 13 | 2190 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 5.6 | 42.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.53 | A | 7 | 973 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.76 | 6 | 0
1977-12-01 | 1900-11-30 | 16:00 | 16 | 310 | 1407 | 136 | 1 | 13 | 221 | 1 | 13 | 87 | 1 | 13 | 14300 | 1 | 13 | 17400 | 1 | 13 | 10400 | 1 | 13 | 1700 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | 6.1 | 42.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.51 | A | 7 | 973 | A | 7 | 280 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.56 | 6 | 0
1977-12-01 | 1900-11-30 | 17:00 | 17 | 93 | 1278 | 42 | 1 | 13 | 239 | 1 | 9 | 21 | 1 | 13 | 4000 | 1 | 13 | 11900 | 1 | 9 | 3100 | 1 | 13 | 380 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 5 | 41 | A | 7 | -5 | 23 | A | 7 | 0.49 | A | 7 | 974 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.7 | 6 | 0
1977-12-01 | 1900-11-30 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.53 | A | 7 | 974 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.12 | 6 | 0
1977-12-01 | 1900-11-30 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -5 | 23 | A | 7 | 0.59 | A | 7 | 975 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.6 | 6 | 0
1977-12-01 | 1900-11-30 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.42 | 6 | 0
1977-12-01 | 1900-11-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 2.2 | 35.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.57 | A | 7 | 975 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.42 | 6 | 0
1977-12-01 | 1900-11-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 2.2 | 35.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.62 | A | 7 | 976 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.78 | 6 | 0
1977-12-01 | 1900-11-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 2.2 | 35.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.62 | A | 7 | 975 | A | 7 | 300 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.78 | 6 | 0
1977-12-01 | 1900-11-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 975 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 6 | 0
1977-12-02 | 1900-12-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.85 | A | 7 | 975 | A | 7 | 220 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 7 | 0
1977-12-02 | 1900-12-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.94 | 7 | 0
1977-12-02 | 1900-12-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.96 | 7 | 0
1977-12-02 | 1900-12-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 974 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 7 | 0
1977-12-02 | 1900-12-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.06 | 7 | 0
1977-12-02 | 1900-12-01 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.06 | 7 | 0
1977-12-02 | 1900-12-01 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.06 | 7 | 0
1977-12-02 | 1900-12-01 | 8:00 | 8 | 44 | 880 | 16 | 1 | 13 | 9 | 1 | 9 | 15 | 1 | 13 | 1700 | 1 | 13 | 500 | 1 | 9 | 1700 | 1 | 13 | 370 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.9 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.06 | 7 | 0
1977-12-02 | 1900-12-01 | 9:00 | 9 | 252 | 1407 | 99 | 1 | 13 | 47 | 1 | 9 | 91 | 1 | 13 | 10800 | 1 | 13 | 3800 | 1 | 9 | 10200 | 1 | 13 | 2050 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 973 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 7 | 0
1977-12-02 | 1900-12-01 | 10:00 | 10 | 443 | 1407 | 148 | 1 | 9 | 5 | 1 | 9 | 146 | 1 | 13 | 16300 | 1 | 9 | 400 | 1 | 9 | 16200 | 1 | 13 | 4870 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 973 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 0.9 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 7 | 0
1977-12-02 | 1900-12-01 | 11:00 | 11 | 582 | 1407 | 147 | 1 | 9 | 14 | 1 | 9 | 141 | 1 | 13 | 16800 | 1 | 9 | 1000 | 1 | 9 | 16300 | 1 | 13 | 5600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 972 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 0.9 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 7 | 0
1977-12-02 | 1900-12-01 | 12:00 | 12 | 659 | 1407 | 211 | 1 | 9 | 4 | 1 | 9 | 209 | 1 | 13 | 23700 | 1 | 9 | 300 | 1 | 9 | 23500 | 1 | 13 | 7840 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -1.7 | 28.94 | A | 7 | 0.62 | A | 7 | 971 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 7 | 0
1977-12-02 | 1900-12-01 | 13:00 | 13 | 669 | 1407 | 184 | 1 | 9 | 12 | 1 | 9 | 178 | 1 | 13 | 21000 | 1 | 9 | 1000 | 1 | 9 | 20500 | 1 | 13 | 7120 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.63 | A | 7 | 969 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 1 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.02 | 7 | 0
1977-12-02 | 1900-12-01 | 14:00 | 14 | 610 | 1407 | 170 | 1 | 9 | 0 | 1 | 9 | 170 | 1 | 13 | 19200 | 1 | 9 | 0 | 1 | 9 | 19200 | 1 | 13 | 6540 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 0 | 32 | A | 7 | 0.63 | A | 7 | 967 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28 | 7 | 0
1977-12-02 | 1900-12-01 | 15:00 | 15 | 487 | 1407 | 168 | 1 | 9 | 179 | 1 | 9 | 106 | 1 | 13 | 18200 | 1 | 9 | 17000 | 1 | 9 | 12300 | 1 | 13 | 2060 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 7.8 | 46.04 | A | 7 | 0 | 32 | A | 7 | 0.58 | A | 7 | 968 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 1 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.4 | 7 | 0
1977-12-02 | 1900-12-01 | 16:00 | 16 | 309 | 1407 | 47 | 1 | 13 | 4 | 1 | 9 | 46 | 1 | 13 | 5500 | 1 | 13 | 100 | 1 | 9 | 5400 | 1 | 13 | 1810 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 0 | 32 | A | 7 | 0.6 | A | 7 | 968 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 1 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.6 | 7 | 0
1977-12-02 | 1900-12-01 | 17:00 | 17 | 92 | 1278 | 21 | 1 | 13 | 1 | 1 | 9 | 21 | 1 | 13 | 2400 | 1 | 13 | 0 | 1 | 9 | 2400 | 1 | 13 | 730 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.65 | A | 7 | 968 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.08 | 7 | 0
1977-12-02 | 1900-12-01 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 968 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 7 | 0
1977-12-02 | 1900-12-01 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0 | 32 | A | 7 | 0.79 | A | 7 | 969 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.7 | 7 | 0
1977-12-02 | 1900-12-01 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.82 | A | 7 | 969 | A | 7 | 30 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.02 | 7 | 0
1977-12-02 | 1900-12-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.85 | A | 7 | 970 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 7 | 0
1977-12-02 | 1900-12-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.85 | A | 7 | 971 | A | 7 | 10 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 7 | 0
1977-12-02 | 1900-12-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 30 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.42 | 7 | 0
1977-12-02 | 1900-12-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 972 | A | 7 | 20 | A | 7 | 3.6 | A | 7 | 800 | A | 7 | 90 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 7 | 0
1977-12-03 | 1900-12-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 972 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 2400 | A | 7 | 90 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 1 | 0
1977-12-03 | 1900-12-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 1 | 0
1977-12-03 | 1900-12-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 1 | 0
1977-12-03 | 1900-12-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 1600 | A | 7 | 120 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 1 | 0
1977-12-03 | 1900-12-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 90 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 1 | 0
1977-12-03 | 1900-12-02 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 120 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 1 | 0
1977-12-03 | 1900-12-02 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 120 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.92 | 1 | 0
1977-12-03 | 1900-12-02 | 8:00 | 8 | 42 | 856 | 11 | 1 | 13 | 1 | 1 | 9 | 11 | 1 | 13 | 1300 | 1 | 13 | 0 | 1 | 9 | 1300 | 1 | 13 | 400 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 974 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 120 | A | 7 | 1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 1 | 0
1977-12-03 | 1900-12-02 | 9:00 | 9 | 248 | 1408 | 48 | 1 | 13 | 1 | 1 | 9 | 48 | 1 | 13 | 5500 | 1 | 13 | 0 | 1 | 9 | 5500 | 1 | 13 | 1740 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 100 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 120 | A | 7 | 1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 1 | 0
1977-12-03 | 1900-12-02 | 10:00 | 10 | 439 | 1408 | 103 | 1 | 9 | 8 | 1 | 9 | 100 | 1 | 13 | 11600 | 1 | 9 | 500 | 1 | 9 | 11500 | 1 | 13 | 3800 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 180 | A | 7 | 1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 1 | 0
1977-12-03 | 1900-12-02 | 11:00 | 11 | 579 | 1408 | 151 | 1 | 9 | 2 | 1 | 9 | 150 | 1 | 13 | 17100 | 1 | 9 | 100 | 1 | 9 | 17100 | 1 | 13 | 5830 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 0 | 32 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.8 | 1 | 0
1977-12-03 | 1900-12-02 | 12:00 | 12 | 656 | 1408 | 218 | 1 | 9 | 6 | 1 | 9 | 215 | 1 | 13 | 24400 | 1 | 9 | 500 | 1 | 9 | 24200 | 1 | 13 | 7940 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.85 | A | 7 | 975 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 1 | 0
1977-12-03 | 1900-12-02 | 13:00 | 13 | 666 | 1408 | 217 | 1 | 9 | 4 | 1 | 9 | 215 | 1 | 13 | 24300 | 1 | 9 | 300 | 1 | 9 | 24200 | 1 | 13 | 8030 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 0 | 32 | A | 7 | 0.85 | A | 7 | 973 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 180 | A | 7 | 1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 1 | 0
1977-12-03 | 1900-12-02 | 14:00 | 14 | 608 | 1408 | 217 | 1 | 9 | 2 | 1 | 9 | 217 | 1 | 13 | 24200 | 1 | 9 | 200 | 1 | 9 | 24100 | 1 | 13 | 7550 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 0 | 32 | A | 7 | 0.85 | A | 7 | 974 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 1 | 0
1977-12-03 | 1900-12-02 | 15:00 | 15 | 486 | 1408 | 162 | 1 | 9 | 0 | 1 | 9 | 162 | 1 | 13 | 17900 | 1 | 9 | 0 | 1 | 9 | 17900 | 1 | 13 | 5480 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.85 | A | 7 | 974 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 1 | 0
1977-12-03 | 1900-12-02 | 16:00 | 16 | 308 | 1408 | 97 | 1 | 13 | 0 | 1 | 9 | 97 | 1 | 13 | 10600 | 1 | 13 | 0 | 1 | 9 | 10600 | 1 | 13 | 3080 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.85 | A | 7 | 974 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 1 | 0
1977-12-03 | 1900-12-02 | 17:00 | 17 | 92 | 1279 | 25 | 1 | 13 | 0 | 1 | 9 | 25 | 1 | 13 | 2800 | 1 | 13 | 0 | 1 | 9 | 2800 | 1 | 13 | 820 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.85 | A | 7 | 974 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 210 | A | 7 | 1 | E | 8 | 0.082 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.52 | 1 | 0
1977-12-03 | 1900-12-02 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.82 | A | 7 | 975 | A | 7 | 60 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.14 | 1 | 0
1977-12-03 | 1900-12-02 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 976 | A | 7 | 90 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 210 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 1 | 0
1977-12-03 | 1900-12-02 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 976 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 210 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 1 | 0
1977-12-03 | 1900-12-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 976 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 210 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 1 | 0
1977-12-03 | 1900-12-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 976 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 150 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 1 | 0
1977-12-03 | 1900-12-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 976 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 120 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 1 | 0
1977-12-03 | 1900-12-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 975 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 3200 | A | 7 | 120 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 1 | 0
1977-12-04 | 1900-12-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 100 | A | 7 | 2.1 | A | 7 | 800 | A | 7 | 60 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.94 | 2 | 0
1977-12-04 | 1900-12-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 400 | A | 7 | 30 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.94 | 2 | 0
1977-12-04 | 1900-12-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 975 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 2 | 0
1977-12-04 | 1900-12-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 974 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 2 | 0
1977-12-04 | 1900-12-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 974 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 2 | 0
1977-12-04 | 1900-12-03 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 974 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 2 | 0
1977-12-04 | 1900-12-03 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 2 | 0
1977-12-04 | 1900-12-03 | 8:00 | 8 | 40 | 833 | 15 | 1 | 13 | 0 | 1 | 9 | 15 | 1 | 13 | 1700 | 1 | 13 | 0 | 1 | 9 | 1700 | 1 | 13 | 510 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0.9 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 2 | 0
1977-12-04 | 1900-12-03 | 9:00 | 9 | 244 | 1408 | 70 | 1 | 13 | 0 | 1 | 9 | 70 | 1 | 13 | 7700 | 1 | 13 | 0 | 1 | 9 | 7700 | 1 | 13 | 2240 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 972 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0.9 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 2 | 0
1977-12-04 | 1900-12-03 | 10:00 | 10 | 436 | 1408 | 143 | 1 | 9 | 1 | 1 | 9 | 143 | 1 | 13 | 15800 | 1 | 9 | 100 | 1 | 9 | 15800 | 1 | 13 | 4760 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0.9 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 2 | 0
1977-12-04 | 1900-12-03 | 11:00 | 11 | 575 | 1408 | 217 | 1 | 9 | 0 | 1 | 9 | 217 | 1 | 13 | 23900 | 1 | 9 | 0 | 1 | 9 | 23900 | 1 | 13 | 7230 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 0.9 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 2 | 0
1977-12-04 | 1900-12-03 | 12:00 | 12 | 653 | 1408 | 222 | 1 | 9 | 1 | 1 | 9 | 221 | 1 | 13 | 24700 | 1 | 9 | 100 | 1 | 9 | 24700 | 1 | 13 | 8040 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.62 | 2 | 0
1977-12-04 | 1900-12-03 | 13:00 | 13 | 663 | 1408 | 240 | 1 | 9 | 1 | 1 | 9 | 239 | 1 | 13 | 26600 | 1 | 9 | 100 | 1 | 9 | 26600 | 1 | 13 | 8490 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 972 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1977-12-04 | 1900-12-03 | 14:00 | 14 | 606 | 1408 | 228 | 1 | 9 | 0 | 1 | 9 | 228 | 1 | 13 | 25200 | 1 | 9 | 0 | 1 | 9 | 25200 | 1 | 13 | 7720 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 971 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1977-12-04 | 1900-12-03 | 15:00 | 15 | 484 | 1408 | 96 | 1 | 9 | 1 | 1 | 9 | 95 | 1 | 13 | 11000 | 1 | 9 | 100 | 1 | 9 | 11000 | 1 | 13 | 3820 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 970 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 2 | 0
1977-12-04 | 1900-12-03 | 16:00 | 16 | 307 | 1408 | 56 | 1 | 13 | 0 | 1 | 9 | 56 | 1 | 13 | 6400 | 1 | 13 | 0 | 1 | 9 | 6400 | 1 | 13 | 2120 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 969 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 200 | A | 7 | 30 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 2 | 0
1977-12-04 | 1900-12-03 | 17:00 | 17 | 91 | 1279 | 18 | 1 | 13 | 0 | 1 | 9 | 18 | 1 | 13 | 2100 | 1 | 13 | 0 | 1 | 9 | 2100 | 1 | 13 | 640 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 969 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 400 | A | 7 | 30 | A | 7 | 1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.42 | 2 | 0
1977-12-04 | 1900-12-03 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 968 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1977-12-04 | 1900-12-03 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 967 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 400 | A | 7 | 60 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1977-12-04 | 1900-12-03 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 967 | A | 7 | 80 | A | 7 | 3.6 | A | 7 | 400 | A | 7 | 60 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1977-12-04 | 1900-12-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 967 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1977-12-04 | 1900-12-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 967 | A | 7 | 20 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 30 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1977-12-04 | 1900-12-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 966 | A | 7 | 30 | A | 7 | 3.6 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1977-12-04 | 1900-12-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 966 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 800 | A | 7 | 120 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1977-12-05 | 1900-12-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 966 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 400 | A | 7 | 60 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 3 | 0
1977-12-05 | 1900-12-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 966 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 60 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 3 | 0
1977-12-05 | 1900-12-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 966 | A | 7 | 350 | A | 7 | 5.7 | A | 7 | 1300 | A | 7 | 60 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 3 | 0
1977-12-05 | 1900-12-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 967 | A | 7 | 330 | A | 7 | 5.7 | A | 7 | 1300 | A | 7 | 60 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.94 | 3 | 0
1977-12-05 | 1900-12-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 968 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 1300 | A | 7 | 90 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 3 | 0
1977-12-05 | 1900-12-04 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 968 | A | 7 | 350 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 120 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.96 | 3 | 0
1977-12-05 | 1900-12-04 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 969 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.06 | 3 | 0
1977-12-05 | 1900-12-04 | 8:00 | 8 | 38 | 810 | 8 | 1 | 13 | 0 | 1 | 9 | 8 | 1 | 13 | 1000 | 1 | 13 | 0 | 1 | 9 | 1000 | 1 | 13 | 300 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 970 | A | 7 | 340 | A | 7 | 6.7 | A | 7 | 3200 | A | 7 | 180 | A | 7 | 0.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 3 | 0
1977-12-05 | 1900-12-04 | 9:00 | 9 | 240 | 1409 | 68 | 1 | 13 | 1 | 1 | 9 | 68 | 1 | 13 | 7500 | 1 | 13 | 0 | 1 | 9 | 7500 | 1 | 13 | 2190 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 971 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 1600 | A | 7 | 240 | A | 7 | 0.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 3 | 0
1977-12-05 | 1900-12-04 | 10:00 | 10 | 432 | 1409 | 132 | 1 | 9 | 1 | 1 | 9 | 131 | 1 | 13 | 14600 | 1 | 9 | 100 | 1 | 9 | 14500 | 1 | 13 | 4500 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.85 | A | 7 | 973 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 800 | A | 7 | 150 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.82 | 3 | 0
1977-12-05 | 1900-12-04 | 11:00 | 11 | 572 | 1409 | 205 | 1 | 9 | 1 | 1 | 9 | 205 | 1 | 13 | 22700 | 1 | 9 | 100 | 1 | 9 | 22700 | 1 | 13 | 7000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.85 | A | 7 | 974 | A | 7 | 320 | A | 7 | 9.3 | A | 7 | 800 | A | 7 | 210 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.94 | 3 | 0
1977-12-05 | 1900-12-04 | 12:00 | 12 | 650 | 1409 | 232 | 1 | 9 | 0 | 1 | 9 | 232 | 1 | 13 | 25800 | 1 | 9 | 0 | 1 | 9 | 25800 | 1 | 13 | 8230 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.85 | A | 7 | 974 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 800 | A | 7 | 240 | A | 7 | 0.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.86 | 3 | 0
1977-12-05 | 1900-12-04 | 13:00 | 13 | 661 | 1409 | 220 | 1 | 9 | 2 | 1 | 9 | 219 | 1 | 13 | 24600 | 1 | 9 | 200 | 1 | 9 | 24500 | 1 | 13 | 8070 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.84 | A | 7 | 975 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 3200 | A | 7 | 340 | A | 7 | 0.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 3 | 0
1977-12-05 | 1900-12-04 | 14:00 | 14 | 604 | 1409 | 203 | 1 | 9 | 1 | 1 | 9 | 203 | 1 | 13 | 22700 | 1 | 9 | 100 | 1 | 9 | 22600 | 1 | 13 | 7240 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.84 | A | 7 | 976 | A | 7 | 330 | A | 7 | 8.2 | A | 7 | 1600 | A | 7 | 210 | A | 7 | 0.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 3 | 0
1977-12-05 | 1900-12-04 | 15:00 | 15 | 483 | 1409 | 147 | 1 | 9 | 1 | 1 | 9 | 147 | 1 | 13 | 16400 | 1 | 9 | 100 | 1 | 9 | 16400 | 1 | 13 | 5170 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 320 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 460 | A | 7 | 0.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 3 | 0
1977-12-05 | 1900-12-04 | 16:00 | 16 | 306 | 1409 | 94 | 1 | 13 | 0 | 1 | 9 | 94 | 1 | 13 | 10300 | 1 | 13 | 0 | 1 | 9 | 10300 | 1 | 13 | 3020 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 979 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 0.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.54 | 3 | 0
1977-12-05 | 1900-12-04 | 17:00 | 17 | 90 | 1256 | 30 | 1 | 13 | 41 | 1 | 13 | 26 | 1 | 13 | 3200 | 1 | 13 | 2000 | 1 | 13 | 3000 | 1 | 13 | 540 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | -8.3 | 17.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 0.5 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.64 | 3 | 0
1977-12-05 | 1900-12-04 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 982 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 6100 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.68 | 3 | 0
1977-12-05 | 1900-12-04 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -13.9 | 6.98 | A | 7 | 0.77 | A | 7 | 983 | A | 7 | 330 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.88 | 3 | 0
1977-12-05 | 1900-12-04 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 984 | A | 7 | 320 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 3 | 0
1977-12-05 | 1900-12-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -15 | 5 | A | 7 | 0.73 | A | 7 | 985 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.8 | 3 | 0
1977-12-05 | 1900-12-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -17.2 | 1.04 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.26 | 3 | 0
1977-12-05 | 1900-12-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -17.8 | -0.04 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.34 | 3 | 0
1977-12-05 | 1900-12-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -18.9 | -2.02 | A | 7 | 0.63 | A | 7 | 988 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.22 | 3 | 0
1977-12-06 | 1900-12-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -20 | -4 | A | 7 | 0.6 | A | 7 | 989 | A | 7 | 340 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.2 | 4 | 0
1977-12-06 | 1900-12-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -19.4 | -2.92 | A | 7 | 0.66 | A | 7 | 989 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.02 | 4 | 0
1977-12-06 | 1900-12-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -20 | -4 | A | 7 | 0.63 | A | 7 | 990 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.1 | 4 | 0
1977-12-06 | 1900-12-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -19.4 | -2.92 | A | 7 | 0.66 | A | 7 | 990 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.02 | 4 | 0
1977-12-06 | 1900-12-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -19.4 | -2.92 | A | 7 | 0.66 | A | 7 | 990 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.02 | 4 | 0
1977-12-06 | 1900-12-05 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -19.4 | -2.92 | A | 7 | 0.69 | A | 7 | 991 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.92 | 4 | 0
1977-12-06 | 1900-12-05 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -21.1 | -5.98 | A | 7 | 0.6 | A | 7 | 991 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -7.08 | 4 | 0
1977-12-06 | 1900-12-05 | 8:00 | 8 | 36 | 810 | 27 | 1 | 13 | 166 | 1 | 9 | 11 | 1 | 13 | 2000 | 1 | 13 | 6900 | 1 | 9 | 1700 | 1 | 13 | 210 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -21.7 | -7.06 | A | 7 | 0.63 | A | 7 | 992 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.06 | 4 | 0
1977-12-06 | 1900-12-05 | 9:00 | 9 | 237 | 1409 | 137 | 1 | 13 | 631 | 1 | 9 | 29 | 1 | 13 | 14300 | 1 | 13 | 48900 | 1 | 9 | 6000 | 1 | 13 | 630 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -21.1 | -5.98 | A | 7 | 0.66 | A | 7 | 993 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.88 | 4 | 0
1977-12-06 | 1900-12-05 | 10:00 | 10 | 429 | 1409 | 291 | 1 | 9 | 812 | 1 | 9 | 42 | 1 | 13 | 30600 | 1 | 9 | 73300 | 1 | 9 | 8200 | 1 | 13 | 990 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -20 | -4 | A | 7 | 0.63 | A | 7 | 993 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.1 | 4 | 0
1977-12-06 | 1900-12-05 | 11:00 | 11 | 569 | 1409 | 417 | 1 | 9 | 898 | 1 | 9 | 52 | 1 | 13 | 43800 | 1 | 9 | 85300 | 1 | 9 | 9300 | 1 | 13 | 1240 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -19.4 | -2.92 | A | 7 | 0.6 | A | 7 | 993 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.12 | 4 | 0
1977-12-06 | 1900-12-05 | 12:00 | 12 | 648 | 1409 | 485 | 1 | 9 | 923 | 1 | 9 | 57 | 1 | 13 | 50800 | 1 | 9 | 89200 | 1 | 9 | 9600 | 1 | 13 | 1370 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -18.3 | -0.94 | A | 7 | 0.61 | A | 7 | 992 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.24 | 4 | 0
1977-12-06 | 1900-12-05 | 13:00 | 13 | 659 | 1409 | 499 | 1 | 9 | 935 | 1 | 9 | 58 | 1 | 13 | 52300 | 1 | 9 | 90500 | 1 | 9 | 9800 | 1 | 13 | 1390 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -17.8 | -0.04 | A | 7 | 0.61 | A | 7 | 991 | A | 7 | 270 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.44 | 4 | 0
1977-12-06 | 1900-12-05 | 14:00 | 14 | 602 | 1409 | 447 | 1 | 9 | 912 | 1 | 9 | 54 | 1 | 13 | 46900 | 1 | 9 | 87300 | 1 | 9 | 9400 | 1 | 13 | 1290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -17.8 | -0.04 | A | 7 | 0.58 | A | 7 | 991 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.54 | 4 | 0
1977-12-06 | 1900-12-05 | 15:00 | 15 | 481 | 1409 | 340 | 1 | 9 | 852 | 1 | 9 | 46 | 1 | 13 | 35700 | 1 | 9 | 78700 | 1 | 9 | 8700 | 1 | 13 | 1090 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -17.2 | 1.04 | A | 7 | 0.58 | A | 7 | 990 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.46 | 4 | 0
1977-12-06 | 1900-12-05 | 16:00 | 16 | 305 | 1409 | 180 | 1 | 13 | 629 | 1 | 9 | 41 | 1 | 13 | 18200 | 1 | 13 | 51300 | 1 | 9 | 7100 | 1 | 13 | 800 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | -10.6 | 12.92 | A | 7 | -17.8 | -0.04 | A | 7 | 0.56 | A | 7 | 990 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.54 | 4 | 0
1977-12-06 | 1900-12-05 | 17:00 | 17 | 90 | 1256 | 34 | 1 | 13 | 22 | 1 | 13 | 32 | 1 | 13 | 3700 | 1 | 13 | 1300 | 1 | 13 | 3600 | 1 | 13 | 720 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | -11.7 | 10.94 | A | 7 | -17.8 | -0.04 | A | 7 | 0.61 | A | 7 | 990 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.44 | 4 | 0
1977-12-06 | 1900-12-05 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 989 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.64 | 4 | 0
1977-12-06 | 1900-12-05 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 989 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.64 | 4 | 0
1977-12-06 | 1900-12-05 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -17.2 | 1.04 | A | 7 | 0.61 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.36 | 4 | 0
1977-12-06 | 1900-12-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -16.7 | 1.94 | A | 7 | 0.64 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.54 | 4 | 0
1977-12-06 | 1900-12-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -16.1 | 3.02 | A | 7 | 0.67 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.72 | 4 | 0
1977-12-06 | 1900-12-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -15.6 | 3.92 | A | 7 | 0.67 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.52 | 4 | 0
1977-12-06 | 1900-12-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -15 | 5 | A | 7 | 0.7 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.7 | 4 | 0
1977-12-07 | 1900-12-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -15.6 | 3.92 | A | 7 | 0.67 | A | 7 | 987 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.52 | 5 | 0
1977-12-07 | 1900-12-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -15.6 | 3.92 | A | 7 | 0.67 | A | 7 | 987 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.52 | 5 | 0
1977-12-07 | 1900-12-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -10 | 14 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 986 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.6 | 5 | 0
1977-12-07 | 1900-12-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 985 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 5 | 0
1977-12-07 | 1900-12-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 985 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 5 | 0
1977-12-07 | 1900-12-06 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 985 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 5 | 0
1977-12-07 | 1900-12-06 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 984 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 5 | 0
1977-12-07 | 1900-12-06 | 8:00 | 8 | 34 | 787 | 11 | 1 | 13 | 3 | 1 | 9 | 11 | 1 | 13 | 1300 | 1 | 13 | 0 | 1 | 9 | 1300 | 1 | 13 | 390 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 984 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 0.5 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.68 | 5 | 0
1977-12-07 | 1900-12-06 | 9:00 | 9 | 233 | 1409 | 81 | 1 | 13 | 80 | 1 | 13 | 67 | 1 | 13 | 8700 | 1 | 13 | 5700 | 1 | 13 | 7700 | 1 | 13 | 1430 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -10 | 14 | A | 7 | -13.9 | 6.98 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.5 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.78 | 5 | 0
1977-12-07 | 1900-12-06 | 10:00 | 10 | 425 | 1409 | 245 | 1 | 9 | 565 | 1 | 9 | 72 | 1 | 13 | 25200 | 1 | 9 | 50000 | 1 | 9 | 10000 | 1 | 13 | 1350 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -13.9 | 6.98 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.18 | 5 | 0
1977-12-07 | 1900-12-06 | 11:00 | 11 | 566 | 1409 | 384 | 1 | 9 | 725 | 1 | 9 | 90 | 1 | 13 | 40000 | 1 | 9 | 69000 | 1 | 9 | 12200 | 1 | 13 | 1790 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 981 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.04 | 5 | 0
1977-12-07 | 1900-12-06 | 12:00 | 12 | 645 | 1409 | 448 | 1 | 9 | 754 | 1 | 9 | 99 | 1 | 13 | 46900 | 1 | 9 | 73600 | 1 | 9 | 13000 | 1 | 13 | 2060 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.58 | A | 7 | 980 | A | 7 | 130 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.64 | 5 | 0
1977-12-07 | 1900-12-06 | 13:00 | 13 | 657 | 1409 | 463 | 1 | 9 | 770 | 1 | 9 | 101 | 1 | 13 | 48600 | 1 | 9 | 75400 | 1 | 9 | 13300 | 1 | 13 | 2110 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.42 | 5 | 0
1977-12-07 | 1900-12-06 | 14:00 | 14 | 601 | 1409 | 410 | 1 | 9 | 735 | 1 | 9 | 94 | 1 | 13 | 42900 | 1 | 9 | 70800 | 1 | 9 | 12500 | 1 | 13 | 1910 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -10 | 14 | A | 7 | 0.53 | A | 7 | 977 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.1 | 5 | 0
1977-12-07 | 1900-12-06 | 15:00 | 15 | 480 | 1409 | 306 | 1 | 9 | 656 | 1 | 9 | 80 | 1 | 13 | 31700 | 1 | 9 | 60100 | 1 | 9 | 11100 | 1 | 13 | 1530 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.56 | A | 7 | 976 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.08 | 5 | 0
1977-12-07 | 1900-12-06 | 16:00 | 16 | 304 | 1409 | 163 | 1 | 13 | 472 | 1 | 9 | 60 | 1 | 13 | 16600 | 1 | 13 | 37000 | 1 | 9 | 8500 | 1 | 13 | 1070 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.58 | A | 7 | 975 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.18 | 5 | 0
1977-12-07 | 1900-12-06 | 17:00 | 17 | 90 | 1257 | 26 | 1 | 13 | 26 | 1 | 13 | 24 | 1 | 13 | 2900 | 1 | 13 | 1200 | 1 | 13 | 2800 | 1 | 13 | 500 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | -2.2 | 28.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.61 | A | 7 | 975 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.38 | 5 | 0
1977-12-07 | 1900-12-06 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | -2.8 | 26.96 | A | 7 | -8.9 | 15.98 | A | 7 | 0.63 | A | 7 | 974 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.58 | 5 | 0
1977-12-07 | 1900-12-06 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.66 | A | 7 | 974 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 5 | 0
1977-12-07 | 1900-12-06 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.66 | A | 7 | 973 | A | 7 | 110 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 5 | 0
1977-12-07 | 1900-12-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -8.3 | 17.06 | A | 7 | 0.66 | A | 7 | 972 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.76 | 5 | 0
1977-12-07 | 1900-12-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.63 | A | 7 | 972 | A | 7 | 150 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.36 | 5 | 0
1977-12-07 | 1900-12-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.63 | A | 7 | 971 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.36 | 5 | 0
1977-12-07 | 1900-12-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 970 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 5 | 0
1977-12-08 | 1900-12-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 969 | A | 7 | 170 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 6 | 0
1977-12-08 | 1900-12-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -5 | 23 | A | 7 | 0.72 | A | 7 | 969 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 490 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.7 | 6 | 0
1977-12-08 | 1900-12-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.75 | A | 7 | 969 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 460 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 6 | 0
1977-12-08 | 1900-12-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 969 | A | 7 | 50 | A | 7 | 5.2 | A | 7 | 1300 | A | 7 | 120 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1977-12-08 | 1900-12-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 969 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 1300 | A | 7 | 120 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1977-12-08 | 1900-12-07 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 968 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 3200 | A | 7 | 90 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.98 | 6 | 0
1977-12-08 | 1900-12-07 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.96 | A | 7 | 968 | A | 7 | 110 | A | 7 | 5.2 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.66 | 6 | 0
1977-12-08 | 1900-12-07 | 8:00 | 8 | 32 | 764 | 10 | 1 | 13 | 2 | 1 | 9 | 9 | 1 | 13 | 1100 | 1 | 13 | 0 | 1 | 9 | 1100 | 1 | 13 | 330 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.92 | A | 7 | 968 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 3200 | A | 7 | 120 | A | 7 | 0.8 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.28 | 6 | 0
1977-12-08 | 1900-12-07 | 9:00 | 9 | 230 | 1410 | 32 | 1 | 13 | 7 | 1 | 9 | 31 | 1 | 13 | 3800 | 1 | 13 | 100 | 1 | 9 | 3700 | 1 | 13 | 1200 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.92 | A | 7 | 969 | A | 7 | 20 | A | 7 | 2.6 | A | 7 | 2400 | A | 7 | 120 | A | 7 | 0.9 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.26 | 6 | 0
1977-12-08 | 1900-12-07 | 10:00 | 10 | 422 | 1410 | 134 | 1 | 9 | 9 | 1 | 9 | 131 | 1 | 13 | 14800 | 1 | 9 | 600 | 1 | 9 | 14600 | 1 | 13 | 4430 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.92 | A | 7 | 970 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 2400 | A | 7 | 90 | A | 7 | 0.9 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.26 | 6 | 0
1977-12-08 | 1900-12-07 | 11:00 | 11 | 563 | 1410 | 214 | 1 | 9 | 7 | 1 | 9 | 211 | 1 | 13 | 23500 | 1 | 9 | 600 | 1 | 9 | 23300 | 1 | 13 | 7000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.92 | A | 7 | 971 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 4800 | A | 7 | 210 | A | 7 | 0.9 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 6 | 0
1977-12-08 | 1900-12-07 | 12:00 | 12 | 642 | 1410 | 272 | 1 | 9 | 3 | 1 | 9 | 270 | 1 | 13 | 29700 | 1 | 9 | 300 | 1 | 9 | 29600 | 1 | 13 | 8740 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 972 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 800 | A | 7 | 210 | A | 7 | 0.8 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 6 | 0
1977-12-08 | 1900-12-07 | 13:00 | 13 | 655 | 1410 | 221 | 1 | 9 | 9 | 1 | 9 | 216 | 1 | 13 | 24600 | 1 | 9 | 800 | 1 | 9 | 24300 | 1 | 13 | 7950 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -7.2 | 19.04 | A | 7 | 0.81 | A | 7 | 972 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 8000 | A | 7 | 430 | A | 7 | 0.7 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 6 | 0
1977-12-08 | 1900-12-07 | 14:00 | 14 | 599 | 1410 | 237 | 1 | 9 | 3 | 1 | 9 | 235 | 1 | 13 | 26000 | 1 | 9 | 300 | 1 | 9 | 25900 | 1 | 13 | 7750 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -8.3 | 17.06 | A | 7 | 0.78 | A | 7 | 974 | A | 7 | 330 | A | 7 | 10.3 | A | 7 | 8000 | A | 7 | 430 | A | 7 | 0.7 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.56 | 6 | 0
1977-12-08 | 1900-12-07 | 15:00 | 15 | 479 | 1410 | 164 | 1 | 9 | 5 | 1 | 9 | 163 | 1 | 13 | 18200 | 1 | 9 | 400 | 1 | 9 | 18000 | 1 | 13 | 5450 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -8.9 | 15.98 | A | 7 | 0.74 | A | 7 | 976 | A | 7 | 330 | A | 7 | 9.3 | A | 7 | 9700 | A | 7 | 460 | A | 7 | 0.6 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.28 | 6 | 0
1977-12-08 | 1900-12-07 | 16:00 | 16 | 304 | 1410 | 97 | 1 | 13 | 79 | 1 | 9 | 79 | 1 | 13 | 10500 | 1 | 13 | 6400 | 1 | 9 | 9100 | 1 | 13 | 1710 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 9700 | A | 7 | 1070 | A | 7 | 0.6 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 6 | 0
1977-12-08 | 1900-12-07 | 17:00 | 17 | 90 | 1257 | 46 | 1 | 13 | 246 | 1 | 13 | 23 | 1 | 13 | 4200 | 1 | 13 | 12000 | 1 | 13 | 3300 | 1 | 13 | 400 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | -8.9 | 15.98 | A | 7 | -13.9 | 6.98 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.38 | 6 | 0
1977-12-08 | 1900-12-07 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -11.1 | 12.02 | A | 7 | -16.7 | 1.94 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 330 | A | 7 | 9.3 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.54 | 6 | 0
1977-12-08 | 1900-12-07 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -12.2 | 10.04 | A | 7 | -17.8 | -0.04 | A | 7 | 0.64 | A | 7 | 985 | A | 7 | 340 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.34 | 6 | 0
1977-12-08 | 1900-12-07 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -18.9 | -2.02 | A | 7 | 0.63 | A | 7 | 987 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.22 | 6 | 0
1977-12-08 | 1900-12-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -19.4 | -2.92 | A | 7 | 0.66 | A | 7 | 988 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.02 | 6 | 0
1977-12-08 | 1900-12-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -20.6 | -5.08 | A | 7 | 0.63 | A | 7 | 989 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.08 | 6 | 0
1977-12-08 | 1900-12-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -21.1 | -5.98 | A | 7 | 0.63 | A | 7 | 991 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.98 | 6 | 0
1977-12-08 | 1900-12-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -21.7 | -7.06 | A | 7 | 0.63 | A | 7 | 992 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.06 | 6 | 0
1977-12-09 | 1900-12-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -21.1 | -5.98 | A | 7 | 0.69 | A | 7 | 992 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.78 | 7 | 0
1977-12-09 | 1900-12-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -21.1 | -5.98 | A | 7 | 0.69 | A | 7 | 993 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.78 | 7 | 0
1977-12-09 | 1900-12-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -21.1 | -5.98 | A | 7 | 0.69 | A | 7 | 994 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.78 | 7 | 0
1977-12-09 | 1900-12-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.2 | 1.04 | A | 7 | -23.3 | -9.94 | A | 7 | 0.59 | A | 7 | 995 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.84 | 7 | 0
1977-12-09 | 1900-12-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.2 | 1.04 | A | 7 | -25 | -13 | A | 7 | 0.51 | A | 7 | 996 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -13.9 | 7 | 0
1977-12-09 | 1900-12-08 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -25 | -13 | A | 7 | 0.54 | A | 7 | 997 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -13.9 | 7 | 0
1977-12-09 | 1900-12-08 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -25.6 | -14.08 | A | 7 | 0.51 | A | 7 | 998 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -14.98 | 7 | 0
1977-12-09 | 1900-12-08 | 8:00 | 8 | 30 | 740 | 18 | 1 | 13 | 57 | 1 | 9 | 12 | 1 | 13 | 1600 | 1 | 13 | 1800 | 1 | 9 | 1500 | 1 | 13 | 210 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -26.1 | -14.98 | A | 7 | 0.48 | A | 7 | 999 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -15.88 | 7 | 0
1977-12-09 | 1900-12-08 | 9:00 | 9 | 226 | 1410 | 113 | 1 | 13 | 450 | 1 | 9 | 40 | 1 | 13 | 11600 | 1 | 13 | 31500 | 1 | 9 | 6500 | 1 | 13 | 720 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -25.6 | -14.08 | A | 7 | 0.51 | A | 7 | 1000 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -14.98 | 7 | 0
1977-12-09 | 1900-12-08 | 10:00 | 10 | 419 | 1410 | 264 | 1 | 9 | 689 | 1 | 9 | 57 | 1 | 13 | 27000 | 1 | 9 | 61200 | 1 | 9 | 8700 | 1 | 13 | 1100 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -25 | -13 | A | 7 | 0.47 | A | 7 | 1001 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -14 | 7 | 0
1977-12-09 | 1900-12-08 | 11:00 | 11 | 560 | 1410 | 386 | 1 | 9 | 788 | 1 | 9 | 70 | 1 | 13 | 40000 | 1 | 9 | 74700 | 1 | 9 | 10200 | 1 | 13 | 1420 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -24.4 | -11.92 | A | 7 | 0.47 | A | 7 | 1000 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -13.02 | 7 | 0
1977-12-09 | 1900-12-08 | 12:00 | 12 | 640 | 1410 | 459 | 1 | 9 | 833 | 1 | 9 | 78 | 1 | 13 | 47900 | 1 | 9 | 80700 | 1 | 9 | 11100 | 1 | 13 | 1640 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -23.9 | -11.02 | A | 7 | 0.45 | A | 7 | 1002 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -12.22 | 7 | 0
1977-12-09 | 1900-12-08 | 13:00 | 13 | 653 | 1410 | 471 | 1 | 9 | 842 | 1 | 9 | 79 | 1 | 13 | 49300 | 1 | 9 | 81800 | 1 | 9 | 11200 | 1 | 13 | 1670 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -23.3 | -9.94 | A | 7 | 0.43 | A | 7 | 1002 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -11.24 | 7 | 0
1977-12-09 | 1900-12-08 | 14:00 | 14 | 598 | 1410 | 421 | 1 | 9 | 813 | 1 | 9 | 74 | 1 | 13 | 43800 | 1 | 9 | 77900 | 1 | 9 | 10600 | 1 | 13 | 1520 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -23.3 | -9.94 | A | 7 | 0.41 | A | 7 | 1001 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -11.24 | 7 | 0
1977-12-09 | 1900-12-08 | 15:00 | 15 | 479 | 1410 | 316 | 1 | 9 | 739 | 1 | 9 | 63 | 1 | 13 | 32500 | 1 | 9 | 67800 | 1 | 9 | 9400 | 1 | 13 | 1240 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -23.3 | -9.94 | A | 7 | 0.41 | A | 7 | 1001 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -11.24 | 7 | 0
1977-12-09 | 1900-12-08 | 16:00 | 16 | 304 | 1410 | 172 | 1 | 13 | 571 | 1 | 9 | 47 | 1 | 13 | 17700 | 1 | 13 | 45400 | 1 | 9 | 7900 | 1 | 13 | 870 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -22.8 | -9.04 | A | 7 | 0.43 | A | 7 | 1002 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.34 | 7 | 0
1977-12-09 | 1900-12-08 | 17:00 | 17 | 90 | 1257 | 40 | 1 | 13 | 193 | 1 | 9 | 23 | 1 | 13 | 3800 | 1 | 13 | 9400 | 1 | 9 | 3100 | 1 | 13 | 400 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -23.3 | -9.94 | A | 7 | 0.45 | A | 7 | 1002 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -11.14 | 7 | 0
1977-12-09 | 1900-12-08 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -23.3 | -9.94 | A | 7 | 0.52 | A | 7 | 1002 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -11.04 | 7 | 0
1977-12-09 | 1900-12-08 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -23.3 | -9.94 | A | 7 | 0.52 | A | 7 | 1002 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -11.04 | 7 | 0
1977-12-09 | 1900-12-08 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -23.3 | -9.94 | A | 7 | 0.54 | A | 7 | 1003 | A | 7 | 320 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.94 | 7 | 0
1977-12-09 | 1900-12-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -23.3 | -9.94 | A | 7 | 0.54 | A | 7 | 1002 | A | 7 | 310 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.94 | 7 | 0
1977-12-09 | 1900-12-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -23.3 | -9.94 | A | 7 | 0.57 | A | 7 | 1002 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.94 | 7 | 0
1977-12-09 | 1900-12-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.59 | A | 7 | 1002 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.04 | 7 | 0
1977-12-09 | 1900-12-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -22.2 | -7.96 | A | 7 | 0.62 | A | 7 | 1002 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.86 | 7 | 0
1977-12-10 | 1900-12-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -16.7 | 1.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.59 | A | 7 | 1002 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.04 | 1 | 0
1977-12-10 | 1900-12-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -16.7 | 1.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.59 | A | 7 | 1002 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.04 | 1 | 0
1977-12-10 | 1900-12-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -16.7 | 1.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.59 | A | 7 | 1002 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.04 | 1 | 0
1977-12-10 | 1900-12-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -16.7 | 1.94 | A | 7 | -23.3 | -9.94 | A | 7 | 0.57 | A | 7 | 1001 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.94 | 1 | 0
1977-12-10 | 1900-12-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.2 | 1.04 | A | 7 | -23.9 | -11.02 | A | 7 | 0.56 | A | 7 | 1001 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -11.92 | 1 | 0
1977-12-10 | 1900-12-09 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -17.2 | 1.04 | A | 7 | -23.9 | -11.02 | A | 7 | 0.56 | A | 7 | 1001 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -11.92 | 1 | 0
1977-12-10 | 1900-12-09 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | -17.2 | 1.04 | A | 7 | -23.3 | -9.94 | A | 7 | 0.59 | A | 7 | 1000 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.84 | 1 | 0
1977-12-10 | 1900-12-09 | 8:00 | 8 | 29 | 717 | 18 | 1 | 13 | 55 | 1 | 13 | 13 | 1 | 13 | 1700 | 1 | 13 | 1400 | 1 | 13 | 1600 | 1 | 13 | 220 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | -17.2 | 1.04 | A | 7 | -22.8 | -9.04 | A | 7 | 0.62 | A | 7 | 1000 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -9.94 | 1 | 0
1977-12-10 | 1900-12-09 | 9:00 | 9 | 223 | 1411 | 84 | 1 | 13 | 142 | 1 | 13 | 61 | 1 | 13 | 8800 | 1 | 13 | 9300 | 1 | 13 | 7300 | 1 | 13 | 1160 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | -15.6 | 3.92 | A | 7 | -21.1 | -5.98 | A | 7 | 0.63 | A | 7 | 1000 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 0.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.98 | 1 | 0
1977-12-10 | 1900-12-09 | 10:00 | 10 | 416 | 1411 | 228 | 1 | 9 | 491 | 1 | 9 | 82 | 1 | 13 | 23300 | 1 | 9 | 42800 | 1 | 9 | 10600 | 1 | 13 | 1490 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -12.8 | 8.96 | A | 7 | -20 | -4 | A | 7 | 0.55 | A | 7 | 1000 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.3 | 1 | 0
1977-12-10 | 1900-12-09 | 11:00 | 11 | 558 | 1411 | 393 | 1 | 9 | 856 | 1 | 9 | 53 | 1 | 13 | 41300 | 1 | 9 | 81000 | 1 | 9 | 9200 | 1 | 13 | 1230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -18.3 | -0.94 | A | 7 | 0.56 | A | 7 | 1000 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.44 | 1 | 0
1977-12-10 | 1900-12-09 | 12:00 | 12 | 638 | 1411 | 464 | 1 | 9 | 890 | 1 | 9 | 58 | 1 | 13 | 48600 | 1 | 9 | 85800 | 1 | 9 | 9600 | 1 | 13 | 1370 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -18.9 | -2.02 | A | 7 | 0.47 | A | 7 | 998 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.72 | 1 | 0
1977-12-10 | 1900-12-09 | 13:00 | 13 | 651 | 1411 | 479 | 1 | 9 | 901 | 1 | 9 | 59 | 1 | 13 | 50100 | 1 | 9 | 87100 | 1 | 9 | 9700 | 1 | 13 | 1390 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -18.9 | -2.02 | A | 7 | 0.41 | A | 7 | 997 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.92 | 1 | 0
1977-12-10 | 1900-12-09 | 14:00 | 14 | 597 | 1411 | 430 | 1 | 9 | 879 | 1 | 9 | 55 | 1 | 13 | 45100 | 1 | 9 | 84000 | 1 | 9 | 9400 | 1 | 13 | 1290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -18.9 | -2.02 | A | 7 | 0.35 | A | 7 | 996 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.12 | 1 | 0
1977-12-10 | 1900-12-09 | 15:00 | 15 | 478 | 1411 | 326 | 1 | 9 | 813 | 1 | 9 | 47 | 1 | 13 | 34100 | 1 | 9 | 74900 | 1 | 9 | 8600 | 1 | 13 | 1090 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -16.1 | 3.02 | A | 7 | 0.42 | A | 7 | 995 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.72 | 1 | 0
1977-12-10 | 1900-12-09 | 16:00 | 16 | 304 | 1411 | 181 | 1 | 13 | 666 | 1 | 9 | 36 | 1 | 13 | 18700 | 1 | 13 | 54600 | 1 | 9 | 6900 | 1 | 13 | 740 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -13.3 | 8.06 | A | 7 | 0.52 | A | 7 | 994 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.76 | 1 | 0
1977-12-10 | 1900-12-09 | 17:00 | 17 | 90 | 1281 | 46 | 1 | 13 | 294 | 1 | 9 | 19 | 1 | 13 | 4200 | 1 | 13 | 14600 | 1 | 9 | 3100 | 1 | 13 | 340 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -13.9 | 6.98 | A | 7 | 0.52 | A | 7 | 994 | A | 7 | 180 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.78 | 1 | 0
1977-12-10 | 1900-12-09 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -14.4 | 6.08 | A | 7 | 0.59 | A | 7 | 994 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.18 | 1 | 0
1977-12-10 | 1900-12-09 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -13.3 | 8.06 | A | 7 | 0.71 | A | 7 | 994 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.66 | 1 | 0
1977-12-10 | 1900-12-09 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -13.9 | 6.98 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.58 | 1 | 0
1977-12-10 | 1900-12-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -13.9 | 6.98 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.58 | 1 | 0
1977-12-10 | 1900-12-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -13.9 | 6.98 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.58 | 1 | 0
1977-12-10 | 1900-12-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.68 | 1 | 0
1977-12-10 | 1900-12-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 993 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 1 | 0
1977-12-11 | 1900-12-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 992 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 2 | 0
1977-12-11 | 1900-12-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 993 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 2 | 0
1977-12-11 | 1900-12-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -15 | 5 | A | 7 | 0.73 | A | 7 | 993 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.8 | 2 | 0
1977-12-11 | 1900-12-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -11.1 | 12.02 | A | 7 | -14.4 | 6.08 | A | 7 | 0.77 | A | 7 | 992 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.98 | 2 | 0
1977-12-11 | 1900-12-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -9.4 | 15.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.77 | A | 7 | 991 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1040 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.76 | 2 | 0
1977-12-11 | 1900-12-10 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 991 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.54 | 2 | 0
1977-12-11 | 1900-12-10 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 5 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 991 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.54 | 2 | 0
1977-12-11 | 1900-12-10 | 8:00 | 8 | 27 | 694 | 16 | 1 | 13 | 66 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 990 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 2 | 0
1977-12-11 | 1900-12-10 | 9:00 | 9 | 220 | 1411 | 105 | 1 | 13 | 360 | 1 | 9 | 48 | 1 | 13 | 10500 | 1 | 13 | 24500 | 1 | 9 | 6700 | 1 | 13 | 830 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | -4.4 | 24.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.63 | A | 7 | 990 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.72 | 2 | 0
1977-12-11 | 1900-12-10 | 10:00 | 10 | 413 | 1411 | 265 | 1 | 9 | 741 | 1 | 9 | 46 | 1 | 13 | 27700 | 1 | 9 | 66300 | 1 | 9 | 8200 | 1 | 13 | 970 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.58 | A | 7 | 990 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.18 | 2 | 0
1977-12-11 | 1900-12-10 | 11:00 | 11 | 555 | 1411 | 383 | 1 | 9 | 823 | 1 | 9 | 57 | 1 | 13 | 40100 | 1 | 9 | 77800 | 1 | 9 | 9400 | 1 | 13 | 1250 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.5 | A | 7 | 989 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.46 | 2 | 0
1977-12-11 | 1900-12-10 | 12:00 | 12 | 636 | 1411 | 456 | 1 | 9 | 867 | 1 | 9 | 63 | 1 | 13 | 47800 | 1 | 9 | 83500 | 1 | 9 | 10000 | 1 | 13 | 1400 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -7.2 | 19.04 | A | 7 | 0.46 | A | 7 | 988 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.04 | 2 | 0
1977-12-11 | 1900-12-10 | 13:00 | 13 | 650 | 1411 | 464 | 1 | 9 | 864 | 1 | 9 | 64 | 1 | 13 | 48600 | 1 | 9 | 83400 | 1 | 9 | 10000 | 1 | 13 | 1430 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.45 | A | 7 | 986 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.74 | 2 | 0
1977-12-11 | 1900-12-10 | 14:00 | 14 | 596 | 1411 | 121 | 1 | 9 | 14 | 1 | 9 | 115 | 1 | 13 | 14100 | 1 | 9 | 900 | 1 | 9 | 13700 | 1 | 13 | 4850 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.49 | A | 7 | 984 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 430 | A | 7 | 0.8 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.82 | 2 | 0
1977-12-11 | 1900-12-10 | 15:00 | 15 | 478 | 1411 | 109 | 1 | 9 | 1 | 1 | 9 | 109 | 1 | 13 | 12500 | 1 | 9 | 100 | 1 | 9 | 12400 | 1 | 13 | 4210 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -5 | 23 | A | 7 | 0.53 | A | 7 | 984 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 0.8 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.1 | 2 | 0
1977-12-11 | 1900-12-10 | 16:00 | 16 | 304 | 1411 | 68 | 1 | 13 | 7 | 1 | 9 | 66 | 1 | 13 | 7600 | 1 | 13 | 300 | 1 | 9 | 7600 | 1 | 13 | 2390 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.73 | A | 7 | 983 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.44 | 2 | 0
1977-12-11 | 1900-12-10 | 17:00 | 17 | 90 | 1282 | 18 | 1 | 13 | 2 | 1 | 9 | 18 | 1 | 13 | 2100 | 1 | 13 | 0 | 1 | 9 | 2100 | 1 | 13 | 640 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.06 | 2 | 0
1977-12-11 | 1900-12-10 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.55 | A | 7 | 982 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.52 | 2 | 0
1977-12-11 | 1900-12-10 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.5 | A | 7 | 982 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.12 | 2 | 0
1977-12-11 | 1900-12-10 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.57 | A | 7 | 982 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.18 | 2 | 0
1977-12-11 | 1900-12-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.48 | A | 7 | 981 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.92 | 2 | 0
1977-12-11 | 1900-12-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 3.3 | 37.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.5 | A | 7 | 980 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.12 | 2 | 0
1977-12-11 | 1900-12-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 3.9 | 39.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.48 | A | 7 | 980 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.92 | 2 | 0
1977-12-11 | 1900-12-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 5 | A | 7 | 3.3 | 37.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.6 | A | 7 | 980 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.48 | 2 | 0
1977-12-12 | 1900-12-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 4.4 | 39.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 3 | 0
1977-12-12 | 1900-12-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 3 | 0
1977-12-12 | 1900-12-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.53 | A | 7 | 978 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.98 | 3 | 0
1977-12-12 | 1900-12-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -5 | 23 | A | 7 | 0.49 | A | 7 | 977 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.7 | 3 | 0
1977-12-12 | 1900-12-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -5 | 23 | A | 7 | 0.49 | A | 7 | 976 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.7 | 3 | 0
1977-12-12 | 1900-12-11 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -3.3 | 26.06 | A | 7 | 0.55 | A | 7 | 976 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 760 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.96 | 3 | 0
1977-12-12 | 1900-12-11 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -2.8 | 26.96 | A | 7 | 0.58 | A | 7 | 976 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.96 | 3 | 0
1977-12-12 | 1900-12-11 | 8:00 | 8 | 26 | 694 | 11 | 1 | 13 | 1 | 1 | 9 | 11 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 976 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.9 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 3 | 0
1977-12-12 | 1900-12-11 | 9:00 | 9 | 217 | 1411 | 62 | 1 | 13 | 3 | 1 | 9 | 61 | 1 | 13 | 6800 | 1 | 13 | 100 | 1 | 9 | 6800 | 1 | 13 | 1950 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.58 | A | 7 | 976 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.9 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.94 | 3 | 0
1977-12-12 | 1900-12-11 | 10:00 | 10 | 410 | 1411 | 116 | 1 | 9 | 1 | 1 | 9 | 116 | 1 | 13 | 13000 | 1 | 9 | 100 | 1 | 9 | 12900 | 1 | 13 | 4050 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.6 | A | 7 | 976 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 1 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.92 | 3 | 0
1977-12-12 | 1900-12-11 | 11:00 | 11 | 553 | 1411 | 206 | 1 | 9 | 4 | 1 | 9 | 204 | 1 | 13 | 22600 | 1 | 9 | 300 | 1 | 9 | 22500 | 1 | 13 | 6790 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 0 | 32 | A | 7 | 0.63 | A | 7 | 975 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 550 | A | 7 | 1.1 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28 | 3 | 0
1977-12-12 | 1900-12-11 | 12:00 | 12 | 634 | 1411 | 241 | 1 | 9 | 1 | 1 | 9 | 241 | 1 | 13 | 26700 | 1 | 9 | 100 | 1 | 9 | 26600 | 1 | 13 | 8210 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.77 | A | 7 | 973 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 1.3 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.04 | 3 | 0
1977-12-12 | 1900-12-11 | 13:00 | 13 | 649 | 1411 | 222 | 1 | 9 | 0 | 1 | 9 | 222 | 1 | 13 | 24800 | 1 | 9 | 0 | 1 | 9 | 24800 | 1 | 13 | 8010 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 3.3 | 37.94 | A | 7 | 0.77 | A | 7 | 972 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 490 | A | 7 | 1.3 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.04 | 3 | 0
1977-12-12 | 1900-12-11 | 14:00 | 14 | 595 | 1411 | 209 | 1 | 9 | 1 | 1 | 9 | 208 | 1 | 13 | 23100 | 1 | 9 | 100 | 1 | 9 | 23100 | 1 | 13 | 7250 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 3.9 | 39.02 | A | 7 | 0.83 | A | 7 | 972 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 490 | A | 7 | 1.3 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.82 | 3 | 0
1977-12-12 | 1900-12-11 | 15:00 | 15 | 477 | 1411 | 108 | 1 | 9 | 0 | 1 | 9 | 108 | 1 | 13 | 12300 | 1 | 9 | 0 | 1 | 9 | 12300 | 1 | 13 | 4180 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 3.9 | 39.02 | A | 7 | 0.86 | A | 7 | 972 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 270 | A | 7 | 1.3 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.22 | 3 | 0
1977-12-12 | 1900-12-11 | 16:00 | 16 | 304 | 1411 | 61 | 1 | 13 | 0 | 1 | 9 | 61 | 1 | 13 | 6900 | 1 | 13 | 0 | 1 | 9 | 6900 | 1 | 13 | 2250 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 972 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 2400 | A | 7 | 180 | A | 7 | 1.4 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40 | 3 | 0
1977-12-12 | 1900-12-11 | 17:00 | 17 | 91 | 1282 | 18 | 1 | 13 | 0 | 1 | 9 | 18 | 1 | 13 | 2100 | 1 | 13 | 0 | 1 | 9 | 2100 | 1 | 13 | 640 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5.6 | 42.08 | A | 7 | 1 | A | 7 | 971 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 1300 | A | 7 | 90 | A | 7 | 1.5 | E | 8 | 0.029 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.98 | 3 | 0
1977-12-12 | 1900-12-11 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 5.6 | 42.08 | A | 7 | 1 | A | 7 | 971 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 1300 | A | 7 | 120 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.98 | 3 | 0
1977-12-12 | 1900-12-11 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 5.6 | 42.08 | A | 7 | 0.93 | A | 7 | 972 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 3200 | A | 7 | 120 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.08 | 3 | 0
1977-12-12 | 1900-12-11 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 2400 | A | 7 | 90 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.38 | 3 | 0
1977-12-12 | 1900-12-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 1300 | A | 7 | 60 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.38 | 3 | 0
1977-12-12 | 1900-12-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.1 | 42.98 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 1300 | A | 7 | 60 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.38 | 3 | 0
1977-12-12 | 1900-12-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 1300 | A | 7 | 60 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.46 | 3 | 0
1977-12-12 | 1900-12-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 800 | A | 7 | 30 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.46 | 3 | 0
1977-12-13 | 1900-12-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 6.7 | 44.06 | A | 7 | 0.96 | A | 7 | 972 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.46 | 4 | 0
1977-12-13 | 1900-12-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 972 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.86 | 4 | 0
1977-12-13 | 1900-12-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.2 | 44.96 | A | 7 | 7.2 | 44.96 | A | 7 | 1 | A | 7 | 972 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.86 | 4 | 0
1977-12-13 | 1900-12-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 973 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 4 | 0
1977-12-13 | 1900-12-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.96 | A | 7 | 973 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 1.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.48 | 4 | 0
1977-12-13 | 1900-12-12 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 5 | 41 | A | 7 | 0.93 | A | 7 | 973 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 2400 | A | 7 | 430 | A | 7 | 1.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40 | 4 | 0
1977-12-13 | 1900-12-12 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 2.8 | 37.04 | A | 7 | 0.93 | A | 7 | 974 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 800 | A | 7 | 90 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.14 | 4 | 0
1977-12-13 | 1900-12-12 | 8:00 | 8 | 24 | 671 | 13 | 1 | 13 | 0 | 1 | 9 | 13 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.92 | A | 7 | 974 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 2440 | A | 7 | 1.1 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.18 | 4 | 0
1977-12-13 | 1900-12-12 | 9:00 | 9 | 214 | 1412 | 85 | 1 | 13 | 243 | 1 | 13 | 48 | 1 | 13 | 8900 | 1 | 13 | 15900 | 1 | 13 | 6400 | 1 | 13 | 860 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | 2.2 | 35.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 4000 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.78 | 4 | 0
1977-12-13 | 1900-12-12 | 10:00 | 10 | 408 | 1412 | 246 | 1 | 9 | 675 | 1 | 9 | 49 | 1 | 13 | 25500 | 1 | 9 | 59900 | 1 | 9 | 8100 | 1 | 13 | 1000 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 3.9 | 39.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.79 | A | 7 | 976 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.68 | 4 | 0
1977-12-13 | 1900-12-12 | 11:00 | 11 | 551 | 1412 | 364 | 1 | 9 | 764 | 1 | 9 | 64 | 1 | 13 | 38100 | 1 | 9 | 72400 | 1 | 9 | 9700 | 1 | 13 | 1340 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | 5.6 | 42.08 | A | 7 | 1.1 | 33.98 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.78 | 4 | 0
1977-12-13 | 1900-12-12 | 12:00 | 12 | 632 | 1412 | 428 | 1 | 9 | 869 | 1 | 9 | 36 | 1 | 13 | 45500 | 1 | 9 | 83900 | 1 | 9 | 7800 | 1 | 13 | 1050 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 6.7 | 44.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.68 | A | 7 | 976 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.28 | 4 | 0
1977-12-13 | 1900-12-12 | 13:00 | 13 | 647 | 1412 | 437 | 1 | 9 | 832 | 1 | 9 | 53 | 1 | 13 | 46000 | 1 | 9 | 80400 | 1 | 9 | 8900 | 1 | 13 | 1330 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 8.9 | 48.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.61 | A | 7 | 975 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.36 | 4 | 0
1977-12-13 | 1900-12-12 | 14:00 | 14 | 594 | 1412 | 421 | 1 | 9 | 904 | 1 | 9 | 37 | 1 | 13 | 44600 | 1 | 9 | 86600 | 1 | 9 | 8000 | 1 | 13 | 1060 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 10 | 50 | A | 7 | 1.1 | 33.98 | A | 7 | 0.54 | A | 7 | 975 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.58 | 4 | 0
1977-12-13 | 1900-12-12 | 15:00 | 15 | 477 | 1412 | 300 | 1 | 9 | 786 | 1 | 9 | 32 | 1 | 13 | 31900 | 1 | 9 | 72600 | 1 | 9 | 7200 | 1 | 13 | 910 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 10 | 50 | A | 7 | 0.6 | 33.08 | A | 7 | 0.52 | A | 7 | 975 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.58 | 4 | 0
1977-12-13 | 1900-12-12 | 16:00 | 16 | 304 | 1412 | 174 | 1 | 13 | 675 | 1 | 9 | 27 | 1 | 13 | 18400 | 1 | 13 | 56300 | 1 | 9 | 6200 | 1 | 13 | 710 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 9.4 | 48.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.54 | A | 7 | 975 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.88 | 4 | 0
1977-12-13 | 1900-12-12 | 17:00 | 17 | 92 | 1282 | 49 | 1 | 13 | 372 | 1 | 9 | 15 | 1 | 13 | 4600 | 1 | 13 | 22900 | 1 | 9 | 2800 | 1 | 13 | 330 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 7.8 | 46.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.61 | A | 7 | 976 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.026 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.68 | 4 | 0
1977-12-13 | 1900-12-12 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 5.6 | 42.08 | A | 7 | 0 | 32 | A | 7 | 0.68 | A | 7 | 976 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.5 | 4 | 0
1977-12-13 | 1900-12-12 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | 0 | 32 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.8 | 4 | 0
1977-12-13 | 1900-12-12 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | 0 | 32 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.1 | 4 | 0
1977-12-13 | 1900-12-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.73 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.12 | 4 | 0
1977-12-13 | 1900-12-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.76 | A | 7 | 977 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.42 | 4 | 0
1977-12-13 | 1900-12-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.79 | A | 7 | 977 | A | 7 | 310 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.72 | 4 | 0
1977-12-13 | 1900-12-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.76 | A | 7 | 978 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.42 | 4 | 0
1977-12-14 | 1900-12-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.7 | A | 7 | 977 | A | 7 | 320 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.92 | 5 | 0
1977-12-14 | 1900-12-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.85 | A | 7 | 977 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 5 | 0
1977-12-14 | 1900-12-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.52 | 5 | 0
1977-12-14 | 1900-12-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.85 | A | 7 | 977 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 5 | 0
1977-12-14 | 1900-12-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.94 | 5 | 0
1977-12-14 | 1900-12-13 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 977 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.94 | 5 | 0
1977-12-14 | 1900-12-13 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 5 | 0
1977-12-14 | 1900-12-13 | 8:00 | 8 | 23 | 647 | 21 | 1 | 13 | 149 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 5 | 0
1977-12-14 | 1900-12-13 | 9:00 | 9 | 211 | 1412 | 117 | 1 | 13 | 629 | 1 | 9 | 22 | 1 | 13 | 12400 | 1 | 13 | 47300 | 1 | 9 | 5300 | 1 | 13 | 550 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.82 | A | 7 | 978 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.02 | 5 | 0
1977-12-14 | 1900-12-13 | 10:00 | 10 | 405 | 1412 | 240 | 1 | 9 | 649 | 1 | 9 | 52 | 1 | 13 | 24700 | 1 | 9 | 57400 | 1 | 9 | 8100 | 1 | 13 | 1030 | 1 | 18 | 5 | A | 7 | 1 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 5 | 0
1977-12-14 | 1900-12-13 | 11:00 | 11 | 549 | 1412 | 196 | 1 | 13 | 107 | 1 | 13 | 154 | 1 | 13 | 21400 | 1 | 13 | 10500 | 1 | 13 | 17300 | 1 | 13 | 3590 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 7.2 | 44.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 1.1 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.88 | 5 | 0
1977-12-14 | 1900-12-13 | 12:00 | 12 | 631 | 1412 | 329 | 1 | 9 | 287 | 1 | 9 | 200 | 1 | 13 | 34800 | 1 | 9 | 29100 | 1 | 9 | 21700 | 1 | 13 | 4440 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | 7.8 | 46.04 | A | 7 | 0 | 32 | A | 7 | 0.58 | A | 7 | 977 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.4 | 5 | 0
1977-12-14 | 1900-12-13 | 13:00 | 13 | 646 | 1412 | 180 | 1 | 9 | 58 | 1 | 9 | 153 | 1 | 13 | 19800 | 1 | 9 | 5700 | 1 | 9 | 17200 | 1 | 13 | 4650 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 8.9 | 48.02 | A | 7 | 0 | 32 | A | 7 | 0.54 | A | 7 | 976 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27 | 5 | 0
1977-12-14 | 1900-12-13 | 14:00 | 14 | 594 | 1412 | 400 | 1 | 13 | 758 | 1 | 13 | 79 | 1 | 13 | 41300 | 1 | 13 | 72300 | 1 | 13 | 10700 | 1 | 13 | 1570 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 12.2 | 53.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.45 | A | 7 | 975 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.78 | 5 | 0
1977-12-14 | 1900-12-13 | 15:00 | 15 | 477 | 1412 | 277 | 1 | 9 | 599 | 1 | 9 | 73 | 1 | 13 | 28900 | 1 | 9 | 54900 | 1 | 9 | 10200 | 1 | 13 | 1410 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 12.8 | 55.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.43 | A | 7 | 975 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.58 | 5 | 0
1977-12-14 | 1900-12-13 | 16:00 | 16 | 305 | 1412 | 160 | 1 | 13 | 498 | 1 | 9 | 52 | 1 | 13 | 16500 | 1 | 13 | 39400 | 1 | 9 | 7900 | 1 | 13 | 950 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | 12.2 | 53.96 | A | 7 | 0 | 32 | A | 7 | 0.43 | A | 7 | 974 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.7 | 5 | 0
1977-12-14 | 1900-12-13 | 17:00 | 17 | 92 | 1282 | 38 | 1 | 13 | 33 | 1 | 13 | 35 | 1 | 13 | 4100 | 1 | 13 | 2000 | 1 | 13 | 3900 | 1 | 13 | 770 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 10 | 50 | A | 7 | -0.6 | 30.92 | A | 7 | 0.48 | A | 7 | 974 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.024 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.42 | 5 | 0
1977-12-14 | 1900-12-13 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 8.9 | 48.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.52 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.82 | 5 | 0
1977-12-14 | 1900-12-13 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 8.3 | 46.94 | A | 7 | 0 | 32 | A | 7 | 0.56 | A | 7 | 974 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.2 | 5 | 0
1977-12-14 | 1900-12-13 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 8.3 | 46.94 | A | 7 | 0 | 32 | A | 7 | 0.56 | A | 7 | 974 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.2 | 5 | 0
1977-12-14 | 1900-12-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | 7.2 | 44.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.58 | A | 7 | 974 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.52 | 5 | 0
1977-12-14 | 1900-12-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.43 | A | 7 | 974 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.32 | 5 | 0
1977-12-14 | 1900-12-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.63 | A | 7 | 974 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.02 | 5 | 0
1977-12-14 | 1900-12-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.22 | 5 | 0
1977-12-15 | 1900-12-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.22 | 6 | 0
1977-12-15 | 1900-12-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -1.1 | 30.02 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.42 | 6 | 0
1977-12-15 | 1900-12-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -1.1 | 30.02 | A | 7 | 0.7 | A | 7 | 974 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.92 | 6 | 0
1977-12-15 | 1900-12-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.7 | A | 7 | 974 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 6 | 0
1977-12-15 | 1900-12-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | 3.9 | 39.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.67 | A | 7 | 973 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 6 | 0
1977-12-15 | 1900-12-14 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | 4.4 | 39.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.65 | A | 7 | 973 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.44 | 6 | 0
1977-12-15 | 1900-12-14 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 5.6 | 42.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.6 | A | 7 | 973 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.94 | 6 | 0
1977-12-15 | 1900-12-14 | 8:00 | 8 | 22 | 624 | 16 | 1 | 13 | 39 | 1 | 13 | 13 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 5.6 | 42.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.6 | A | 7 | 973 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.94 | 6 | 0
1977-12-15 | 1900-12-14 | 9:00 | 9 | 209 | 1412 | 96 | 1 | 13 | 215 | 1 | 13 | 64 | 1 | 13 | 10000 | 1 | 13 | 13500 | 1 | 13 | 8000 | 1 | 13 | 1250 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 6.7 | 44.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.56 | A | 7 | 973 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.54 | 6 | 0
1977-12-15 | 1900-12-14 | 10:00 | 10 | 403 | 1412 | 231 | 1 | 13 | 573 | 1 | 13 | 66 | 1 | 13 | 23900 | 1 | 13 | 50000 | 1 | 13 | 9600 | 1 | 13 | 1240 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 9.4 | 48.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.48 | A | 7 | 972 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.62 | 6 | 0
1977-12-15 | 1900-12-14 | 11:00 | 11 | 547 | 1412 | 307 | 1 | 13 | 415 | 1 | 13 | 145 | 1 | 13 | 31800 | 1 | 13 | 39400 | 1 | 13 | 16500 | 1 | 13 | 2860 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 12.2 | 53.96 | A | 7 | 0 | 32 | A | 7 | 0.43 | A | 7 | 972 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.7 | 6 | 0
1977-12-15 | 1900-12-14 | 12:00 | 12 | 629 | 1412 | 410 | 1 | 13 | 656 | 1 | 13 | 115 | 1 | 13 | 42400 | 1 | 13 | 63300 | 1 | 13 | 14100 | 1 | 13 | 2300 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 13.3 | 55.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.42 | A | 7 | 971 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.48 | 6 | 0
1977-12-15 | 1900-12-14 | 13:00 | 13 | 646 | 1412 | 379 | 1 | 13 | 492 | 1 | 13 | 152 | 1 | 13 | 39900 | 1 | 13 | 48600 | 1 | 13 | 17600 | 1 | 13 | 3090 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 15 | 59 | A | 7 | 1.1 | 33.98 | A | 7 | 0.39 | A | 7 | 969 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.78 | 6 | 0
1977-12-15 | 1900-12-14 | 14:00 | 14 | 594 | 1412 | 272 | 1 | 13 | 187 | 1 | 13 | 192 | 1 | 13 | 29300 | 1 | 13 | 18600 | 1 | 13 | 21500 | 1 | 13 | 4550 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 17.2 | 62.96 | A | 7 | 2.2 | 35.96 | A | 7 | 0.37 | A | 7 | 968 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.06 | 6 | 0
1977-12-15 | 1900-12-14 | 15:00 | 15 | 478 | 1412 | 198 | 1 | 9 | 130 | 1 | 9 | 154 | 1 | 13 | 21400 | 1 | 9 | 12200 | 1 | 9 | 17200 | 1 | 13 | 3500 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 16.1 | 60.98 | A | 7 | 2.2 | 35.96 | A | 7 | 0.39 | A | 7 | 968 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1.2 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.26 | 6 | 0
1977-12-15 | 1900-12-14 | 16:00 | 16 | 305 | 1412 | 97 | 1 | 13 | 60 | 1 | 13 | 84 | 1 | 13 | 10600 | 1 | 13 | 5000 | 1 | 13 | 9500 | 1 | 13 | 2090 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 15.6 | 60.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.39 | A | 7 | 967 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 1.2 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.66 | 6 | 0
1977-12-15 | 1900-12-14 | 17:00 | 17 | 93 | 1306 | 36 | 1 | 13 | 121 | 1 | 13 | 25 | 1 | 13 | 3600 | 1 | 13 | 5300 | 1 | 13 | 3200 | 1 | 13 | 450 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 15 | 59 | A | 7 | 1.7 | 35.06 | A | 7 | 0.41 | A | 7 | 966 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.04 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.86 | 6 | 0
1977-12-15 | 1900-12-14 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 13.9 | 57.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.44 | A | 7 | 966 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.26 | 6 | 0
1977-12-15 | 1900-12-14 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 13.3 | 55.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.44 | A | 7 | 966 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.38 | 6 | 0
1977-12-15 | 1900-12-14 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.47 | A | 7 | 966 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.08 | 6 | 0
1977-12-15 | 1900-12-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | 0 | 32 | A | 7 | 0.45 | A | 7 | 966 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.9 | 6 | 0
1977-12-15 | 1900-12-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 12.2 | 53.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.42 | A | 7 | 964 | A | 7 | 160 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.72 | 6 | 0
1977-12-15 | 1900-12-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 11.7 | 53.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.41 | A | 7 | 964 | A | 7 | 170 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.82 | 6 | 0
1977-12-15 | 1900-12-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.45 | A | 7 | 963 | A | 7 | 170 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.32 | 6 | 0
1977-12-16 | 1900-12-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10.6 | 51.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.46 | A | 7 | 962 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.12 | 7 | 0
1977-12-16 | 1900-12-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 0.6 | 33.08 | A | 7 | 0.52 | A | 7 | 961 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.58 | 7 | 0
1977-12-16 | 1900-12-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | 0.6 | 33.08 | A | 7 | 0.54 | A | 7 | 960 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.88 | 7 | 0
1977-12-16 | 1900-12-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.59 | A | 7 | 959 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.18 | 7 | 0
1977-12-16 | 1900-12-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.61 | A | 7 | 958 | A | 7 | 170 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.36 | 7 | 0
1977-12-16 | 1900-12-15 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.66 | A | 7 | 957 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.66 | 7 | 0
1977-12-16 | 1900-12-15 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.66 | A | 7 | 957 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.66 | 7 | 0
1977-12-16 | 1900-12-15 | 8:00 | 8 | 21 | 624 | 10 | 1 | 13 | 34 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 8.3 | 46.94 | A | 7 | 3.3 | 37.94 | A | 7 | 0.71 | A | 7 | 956 | A | 7 | 160 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.3 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.34 | 7 | 0
1977-12-16 | 1900-12-15 | 9:00 | 9 | 206 | 1412 | 98 | 1 | 13 | 413 | 1 | 9 | 36 | 1 | 13 | 9900 | 1 | 13 | 27800 | 1 | 9 | 5800 | 1 | 13 | 650 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 10 | 50 | A | 7 | 4.4 | 39.92 | A | 7 | 0.69 | A | 7 | 955 | A | 7 | 160 | A | 7 | 9.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.92 | 7 | 0
1977-12-16 | 1900-12-15 | 10:00 | 10 | 401 | 1412 | 232 | 1 | 9 | 623 | 1 | 9 | 54 | 1 | 13 | 23800 | 1 | 9 | 54800 | 1 | 9 | 8200 | 1 | 13 | 1050 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 11.1 | 51.98 | A | 7 | 5.6 | 42.08 | A | 7 | 0.69 | A | 7 | 955 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.4 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.88 | 7 | 0
1977-12-16 | 1900-12-15 | 11:00 | 11 | 545 | 1412 | 357 | 1 | 9 | 748 | 1 | 9 | 66 | 1 | 13 | 37100 | 1 | 9 | 70600 | 1 | 9 | 9700 | 1 | 13 | 1360 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 12.8 | 55.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.67 | A | 7 | 954 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.5 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.36 | 7 | 0
1977-12-16 | 1900-12-15 | 12:00 | 12 | 628 | 1412 | 428 | 1 | 9 | 791 | 1 | 9 | 73 | 1 | 13 | 44800 | 1 | 9 | 76600 | 1 | 9 | 10600 | 1 | 13 | 1550 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 15.6 | 60.08 | A | 7 | 7.8 | 46.04 | A | 7 | 0.6 | A | 7 | 953 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.04 | 7 | 0
1977-12-16 | 1900-12-15 | 13:00 | 13 | 645 | 1412 | 416 | 1 | 9 | 714 | 1 | 9 | 88 | 1 | 13 | 44100 | 1 | 9 | 70000 | 1 | 9 | 12000 | 1 | 13 | 1860 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | 16.7 | 62.06 | A | 7 | 7.8 | 46.04 | A | 7 | 0.56 | A | 7 | 953 | A | 7 | 180 | A | 7 | 9.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.34 | 7 | 0
1977-12-16 | 1900-12-15 | 14:00 | 14 | 594 | 1412 | 342 | 1 | 13 | 513 | 1 | 13 | 125 | 1 | 13 | 36400 | 1 | 13 | 49900 | 1 | 13 | 15300 | 1 | 13 | 2450 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 17.2 | 62.96 | A | 7 | 7.8 | 46.04 | A | 7 | 0.54 | A | 7 | 952 | A | 7 | 180 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.6 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.04 | 7 | 0
1977-12-16 | 1900-12-15 | 15:00 | 15 | 478 | 1412 | 233 | 1 | 13 | 311 | 1 | 13 | 127 | 1 | 13 | 24800 | 1 | 13 | 29300 | 1 | 13 | 14800 | 1 | 13 | 2560 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 16.7 | 62.06 | A | 7 | 8.3 | 46.94 | A | 7 | 0.58 | A | 7 | 952 | A | 7 | 170 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 1220 | A | 7 | 1.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.44 | 7 | 0
1977-12-16 | 1900-12-15 | 16:00 | 16 | 306 | 1412 | 125 | 1 | 13 | 183 | 1 | 13 | 85 | 1 | 13 | 13100 | 1 | 13 | 14300 | 1 | 13 | 10000 | 1 | 13 | 1660 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | 16.1 | 60.98 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | A | 7 | 951 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 1.7 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.84 | 7 | 0
1977-12-16 | 1900-12-15 | 17:00 | 17 | 94 | 1307 | 9 | 1 | 13 | 3 | 1 | 9 | 9 | 1 | 13 | 1000 | 1 | 13 | 200 | 1 | 9 | 1000 | 1 | 13 | 240 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | 15.6 | 60.08 | A | 7 | 8.9 | 48.02 | A | 7 | 0.65 | A | 7 | 951 | A | 7 | 140 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 1830 | A | 7 | 1.8 | E | 8 | 0.084 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.52 | 7 | 0
1977-12-16 | 1900-12-15 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 15 | 59 | A | 7 | 8.3 | 46.94 | A | 7 | 0.65 | A | 7 | 950 | A | 7 | 130 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 1490 | A | 7 | 1.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.64 | 7 | 0
1977-12-16 | 1900-12-15 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 13.9 | 57.02 | A | 7 | 9.4 | 48.92 | A | 7 | 0.75 | A | 7 | 950 | A | 7 | 170 | A | 7 | 10.8 | A | 7 | 19300 | A | 7 | 1490 | A | 7 | 1.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.02 | 7 | 0
1977-12-16 | 1900-12-15 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | 12.2 | 53.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.49 | A | 7 | 950 | A | 7 | 200 | A | 7 | 11.3 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.86 | 7 | 0
1977-12-16 | 1900-12-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 10 | 50 | A | 7 | 2.2 | 35.96 | A | 7 | 0.59 | A | 7 | 952 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.86 | 7 | 0
1977-12-16 | 1900-12-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 9.4 | 48.92 | A | 7 | 2.2 | 35.96 | A | 7 | 0.61 | A | 7 | 952 | A | 7 | 210 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.06 | 7 | 0
1977-12-16 | 1900-12-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | 7.2 | 44.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.68 | A | 7 | 953 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1490 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.16 | 7 | 0
1977-12-16 | 1900-12-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 953 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 7 | 0
1977-12-17 | 1900-12-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 1.7 | 35.06 | A | 7 | 0.73 | A | 7 | 954 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 1 | 0
1977-12-17 | 1900-12-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 955 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 460 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 1 | 0
1977-12-17 | 1900-12-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 1.1 | 33.98 | A | 7 | 0.79 | A | 7 | 955 | A | 7 | 220 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 1 | 0
1977-12-17 | 1900-12-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 1.1 | 33.98 | A | 7 | 0.82 | A | 7 | 955 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 1 | 0
1977-12-17 | 1900-12-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.86 | A | 7 | 955 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 430 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.38 | 1 | 0
1977-12-17 | 1900-12-16 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.1 | 33.98 | A | 7 | 0.86 | A | 7 | 955 | A | 7 | 250 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 340 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.38 | 1 | 0
1977-12-17 | 1900-12-16 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.89 | A | 7 | 956 | A | 7 | 250 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 1 | 0
1977-12-17 | 1900-12-16 | 8:00 | 8 | 20 | 600 | 3 | 1 | 13 | 2 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 0.6 | 33.08 | A | 7 | 0.85 | A | 7 | 957 | A | 7 | 260 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.38 | 1 | 0
1977-12-17 | 1900-12-16 | 9:00 | 9 | 204 | 1413 | 33 | 1 | 13 | 15 | 1 | 9 | 31 | 1 | 13 | 3700 | 1 | 13 | 1100 | 1 | 9 | 3500 | 1 | 13 | 820 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 958 | A | 7 | 250 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 340 | A | 7 | 1.1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 1 | 0
1977-12-17 | 1900-12-16 | 10:00 | 10 | 399 | 1413 | 65 | 1 | 9 | 2 | 1 | 9 | 64 | 1 | 13 | 7500 | 1 | 9 | 100 | 1 | 9 | 7500 | 1 | 13 | 2580 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 959 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 1.1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 1 | 0
1977-12-17 | 1900-12-16 | 11:00 | 11 | 543 | 1413 | 168 | 1 | 9 | 12 | 1 | 9 | 164 | 1 | 13 | 18900 | 1 | 9 | 900 | 1 | 9 | 18500 | 1 | 13 | 5940 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.82 | A | 7 | 960 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 1.1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 1 | 0
1977-12-17 | 1900-12-16 | 12:00 | 12 | 627 | 1413 | 179 | 1 | 9 | 9 | 1 | 9 | 175 | 1 | 13 | 20300 | 1 | 9 | 700 | 1 | 9 | 20000 | 1 | 13 | 6770 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.79 | A | 7 | 960 | A | 7 | 260 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 1.1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.68 | 1 | 0
1977-12-17 | 1900-12-16 | 13:00 | 13 | 644 | 1413 | 200 | 1 | 9 | 4 | 1 | 9 | 198 | 1 | 13 | 22500 | 1 | 9 | 300 | 1 | 9 | 22300 | 1 | 13 | 7450 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 0.6 | 33.08 | A | 7 | 0.79 | A | 7 | 960 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 1.1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.68 | 1 | 0
1977-12-17 | 1900-12-16 | 14:00 | 14 | 594 | 1413 | 178 | 1 | 9 | 2 | 1 | 9 | 177 | 1 | 13 | 20000 | 1 | 9 | 200 | 1 | 9 | 19900 | 1 | 13 | 6590 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 0 | 32 | A | 7 | 0.76 | A | 7 | 961 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 700 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.4 | 1 | 0
1977-12-17 | 1900-12-16 | 15:00 | 15 | 478 | 1413 | 182 | 1 | 9 | 0 | 1 | 9 | 182 | 1 | 13 | 19900 | 1 | 9 | 0 | 1 | 9 | 19900 | 1 | 13 | 5730 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.73 | A | 7 | 962 | A | 7 | 260 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 700 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.12 | 1 | 0
1977-12-17 | 1900-12-16 | 16:00 | 16 | 307 | 1413 | 98 | 1 | 13 | 2 | 1 | 9 | 97 | 1 | 13 | 10700 | 1 | 13 | 100 | 1 | 9 | 10700 | 1 | 13 | 3070 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.73 | A | 7 | 963 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 700 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.12 | 1 | 0
1977-12-17 | 1900-12-16 | 17:00 | 17 | 95 | 1307 | 35 | 1 | 13 | 1 | 1 | 9 | 35 | 1 | 13 | 3800 | 1 | 13 | 0 | 1 | 9 | 3800 | 1 | 13 | 1020 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.68 | A | 7 | 964 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1340 | A | 7 | 1 | E | 8 | 0.028 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.72 | 1 | 0
1977-12-17 | 1900-12-16 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.65 | A | 7 | 964 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.44 | 1 | 0
1977-12-17 | 1900-12-16 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.62 | A | 7 | 965 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.34 | 1 | 0
1977-12-17 | 1900-12-16 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 966 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1490 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.64 | 1 | 0
1977-12-17 | 1900-12-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 3.3 | 37.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.62 | A | 7 | 966 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.56 | 1 | 0
1977-12-17 | 1900-12-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.62 | A | 7 | 967 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.58 | 1 | 0
1977-12-17 | 1900-12-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.64 | A | 7 | 968 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 1 | 0
1977-12-17 | 1900-12-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.67 | A | 7 | 968 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.28 | 1 | 0
1977-12-18 | 1900-12-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.7 | A | 7 | 968 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.48 | 2 | 0
1977-12-18 | 1900-12-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5 | 23 | A | 7 | 0.69 | A | 7 | 968 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.4 | 2 | 0
1977-12-18 | 1900-12-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.75 | A | 7 | 969 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 2 | 0
1977-12-18 | 1900-12-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.78 | A | 7 | 969 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.18 | 2 | 0
1977-12-18 | 1900-12-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 970 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.2 | 2 | 0
1977-12-18 | 1900-12-17 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 970 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.2 | 2 | 0
1977-12-18 | 1900-12-17 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.2 | 2 | 0
1977-12-18 | 1900-12-17 | 8:00 | 8 | 19 | 577 | 20 | 1 | 13 | 135 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 971 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.2 | 2 | 0
1977-12-18 | 1900-12-17 | 9:00 | 9 | 201 | 1413 | 110 | 1 | 13 | 618 | 1 | 9 | 21 | 1 | 13 | 11600 | 1 | 13 | 45800 | 1 | 9 | 5100 | 1 | 13 | 530 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.78 | A | 7 | 972 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 2 | 0
1977-12-18 | 1900-12-17 | 10:00 | 10 | 397 | 1413 | 261 | 1 | 9 | 816 | 1 | 9 | 30 | 1 | 13 | 27700 | 1 | 9 | 72600 | 1 | 9 | 7200 | 1 | 13 | 830 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.67 | A | 7 | 973 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.06 | 2 | 0
1977-12-18 | 1900-12-17 | 11:00 | 11 | 542 | 1413 | 357 | 1 | 9 | 808 | 1 | 9 | 45 | 1 | 13 | 37700 | 1 | 9 | 76200 | 1 | 9 | 8300 | 1 | 13 | 1140 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 973 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 2 | 0
1977-12-18 | 1900-12-17 | 12:00 | 12 | 626 | 1413 | 410 | 1 | 9 | 798 | 1 | 9 | 54 | 1 | 13 | 43100 | 1 | 9 | 76800 | 1 | 9 | 8900 | 1 | 13 | 1320 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | 5.6 | 42.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.55 | A | 7 | 972 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.76 | 2 | 0
1977-12-18 | 1900-12-17 | 13:00 | 13 | 644 | 1413 | 393 | 1 | 13 | 665 | 1 | 13 | 88 | 1 | 13 | 41600 | 1 | 13 | 65200 | 1 | 13 | 11800 | 1 | 13 | 1860 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 6.7 | 44.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.51 | A | 7 | 971 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 2 | 0
1977-12-18 | 1900-12-17 | 14:00 | 14 | 594 | 1413 | 367 | 1 | 13 | 654 | 1 | 13 | 90 | 1 | 13 | 38500 | 1 | 13 | 63000 | 1 | 13 | 11900 | 1 | 13 | 1830 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | 7.2 | 44.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.49 | A | 7 | 970 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 2 | 0
1977-12-18 | 1900-12-17 | 15:00 | 15 | 479 | 1413 | 292 | 1 | 13 | 636 | 1 | 13 | 75 | 1 | 13 | 30400 | 1 | 13 | 58300 | 1 | 13 | 10600 | 1 | 13 | 1450 | 1 | 23 | 7 | A | 7 | 4 | A | 7 | 6.7 | 44.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.51 | A | 7 | 970 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 2 | 0
1977-12-18 | 1900-12-17 | 16:00 | 16 | 308 | 1413 | 141 | 1 | 13 | 384 | 1 | 13 | 57 | 1 | 13 | 14500 | 1 | 13 | 30400 | 1 | 13 | 7800 | 1 | 13 | 1030 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | 7.8 | 46.04 | A | 7 | -2.8 | 26.96 | A | 7 | 0.48 | A | 7 | 970 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.06 | 2 | 0
1977-12-18 | 1900-12-17 | 17:00 | 17 | 97 | 1331 | 43 | 1 | 13 | 159 | 1 | 13 | 29 | 1 | 13 | 4300 | 1 | 13 | 7000 | 1 | 13 | 3700 | 1 | 13 | 520 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | 4.4 | 39.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.57 | A | 7 | 970 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.16 | 2 | 0
1977-12-18 | 1900-12-17 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 970 | A | 7 | 50 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 2 | 0
1977-12-18 | 1900-12-17 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 970 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 2 | 0
1977-12-18 | 1900-12-17 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | 2.2 | 35.96 | A | 7 | -2.8 | 26.96 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 90 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 2 | 0
1977-12-18 | 1900-12-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 1.7 | 35.06 | A | 7 | -3.3 | 26.06 | A | 7 | 0.7 | A | 7 | 971 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.36 | 2 | 0
1977-12-18 | 1900-12-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.75 | A | 7 | 970 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 2 | 0
1977-12-18 | 1900-12-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.75 | A | 7 | 970 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 2 | 0
1977-12-18 | 1900-12-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -3.3 | 26.06 | A | 7 | 0.79 | A | 7 | 970 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 2 | 0
1977-12-19 | 1900-12-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -3.3 | 26.06 | A | 7 | 0.79 | A | 7 | 970 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 3 | 0
1977-12-19 | 1900-12-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.82 | A | 7 | 969 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 3 | 0
1977-12-19 | 1900-12-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -3.3 | 26.06 | A | 7 | 0.79 | A | 7 | 969 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.16 | 3 | 0
1977-12-19 | 1900-12-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 969 | A | 7 | 70 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.38 | 3 | 0
1977-12-19 | 1900-12-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.82 | A | 7 | 968 | A | 7 | 60 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 3 | 0
1977-12-19 | 1900-12-18 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.82 | A | 7 | 968 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 3 | 0
1977-12-19 | 1900-12-18 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.82 | A | 7 | 969 | A | 7 | 40 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 3 | 0
1977-12-19 | 1900-12-18 | 8:00 | 8 | 18 | 577 | 8 | 1 | 13 | 11 | 1 | 13 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 970 | A | 7 | 20 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.38 | 3 | 0
1977-12-19 | 1900-12-18 | 9:00 | 9 | 199 | 1413 | 66 | 1 | 13 | 86 | 1 | 13 | 54 | 1 | 13 | 7200 | 1 | 13 | 5700 | 1 | 13 | 6400 | 1 | 13 | 1140 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 971 | A | 7 | 360 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 3 | 0
1977-12-19 | 1900-12-18 | 10:00 | 10 | 395 | 1413 | 152 | 1 | 9 | 122 | 1 | 9 | 117 | 1 | 13 | 16400 | 1 | 9 | 10900 | 1 | 9 | 13300 | 1 | 13 | 2590 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 972 | A | 7 | 350 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 0.9 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 3 | 0
1977-12-19 | 1900-12-18 | 11:00 | 11 | 540 | 1413 | 279 | 1 | 9 | 325 | 1 | 9 | 154 | 1 | 13 | 29600 | 1 | 9 | 31700 | 1 | 9 | 17400 | 1 | 13 | 3220 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 972 | A | 7 | 10 | A | 7 | 10.3 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 1 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 3 | 0
1977-12-19 | 1900-12-18 | 12:00 | 12 | 625 | 1413 | 244 | 1 | 9 | 119 | 1 | 9 | 191 | 1 | 13 | 26500 | 1 | 9 | 12000 | 1 | 9 | 21200 | 1 | 13 | 4590 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 1.1 | 33.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 972 | A | 7 | 360 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 3 | 0
1977-12-19 | 1900-12-18 | 13:00 | 13 | 644 | 1413 | 183 | 1 | 9 | 4 | 1 | 9 | 181 | 1 | 13 | 20700 | 1 | 9 | 300 | 1 | 9 | 20600 | 1 | 13 | 7030 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.75 | A | 7 | 972 | A | 7 | 360 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 0.9 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 3 | 0
1977-12-19 | 1900-12-18 | 14:00 | 14 | 594 | 1413 | 138 | 1 | 9 | 5 | 1 | 9 | 136 | 1 | 13 | 15900 | 1 | 9 | 400 | 1 | 9 | 15700 | 1 | 13 | 5500 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 972 | A | 7 | 350 | A | 7 | 7.2 | A | 7 | 1600 | A | 7 | 240 | A | 7 | 0.9 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 3 | 0
1977-12-19 | 1900-12-18 | 15:00 | 15 | 480 | 1413 | 102 | 1 | 9 | 8 | 1 | 9 | 99 | 1 | 13 | 11700 | 1 | 9 | 500 | 1 | 9 | 11500 | 1 | 13 | 3920 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 974 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 800 | A | 7 | 150 | A | 7 | 0.9 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 3 | 0
1977-12-19 | 1900-12-18 | 16:00 | 16 | 310 | 1413 | 85 | 1 | 13 | 6 | 1 | 9 | 83 | 1 | 13 | 9400 | 1 | 13 | 300 | 1 | 9 | 9300 | 1 | 13 | 2810 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 310 | A | 7 | 0.8 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 3 | 0
1977-12-19 | 1900-12-18 | 17:00 | 17 | 98 | 1331 | 26 | 1 | 13 | 1 | 1 | 9 | 26 | 1 | 13 | 2900 | 1 | 13 | 0 | 1 | 9 | 2900 | 1 | 13 | 850 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 430 | A | 7 | 0.8 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.38 | 3 | 0
1977-12-19 | 1900-12-18 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 370 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.2 | 3 | 0
1977-12-19 | 1900-12-18 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.72 | A | 7 | 978 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 3 | 0
1977-12-19 | 1900-12-18 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 330 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.84 | 3 | 0
1977-12-19 | 1900-12-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -7.8 | 17.96 | A | 7 | 0.69 | A | 7 | 980 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 3 | 0
1977-12-19 | 1900-12-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -3.3 | 26.06 | A | 7 | -7.2 | 19.04 | A | 7 | 0.75 | A | 7 | 980 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.24 | 3 | 0
1977-12-19 | 1900-12-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 3 | 0
1977-12-19 | 1900-12-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -3.9 | 24.98 | A | 7 | -8.9 | 15.98 | A | 7 | 0.69 | A | 7 | 981 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.98 | 3 | 0
1977-12-20 | 1900-12-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 4 | 0
1977-12-20 | 1900-12-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 980 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 4 | 0
1977-12-20 | 1900-12-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -3.9 | 24.98 | A | 7 | -10 | 14 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.7 | 4 | 0
1977-12-20 | 1900-12-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -3.9 | 24.98 | A | 7 | -10 | 14 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.7 | 4 | 0
1977-12-20 | 1900-12-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.72 | 4 | 0
1977-12-20 | 1900-12-19 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -11.1 | 12.02 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.92 | 4 | 0
1977-12-20 | 1900-12-19 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -5 | 23 | A | 7 | -11.1 | 12.02 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.92 | 4 | 0
1977-12-20 | 1900-12-19 | 8:00 | 8 | 17 | 554 | 4 | 1 | 13 | 0 | 1 | 9 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.62 | A | 7 | 981 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.6 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 4 | 0
1977-12-20 | 1900-12-19 | 9:00 | 9 | 197 | 1413 | 53 | 1 | 13 | 0 | 1 | 9 | 53 | 1 | 13 | 5900 | 1 | 13 | 0 | 1 | 9 | 5900 | 1 | 13 | 1700 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -10.6 | 12.92 | A | 7 | 0.68 | A | 7 | 982 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 0.6 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.02 | 4 | 0
1977-12-20 | 1900-12-19 | 10:00 | 10 | 393 | 1413 | 128 | 1 | 9 | 64 | 1 | 9 | 110 | 1 | 13 | 14000 | 1 | 9 | 5700 | 1 | 9 | 12400 | 1 | 13 | 2850 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | -5.6 | 21.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.57 | A | 7 | 983 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 4 | 0
1977-12-20 | 1900-12-19 | 11:00 | 11 | 539 | 1413 | 231 | 1 | 9 | 123 | 1 | 9 | 184 | 1 | 13 | 24900 | 1 | 9 | 11900 | 1 | 9 | 20300 | 1 | 13 | 4280 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -5.6 | 21.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.94 | 4 | 0
1977-12-20 | 1900-12-19 | 12:00 | 12 | 625 | 1413 | 143 | 1 | 9 | 16 | 1 | 9 | 136 | 1 | 13 | 16500 | 1 | 9 | 1100 | 1 | 9 | 16000 | 1 | 13 | 5640 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.58 | A | 7 | 982 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.64 | 4 | 0
1977-12-20 | 1900-12-19 | 13:00 | 13 | 644 | 1413 | 217 | 1 | 9 | 8 | 1 | 9 | 213 | 1 | 13 | 24200 | 1 | 9 | 700 | 1 | 9 | 23900 | 1 | 13 | 7770 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 3200 | A | 7 | 460 | A | 7 | 0.6 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.72 | 4 | 0
1977-12-20 | 1900-12-19 | 14:00 | 14 | 595 | 1413 | 253 | 1 | 9 | 183 | 1 | 9 | 176 | 1 | 13 | 27600 | 1 | 9 | 18200 | 1 | 9 | 19900 | 1 | 13 | 4170 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -5 | 23 | A | 7 | -12.8 | 8.96 | A | 7 | 0.54 | A | 7 | 981 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 460 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.66 | 4 | 0
1977-12-20 | 1900-12-19 | 15:00 | 15 | 481 | 1413 | 209 | 1 | 9 | 281 | 1 | 9 | 113 | 1 | 13 | 22500 | 1 | 9 | 26600 | 1 | 9 | 13400 | 1 | 13 | 2230 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -5.6 | 21.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 460 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 4 | 0
1977-12-20 | 1900-12-19 | 16:00 | 16 | 311 | 1413 | 79 | 1 | 13 | 6 | 1 | 9 | 78 | 1 | 13 | 8900 | 1 | 13 | 200 | 1 | 9 | 8800 | 1 | 13 | 2710 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 760 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.96 | 4 | 0
1977-12-20 | 1900-12-19 | 17:00 | 17 | 99 | 1331 | 16 | 1 | 13 | 3 | 1 | 9 | 16 | 1 | 13 | 1900 | 1 | 13 | 0 | 1 | 9 | 1900 | 1 | 13 | 590 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.62 | A | 7 | 981 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 1130 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.06 | 4 | 0
1977-12-20 | 1900-12-19 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 310 | A | 7 | 10.3 | A | 7 | 11300 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 4 | 0
1977-12-20 | 1900-12-19 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 300 | A | 7 | 10.3 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 4 | 0
1977-12-20 | 1900-12-19 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -12.8 | 8.96 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 300 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 760 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.16 | 4 | 0
1977-12-20 | 1900-12-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 4800 | A | 7 | 460 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 4 | 0
1977-12-20 | 1900-12-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -8.3 | 17.06 | A | 7 | -13.3 | 8.06 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.46 | 4 | 0
1977-12-20 | 1900-12-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -8.3 | 17.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 981 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 4800 | A | 7 | 610 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.46 | 4 | 0
1977-12-20 | 1900-12-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 320 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 4 | 0
1977-12-21 | 1900-12-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | -9.4 | 15.08 | A | 7 | -13.9 | 6.98 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.58 | 5 | 0
1977-12-21 | 1900-12-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -9.4 | 15.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 6400 | A | 7 | 400 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 5 | 0
1977-12-21 | 1900-12-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 460 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 5 | 0
1977-12-21 | 1900-12-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -13.9 | 6.98 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.38 | 5 | 0
1977-12-21 | 1900-12-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -13.9 | 6.98 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 550 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.38 | 5 | 0
1977-12-21 | 1900-12-20 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 981 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 5 | 0
1977-12-21 | 1900-12-20 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 5 | 0
1977-12-21 | 1900-12-20 | 8:00 | 8 | 16 | 554 | 3 | 1 | 13 | 1 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 0.5 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 5 | 0
1977-12-21 | 1900-12-20 | 9:00 | 9 | 195 | 1414 | 37 | 1 | 13 | 2 | 1 | 9 | 37 | 1 | 13 | 4200 | 1 | 13 | 0 | 1 | 9 | 4200 | 1 | 13 | 1320 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -14.4 | 6.08 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 300 | A | 7 | 9.8 | A | 7 | 8000 | A | 7 | 610 | A | 7 | 0.5 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.48 | 5 | 0
1977-12-21 | 1900-12-20 | 10:00 | 10 | 392 | 1414 | 147 | 1 | 9 | 99 | 1 | 9 | 120 | 1 | 13 | 15900 | 1 | 9 | 8800 | 1 | 9 | 13500 | 1 | 13 | 2660 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | -8.9 | 15.98 | A | 7 | -15 | 5 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 850 | A | 7 | 0.5 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.4 | 5 | 0
1977-12-21 | 1900-12-20 | 11:00 | 11 | 538 | 1414 | 327 | 1 | 13 | 588 | 1 | 13 | 101 | 1 | 13 | 33600 | 1 | 13 | 54900 | 1 | 13 | 12600 | 1 | 13 | 1930 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -7.2 | 19.04 | A | 7 | -13.9 | 6.98 | A | 7 | 0.59 | A | 7 | 984 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.08 | 5 | 0
1977-12-21 | 1900-12-20 | 12:00 | 12 | 624 | 1414 | 447 | 1 | 9 | 864 | 1 | 9 | 63 | 1 | 13 | 46800 | 1 | 9 | 83000 | 1 | 9 | 10000 | 1 | 13 | 1380 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -13.3 | 8.06 | A | 7 | 0.55 | A | 7 | 983 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.86 | 5 | 0
1977-12-21 | 1900-12-20 | 13:00 | 13 | 644 | 1414 | 461 | 1 | 9 | 868 | 1 | 9 | 64 | 1 | 13 | 48300 | 1 | 9 | 83700 | 1 | 9 | 10000 | 1 | 13 | 1410 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.55 | A | 7 | 983 | A | 7 | 290 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.64 | 5 | 0
1977-12-21 | 1900-12-20 | 14:00 | 14 | 595 | 1414 | 420 | 1 | 9 | 850 | 1 | 9 | 61 | 1 | 13 | 44100 | 1 | 9 | 81100 | 1 | 9 | 9800 | 1 | 13 | 1330 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.54 | 5 | 0
1977-12-21 | 1900-12-20 | 15:00 | 15 | 482 | 1414 | 320 | 1 | 9 | 783 | 1 | 9 | 52 | 1 | 13 | 33700 | 1 | 9 | 72200 | 1 | 9 | 8900 | 1 | 13 | 1120 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.53 | A | 7 | 982 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 5 | 0
1977-12-21 | 1900-12-20 | 16:00 | 16 | 312 | 1414 | 181 | 1 | 13 | 636 | 1 | 9 | 40 | 1 | 13 | 18700 | 1 | 13 | 52300 | 1 | 9 | 7100 | 1 | 13 | 800 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.51 | A | 7 | 983 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.24 | 5 | 0
1977-12-21 | 1900-12-20 | 17:00 | 17 | 101 | 1355 | 45 | 1 | 13 | 274 | 1 | 9 | 21 | 1 | 13 | 4400 | 1 | 13 | 13800 | 1 | 9 | 3300 | 1 | 13 | 380 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.51 | A | 7 | 983 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.44 | 5 | 0
1977-12-21 | 1900-12-20 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.53 | A | 7 | 983 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.56 | 5 | 0
1977-12-21 | 1900-12-20 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -12.2 | 10.04 | A | 7 | 0.57 | A | 7 | 983 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.74 | 5 | 0
1977-12-21 | 1900-12-20 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -11.7 | 10.94 | A | 7 | 0.6 | A | 7 | 983 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.74 | 5 | 0
1977-12-21 | 1900-12-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 5 | 0
1977-12-21 | 1900-12-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 5 | 0
1977-12-21 | 1900-12-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 5 | 0
1977-12-21 | 1900-12-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 5 | 0
1977-12-22 | 1900-12-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 6 | 0
1977-12-22 | 1900-12-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 6 | 0
1977-12-22 | 1900-12-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 981 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 6 | 0
1977-12-22 | 1900-12-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.57 | A | 7 | 979 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 6 | 0
1977-12-22 | 1900-12-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.55 | A | 7 | 978 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.64 | 6 | 0
1977-12-22 | 1900-12-21 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -12.8 | 8.96 | A | 7 | 0.47 | A | 7 | 977 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.26 | 6 | 0
1977-12-22 | 1900-12-21 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -2.2 | 28.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.49 | A | 7 | 976 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.14 | 6 | 0
1977-12-22 | 1900-12-21 | 8:00 | 8 | 15 | 530 | 12 | 1 | 13 | 12 | 1 | 13 | 11 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | -1.1 | 30.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.41 | A | 7 | 975 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.5 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.96 | 6 | 0
1977-12-22 | 1900-12-21 | 9:00 | 9 | 194 | 1414 | 68 | 1 | 13 | 109 | 1 | 13 | 53 | 1 | 13 | 7100 | 1 | 13 | 6500 | 1 | 13 | 6200 | 1 | 13 | 1000 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 0 | 32 | A | 7 | -12.2 | 10.04 | A | 7 | 0.4 | A | 7 | 975 | A | 7 | 200 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.84 | 6 | 0
1977-12-22 | 1900-12-21 | 10:00 | 10 | 390 | 1414 | 185 | 1 | 13 | 288 | 1 | 13 | 105 | 1 | 13 | 19600 | 1 | 13 | 25200 | 1 | 13 | 12600 | 1 | 13 | 2070 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 1.7 | 35.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.34 | A | 7 | 975 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.66 | 6 | 0
1977-12-22 | 1900-12-21 | 11:00 | 11 | 537 | 1414 | 293 | 1 | 13 | 416 | 1 | 13 | 134 | 1 | 13 | 30600 | 1 | 13 | 39400 | 1 | 13 | 15500 | 1 | 13 | 2610 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 5 | 41 | A | 7 | -12.8 | 8.96 | A | 7 | 0.27 | A | 7 | 973 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.26 | 6 | 0
1977-12-22 | 1900-12-21 | 12:00 | 12 | 624 | 1414 | 217 | 1 | 9 | 51 | 1 | 9 | 194 | 1 | 13 | 23800 | 1 | 9 | 5000 | 1 | 9 | 21500 | 1 | 13 | 5510 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 6.7 | 44.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.25 | A | 7 | 971 | A | 7 | 180 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 5490 | A | 7 | 0.5 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.04 | 6 | 0
1977-12-22 | 1900-12-21 | 13:00 | 13 | 644 | 1414 | 269 | 1 | 13 | 207 | 1 | 13 | 174 | 1 | 13 | 28800 | 1 | 13 | 21100 | 1 | 13 | 19200 | 1 | 13 | 3760 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 8.3 | 46.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.23 | A | 7 | 969 | A | 7 | 200 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 5490 | A | 7 | 0.5 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.74 | 6 | 0
1977-12-22 | 1900-12-21 | 14:00 | 14 | 596 | 1414 | 205 | 1 | 9 | 35 | 1 | 9 | 190 | 1 | 13 | 22500 | 1 | 9 | 3400 | 1 | 9 | 21000 | 1 | 13 | 5290 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 9.4 | 48.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.21 | A | 7 | 968 | A | 7 | 200 | A | 7 | 10.8 | A | 7 | 24100 | A | 7 | 5490 | A | 7 | 0.5 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.64 | 6 | 0
1977-12-22 | 1900-12-21 | 15:00 | 15 | 483 | 1414 | 155 | 1 | 9 | 113 | 1 | 9 | 116 | 1 | 13 | 17000 | 1 | 9 | 10800 | 1 | 9 | 13300 | 1 | 13 | 2640 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 8.9 | 48.02 | A | 7 | -11.7 | 10.94 | A | 7 | 0.22 | A | 7 | 966 | A | 7 | 190 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 5490 | A | 7 | 0.5 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.64 | 6 | 0
1977-12-22 | 1900-12-21 | 16:00 | 16 | 314 | 1414 | 99 | 1 | 13 | 28 | 1 | 9 | 92 | 1 | 13 | 10700 | 1 | 13 | 2400 | 1 | 9 | 10200 | 1 | 13 | 2270 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | -11.7 | 10.94 | A | 7 | 0.21 | A | 7 | 965 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 5490 | A | 7 | 0.6 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.64 | 6 | 0
1977-12-22 | 1900-12-21 | 17:00 | 17 | 103 | 1355 | 20 | 1 | 13 | 3 | 1 | 9 | 20 | 1 | 13 | 2300 | 1 | 13 | 0 | 1 | 9 | 2300 | 1 | 13 | 710 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 8.3 | 46.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.23 | A | 7 | 966 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 5490 | A | 7 | 0.5 | E | 8 | 0.031 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.74 | 6 | 0
1977-12-22 | 1900-12-21 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.24 | A | 7 | 966 | A | 7 | 200 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 5490 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.74 | 6 | 0
1977-12-22 | 1900-12-21 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 2 | A | 7 | 6.7 | 44.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.26 | A | 7 | 965 | A | 7 | 190 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.94 | 6 | 0
1977-12-22 | 1900-12-21 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 6.1 | 42.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.27 | A | 7 | 966 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.94 | 6 | 0
1977-12-22 | 1900-12-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 5.6 | 42.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.31 | A | 7 | 967 | A | 7 | 220 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.82 | 6 | 0
1977-12-22 | 1900-12-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -10.6 | 12.92 | A | 7 | 0.32 | A | 7 | 967 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.92 | 6 | 0
1977-12-22 | 1900-12-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -10 | 14 | A | 7 | 0.35 | A | 7 | 968 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10 | 6 | 0
1977-12-22 | 1900-12-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -10 | 14 | A | 7 | 0.35 | A | 7 | 969 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10 | 6 | 0
1977-12-23 | 1900-12-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.42 | A | 7 | 970 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.38 | 7 | 0
1977-12-23 | 1900-12-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.5 | A | 7 | 971 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.46 | 7 | 0
1977-12-23 | 1900-12-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.59 | A | 7 | 972 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.82 | 7 | 0
1977-12-23 | 1900-12-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 973 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.24 | 7 | 0
1977-12-23 | 1900-12-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 973 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 7 | 0
1977-12-23 | 1900-12-22 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.72 | A | 7 | 974 | A | 7 | 280 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 7 | 0
1977-12-23 | 1900-12-22 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 975 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 7 | 0
1977-12-23 | 1900-12-22 | 8:00 | 8 | 15 | 530 | 18 | 1 | 13 | 113 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 7 | 0
1977-12-23 | 1900-12-22 | 9:00 | 9 | 192 | 1414 | 101 | 1 | 13 | 581 | 1 | 9 | 21 | 1 | 13 | 10600 | 1 | 13 | 42400 | 1 | 9 | 4900 | 1 | 13 | 510 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 976 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.92 | 7 | 0
1977-12-23 | 1900-12-22 | 10:00 | 10 | 389 | 1414 | 251 | 1 | 9 | 794 | 1 | 9 | 31 | 1 | 13 | 26600 | 1 | 9 | 70300 | 1 | 9 | 7200 | 1 | 13 | 830 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.64 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 7 | 0
1977-12-23 | 1900-12-22 | 11:00 | 11 | 537 | 1414 | 377 | 1 | 9 | 886 | 1 | 9 | 39 | 1 | 13 | 40000 | 1 | 9 | 83500 | 1 | 9 | 8200 | 1 | 13 | 1050 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.53 | A | 7 | 977 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.12 | 7 | 0
1977-12-23 | 1900-12-22 | 12:00 | 12 | 624 | 1414 | 453 | 1 | 9 | 923 | 1 | 9 | 43 | 1 | 13 | 47900 | 1 | 9 | 88900 | 1 | 9 | 8500 | 1 | 13 | 1170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -6.1 | 21.02 | A | 7 | 0.45 | A | 7 | 976 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.72 | 7 | 0
1977-12-23 | 1900-12-22 | 13:00 | 13 | 644 | 1414 | 472 | 1 | 9 | 934 | 1 | 9 | 44 | 1 | 13 | 50000 | 1 | 9 | 90300 | 1 | 9 | 8600 | 1 | 13 | 1200 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.38 | A | 7 | 976 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.24 | 7 | 0
1977-12-23 | 1900-12-22 | 14:00 | 14 | 597 | 1414 | 432 | 1 | 9 | 922 | 1 | 9 | 42 | 1 | 13 | 45900 | 1 | 9 | 88300 | 1 | 9 | 8500 | 1 | 13 | 1140 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.3 | A | 7 | 975 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.26 | 7 | 0
1977-12-23 | 1900-12-22 | 15:00 | 15 | 485 | 1414 | 335 | 1 | 9 | 872 | 1 | 9 | 36 | 1 | 13 | 35700 | 1 | 9 | 80700 | 1 | 9 | 7900 | 1 | 13 | 980 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.9 | 48.02 | A | 7 | -7.2 | 19.04 | A | 7 | 0.32 | A | 7 | 975 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.04 | 7 | 0
1977-12-23 | 1900-12-22 | 16:00 | 16 | 316 | 1414 | 195 | 1 | 13 | 753 | 1 | 9 | 27 | 1 | 13 | 20900 | 1 | 13 | 63400 | 1 | 9 | 6600 | 1 | 13 | 720 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 9.4 | 48.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.33 | A | 7 | 975 | A | 7 | 170 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.72 | 7 | 0
1977-12-23 | 1900-12-22 | 17:00 | 17 | 105 | 1379 | 51 | 1 | 13 | 409 | 1 | 9 | 16 | 1 | 13 | 5200 | 1 | 13 | 25600 | 1 | 9 | 3100 | 1 | 13 | 350 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.42 | A | 7 | 974 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.42 | 7 | 0
1977-12-23 | 1900-12-22 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.47 | A | 7 | 974 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.82 | 7 | 0
1977-12-23 | 1900-12-22 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.55 | A | 7 | 974 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.52 | 7 | 0
1977-12-23 | 1900-12-22 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -5 | 23 | A | 7 | 0.57 | A | 7 | 973 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.4 | 7 | 0
1977-12-23 | 1900-12-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -5 | 23 | A | 7 | 0.53 | A | 7 | 972 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.1 | 7 | 0
1977-12-23 | 1900-12-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | 4.4 | 39.92 | A | 7 | -5 | 23 | A | 7 | 0.51 | A | 7 | 972 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.9 | 7 | 0
1977-12-23 | 1900-12-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 5.6 | 42.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.43 | A | 7 | 972 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.52 | 7 | 0
1977-12-23 | 1900-12-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.42 | A | 7 | 971 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.42 | 7 | 0
1977-12-24 | 1900-12-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | 6.7 | 44.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.38 | A | 7 | 970 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.24 | 1 | 0
1977-12-24 | 1900-12-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 5 | A | 7 | 7.2 | 44.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.37 | A | 7 | 968 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.14 | 1 | 0
1977-12-24 | 1900-12-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 7.2 | 44.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.37 | A | 7 | 966 | A | 7 | 170 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.14 | 1 | 0
1977-12-24 | 1900-12-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | 7.8 | 46.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.36 | A | 7 | 964 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.04 | 1 | 0
1977-12-24 | 1900-12-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 6.7 | 44.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.4 | A | 7 | 964 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.32 | 1 | 0
1977-12-24 | 1900-12-23 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | 5 | 41 | A | 7 | -5 | 23 | A | 7 | 0.49 | A | 7 | 963 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.7 | 1 | 0
1977-12-24 | 1900-12-23 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 4.4 | 39.92 | A | 7 | -5 | 23 | A | 7 | 0.51 | A | 7 | 963 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.9 | 1 | 0
1977-12-24 | 1900-12-23 | 8:00 | 8 | 14 | 507 | 9 | 1 | 13 | 15 | 1 | 13 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 3.9 | 39.02 | A | 7 | -5 | 23 | A | 7 | 0.53 | A | 7 | 963 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 6100 | A | 7 | 0.8 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.1 | 1 | 0
1977-12-24 | 1900-12-23 | 9:00 | 9 | 190 | 1414 | 84 | 1 | 13 | 321 | 1 | 9 | 40 | 1 | 13 | 8500 | 1 | 13 | 20500 | 1 | 9 | 5700 | 1 | 13 | 700 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | 4.4 | 39.92 | A | 7 | -5 | 23 | A | 7 | 0.51 | A | 7 | 964 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.9 | 1 | 0
1977-12-24 | 1900-12-23 | 10:00 | 10 | 388 | 1414 | 239 | 1 | 9 | 706 | 1 | 9 | 44 | 1 | 13 | 25000 | 1 | 9 | 62100 | 1 | 9 | 7800 | 1 | 13 | 920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.6 | A | 7 | 967 | A | 7 | 320 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 1 | 0
1977-12-24 | 1900-12-23 | 11:00 | 11 | 536 | 1414 | 148 | 1 | 9 | 11 | 1 | 9 | 144 | 1 | 13 | 16700 | 1 | 9 | 800 | 1 | 9 | 16400 | 1 | 13 | 5420 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.73 | A | 7 | 970 | A | 7 | 310 | A | 7 | 10.8 | A | 7 | 6400 | A | 7 | 340 | A | 7 | 0.9 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.46 | 1 | 0
1977-12-24 | 1900-12-23 | 12:00 | 12 | 624 | 1414 | 158 | 1 | 9 | 0 | 1 | 9 | 158 | 1 | 13 | 18000 | 1 | 9 | 0 | 1 | 9 | 18000 | 1 | 13 | 6290 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -5 | 23 | A | 7 | 0.69 | A | 7 | 971 | A | 7 | 330 | A | 7 | 8.2 | A | 7 | 6400 | A | 7 | 430 | A | 7 | 0.8 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.4 | 1 | 0
1977-12-24 | 1900-12-23 | 13:00 | 13 | 645 | 1414 | 167 | 1 | 9 | 3 | 1 | 9 | 166 | 1 | 13 | 19100 | 1 | 9 | 200 | 1 | 9 | 19000 | 1 | 13 | 6630 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 973 | A | 7 | 330 | A | 7 | 9.8 | A | 7 | 9700 | A | 7 | 520 | A | 7 | 0.7 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.62 | 1 | 0
1977-12-24 | 1900-12-23 | 14:00 | 14 | 598 | 1414 | 246 | 1 | 13 | 219 | 1 | 13 | 153 | 1 | 13 | 26400 | 1 | 13 | 22000 | 1 | 13 | 17100 | 1 | 13 | 3200 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 0 | 32 | A | 7 | -7.8 | 17.96 | A | 7 | 0.56 | A | 7 | 974 | A | 7 | 320 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 0.7 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.86 | 1 | 0
1977-12-24 | 1900-12-23 | 15:00 | 15 | 487 | 1414 | 251 | 1 | 13 | 318 | 1 | 13 | 141 | 1 | 13 | 26500 | 1 | 13 | 30100 | 1 | 13 | 16100 | 1 | 13 | 2910 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 976 | A | 7 | 330 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 640 | A | 7 | 0.6 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 1 | 0
1977-12-24 | 1900-12-23 | 16:00 | 16 | 318 | 1414 | 143 | 1 | 13 | 230 | 1 | 13 | 91 | 1 | 13 | 15000 | 1 | 13 | 18300 | 1 | 13 | 10900 | 1 | 13 | 1790 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -1.7 | 28.94 | A | 7 | -10 | 14 | A | 7 | 0.53 | A | 7 | 978 | A | 7 | 330 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.1 | 1 | 0
1977-12-24 | 1900-12-23 | 17:00 | 17 | 107 | 1402 | 31 | 1 | 13 | 96 | 1 | 13 | 23 | 1 | 13 | 3300 | 1 | 13 | 4000 | 1 | 13 | 3000 | 1 | 13 | 400 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -2.8 | 26.96 | A | 7 | -10.6 | 12.92 | A | 7 | 0.55 | A | 7 | 979 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 1 | 0
1977-12-24 | 1900-12-23 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 1 | 0
1977-12-24 | 1900-12-23 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.72 | 1 | 0
1977-12-24 | 1900-12-23 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -11.7 | 10.94 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.74 | 1 | 0
1977-12-24 | 1900-12-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -11.7 | 10.94 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.04 | 1 | 0
1977-12-24 | 1900-12-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.57 | A | 7 | 984 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.96 | 1 | 0
1977-12-24 | 1900-12-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.6 | A | 7 | 984 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.06 | 1 | 0
1977-12-24 | 1900-12-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -13.3 | 8.06 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.16 | 1 | 0
1977-12-25 | 1900-12-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -13.3 | 8.06 | A | 7 | 0.65 | A | 7 | 984 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.36 | 2 | 0
1977-12-25 | 1900-12-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -13.9 | 6.98 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.38 | 2 | 0
1977-12-25 | 1900-12-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -13.9 | 6.98 | A | 7 | 0.65 | A | 7 | 984 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.38 | 2 | 0
1977-12-25 | 1900-12-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 983 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 2 | 0
1977-12-25 | 1900-12-24 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.67 | A | 7 | 983 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.58 | 2 | 0
1977-12-25 | 1900-12-24 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -15 | 5 | A | 7 | 0.64 | A | 7 | 983 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.4 | 2 | 0
1977-12-25 | 1900-12-24 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -15 | 5 | A | 7 | 0.64 | A | 7 | 984 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.4 | 2 | 0
1977-12-25 | 1900-12-24 | 8:00 | 8 | 14 | 507 | 18 | 1 | 13 | 110 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.59 | A | 7 | 984 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.22 | 2 | 0
1977-12-25 | 1900-12-24 | 9:00 | 9 | 189 | 1414 | 104 | 1 | 13 | 610 | 1 | 9 | 21 | 1 | 13 | 10900 | 1 | 13 | 44300 | 1 | 9 | 5000 | 1 | 13 | 510 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -16.7 | 1.94 | A | 7 | 0.51 | A | 7 | 985 | A | 7 | 320 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.04 | 2 | 0
1977-12-25 | 1900-12-24 | 10:00 | 10 | 387 | 1414 | 258 | 1 | 9 | 823 | 1 | 9 | 31 | 1 | 13 | 27400 | 1 | 9 | 72700 | 1 | 9 | 7400 | 1 | 13 | 830 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.49 | A | 7 | 986 | A | 7 | 320 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.04 | 2 | 0
1977-12-25 | 1900-12-24 | 11:00 | 11 | 536 | 1414 | 384 | 1 | 9 | 907 | 1 | 9 | 39 | 1 | 13 | 40800 | 1 | 9 | 85400 | 1 | 9 | 8300 | 1 | 13 | 1050 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -16.7 | 1.94 | A | 7 | 0.43 | A | 7 | 987 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.26 | 2 | 0
1977-12-25 | 1900-12-24 | 12:00 | 12 | 624 | 1414 | 464 | 1 | 9 | 948 | 1 | 9 | 43 | 1 | 13 | 49100 | 1 | 9 | 91300 | 1 | 9 | 8600 | 1 | 13 | 1170 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -16.7 | 1.94 | A | 7 | 0.4 | A | 7 | 986 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.36 | 2 | 0
1977-12-25 | 1900-12-24 | 13:00 | 13 | 646 | 1414 | 483 | 1 | 9 | 956 | 1 | 9 | 45 | 1 | 13 | 51200 | 1 | 9 | 92400 | 1 | 9 | 8800 | 1 | 13 | 1220 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.38 | A | 7 | 986 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.36 | 2 | 0
1977-12-25 | 1900-12-24 | 14:00 | 14 | 599 | 1414 | 441 | 1 | 9 | 939 | 1 | 9 | 42 | 1 | 13 | 46800 | 1 | 9 | 89900 | 1 | 9 | 8600 | 1 | 13 | 1140 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.38 | A | 7 | 985 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.36 | 2 | 0
1977-12-25 | 1900-12-24 | 15:00 | 15 | 488 | 1414 | 342 | 1 | 9 | 886 | 1 | 9 | 36 | 1 | 13 | 36500 | 1 | 9 | 82100 | 1 | 9 | 8000 | 1 | 13 | 980 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.4 | A | 7 | 985 | A | 7 | 280 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.62 | 2 | 0
1977-12-25 | 1900-12-24 | 16:00 | 16 | 320 | 1414 | 200 | 1 | 13 | 763 | 1 | 9 | 27 | 1 | 13 | 21400 | 1 | 13 | 64400 | 1 | 9 | 6700 | 1 | 13 | 720 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.46 | A | 7 | 985 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.68 | 2 | 0
1977-12-25 | 1900-12-24 | 17:00 | 17 | 109 | 1403 | 54 | 1 | 13 | 448 | 1 | 9 | 15 | 1 | 13 | 5500 | 1 | 13 | 28200 | 1 | 9 | 3200 | 1 | 13 | 350 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -16.1 | 3.02 | A | 7 | 0.42 | A | 7 | 985 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.025 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.72 | 2 | 0
1977-12-25 | 1900-12-24 | 18:00 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -16.1 | 3.02 | A | 7 | 0.47 | A | 7 | 985 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.92 | 2 | 0
1977-12-25 | 1900-12-24 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -15.6 | 3.92 | A | 7 | 0.54 | A | 7 | 985 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.02 | 2 | 0
1977-12-25 | 1900-12-24 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -15.6 | 3.92 | A | 7 | 0.54 | A | 7 | 984 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.02 | 2 | 0
1977-12-25 | 1900-12-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.59 | A | 7 | 984 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.22 | 2 | 0
1977-12-25 | 1900-12-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -15 | 5 | A | 7 | 0.62 | A | 7 | 984 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.4 | 2 | 0
1977-12-25 | 1900-12-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -15.6 | 3.92 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.32 | 2 | 0
1977-12-25 | 1900-12-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -15.6 | 3.92 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.32 | 2 | 0
1977-12-26 | 1900-12-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -15.6 | 3.92 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 220 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.92 | 3 | 0
1977-12-26 | 1900-12-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 240 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.6 | 3 | 0
1977-12-26 | 1900-12-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.6 | 3 | 0
1977-12-26 | 1900-12-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -15 | 5 | A | 7 | 0.64 | A | 7 | 981 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.4 | 3 | 0
1977-12-26 | 1900-12-25 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -15 | 5 | A | 7 | 0.64 | A | 7 | 981 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.4 | 3 | 0
1977-12-26 | 1900-12-25 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -15.6 | 3.92 | A | 7 | 0.67 | A | 7 | 980 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.52 | 3 | 0
1977-12-26 | 1900-12-25 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -15 | 5 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.7 | 3 | 0
1977-12-26 | 1900-12-25 | 8:00 | 8 | 13 | 507 | 8 | 1 | 13 | 29 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -10.6 | 12.92 | A | 7 | -15 | 5 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.7 | 3 | 0
1977-12-26 | 1900-12-25 | 9:00 | 9 | 188 | 1414 | 90 | 1 | 13 | 414 | 1 | 9 | 34 | 1 | 13 | 9100 | 1 | 13 | 26600 | 1 | 9 | 5600 | 1 | 13 | 610 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.62 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.06 | 3 | 0
1977-12-26 | 1900-12-25 | 10:00 | 10 | 386 | 1414 | 141 | 1 | 13 | 192 | 1 | 13 | 88 | 1 | 13 | 15100 | 1 | 13 | 16700 | 1 | 13 | 10500 | 1 | 13 | 1680 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | -6.1 | 21.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.96 | 3 | 0
1977-12-26 | 1900-12-25 | 11:00 | 11 | 535 | 1414 | 318 | 1 | 13 | 620 | 1 | 13 | 82 | 1 | 13 | 33300 | 1 | 13 | 58400 | 1 | 13 | 11100 | 1 | 13 | 1620 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | -4.4 | 24.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.6 | A | 7 | 982 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.72 | 3 | 0
1977-12-26 | 1900-12-25 | 12:00 | 12 | 624 | 1414 | 456 | 1 | 13 | 780 | 1 | 13 | 110 | 1 | 13 | 47400 | 1 | 13 | 75200 | 1 | 13 | 14100 | 1 | 13 | 2210 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -2.2 | 28.04 | A | 7 | -12.8 | 8.96 | A | 7 | 0.45 | A | 7 | 981 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.16 | 3 | 0
1977-12-26 | 1900-12-25 | 13:00 | 13 | 647 | 1414 | 338 | 1 | 13 | 448 | 1 | 13 | 133 | 1 | 13 | 36200 | 1 | 13 | 44300 | 1 | 13 | 15900 | 1 | 13 | 2670 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | -0.6 | 30.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.4 | A | 7 | 981 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.96 | 3 | 0
1977-12-26 | 1900-12-25 | 14:00 | 14 | 601 | 1414 | 298 | 1 | 13 | 357 | 1 | 13 | 146 | 1 | 13 | 31300 | 1 | 13 | 34700 | 1 | 13 | 16500 | 1 | 13 | 2920 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 1.1 | 33.98 | A | 7 | -13.3 | 8.06 | A | 7 | 0.34 | A | 7 | 981 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.86 | 3 | 0
1977-12-26 | 1900-12-25 | 15:00 | 15 | 490 | 1414 | 178 | 1 | 13 | 145 | 1 | 13 | 128 | 1 | 13 | 19500 | 1 | 13 | 13800 | 1 | 13 | 14700 | 1 | 13 | 2920 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -0.6 | 30.92 | A | 7 | -15 | 5 | A | 7 | 0.33 | A | 7 | 982 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.1 | 3 | 0
1977-12-26 | 1900-12-25 | 16:00 | 16 | 323 | 1414 | 86 | 1 | 13 | 91 | 1 | 13 | 65 | 1 | 13 | 9500 | 1 | 13 | 7600 | 1 | 13 | 7800 | 1 | 13 | 1410 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -1.7 | 28.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.31 | A | 7 | 983 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.4 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.66 | 3 | 0
1977-12-26 | 1900-12-25 | 17:00 | 17 | 112 | 1414 | 43 | 1 | 13 | 217 | 1 | 9 | 23 | 1 | 13 | 4100 | 1 | 13 | 10900 | 1 | 9 | 3200 | 1 | 13 | 410 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -2.8 | 26.96 | A | 7 | -15.6 | 3.92 | A | 7 | 0.37 | A | 7 | 984 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.32 | 3 | 0
1977-12-26 | 1900-12-25 | 18:00 | 18 | 0 | 12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -15 | 5 | A | 7 | 0.44 | A | 7 | 985 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.6 | 3 | 0
1977-12-26 | 1900-12-25 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.5 | A | 7 | 985 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.78 | 3 | 0
1977-12-26 | 1900-12-25 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -13.9 | 6.98 | A | 7 | 0.55 | A | 7 | 986 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 3 | 0
1977-12-26 | 1900-12-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -13.9 | 6.98 | A | 7 | 0.57 | A | 7 | 987 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.98 | 3 | 0
1977-12-26 | 1900-12-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -15 | 5 | A | 7 | 0.57 | A | 7 | 988 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.1 | 3 | 0
1977-12-26 | 1900-12-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.59 | A | 7 | 989 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.42 | 3 | 0
1977-12-26 | 1900-12-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.59 | A | 7 | 988 | A | 7 | 330 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.42 | 3 | 0
1977-12-27 | 1900-12-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 989 | A | 7 | 330 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.64 | 4 | 0
1977-12-27 | 1900-12-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -16.1 | 3.02 | A | 7 | 0.7 | A | 7 | 990 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.82 | 4 | 0
1977-12-27 | 1900-12-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -17.8 | -0.04 | A | 7 | 0.61 | A | 7 | 991 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.44 | 4 | 0
1977-12-27 | 1900-12-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -17.8 | -0.04 | A | 7 | 0.67 | A | 7 | 990 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.24 | 4 | 0
1977-12-27 | 1900-12-26 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -17.8 | -0.04 | A | 7 | 0.67 | A | 7 | 991 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.24 | 4 | 0
1977-12-27 | 1900-12-26 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -17.8 | -0.04 | A | 7 | 0.73 | A | 7 | 991 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.04 | 4 | 0
1977-12-27 | 1900-12-26 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -17.8 | -0.04 | A | 7 | 0.76 | A | 7 | 991 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.94 | 4 | 0
1977-12-27 | 1900-12-26 | 8:00 | 8 | 13 | 483 | 13 | 1 | 13 | 60 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -17.8 | -0.04 | A | 7 | 0.76 | A | 7 | 991 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.94 | 4 | 0
1977-12-27 | 1900-12-26 | 9:00 | 9 | 187 | 1415 | 95 | 1 | 13 | 500 | 1 | 9 | 28 | 1 | 13 | 9600 | 1 | 13 | 34300 | 1 | 9 | 5000 | 1 | 13 | 530 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.73 | A | 7 | 992 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.94 | 4 | 0
1977-12-27 | 1900-12-26 | 10:00 | 10 | 386 | 1415 | 246 | 1 | 9 | 744 | 1 | 9 | 42 | 1 | 13 | 25900 | 1 | 9 | 65500 | 1 | 9 | 7900 | 1 | 13 | 930 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -17.2 | 1.04 | A | 7 | 0.61 | A | 7 | 992 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.36 | 4 | 0
1977-12-27 | 1900-12-26 | 11:00 | 11 | 535 | 1415 | 372 | 1 | 9 | 842 | 1 | 9 | 52 | 1 | 13 | 39200 | 1 | 9 | 79100 | 1 | 9 | 9100 | 1 | 13 | 1190 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -17.2 | 1.04 | A | 7 | 0.54 | A | 7 | 992 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.66 | 4 | 0
1977-12-27 | 1900-12-26 | 12:00 | 12 | 625 | 1415 | 451 | 1 | 9 | 888 | 1 | 9 | 58 | 1 | 13 | 47500 | 1 | 9 | 85300 | 1 | 9 | 9600 | 1 | 13 | 1350 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -17.2 | 1.04 | A | 7 | 0.47 | A | 7 | 991 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.86 | 4 | 0
1977-12-27 | 1900-12-26 | 13:00 | 13 | 648 | 1415 | 475 | 1 | 9 | 904 | 1 | 9 | 59 | 1 | 13 | 49900 | 1 | 9 | 87300 | 1 | 9 | 9700 | 1 | 13 | 1390 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.42 | A | 7 | 990 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.26 | 4 | 0
1977-12-27 | 1900-12-26 | 14:00 | 14 | 602 | 1415 | 429 | 1 | 9 | 873 | 1 | 9 | 56 | 1 | 13 | 45200 | 1 | 9 | 83500 | 1 | 9 | 9400 | 1 | 13 | 1310 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -16.1 | 3.02 | A | 7 | 0.42 | A | 7 | 989 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.72 | 4 | 0
1977-12-27 | 1900-12-26 | 15:00 | 15 | 492 | 1415 | 333 | 1 | 9 | 818 | 1 | 9 | 49 | 1 | 13 | 35300 | 1 | 9 | 75800 | 1 | 9 | 8800 | 1 | 13 | 1120 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -15 | 5 | A | 7 | 0.42 | A | 7 | 989 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.5 | 4 | 0
1977-12-27 | 1900-12-26 | 16:00 | 16 | 325 | 1415 | 192 | 1 | 13 | 669 | 1 | 9 | 39 | 1 | 13 | 20100 | 1 | 13 | 55800 | 1 | 9 | 7200 | 1 | 13 | 800 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -14.4 | 6.08 | A | 7 | 0.46 | A | 7 | 988 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.68 | 4 | 0
1977-12-27 | 1900-12-26 | 17:00 | 17 | 114 | 1415 | 46 | 1 | 13 | 273 | 1 | 9 | 22 | 1 | 13 | 4500 | 1 | 13 | 13900 | 1 | 9 | 3400 | 1 | 13 | 390 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | -5 | 23 | A | 7 | -14.4 | 6.08 | A | 7 | 0.48 | A | 7 | 988 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.78 | 4 | 0
1977-12-27 | 1900-12-26 | 18:00 | 18 | 0 | 12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -14.4 | 6.08 | A | 7 | 0.54 | A | 7 | 988 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.98 | 4 | 0
1977-12-27 | 1900-12-26 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -7.8 | 17.96 | A | 7 | -14.4 | 6.08 | A | 7 | 0.59 | A | 7 | 988 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.18 | 4 | 0
1977-12-27 | 1900-12-26 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | -7.2 | 19.04 | A | 7 | -13.3 | 8.06 | A | 7 | 0.62 | A | 7 | 987 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.16 | 4 | 0
1977-12-27 | 1900-12-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | -6.7 | 19.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.06 | 4 | 0
1977-12-27 | 1900-12-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 4 | A | 7 | -6.1 | 21.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.57 | A | 7 | 987 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.96 | 4 | 0
1977-12-27 | 1900-12-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 4 | A | 7 | -6.7 | 19.94 | A | 7 | -12.8 | 8.96 | A | 7 | 0.62 | A | 7 | 987 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.06 | 4 | 0
1977-12-27 | 1900-12-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 4 | A | 7 | -5.6 | 21.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.57 | A | 7 | 987 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 4 | 0
1977-12-28 | 1900-12-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 2 | A | 7 | -5.6 | 21.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.6 | A | 7 | 986 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.94 | 5 | 0
1977-12-28 | 1900-12-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -5.6 | 21.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.94 | 5 | 0
1977-12-28 | 1900-12-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 985 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.14 | 5 | 0
1977-12-28 | 1900-12-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 985 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 5 | 0
1977-12-28 | 1900-12-27 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 985 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 5 | 0
1977-12-28 | 1900-12-27 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.46 | 5 | 0
1977-12-28 | 1900-12-27 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 986 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.54 | 5 | 0
1977-12-28 | 1900-12-27 | 8:00 | 8 | 13 | 483 | 13 | 1 | 13 | 68 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.34 | 5 | 0
1977-12-28 | 1900-12-27 | 9:00 | 9 | 186 | 1415 | 94 | 1 | 13 | 509 | 1 | 9 | 26 | 1 | 13 | 9500 | 1 | 13 | 35100 | 1 | 9 | 4900 | 1 | 13 | 510 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -10.6 | 12.92 | A | 7 | 0.68 | A | 7 | 987 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.02 | 5 | 0
1977-12-28 | 1900-12-27 | 10:00 | 10 | 385 | 1415 | 247 | 1 | 9 | 764 | 1 | 9 | 38 | 1 | 13 | 26100 | 1 | 9 | 67300 | 1 | 9 | 7700 | 1 | 13 | 900 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -10 | 14 | A | 7 | 0.6 | A | 7 | 987 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.6 | 5 | 0
1977-12-28 | 1900-12-27 | 11:00 | 11 | 535 | 1415 | 372 | 1 | 9 | 853 | 1 | 9 | 47 | 1 | 13 | 39200 | 1 | 9 | 80200 | 1 | 9 | 8700 | 1 | 13 | 1150 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.54 | A | 7 | 987 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.98 | 5 | 0
1977-12-28 | 1900-12-27 | 12:00 | 12 | 625 | 1415 | 451 | 1 | 9 | 896 | 1 | 9 | 53 | 1 | 13 | 47500 | 1 | 9 | 86200 | 1 | 9 | 9200 | 1 | 13 | 1300 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.44 | A | 7 | 986 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.48 | 5 | 0
1977-12-28 | 1900-12-27 | 13:00 | 13 | 649 | 1415 | 470 | 1 | 9 | 903 | 1 | 9 | 54 | 1 | 13 | 49500 | 1 | 9 | 87200 | 1 | 9 | 9300 | 1 | 13 | 1340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.41 | A | 7 | 984 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.08 | 5 | 0
1977-12-28 | 1900-12-27 | 14:00 | 14 | 604 | 1415 | 432 | 1 | 9 | 890 | 1 | 9 | 52 | 1 | 13 | 45700 | 1 | 9 | 85200 | 1 | 9 | 9200 | 1 | 13 | 1270 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.38 | A | 7 | 984 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.88 | 5 | 0
1977-12-28 | 1900-12-27 | 15:00 | 15 | 494 | 1415 | 336 | 1 | 9 | 835 | 1 | 9 | 45 | 1 | 13 | 35700 | 1 | 9 | 77500 | 1 | 9 | 8500 | 1 | 13 | 1090 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | -9.4 | 15.08 | A | 7 | 0.35 | A | 7 | 983 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.98 | 5 | 0
1977-12-28 | 1900-12-27 | 16:00 | 16 | 328 | 1415 | 197 | 1 | 13 | 709 | 1 | 9 | 34 | 1 | 13 | 21000 | 1 | 13 | 60100 | 1 | 9 | 7100 | 1 | 13 | 800 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -10 | 14 | A | 7 | 0.35 | A | 7 | 983 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10 | 5 | 0
1977-12-28 | 1900-12-27 | 17:00 | 17 | 117 | 1415 | 54 | 1 | 13 | 382 | 1 | 9 | 20 | 1 | 13 | 5200 | 1 | 13 | 22000 | 1 | 9 | 3400 | 1 | 13 | 370 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -10 | 14 | A | 7 | 0.39 | A | 7 | 983 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.3 | 5 | 0
1977-12-28 | 1900-12-27 | 18:00 | 18 | 0 | 35 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.44 | A | 7 | 983 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.62 | 5 | 0
1977-12-28 | 1900-12-27 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -10 | 14 | A | 7 | 0.47 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.8 | 5 | 0
1977-12-28 | 1900-12-27 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -9.4 | 15.08 | A | 7 | 0.51 | A | 7 | 982 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.98 | 5 | 0
1977-12-28 | 1900-12-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.54 | A | 7 | 982 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.18 | 5 | 0
1977-12-28 | 1900-12-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.28 | 5 | 0
1977-12-28 | 1900-12-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.08 | 5 | 0
1977-12-28 | 1900-12-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.56 | A | 7 | 981 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.08 | 5 | 0
1977-12-29 | 1900-12-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.58 | A | 7 | 981 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.18 | 6 | 0
1977-12-29 | 1900-12-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.61 | A | 7 | 980 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.36 | 6 | 0
1977-12-29 | 1900-12-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.56 | 6 | 0
1977-12-29 | 1900-12-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.63 | A | 7 | 980 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.56 | 6 | 0
1977-12-29 | 1900-12-28 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 1 | A | 7 | -2.2 | 28.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.56 | 6 | 0
1977-12-29 | 1900-12-28 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 4 | A | 7 | -2.2 | 28.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.63 | A | 7 | 979 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.56 | 6 | 0
1977-12-29 | 1900-12-28 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 7 | A | 7 | -2.8 | 26.96 | A | 7 | -8.3 | 17.06 | A | 7 | 0.66 | A | 7 | 979 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.76 | 6 | 0
1977-12-29 | 1900-12-28 | 8:00 | 8 | 12 | 483 | 6 | 1 | 13 | 13 | 1 | 13 | 4 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | -2.8 | 26.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.72 | A | 7 | 979 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 6100 | A | 7 | 0.7 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.04 | 6 | 0
1977-12-29 | 1900-12-28 | 9:00 | 9 | 185 | 1415 | 50 | 1 | 13 | 59 | 1 | 13 | 42 | 1 | 13 | 5500 | 1 | 13 | 3800 | 1 | 13 | 5000 | 1 | 13 | 880 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.66 | A | 7 | 979 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 6100 | A | 7 | 0.7 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.32 | 6 | 0
1977-12-29 | 1900-12-28 | 10:00 | 10 | 385 | 1415 | 142 | 1 | 13 | 106 | 1 | 13 | 113 | 1 | 13 | 15400 | 1 | 13 | 9300 | 1 | 13 | 12800 | 1 | 13 | 2500 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.7 | A | 7 | 980 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 6100 | A | 7 | 0.8 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.28 | 6 | 0
1977-12-29 | 1900-12-28 | 11:00 | 11 | 536 | 1415 | 311 | 1 | 13 | 493 | 1 | 13 | 123 | 1 | 13 | 32700 | 1 | 13 | 46700 | 1 | 13 | 14900 | 1 | 13 | 2380 | 1 | 23 | 9 | A | 7 | 5 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 979 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.66 | 6 | 0
1977-12-29 | 1900-12-28 | 12:00 | 12 | 626 | 1415 | 330 | 1 | 13 | 481 | 1 | 13 | 116 | 1 | 13 | 35600 | 1 | 13 | 47300 | 1 | 13 | 14600 | 1 | 13 | 2280 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 5 | 41 | A | 7 | -2.2 | 28.04 | A | 7 | 0.6 | A | 7 | 978 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.14 | 6 | 0
1977-12-29 | 1900-12-28 | 13:00 | 13 | 650 | 1415 | 321 | 1 | 13 | 373 | 1 | 13 | 149 | 1 | 13 | 34000 | 1 | 13 | 36900 | 1 | 13 | 17000 | 1 | 13 | 3030 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | 6.7 | 44.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.56 | A | 7 | 977 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.54 | 6 | 0
1977-12-29 | 1900-12-28 | 14:00 | 14 | 606 | 1415 | 376 | 1 | 13 | 635 | 1 | 13 | 104 | 1 | 13 | 39300 | 1 | 13 | 61000 | 1 | 13 | 13000 | 1 | 13 | 2080 | 1 | 23 | 6 | A | 7 | 3 | A | 7 | 8.3 | 46.94 | A | 7 | -1.1 | 30.02 | A | 7 | 0.52 | A | 7 | 977 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.02 | 6 | 0
1977-12-29 | 1900-12-28 | 15:00 | 15 | 497 | 1415 | 297 | 1 | 9 | 608 | 1 | 9 | 83 | 1 | 13 | 30900 | 1 | 9 | 56100 | 1 | 9 | 11100 | 1 | 13 | 1590 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | 8.9 | 48.02 | A | 7 | -0.6 | 30.92 | A | 7 | 0.52 | A | 7 | 977 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.82 | 6 | 0
1977-12-29 | 1900-12-28 | 16:00 | 16 | 330 | 1415 | 191 | 1 | 13 | 652 | 1 | 9 | 39 | 1 | 13 | 20000 | 1 | 13 | 54700 | 1 | 9 | 7100 | 1 | 13 | 800 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 0.6 | 33.08 | A | 7 | 0.58 | A | 7 | 977 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.28 | 6 | 0
1977-12-29 | 1900-12-28 | 17:00 | 17 | 120 | 1415 | 51 | 1 | 13 | 360 | 1 | 9 | 20 | 1 | 13 | 5100 | 1 | 13 | 20900 | 1 | 9 | 3300 | 1 | 13 | 370 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | 0 | 32 | A | 7 | 0.63 | A | 7 | 978 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.047 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28 | 6 | 0
1977-12-29 | 1900-12-28 | 18:00 | 18 | 0 | 59 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | 0.6 | 33.08 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.78 | 6 | 0
1977-12-29 | 1900-12-28 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.79 | A | 7 | 978 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.72 | 6 | 0
1977-12-29 | 1900-12-28 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.85 | A | 7 | 978 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.52 | 6 | 0
1977-12-29 | 1900-12-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 190 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.52 | 6 | 0
1977-12-29 | 1900-12-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.89 | A | 7 | 979 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.84 | 6 | 0
1977-12-29 | 1900-12-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 979 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 6 | 0
1977-12-29 | 1900-12-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 979 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 400 | A | 7 | 60 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.1 | 6 | 0
1977-12-30 | 1900-12-29 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 979 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 0 | A | 7 | 90 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 7 | 0
1977-12-30 | 1900-12-29 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 90 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 7 | 0
1977-12-30 | 1900-12-29 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 0 | A | 7 | 90 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.14 | 7 | 0
1977-12-30 | 1900-12-29 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -2.8 | 26.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 400 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 7 | 0
1977-12-30 | 1900-12-29 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -5 | 23 | A | 7 | -6.1 | 21.02 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 4000 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.32 | 7 | 0
1977-12-30 | 1900-12-29 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 0 | A | 7 | 0 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.62 | 7 | 0
1977-12-30 | 1900-12-29 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.88 | A | 7 | 980 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.14 | 7 | 0
1977-12-30 | 1900-12-29 | 8:00 | 8 | 12 | 460 | 13 | 1 | 13 | 60 | 1 | 13 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -6.7 | 19.94 | A | 7 | -8.9 | 15.98 | A | 7 | 0.84 | A | 7 | 981 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 3200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 7 | 0
1977-12-30 | 1900-12-29 | 9:00 | 9 | 185 | 1415 | 50 | 1 | 13 | 3 | 1 | 9 | 49 | 1 | 13 | 5500 | 1 | 13 | 0 | 1 | 9 | 5500 | 1 | 13 | 1580 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.92 | A | 7 | 982 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 1220 | A | 7 | 0.7 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.34 | 7 | 0
1977-12-30 | 1900-12-29 | 10:00 | 10 | 385 | 1415 | 146 | 1 | 13 | 168 | 1 | 13 | 100 | 1 | 13 | 15500 | 1 | 13 | 14600 | 1 | 13 | 11500 | 1 | 13 | 1960 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -3.9 | 24.98 | A | 7 | -5 | 23 | A | 7 | 0.92 | A | 7 | 982 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.3 | 7 | 0
1977-12-30 | 1900-12-29 | 11:00 | 11 | 536 | 1415 | 361 | 1 | 9 | 849 | 1 | 9 | 37 | 1 | 13 | 38300 | 1 | 9 | 80000 | 1 | 9 | 7800 | 1 | 13 | 1020 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 982 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.96 | 7 | 0
1977-12-30 | 1900-12-29 | 12:00 | 12 | 627 | 1415 | 452 | 1 | 9 | 922 | 1 | 9 | 42 | 1 | 13 | 48000 | 1 | 9 | 88800 | 1 | 9 | 8500 | 1 | 13 | 1160 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 982 | A | 7 | 50 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 7 | 0
1977-12-30 | 1900-12-29 | 13:00 | 13 | 652 | 1415 | 473 | 1 | 9 | 930 | 1 | 9 | 43 | 1 | 13 | 50200 | 1 | 9 | 90000 | 1 | 9 | 8500 | 1 | 13 | 1190 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.6 | A | 7 | 981 | A | 7 | 50 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 7 | 0
1977-12-30 | 1900-12-29 | 14:00 | 14 | 608 | 1415 | 433 | 1 | 9 | 911 | 1 | 9 | 41 | 1 | 13 | 46100 | 1 | 9 | 87400 | 1 | 9 | 8300 | 1 | 13 | 1130 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.55 | A | 7 | 981 | A | 7 | 70 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.76 | 7 | 0
1977-12-30 | 1900-12-29 | 15:00 | 15 | 499 | 1415 | 342 | 1 | 9 | 868 | 1 | 9 | 35 | 1 | 13 | 36500 | 1 | 9 | 80800 | 1 | 9 | 7800 | 1 | 13 | 970 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.1 | 42.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.51 | A | 7 | 981 | A | 7 | 90 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.56 | 7 | 0
1977-12-30 | 1900-12-29 | 16:00 | 16 | 333 | 1415 | 204 | 1 | 13 | 756 | 1 | 9 | 27 | 1 | 13 | 21900 | 1 | 13 | 64500 | 1 | 9 | 6700 | 1 | 13 | 740 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 4.4 | 39.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.65 | A | 7 | 981 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.44 | 7 | 0
1977-12-30 | 1900-12-29 | 17:00 | 17 | 123 | 1415 | 58 | 1 | 13 | 481 | 1 | 9 | 15 | 1 | 13 | 6000 | 1 | 13 | 30800 | 1 | 9 | 3400 | 1 | 13 | 360 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 981 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.023 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.14 | 7 | 0
1977-12-30 | 1900-12-29 | 18:00 | 18 | 0 | 83 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 4 | A | 7 | 4 | A | 7 | 0 | 32 | A | 7 | -3.9 | 24.98 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 7 | 0
1977-12-30 | 1900-12-29 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.76 | A | 7 | 981 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 240 | A | 7 | 0.9 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.74 | 7 | 0
1977-12-30 | 1900-12-29 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 120 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.84 | 7 | 0
1977-12-30 | 1900-12-29 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -0.6 | 30.92 | A | 7 | 0.85 | A | 7 | 981 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 7 | 0
1977-12-30 | 1900-12-29 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 0 | 32 | A | 7 | 0.89 | A | 7 | 981 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.8 | 7 | 0
1977-12-30 | 1900-12-29 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 0 | 32 | A | 7 | 0.89 | A | 7 | 981 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.8 | 7 | 0
1977-12-30 | 1900-12-29 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 0 | A | 7 | 0 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.1 | 7 | 0
1977-12-31 | 1900-12-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 0 | A | 7 | 30 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.1 | 1 | 0
1977-12-31 | 1900-12-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 30 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.1 | 1 | 0
1977-12-31 | 1900-12-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 0 | A | 7 | 60 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.18 | 1 | 0
1977-12-31 | 1900-12-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 800 | A | 7 | 120 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.56 | 1 | 0
1977-12-31 | 1900-12-30 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 400 | A | 7 | 90 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.56 | 1 | 0
1977-12-31 | 1900-12-30 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 150 | A | 7 | 2.1 | A | 7 | 400 | A | 7 | 60 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.56 | 1 | 0
1977-12-31 | 1900-12-30 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 400 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.08 | 1 | 0
1977-12-31 | 1900-12-30 | 8:00 | 8 | 12 | 460 | 0 | 1 | 13 | 4 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 110 | A | 7 | 3.1 | A | 7 | 200 | A | 7 | 90 | A | 7 | 1.1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.08 | 1 | 0
1977-12-31 | 1900-12-30 | 9:00 | 9 | 184 | 1415 | 24 | 1 | 13 | 1 | 1 | 9 | 24 | 1 | 13 | 2800 | 1 | 13 | 0 | 1 | 9 | 2800 | 1 | 13 | 920 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.1 | 33.98 | A | 7 | 0.92 | A | 7 | 981 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 200 | A | 7 | 30 | A | 7 | 1.1 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.08 | 1 | 0
1977-12-31 | 1900-12-30 | 10:00 | 10 | 385 | 1415 | 49 | 1 | 9 | 2 | 1 | 9 | 49 | 1 | 13 | 5900 | 1 | 9 | 100 | 1 | 9 | 5800 | 1 | 13 | 2040 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 400 | A | 7 | 90 | A | 7 | 1.2 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.56 | 1 | 0
1977-12-31 | 1900-12-30 | 11:00 | 11 | 537 | 1415 | 86 | 1 | 9 | 6 | 1 | 9 | 84 | 1 | 13 | 10200 | 1 | 9 | 400 | 1 | 9 | 10000 | 1 | 13 | 3600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 980 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 1300 | A | 7 | 120 | A | 7 | 1.2 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.16 | 1 | 0
1977-12-31 | 1900-12-30 | 12:00 | 12 | 628 | 1415 | 106 | 1 | 9 | 4 | 1 | 9 | 104 | 1 | 13 | 12500 | 1 | 9 | 300 | 1 | 9 | 12400 | 1 | 13 | 4570 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 1.7 | 35.06 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 800 | A | 7 | 120 | A | 7 | 1.2 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.76 | 1 | 0
1977-12-31 | 1900-12-30 | 13:00 | 13 | 653 | 1415 | 112 | 1 | 9 | 4 | 1 | 9 | 111 | 1 | 13 | 13300 | 1 | 9 | 300 | 1 | 9 | 13200 | 1 | 13 | 4900 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 120 | A | 7 | 1.2 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.06 | 1 | 0
1977-12-31 | 1900-12-30 | 14:00 | 14 | 610 | 1415 | 128 | 1 | 9 | 4 | 1 | 9 | 126 | 1 | 13 | 14800 | 1 | 9 | 300 | 1 | 9 | 14700 | 1 | 13 | 5260 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 3200 | A | 7 | 150 | A | 7 | 1.2 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.06 | 1 | 0
1977-12-31 | 1900-12-30 | 15:00 | 15 | 502 | 1415 | 100 | 1 | 9 | 1 | 1 | 9 | 100 | 1 | 13 | 11600 | 1 | 9 | 100 | 1 | 9 | 11500 | 1 | 13 | 4030 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 2.8 | 37.04 | A | 7 | 0.96 | A | 7 | 978 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 3200 | A | 7 | 150 | A | 7 | 1.2 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 1 | 0
1977-12-31 | 1900-12-30 | 16:00 | 16 | 336 | 1415 | 56 | 1 | 13 | 2 | 1 | 9 | 55 | 1 | 13 | 6400 | 1 | 13 | 100 | 1 | 9 | 6400 | 1 | 13 | 2150 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 180 | A | 7 | 1.2 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.06 | 1 | 0
1977-12-31 | 1900-12-30 | 17:00 | 17 | 126 | 1415 | 19 | 1 | 13 | 0 | 1 | 9 | 19 | 1 | 13 | 2200 | 1 | 13 | 0 | 1 | 9 | 2200 | 1 | 13 | 690 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 800 | A | 7 | 90 | A | 7 | 1.2 | E | 8 | 0.05 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.06 | 1 | 0
1977-12-31 | 1900-12-30 | 18:00 | 18 | 0 | 83 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.93 | A | 7 | 978 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1.2 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.06 | 1 | 0
1977-12-31 | 1900-12-30 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.89 | A | 7 | 980 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 150 | A | 7 | 1 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.92 | 1 | 0
1977-12-31 | 1900-12-30 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 270 | A | 7 | 0.8 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.38 | 1 | 0
1977-12-31 | 1900-12-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 983 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 12900 | A | 7 | 270 | A | 7 | 0.7 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.04 | 1 | 0
1977-12-31 | 1900-12-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.74 | A | 7 | 984 | A | 7 | 330 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.4 | 1 | 0
1977-12-31 | 1900-12-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 985 | A | 7 | 310 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 460 | A | 7 | 0.6 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 1 | 0
1977-12-31 | 1900-12-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -8.9 | 15.98 | A | 7 | -13.3 | 8.06 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 320 | A | 7 | 10.3 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | -9900 | ? | 0 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.66 | 1 | 0

## Indianapolis Intl AP (hidden)
724380 |  | INDIANAPOLIS INTL AP |  | IN | -5 | 39.717 | -86.267 | 241
Date (MM/DD/YYYY) | 2014 Date | Time (HH:MM) | Hour | ETR (W/m^2) | ETRN (W/m^2) | GHI (W/m^2) | GHI source | GHI uncert (%) | DNI (W/m^2) | DNI source | DNI uncert (%) | DHI (W/m^2) | DHI source | DHI uncert (%) | GH illum (lx) | GH illum source | Global illum uncert (%) | DN illum (lx) | DN illum source | DN illum uncert (%) | DH illum (lx) | DH illum source | DH illum uncert (%) | Zenith lum (cd/m^2) | Zenith lum source | Zenith lum uncert (%) | TotCld (tenths) | TotCld source | TotCld uncert (code) | OpqCld (tenths) | OpqCld source | OpqCld uncert (code) | Dry-bulb (C) | Dry-bulb (F) | Dry-bulb source | Dry-bulb uncert (code) | Dew-point (C) | Dew-point (F) | Dew-point source | Dew-point uncert (code) | RHum (%) | RHum source | RHum uncert (code) | Pressure (mbar) | Pressure source | Pressure uncert (code) | Wdir (degrees) | Wdir source | Wdir uncert (code) | Wspd (m/s) | Wspd source | Wspd uncert (code) | Hvis (m) | Hvis source | Hvis uncert (code) | CeilHgt (m) | CeilHgt source | CeilHgt uncert (code) | Pwat (cm) | Pwat source | Pwat uncert (code) | AOD (unitless) | AOD source | AOD uncert (code) | Alb (unitless) | Alb source | Alb uncert (code) | Lprecip depth (mm) | Lprecip quantity (hr) | Lprecip source | Lprecip uncert (code) | Wetbulb (F) | Day of Week | Primary Schedule
1976-01-01 | 1899-12-31 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 987 | A | 7 | 30 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 0.9 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.84 | 5 | 0 | Max | 96.98
1976-01-01 | 1899-12-31 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | -2.8 | 26.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.92 | A | 7 | 989 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 5 | 0 | Min | -9.94
1976-01-01 | 1899-12-31 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -3.3 | 26.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.66 | 5 | 0
1976-01-01 | 1899-12-31 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.96 | A | 7 | 990 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.58 | 5 | 0
1976-01-01 | 1899-12-31 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -3.9 | 24.98 | A | 7 | 1 | A | 7 | 990 | A | 7 | 10 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.88 | 5 | 0
1976-01-01 | 1899-12-31 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.58 | 5 | 0
1976-01-01 | 1899-12-31 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -3.3 | 26.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.96 | A | 7 | 992 | A | 7 | 40 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 0.9 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.66 | 5 | 0
1976-01-01 | 1899-12-31 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -2.8 | 26.96 | A | 7 | -2.8 | 26.96 | A | 7 | 1 | A | 7 | 992 | A | 7 | 80 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 370 | A | 7 | 0.9 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.86 | 5 | 0
1976-01-01 | 1899-12-31 | 9:00 | 9 | 84 | 1238 | 36 | 1 | 13 | 24 | 1 | 13 | 34 | 1 | 13 | 3899 | 1 | 13 | 1422 | 1 | 13 | 3796 | 1 | 13 | 747 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | -2.8 | 26.96 | A | 7 | -2.8 | 26.96 | A | 7 | 1 | A | 7 | 992 | A | 7 | 80 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 340 | A | 7 | 0.9 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.86 | 5 | 0
1976-01-01 | 1899-12-31 | 10:00 | 10 | 295 | 1415 | 72 | 1 | 13 | 14 | 1 | 9 | 69 | 1 | 13 | 8078 | 1 | 13 | 509 | 1 | 9 | 7971 | 1 | 13 | 2430 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -2.2 | 28.04 | A | 7 | -2.2 | 28.04 | A | 7 | 1 | A | 7 | 993 | A | 7 | 100 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 0.9 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.94 | 5 | 0
1976-01-01 | 1899-12-31 | 11:00 | 11 | 469 | 1415 | 189 | 1 | 9 | 126 | 1 | 9 | 147 | 1 | 13 | 20434 | 1 | 9 | 11810 | 1 | 9 | 16497 | 1 | 13 | 3334 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -2.2 | 28.04 | A | 7 | -2.2 | 28.04 | A | 7 | 1 | A | 7 | 993 | A | 7 | 90 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 0.9 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.94 | 5 | 0
1976-01-01 | 1899-12-31 | 12:00 | 12 | 588 | 1415 | 211 | 1 | 9 | 66 | 1 | 9 | 184 | 1 | 13 | 23193 | 1 | 9 | 6427 | 1 | 9 | 20511 | 1 | 13 | 5119 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -1.7 | 28.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.96 | A | 7 | 993 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 370 | A | 7 | 0.9 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.54 | 5 | 0
1976-01-01 | 1899-12-31 | 13:00 | 13 | 642 | 1415 | 156 | 1 | 9 | 36 | 1 | 9 | 139 | 1 | 13 | 17118 | 1 | 9 | 3505 | 1 | 9 | 15520 | 1 | 13 | 4275 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.96 | A | 7 | 993 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 340 | A | 7 | 1 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.62 | 5 | 0
1976-01-01 | 1899-12-31 | 14:00 | 14 | 629 | 1415 | 191 | 1 | 9 | 2 | 1 | 9 | 190 | 1 | 13 | 21475 | 1 | 9 | 164 | 1 | 9 | 21402 | 1 | 13 | 7143 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.96 | A | 7 | 992 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 370 | A | 7 | 1 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.62 | 5 | 0
1976-01-01 | 1899-12-31 | 15:00 | 15 | 550 | 1415 | 209 | 1 | 9 | 11 | 1 | 9 | 205 | 1 | 13 | 23007 | 1 | 9 | 941 | 1 | 9 | 22640 | 1 | 13 | 6756 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.96 | A | 7 | 992 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 9700 | A | 7 | 370 | A | 7 | 1 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.42 | 5 | 0
1976-01-01 | 1899-12-31 | 16:00 | 16 | 409 | 1415 | 116 | 1 | 9 | 8 | 1 | 9 | 113 | 1 | 13 | 12867 | 1 | 9 | 481 | 1 | 9 | 12727 | 1 | 13 | 3968 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 992 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 370 | A | 7 | 1 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 5 | 0
1976-01-01 | 1899-12-31 | 17:00 | 17 | 217 | 1415 | 57 | 1 | 13 | 3 | 1 | 9 | 57 | 1 | 13 | 6363 | 1 | 13 | 62 | 1 | 9 | 6353 | 1 | 13 | 1862 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.96 | A | 7 | 993 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 340 | A | 7 | 1 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.62 | 5 | 0
1976-01-01 | 1899-12-31 | 18:00 | 18 | 26 | 696 | 11 | 1 | 13 | 0 | 1 | 9 | 11 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 993 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 340 | A | 7 | 1 | E | 8 | 0.039 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 5 | 0
1976-01-01 | 1899-12-31 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 993 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 340 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 5 | 0
1976-01-01 | 1899-12-31 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 992 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 5 | 0
1976-01-01 | 1899-12-31 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 991 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 5 | 0
1976-01-01 | 1899-12-31 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 991 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 270 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 5 | 0
1976-01-01 | 1899-12-31 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 990 | A | 7 | 130 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 270 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 5 | 0
1976-01-01 | 1899-12-31 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 990 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 270 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 5 | 0
1976-01-02 | 1900-01-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 989 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 240 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 6 | 0
1976-01-02 | 1900-01-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 990 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 240 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 6 | 0
1976-01-02 | 1900-01-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 989 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 6 | 0
1976-01-02 | 1900-01-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 989 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 6 | 0
1976-01-02 | 1900-01-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 988 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 6 | 0
1976-01-02 | 1900-01-01 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 988 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 6 | 0
1976-01-02 | 1900-01-01 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 987 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 6 | 0
1976-01-02 | 1900-01-01 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0.6 | 33.08 | A | 7 | 1 | A | 7 | 987 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.98 | 6 | 0
1976-01-02 | 1900-01-01 | 9:00 | 9 | 83 | 1238 | 25 | 1 | 13 | 0 | 1 | 9 | 25 | 1 | 13 | 28 | 1 | 13 | 0 | 1 | 9 | 28 | 1 | 13 | 81 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0.6 | 33.08 | A | 7 | 1 | A | 7 | 987 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 3200 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.98 | 6 | 0
1976-01-02 | 1900-01-01 | 10:00 | 10 | 295 | 1415 | 55 | 1 | 13 | 3 | 1 | 9 | 54 | 1 | 13 | 63 | 1 | 13 | 1 | 1 | 9 | 62 | 1 | 13 | 203 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 1.1 | 33.98 | A | 7 | 1 | A | 7 | 988 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 2400 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.88 | 6 | 0
1976-01-02 | 1900-01-01 | 11:00 | 11 | 470 | 1415 | 92 | 1 | 9 | 0 | 1 | 9 | 92 | 1 | 13 | 106 | 1 | 9 | 0 | 1 | 9 | 106 | 1 | 13 | 367 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 1.7 | 35.06 | A | 7 | 1 | A | 7 | 988 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 400 | A | 7 | 120 | A | 7 | 1.2 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.96 | 6 | 0
1976-01-02 | 1900-01-01 | 12:00 | 12 | 589 | 1415 | 131 | 1 | 9 | 1 | 1 | 9 | 131 | 1 | 13 | 151 | 1 | 9 | 1 | 1 | 9 | 151 | 1 | 13 | 533 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.8 | 37.04 | A | 7 | 1 | A | 7 | 987 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 1.3 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.04 | 6 | 0
1976-01-02 | 1900-01-01 | 13:00 | 13 | 644 | 1415 | 142 | 1 | 9 | 0 | 1 | 9 | 142 | 1 | 13 | 164 | 1 | 9 | 0 | 1 | 9 | 164 | 1 | 13 | 592 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 985 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 400 | A | 7 | 90 | A | 7 | 1.3 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 6 | 0
1976-01-02 | 1900-01-01 | 14:00 | 14 | 632 | 1415 | 130 | 1 | 9 | 0 | 1 | 9 | 130 | 1 | 13 | 151 | 1 | 9 | 0 | 1 | 9 | 151 | 1 | 13 | 548 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 3.9 | 39.02 | A | 7 | 1 | A | 7 | 985 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 400 | A | 7 | 60 | A | 7 | 1.3 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.92 | 6 | 0
1976-01-02 | 1900-01-01 | 15:00 | 15 | 552 | 1415 | 117 | 1 | 9 | 0 | 1 | 9 | 116 | 1 | 13 | 134 | 1 | 9 | 0 | 1 | 9 | 134 | 1 | 13 | 471 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 4.4 | 39.92 | A | 7 | 1 | A | 7 | 985 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 3200 | A | 7 | 210 | A | 7 | 1.4 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.92 | 6 | 0
1976-01-02 | 1900-01-01 | 16:00 | 16 | 412 | 1415 | 136 | 1 | 9 | 1 | 1 | 9 | 136 | 1 | 13 | 150 | 1 | 9 | 1 | 1 | 9 | 150 | 1 | 13 | 444 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 985 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 490 | A | 7 | 1.4 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.9 | 6 | 0
1976-01-02 | 1900-01-01 | 17:00 | 17 | 220 | 1415 | 40 | 1 | 13 | 1 | 1 | 9 | 40 | 1 | 13 | 46 | 1 | 13 | 0 | 1 | 9 | 46 | 1 | 13 | 146 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.85 | A | 7 | 986 | A | 7 | 250 | A | 7 | 7.7 | A | 7 | 4800 | A | 7 | 940 | A | 7 | 1.2 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.12 | 6 | 0
1976-01-02 | 1900-01-01 | 18:00 | 18 | 27 | 719 | 8 | 1 | 13 | 0 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 1.1 | 33.98 | A | 7 | 1 | A | 7 | 987 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 3200 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.88 | 6 | 0
1976-01-02 | 1900-01-01 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0.6 | 33.08 | A | 7 | 1 | A | 7 | 986 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 3200 | A | 7 | 90 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.98 | 6 | 0
1976-01-02 | 1900-01-01 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 986 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 6 | 0
1976-01-02 | 1900-01-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 1190 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.8 | 6 | 0
1976-01-02 | 1900-01-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 987 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 1520 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 6 | 0
1976-01-02 | 1900-01-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 987 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 550 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 6 | 0
1976-01-02 | 1900-01-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.96 | A | 7 | 986 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.42 | 6 | 0
1976-01-03 | 1900-01-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 760 | A | 7 | 0.9 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 7 | 0
1976-01-03 | 1900-01-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 760 | A | 7 | 0.9 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 7 | 0
1976-01-03 | 1900-01-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.92 | A | 7 | 986 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.9 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 7 | 0
1976-01-03 | 1900-01-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.85 | A | 7 | 986 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 7 | 0
1976-01-03 | 1900-01-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.88 | A | 7 | 986 | A | 7 | 280 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 640 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.86 | 7 | 0
1976-01-03 | 1900-01-02 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5 | 23 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 280 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.96 | 7 | 0
1976-01-03 | 1900-01-02 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5 | 23 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.96 | 7 | 0
1976-01-03 | 1900-01-02 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 290 | A | 7 | 9.3 | A | 7 | 19300 | A | 7 | 640 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 7 | 0
1976-01-03 | 1900-01-02 | 9:00 | 9 | 83 | 1238 | 25 | 1 | 13 | 0 | 1 | 9 | 25 | 1 | 13 | 28 | 1 | 13 | 0 | 1 | 9 | 28 | 1 | 13 | 81 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 988 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 7 | 0
1976-01-03 | 1900-01-02 | 10:00 | 10 | 295 | 1415 | 83 | 1 | 13 | 0 | 1 | 9 | 83 | 1 | 13 | 92 | 1 | 13 | 0 | 1 | 9 | 92 | 1 | 13 | 274 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.85 | A | 7 | 989 | A | 7 | 260 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 580 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 7 | 0
1976-01-03 | 1900-01-02 | 11:00 | 11 | 471 | 1415 | 179 | 1 | 13 | 101 | 1 | 13 | 145 | 1 | 13 | 193 | 1 | 13 | 95 | 1 | 13 | 162 | 1 | 13 | 329 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 240 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 7 | 0
1976-01-03 | 1900-01-02 | 12:00 | 12 | 590 | 1415 | 327 | 1 | 13 | 460 | 1 | 13 | 134 | 1 | 13 | 345 | 1 | 13 | 446 | 1 | 13 | 158 | 1 | 13 | 264 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 260 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.4 | 7 | 0
1976-01-03 | 1900-01-02 | 13:00 | 13 | 646 | 1415 | 337 | 1 | 13 | 479 | 1 | 13 | 117 | 1 | 13 | 365 | 1 | 13 | 474 | 1 | 13 | 147 | 1 | 13 | 232 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | -4.4 | 24.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.75 | A | 7 | 990 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 7 | 0
1976-01-03 | 1900-01-02 | 14:00 | 14 | 634 | 1415 | 388 | 1 | 13 | 529 | 1 | 13 | 151 | 1 | 13 | 410 | 1 | 13 | 520 | 1 | 13 | 176 | 1 | 13 | 306 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 989 | A | 7 | 260 | A | 7 | 8.8 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.58 | 7 | 0
1976-01-03 | 1900-01-02 | 15:00 | 15 | 555 | 1415 | 224 | 1 | 13 | 77 | 1 | 13 | 193 | 1 | 13 | 245 | 1 | 13 | 75 | 1 | 13 | 215 | 1 | 13 | 513 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | -4.4 | 24.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.75 | A | 7 | 990 | A | 7 | 270 | A | 7 | 9.3 | A | 7 | 48300 | A | 7 | 910 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 7 | 0
1976-01-03 | 1900-01-02 | 16:00 | 16 | 415 | 1415 | 143 | 1 | 9 | 71 | 1 | 9 | 122 | 1 | 13 | 156 | 1 | 9 | 64 | 1 | 9 | 137 | 1 | 13 | 315 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.78 | A | 7 | 990 | A | 7 | 280 | A | 7 | 9.8 | A | 7 | 32200 | A | 7 | 820 | A | 7 | 0.6 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 7 | 0
1976-01-03 | 1900-01-02 | 17:00 | 17 | 223 | 1415 | 51 | 1 | 13 | 22 | 1 | 9 | 47 | 1 | 13 | 55 | 1 | 13 | 17 | 1 | 9 | 53 | 1 | 13 | 119 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -6.7 | 19.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.81 | A | 7 | 991 | A | 7 | 270 | A | 7 | 8.8 | A | 7 | 3200 | A | 7 | 850 | A | 7 | 0.6 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.54 | 7 | 0
1976-01-03 | 1900-01-02 | 18:00 | 18 | 29 | 719 | 16 | 1 | 13 | 19 | 1 | 13 | 14 | 1 | 13 | 16 | 1 | 13 | 7 | 1 | 13 | 16 | 1 | 13 | 29 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -7.2 | 19.04 | A | 7 | -10 | 14 | A | 7 | 0.81 | A | 7 | 992 | A | 7 | 280 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 7 | 0
1976-01-03 | 1900-01-02 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -7.2 | 19.04 | A | 7 | -10 | 14 | A | 7 | 0.81 | A | 7 | 992 | A | 7 | 280 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 1190 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 7 | 0
1976-01-03 | 1900-01-02 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 993 | A | 7 | 280 | A | 7 | 9.8 | A | 7 | 16100 | A | 7 | 1040 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 7 | 0
1976-01-03 | 1900-01-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 993 | A | 7 | 280 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1190 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 7 | 0
1976-01-03 | 1900-01-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -8.9 | 15.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.74 | A | 7 | 994 | A | 7 | 280 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.28 | 7 | 0
1976-01-03 | 1900-01-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.77 | A | 7 | 995 | A | 7 | 270 | A | 7 | 9.3 | A | 7 | 3200 | A | 7 | 910 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.48 | 7 | 0
1976-01-03 | 1900-01-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.8 | A | 7 | 995 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 1040 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 7 | 0
1976-01-04 | 1900-01-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.77 | A | 7 | 995 | A | 7 | 280 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 1130 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.58 | 1 | 0
1976-01-04 | 1900-01-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10 | 14 | A | 7 | -12.2 | 10.04 | A | 7 | 0.84 | A | 7 | 995 | A | 7 | 290 | A | 7 | 8.8 | A | 7 | 9700 | A | 7 | 1130 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13 | 1 | 0
1976-01-04 | 1900-01-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -13.9 | 6.98 | A | 7 | 0.77 | A | 7 | 996 | A | 7 | 280 | A | 7 | 7.7 | A | 7 | 11300 | A | 7 | 980 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.52 | 1 | 0
1976-01-04 | 1900-01-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.84 | A | 7 | 997 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 3200 | A | 7 | 940 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.92 | 1 | 0
1976-01-04 | 1900-01-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -15 | 5 | A | 7 | 0.77 | A | 7 | 997 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 980 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.64 | 1 | 0
1976-01-04 | 1900-01-03 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -12.8 | 8.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.73 | A | 7 | 998 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.56 | 1 | 0
1976-01-04 | 1900-01-03 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -13.3 | 8.06 | A | 7 | -15.6 | 3.92 | A | 7 | 0.84 | A | 7 | 999 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.26 | 1 | 0
1976-01-04 | 1900-01-03 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -14.4 | 6.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.87 | A | 7 | 999 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.48 | 1 | 0
1976-01-04 | 1900-01-03 | 9:00 | 9 | 83 | 1214 | 34 | 1 | 13 | 84 | 1 | 13 | 27 | 1 | 13 | 35 | 1 | 13 | 32 | 1 | 13 | 33 | 1 | 13 | 49 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | -13.9 | 6.98 | A | 7 | -16.1 | 3.02 | A | 7 | 0.83 | A | 7 | 1000 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 850 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.18 | 1 | 0
1976-01-04 | 1900-01-03 | 10:00 | 10 | 296 | 1415 | 128 | 1 | 13 | 291 | 1 | 13 | 67 | 1 | 13 | 134 | 1 | 13 | 223 | 1 | 13 | 87 | 1 | 13 | 122 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -13.9 | 6.98 | A | 7 | -16.7 | 1.94 | A | 7 | 0.8 | A | 7 | 1001 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.98 | 1 | 0
1976-01-04 | 1900-01-03 | 11:00 | 11 | 471 | 1415 | 231 | 1 | 13 | 420 | 1 | 13 | 90 | 1 | 13 | 247 | 1 | 13 | 385 | 1 | 13 | 118 | 1 | 13 | 167 | 1 | 23 | 6 | A | 7 | 5 | A | 7 | -13.3 | 8.06 | A | 7 | -20 | -4 | A | 7 | 0.58 | A | 7 | 1002 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 790 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.96 | 1 | 0
1976-01-04 | 1900-01-03 | 12:00 | 12 | 592 | 1415 | 192 | 1 | 13 | 37 | 1 | 13 | 177 | 1 | 13 | 211 | 1 | 13 | 36 | 1 | 13 | 196 | 1 | 13 | 499 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | -12.8 | 8.96 | A | 7 | -18.9 | -2.02 | A | 7 | 0.61 | A | 7 | 1003 | A | 7 | 290 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.96 | 1 | 0
1976-01-04 | 1900-01-03 | 13:00 | 13 | 648 | 1415 | 381 | 1 | 13 | 453 | 1 | 13 | 173 | 1 | 13 | 397 | 1 | 13 | 446 | 1 | 13 | 192 | 1 | 13 | 357 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -12.2 | 10.04 | A | 7 | -18.3 | -0.94 | A | 7 | 0.61 | A | 7 | 1002 | A | 7 | 280 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.94 | 1 | 0
1976-01-04 | 1900-01-03 | 14:00 | 14 | 636 | 1415 | 315 | 1 | 13 | 390 | 1 | 13 | 139 | 1 | 13 | 335 | 1 | 13 | 384 | 1 | 13 | 161 | 1 | 13 | 279 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -11.1 | 12.02 | A | 7 | -17.2 | 1.04 | A | 7 | 0.61 | A | 7 | 1002 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.82 | 1 | 0
1976-01-04 | 1900-01-03 | 15:00 | 15 | 558 | 1415 | 318 | 1 | 13 | 508 | 1 | 13 | 118 | 1 | 13 | 339 | 1 | 13 | 487 | 1 | 13 | 146 | 1 | 13 | 228 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -11.7 | 10.94 | A | 7 | -17.8 | -0.04 | A | 7 | 0.61 | A | 7 | 1002 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 1 | 0
1976-01-04 | 1900-01-03 | 16:00 | 16 | 418 | 1415 | 262 | 1 | 9 | 670 | 1 | 9 | 65 | 1 | 13 | 275 | 1 | 9 | 592 | 1 | 9 | 99 | 1 | 13 | 124 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -10.6 | 12.92 | A | 7 | -17.2 | 1.04 | A | 7 | 0.58 | A | 7 | 1002 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.42 | 1 | 0
1976-01-04 | 1900-01-03 | 17:00 | 17 | 227 | 1415 | 102 | 1 | 13 | 298 | 1 | 13 | 54 | 1 | 13 | 106 | 1 | 13 | 201 | 1 | 13 | 73 | 1 | 13 | 98 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -11.1 | 12.02 | A | 7 | -17.2 | 1.04 | A | 7 | 0.61 | A | 7 | 1003 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.82 | 1 | 0
1976-01-04 | 1900-01-03 | 18:00 | 18 | 31 | 743 | 22 | 1 | 13 | 124 | 1 | 9 | 10 | 1 | 13 | 16 | 1 | 13 | 50 | 1 | 9 | 14 | 1 | 13 | 19 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -17.2 | 1.04 | A | 7 | 0.67 | A | 7 | 1003 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.044 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 1 | 0
1976-01-04 | 1900-01-03 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -12.8 | 8.96 | A | 7 | -16.1 | 3.02 | A | 7 | 0.76 | A | 7 | 1004 | A | 7 | 270 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.76 | 1 | 0
1976-01-04 | 1900-01-03 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -16.1 | 3.02 | A | 7 | 0.76 | A | 7 | 1004 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.76 | 1 | 0
1976-01-04 | 1900-01-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -16.1 | 3.02 | A | 7 | 0.8 | A | 7 | 1004 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.06 | 1 | 0
1976-01-04 | 1900-01-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -16.1 | 3.02 | A | 7 | 0.8 | A | 7 | 1003 | A | 7 | 220 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.06 | 1 | 0
1976-01-04 | 1900-01-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -16.1 | 3.02 | A | 7 | 0.83 | A | 7 | 1003 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.18 | 1 | 0
1976-01-04 | 1900-01-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.87 | A | 7 | 1003 | A | 7 | 230 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.48 | 1 | 0
1976-01-05 | 1900-01-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.87 | A | 7 | 1003 | A | 7 | 230 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.48 | 2 | 0
1976-01-05 | 1900-01-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.87 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.48 | 2 | 0
1976-01-05 | 1900-01-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -16.7 | 1.94 | A | 7 | 0.87 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 2 | 0
1976-01-05 | 1900-01-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -16.7 | 1.94 | A | 7 | 0.87 | A | 7 | 1003 | A | 7 | 160 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 2 | 0
1976-01-05 | 1900-01-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -17.2 | 1.04 | A | 7 | 0.83 | A | 7 | 1003 | A | 7 | 180 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.2 | 2 | 0
1976-01-05 | 1900-01-04 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -16.7 | 1.94 | A | 7 | 0.87 | A | 7 | 1004 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.4 | 2 | 0
1976-01-05 | 1900-01-04 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -17.2 | 1.04 | A | 7 | 0.87 | A | 7 | 1004 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.32 | 2 | 0
1976-01-05 | 1900-01-04 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -14.4 | 6.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.87 | A | 7 | 1004 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.48 | 2 | 0
1976-01-05 | 1900-01-04 | 9:00 | 9 | 83 | 1214 | 41 | 1 | 13 | 28 | 1 | 13 | 39 | 1 | 13 | 45 | 1 | 13 | 17 | 1 | 13 | 43 | 1 | 13 | 82 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | -12.8 | 8.96 | A | 7 | -15 | 5 | A | 7 | 0.84 | A | 7 | 1004 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 0.5 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.16 | 2 | 0
1976-01-05 | 1900-01-04 | 10:00 | 10 | 296 | 1415 | 87 | 1 | 13 | 10 | 1 | 9 | 85 | 1 | 13 | 96 | 1 | 13 | 4 | 1 | 9 | 95 | 1 | 13 | 279 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -11.7 | 10.94 | A | 7 | -13.9 | 6.98 | A | 7 | 0.84 | A | 7 | 1005 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.5 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.04 | 2 | 0
1976-01-05 | 1900-01-04 | 11:00 | 11 | 472 | 1415 | 115 | 1 | 9 | 10 | 1 | 9 | 112 | 1 | 13 | 131 | 1 | 9 | 6 | 1 | 9 | 129 | 1 | 13 | 426 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.84 | A | 7 | 1005 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.5 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.12 | 2 | 0
1976-01-05 | 1900-01-04 | 12:00 | 12 | 593 | 1415 | 211 | 1 | 9 | 3 | 1 | 9 | 209 | 1 | 13 | 233 | 1 | 9 | 3 | 1 | 9 | 232 | 1 | 13 | 724 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -10 | 14 | A | 7 | -13.9 | 6.98 | A | 7 | 0.74 | A | 7 | 1004 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.5 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.4 | 2 | 0
1976-01-05 | 1900-01-04 | 13:00 | 13 | 650 | 1415 | 256 | 1 | 9 | 130 | 1 | 9 | 196 | 1 | 13 | 279 | 1 | 9 | 131 | 1 | 9 | 218 | 1 | 13 | 476 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -8.9 | 15.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.81 | A | 7 | 1003 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.6 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.68 | 2 | 0
1976-01-05 | 1900-01-04 | 14:00 | 14 | 639 | 1415 | 424 | 1 | 13 | 665 | 1 | 13 | 123 | 1 | 13 | 439 | 1 | 13 | 641 | 1 | 13 | 149 | 1 | 13 | 245 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 1001 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 2 | 0
1976-01-05 | 1900-01-04 | 15:00 | 15 | 561 | 1415 | 395 | 1 | 9 | 881 | 1 | 9 | 46 | 1 | 13 | 420 | 1 | 9 | 835 | 1 | 9 | 87 | 1 | 13 | 117 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 1000 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.74 | 2 | 0
1976-01-05 | 1900-01-04 | 16:00 | 16 | 421 | 1415 | 274 | 1 | 9 | 797 | 1 | 9 | 37 | 1 | 13 | 292 | 1 | 9 | 717 | 1 | 9 | 77 | 1 | 13 | 94 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.71 | A | 7 | 1000 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.72 | 2 | 0
1976-01-05 | 1900-01-04 | 17:00 | 17 | 230 | 1415 | 123 | 1 | 13 | 599 | 1 | 9 | 26 | 1 | 13 | 131 | 1 | 13 | 461 | 1 | 9 | 56 | 1 | 13 | 60 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 1001 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.52 | 2 | 0
1976-01-05 | 1900-01-04 | 18:00 | 18 | 33 | 766 | 24 | 1 | 13 | 145 | 1 | 9 | 10 | 1 | 13 | 18 | 1 | 13 | 60 | 1 | 9 | 15 | 1 | 13 | 19 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 1000 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.036 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 2 | 0
1976-01-05 | 1900-01-04 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 1000 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 2 | 0
1976-01-05 | 1900-01-04 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 999 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 2 | 0
1976-01-05 | 1900-01-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 999 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 2 | 0
1976-01-05 | 1900-01-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.84 | A | 7 | 999 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 2 | 0
1976-01-05 | 1900-01-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.84 | A | 7 | 998 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 2 | 0
1976-01-05 | 1900-01-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.88 | A | 7 | 998 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.18 | 2 | 0
1976-01-06 | 1900-01-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.92 | A | 7 | 998 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.58 | 3 | 0
1976-01-06 | 1900-01-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.88 | A | 7 | 997 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.18 | 3 | 0
1976-01-06 | 1900-01-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -8.9 | 15.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.88 | A | 7 | 997 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.18 | 3 | 0
1976-01-06 | 1900-01-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 1 | A | 7 | -8.9 | 15.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.88 | A | 7 | 997 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.18 | 3 | 0
1976-01-06 | 1900-01-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | -8.3 | 17.06 | A | 7 | -10 | 14 | A | 7 | 0.88 | A | 7 | 996 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.26 | 3 | 0
1976-01-06 | 1900-01-05 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -8.9 | 15.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.88 | A | 7 | 996 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.18 | 3 | 0
1976-01-06 | 1900-01-05 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | -8.3 | 17.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.84 | A | 7 | 995 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 3 | 0
1976-01-06 | 1900-01-05 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -8.3 | 17.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.84 | A | 7 | 995 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 3 | 0
1976-01-06 | 1900-01-05 | 9:00 | 9 | 83 | 1214 | 29 | 1 | 13 | 97 | 1 | 9 | 21 | 1 | 13 | 30 | 1 | 13 | 41 | 1 | 9 | 27 | 1 | 13 | 37 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -8.3 | 17.06 | A | 7 | -10 | 14 | A | 7 | 0.88 | A | 7 | 995 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.26 | 3 | 0
1976-01-06 | 1900-01-05 | 10:00 | 10 | 297 | 1415 | 141 | 1 | 13 | 369 | 1 | 9 | 62 | 1 | 13 | 147 | 1 | 13 | 284 | 1 | 9 | 87 | 1 | 13 | 112 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.78 | A | 7 | 994 | A | 7 | 160 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 3 | 0
1976-01-06 | 1900-01-05 | 11:00 | 11 | 474 | 1415 | 184 | 1 | 13 | 90 | 1 | 13 | 154 | 1 | 13 | 202 | 1 | 13 | 84 | 1 | 13 | 173 | 1 | 13 | 400 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | -2.8 | 26.96 | A | 7 | -8.3 | 17.06 | A | 7 | 0.66 | A | 7 | 994 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 3 | 0
1976-01-06 | 1900-01-05 | 12:00 | 12 | 595 | 1415 | 217 | 1 | 9 | 78 | 1 | 9 | 184 | 1 | 13 | 238 | 1 | 9 | 76 | 1 | 9 | 206 | 1 | 13 | 515 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -0.6 | 30.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.61 | A | 7 | 993 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.82 | 3 | 0
1976-01-06 | 1900-01-05 | 13:00 | 13 | 652 | 1415 | 335 | 1 | 13 | 347 | 1 | 13 | 175 | 1 | 13 | 360 | 1 | 13 | 355 | 1 | 13 | 196 | 1 | 13 | 379 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | 1.1 | 33.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.54 | A | 7 | 991 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.58 | 3 | 0
1976-01-06 | 1900-01-05 | 14:00 | 14 | 642 | 1415 | 355 | 1 | 13 | 342 | 1 | 13 | 200 | 1 | 13 | 377 | 1 | 13 | 348 | 1 | 13 | 219 | 1 | 13 | 445 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 2.2 | 35.96 | A | 7 | -7.8 | 17.96 | A | 7 | 0.48 | A | 7 | 990 | A | 7 | 180 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.46 | 3 | 0
1976-01-06 | 1900-01-05 | 15:00 | 15 | 564 | 1415 | 260 | 1 | 13 | 224 | 1 | 13 | 171 | 1 | 13 | 276 | 1 | 13 | 221 | 1 | 13 | 187 | 1 | 13 | 366 | 1 | 23 | 9 | A | 7 | 6 | A | 7 | 3.3 | 37.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.44 | A | 7 | 990 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.54 | 3 | 0
1976-01-06 | 1900-01-05 | 16:00 | 16 | 425 | 1415 | 103 | 1 | 9 | 33 | 1 | 9 | 93 | 1 | 13 | 113 | 1 | 9 | 30 | 1 | 9 | 104 | 1 | 13 | 257 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 3.3 | 37.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.44 | A | 7 | 989 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 0.7 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.54 | 3 | 0
1976-01-06 | 1900-01-05 | 17:00 | 17 | 234 | 1415 | 44 | 1 | 13 | 5 | 1 | 9 | 43 | 1 | 13 | 50 | 1 | 13 | 1 | 1 | 9 | 50 | 1 | 13 | 157 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.5 | A | 7 | 989 | A | 7 | 160 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 1980 | A | 7 | 0.7 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.54 | 3 | 0
1976-01-06 | 1900-01-05 | 18:00 | 18 | 35 | 790 | 11 | 1 | 13 | 0 | 1 | 9 | 11 | 1 | 13 | 13 | 1 | 13 | 0 | 1 | 9 | 13 | 1 | 13 | 40 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.57 | A | 7 | 988 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 0.8 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.56 | 3 | 0
1976-01-06 | 1900-01-05 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.62 | A | 7 | 988 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.16 | 3 | 0
1976-01-06 | 1900-01-05 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.62 | A | 7 | 987 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.16 | 3 | 0
1976-01-06 | 1900-01-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.62 | A | 7 | 986 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.16 | 3 | 0
1976-01-06 | 1900-01-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.59 | A | 7 | 986 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.04 | 3 | 0
1976-01-06 | 1900-01-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -5 | 23 | A | 7 | 0.55 | A | 7 | 986 | A | 7 | 200 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1370 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.24 | 3 | 0
1976-01-06 | 1900-01-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 986 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 1310 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.54 | 3 | 0
1976-01-07 | 1900-01-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 985 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 1490 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.54 | 4 | 0
1976-01-07 | 1900-01-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.57 | A | 7 | 985 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 1130 | A | 7 | 0.8 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.54 | 4 | 0
1976-01-07 | 1900-01-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.67 | A | 7 | 985 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 1400 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.82 | 4 | 0
1976-01-07 | 1900-01-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 986 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 270 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 4 | 0
1976-01-07 | 1900-01-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 985 | A | 7 | 210 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 4 | 0
1976-01-07 | 1900-01-06 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 985 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 4 | 0
1976-01-07 | 1900-01-06 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 985 | A | 7 | 210 | A | 7 | 5.7 | A | 7 | 4000 | A | 7 | 520 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 4 | 0
1976-01-07 | 1900-01-06 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 985 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 3600 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 4 | 0
1976-01-07 | 1900-01-06 | 9:00 | 9 | 84 | 1214 | 19 | 1 | 13 | 3 | 1 | 9 | 18 | 1 | 13 | 21 | 1 | 13 | 0 | 1 | 9 | 21 | 1 | 13 | 64 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 986 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 2400 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 4 | 0
1976-01-07 | 1900-01-06 | 10:00 | 10 | 298 | 1415 | 71 | 1 | 13 | 6 | 1 | 9 | 70 | 1 | 13 | 80 | 1 | 13 | 2 | 1 | 9 | 80 | 1 | 13 | 246 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 986 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 2400 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 4 | 0
1976-01-07 | 1900-01-06 | 11:00 | 11 | 475 | 1415 | 150 | 1 | 9 | 6 | 1 | 9 | 148 | 1 | 13 | 167 | 1 | 9 | 4 | 1 | 9 | 165 | 1 | 13 | 512 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 987 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 4000 | A | 7 | 240 | A | 7 | 1.1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 4 | 0
1976-01-07 | 1900-01-06 | 12:00 | 12 | 597 | 1415 | 192 | 1 | 9 | 7 | 1 | 9 | 189 | 1 | 13 | 215 | 1 | 9 | 6 | 1 | 9 | 212 | 1 | 13 | 687 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 986 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 4 | 0
1976-01-07 | 1900-01-06 | 13:00 | 13 | 655 | 1415 | 239 | 1 | 9 | 1 | 1 | 9 | 239 | 1 | 13 | 266 | 1 | 9 | 1 | 1 | 9 | 265 | 1 | 13 | 838 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 985 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 370 | A | 7 | 1 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 4 | 0
1976-01-07 | 1900-01-06 | 14:00 | 14 | 645 | 1415 | 221 | 1 | 9 | 2 | 1 | 9 | 220 | 1 | 13 | 246 | 1 | 9 | 2 | 1 | 9 | 246 | 1 | 13 | 792 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.96 | A | 7 | 985 | A | 7 | 350 | A | 7 | 7.7 | A | 7 | 1600 | A | 7 | 270 | A | 7 | 0.9 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.54 | 4 | 0
1976-01-07 | 1900-01-06 | 15:00 | 15 | 568 | 1415 | 176 | 1 | 9 | 3 | 1 | 9 | 174 | 1 | 13 | 196 | 1 | 9 | 2 | 1 | 9 | 195 | 1 | 13 | 633 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.92 | A | 7 | 986 | A | 7 | 350 | A | 7 | 8.2 | A | 7 | 1300 | A | 7 | 310 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.26 | 4 | 0
1976-01-07 | 1900-01-06 | 16:00 | 16 | 429 | 1415 | 135 | 1 | 9 | 1 | 1 | 9 | 135 | 1 | 13 | 150 | 1 | 9 | 1 | 1 | 9 | 149 | 1 | 13 | 454 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 350 | A | 7 | 10.3 | A | 7 | 4000 | A | 7 | 550 | A | 7 | 0.8 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 4 | 0
1976-01-07 | 1900-01-06 | 17:00 | 17 | 238 | 1415 | 67 | 1 | 13 | 1 | 1 | 9 | 67 | 1 | 13 | 74 | 1 | 13 | 0 | 1 | 9 | 74 | 1 | 13 | 215 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.78 | A | 7 | 988 | A | 7 | 360 | A | 7 | 10.3 | A | 7 | 6400 | A | 7 | 610 | A | 7 | 0.7 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 4 | 0
1976-01-07 | 1900-01-06 | 18:00 | 18 | 37 | 814 | 14 | 1 | 13 | 0 | 1 | 9 | 14 | 1 | 13 | 16 | 1 | 13 | 0 | 1 | 9 | 16 | 1 | 13 | 48 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 360 | A | 7 | 10.3 | A | 7 | 6400 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.056 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.4 | 4 | 0
1976-01-07 | 1900-01-06 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 989 | A | 7 | 360 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.7 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 4 | 0
1976-01-07 | 1900-01-06 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 350 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1220 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 4 | 0
1976-01-07 | 1900-01-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 990 | A | 7 | 10 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 730 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 4 | 0
1976-01-07 | 1900-01-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.88 | A | 7 | 991 | A | 7 | 340 | A | 7 | 9.3 | A | 7 | 2400 | A | 7 | 240 | A | 7 | 0.7 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.04 | 4 | 0
1976-01-07 | 1900-01-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.84 | A | 7 | 992 | A | 7 | 330 | A | 7 | 9.3 | A | 7 | 8000 | A | 7 | 610 | A | 7 | 0.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 4 | 0
1976-01-07 | 1900-01-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.84 | A | 7 | 992 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 760 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.12 | 4 | 0
1976-01-08 | 1900-01-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -15 | 5 | A | 7 | 0.8 | A | 7 | 992 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 9700 | A | 7 | 880 | A | 7 | 0.5 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.94 | 5 | 0
1976-01-08 | 1900-01-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -13.9 | 6.98 | A | 7 | -16.7 | 1.94 | A | 7 | 0.8 | A | 7 | 992 | A | 7 | 320 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 980 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.98 | 5 | 0
1976-01-08 | 1900-01-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -17.2 | 1.04 | A | 7 | 0.8 | A | 7 | 993 | A | 7 | 330 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 980 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.18 | 5 | 0
1976-01-08 | 1900-01-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -16.7 | 1.94 | A | 7 | -19.4 | -2.92 | A | 7 | 0.79 | A | 7 | 994 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 14500 | A | 7 | 1040 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.14 | 5 | 0
1976-01-08 | 1900-01-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -16.7 | 1.94 | A | 7 | -19.4 | -2.92 | A | 7 | 0.79 | A | 7 | 994 | A | 7 | 310 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 980 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.14 | 5 | 0
1976-01-08 | 1900-01-07 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -18.3 | -0.94 | A | 7 | -25 | -13 | A | 7 | 0.56 | A | 7 | 995 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 1040 | A | 7 | 0.3 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.44 | 5 | 0
1976-01-08 | 1900-01-07 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -19.4 | -2.92 | A | 7 | -25.6 | -14.08 | A | 7 | 0.59 | A | 7 | 995 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.22 | 5 | 0
1976-01-08 | 1900-01-07 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 5 | A | 7 | -19.4 | -2.92 | A | 7 | -26.1 | -14.98 | A | 7 | 0.56 | A | 7 | 996 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 1100 | A | 7 | 0.3 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.32 | 5 | 0
1976-01-08 | 1900-01-07 | 9:00 | 9 | 84 | 1238 | 41 | 1 | 13 | 234 | 1 | 9 | 20 | 1 | 13 | 38 | 1 | 13 | 113 | 1 | 9 | 30 | 1 | 13 | 36 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -20 | -4 | A | 7 | -26.7 | -16.06 | A | 7 | 0.56 | A | 7 | 997 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.3 | 5 | 0
1976-01-08 | 1900-01-07 | 10:00 | 10 | 299 | 1415 | 176 | 1 | 13 | 632 | 1 | 9 | 42 | 1 | 13 | 180 | 1 | 13 | 510 | 1 | 9 | 71 | 1 | 13 | 80 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -19.4 | -2.92 | A | 7 | -25.6 | -14.08 | A | 7 | 0.59 | A | 7 | 997 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.22 | 5 | 0
1976-01-08 | 1900-01-07 | 11:00 | 11 | 476 | 1415 | 325 | 1 | 9 | 792 | 1 | 9 | 57 | 1 | 13 | 339 | 1 | 9 | 729 | 1 | 9 | 92 | 1 | 13 | 117 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -18.9 | -2.02 | A | 7 | -25 | -13 | A | 7 | 0.59 | A | 7 | 998 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.32 | 5 | 0
1976-01-08 | 1900-01-07 | 12:00 | 12 | 599 | 1415 | 430 | 1 | 9 | 856 | 1 | 9 | 67 | 1 | 13 | 454 | 1 | 9 | 824 | 1 | 9 | 104 | 1 | 13 | 143 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -23.9 | -11.02 | A | 7 | 0.59 | A | 7 | 997 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.44 | 5 | 0
1976-01-08 | 1900-01-07 | 13:00 | 13 | 657 | 1415 | 484 | 1 | 9 | 886 | 1 | 9 | 72 | 1 | 13 | 507 | 1 | 9 | 855 | 1 | 9 | 108 | 1 | 13 | 147 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -22.2 | -7.96 | A | 7 | 0.62 | A | 7 | 997 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.44 | 5 | 0
1976-01-08 | 1900-01-07 | 14:00 | 14 | 648 | 1415 | 472 | 1 | 9 | 874 | 1 | 9 | 71 | 1 | 13 | 494 | 1 | 9 | 842 | 1 | 9 | 107 | 1 | 13 | 145 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -21.7 | -7.06 | A | 7 | 0.6 | A | 7 | 996 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.22 | 5 | 0
1976-01-08 | 1900-01-07 | 15:00 | 15 | 571 | 1415 | 404 | 1 | 9 | 841 | 1 | 9 | 64 | 1 | 13 | 426 | 1 | 9 | 803 | 1 | 9 | 101 | 1 | 13 | 136 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -21.1 | -5.98 | A | 7 | 0.6 | A | 7 | 996 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.3 | 5 | 0
1976-01-08 | 1900-01-07 | 16:00 | 16 | 432 | 1415 | 282 | 1 | 9 | 753 | 1 | 9 | 52 | 1 | 13 | 295 | 1 | 9 | 678 | 1 | 9 | 86 | 1 | 13 | 106 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -20.6 | -5.08 | A | 7 | 0.6 | A | 7 | 997 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.28 | 5 | 0
1976-01-08 | 1900-01-07 | 17:00 | 17 | 242 | 1415 | 129 | 1 | 13 | 551 | 1 | 9 | 36 | 1 | 13 | 132 | 1 | 13 | 414 | 1 | 9 | 61 | 1 | 13 | 67 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -21.7 | -7.06 | A | 7 | 0.55 | A | 7 | 998 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.08 | 5 | 0
1976-01-08 | 1900-01-07 | 18:00 | 18 | 39 | 837 | 25 | 1 | 13 | 112 | 1 | 9 | 14 | 1 | 13 | 21 | 1 | 13 | 39 | 1 | 9 | 19 | 1 | 13 | 24 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -21.7 | -7.06 | A | 7 | 0.63 | A | 7 | 998 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.061 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.52 | 5 | 0
1976-01-08 | 1900-01-07 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -21.7 | -7.06 | A | 7 | 0.66 | A | 7 | 998 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.64 | 5 | 0
1976-01-08 | 1900-01-07 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.2 | 1.04 | A | 7 | -21.7 | -7.06 | A | 7 | 0.69 | A | 7 | 998 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.06 | 5 | 0
1976-01-08 | 1900-01-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -22.2 | -7.96 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 260 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.14 | 5 | 0
1976-01-08 | 1900-01-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -22.2 | -7.96 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.14 | 5 | 0
1976-01-08 | 1900-01-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -22.2 | -7.96 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.14 | 5 | 0
1976-01-08 | 1900-01-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -22.2 | -7.96 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.14 | 5 | 0
1976-01-09 | 1900-01-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -22.2 | -7.96 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.14 | 6 | 0
1976-01-09 | 1900-01-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -22.8 | -9.04 | A | 7 | 0.65 | A | 7 | 998 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.24 | 6 | 0
1976-01-09 | 1900-01-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -18.3 | -0.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.04 | 6 | 0
1976-01-09 | 1900-01-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -18.9 | -2.02 | A | 7 | -22.8 | -9.04 | A | 7 | 0.72 | A | 7 | 999 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.92 | 6 | 0
1976-01-09 | 1900-01-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -18.3 | -0.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.04 | 6 | 0
1976-01-09 | 1900-01-08 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -18.3 | -0.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.68 | A | 7 | 999 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.04 | 6 | 0
1976-01-09 | 1900-01-08 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -18.3 | -0.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.68 | A | 7 | 999 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.04 | 6 | 0
1976-01-09 | 1900-01-08 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -18.3 | -0.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.68 | A | 7 | 999 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.04 | 6 | 0
1976-01-09 | 1900-01-08 | 9:00 | 9 | 85 | 1238 | 34 | 1 | 13 | 109 | 1 | 9 | 24 | 1 | 13 | 33 | 1 | 13 | 46 | 1 | 9 | 30 | 1 | 13 | 43 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -18.3 | -0.94 | A | 7 | -22.8 | -9.04 | A | 7 | 0.68 | A | 7 | 1000 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -2.04 | 6 | 0
1976-01-09 | 1900-01-08 | 10:00 | 10 | 300 | 1415 | 159 | 1 | 13 | 462 | 1 | 9 | 61 | 1 | 13 | 162 | 1 | 13 | 359 | 1 | 9 | 86 | 1 | 13 | 108 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | -17.2 | 1.04 | A | 7 | -21.7 | -7.06 | A | 7 | 0.69 | A | 7 | 1001 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.06 | 6 | 0
1976-01-09 | 1900-01-08 | 11:00 | 11 | 478 | 1415 | 292 | 1 | 9 | 578 | 1 | 9 | 95 | 1 | 13 | 299 | 1 | 9 | 523 | 1 | 9 | 121 | 1 | 13 | 176 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | -16.1 | 3.02 | A | 7 | -21.1 | -5.98 | A | 7 | 0.66 | A | 7 | 1002 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.62 | 6 | 0
1976-01-09 | 1900-01-08 | 12:00 | 12 | 601 | 1415 | 409 | 1 | 9 | 523 | 1 | 9 | 187 | 1 | 13 | 419 | 1 | 9 | 506 | 1 | 9 | 203 | 1 | 13 | 385 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | -14.4 | 6.08 | A | 7 | -20.6 | -5.08 | A | 7 | 0.6 | A | 7 | 1001 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.28 | 6 | 0
1976-01-09 | 1900-01-08 | 13:00 | 13 | 660 | 1415 | 441 | 1 | 13 | 574 | 1 | 13 | 172 | 1 | 13 | 461 | 1 | 13 | 568 | 1 | 13 | 195 | 1 | 13 | 357 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -12.8 | 8.96 | A | 7 | -19.4 | -2.92 | A | 7 | 0.58 | A | 7 | 1001 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.86 | 6 | 0
1976-01-09 | 1900-01-08 | 14:00 | 14 | 651 | 1415 | 359 | 1 | 13 | 389 | 1 | 13 | 180 | 1 | 13 | 385 | 1 | 13 | 397 | 1 | 13 | 202 | 1 | 13 | 392 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -11.7 | 10.94 | A | 7 | -18.9 | -2.02 | A | 7 | 0.55 | A | 7 | 1000 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.44 | 6 | 0
1976-01-09 | 1900-01-08 | 15:00 | 15 | 575 | 1415 | 371 | 1 | 9 | 622 | 1 | 9 | 118 | 1 | 13 | 382 | 1 | 9 | 586 | 1 | 9 | 143 | 1 | 13 | 225 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | -11.1 | 12.02 | A | 7 | -19.4 | -2.92 | A | 7 | 0.51 | A | 7 | 999 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.22 | 6 | 0
1976-01-09 | 1900-01-08 | 16:00 | 16 | 436 | 1415 | 250 | 1 | 9 | 464 | 1 | 9 | 107 | 1 | 13 | 261 | 1 | 9 | 414 | 1 | 9 | 133 | 1 | 13 | 202 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -9.4 | 15.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.49 | A | 7 | 1000 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.88 | 6 | 0
1976-01-09 | 1900-01-08 | 17:00 | 17 | 246 | 1415 | 90 | 1 | 13 | 137 | 1 | 13 | 67 | 1 | 13 | 96 | 1 | 13 | 95 | 1 | 13 | 79 | 1 | 13 | 128 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | -10 | 14 | A | 7 | -18.9 | -2.02 | A | 7 | 0.49 | A | 7 | 1000 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.9 | 6 | 0
1976-01-09 | 1900-01-08 | 18:00 | 18 | 41 | 861 | 13 | 1 | 13 | 5 | 1 | 9 | 13 | 1 | 13 | 15 | 1 | 13 | 3 | 1 | 9 | 14 | 1 | 13 | 32 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -10 | 14 | A | 7 | -17.2 | 1.04 | A | 7 | 0.56 | A | 7 | 999 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.4 | E | 8 | 0.124 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.3 | 6 | 0
1976-01-09 | 1900-01-08 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10 | 14 | A | 7 | -16.7 | 1.94 | A | 7 | 0.59 | A | 7 | 1000 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.5 | 6 | 0
1976-01-09 | 1900-01-08 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10 | 14 | A | 7 | -17.8 | -0.04 | A | 7 | 0.53 | A | 7 | 1000 | A | 7 | 220 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.1 | 6 | 0
1976-01-09 | 1900-01-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -10.6 | 12.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.61 | A | 7 | 1000 | A | 7 | 210 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.62 | 6 | 0
1976-01-09 | 1900-01-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -10 | 14 | A | 7 | -16.1 | 3.02 | A | 7 | 0.61 | A | 7 | 1000 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.6 | 6 | 0
1976-01-09 | 1900-01-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -10 | 14 | A | 7 | -16.1 | 3.02 | A | 7 | 0.61 | A | 7 | 1000 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.6 | 6 | 0
1976-01-09 | 1900-01-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 1000 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 6 | 0
1976-01-10 | 1900-01-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -16.7 | 1.94 | A | 7 | 0.7 | A | 7 | 1000 | A | 7 | 160 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.44 | 7 | 0
1976-01-10 | 1900-01-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -16.7 | 1.94 | A | 7 | 0.7 | A | 7 | 1000 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.44 | 7 | 0
1976-01-10 | 1900-01-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -16.7 | 1.94 | A | 7 | 0.7 | A | 7 | 1000 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.44 | 7 | 0
1976-01-10 | 1900-01-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 1000 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 7 | 0
1976-01-10 | 1900-01-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 1000 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 7 | 0
1976-01-10 | 1900-01-09 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 4 | A | 7 | -11.7 | 10.94 | A | 7 | -15.6 | 3.92 | A | 7 | 0.73 | A | 7 | 1000 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.44 | 7 | 0
1976-01-10 | 1900-01-09 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -11.1 | 12.02 | A | 7 | -15 | 5 | A | 7 | 0.73 | A | 7 | 1000 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 7 | 0
1976-01-10 | 1900-01-09 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 3 | A | 7 | -11.1 | 12.02 | A | 7 | -15 | 5 | A | 7 | 0.73 | A | 7 | 1000 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 7 | 0
1976-01-10 | 1900-01-09 | 9:00 | 9 | 85 | 1238 | 17 | 1 | 13 | 6 | 1 | 9 | 16 | 1 | 13 | 18 | 1 | 13 | 3 | 1 | 9 | 18 | 1 | 13 | 41 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -10 | 14 | A | 7 | -13.9 | 6.98 | A | 7 | 0.74 | A | 7 | 999 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 6710 | A | 7 | 0.5 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.4 | 7 | 0
1976-01-10 | 1900-01-09 | 10:00 | 10 | 301 | 1415 | 75 | 1 | 13 | 3 | 1 | 9 | 74 | 1 | 13 | 84 | 1 | 13 | 1 | 1 | 9 | 83 | 1 | 13 | 257 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -13.9 | 6.98 | A | 7 | 0.67 | A | 7 | 999 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 6710 | A | 7 | 0.5 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 7 | 0
1976-01-10 | 1900-01-09 | 11:00 | 11 | 480 | 1415 | 149 | 1 | 9 | 3 | 1 | 9 | 148 | 1 | 13 | 166 | 1 | 9 | 2 | 1 | 9 | 165 | 1 | 13 | 515 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 999 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 6710 | A | 7 | 0.6 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 7 | 0
1976-01-10 | 1900-01-09 | 12:00 | 12 | 603 | 1415 | 182 | 1 | 9 | 10 | 1 | 9 | 178 | 1 | 13 | 205 | 1 | 9 | 8 | 1 | 9 | 202 | 1 | 13 | 668 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -10.6 | 12.92 | A | 7 | 0.74 | A | 7 | 999 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 7010 | A | 7 | 0.6 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.94 | 7 | 0
1976-01-10 | 1900-01-09 | 13:00 | 13 | 663 | 1415 | 194 | 1 | 9 | 5 | 1 | 9 | 192 | 1 | 13 | 220 | 1 | 9 | 4 | 1 | 9 | 218 | 1 | 13 | 743 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.74 | A | 7 | 996 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7010 | A | 7 | 0.6 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 7 | 0
1976-01-10 | 1900-01-09 | 14:00 | 14 | 655 | 1415 | 275 | 1 | 9 | 3 | 1 | 9 | 273 | 1 | 13 | 301 | 1 | 9 | 3 | 1 | 9 | 300 | 1 | 13 | 890 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.71 | A | 7 | 995 | A | 7 | 150 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 7010 | A | 7 | 0.6 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.58 | 7 | 0
1976-01-10 | 1900-01-09 | 15:00 | 15 | 579 | 1415 | 213 | 1 | 9 | 5 | 1 | 9 | 211 | 1 | 13 | 235 | 1 | 9 | 4 | 1 | 9 | 233 | 1 | 13 | 714 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.72 | A | 7 | 993 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 7 | 0
1976-01-10 | 1900-01-09 | 16:00 | 16 | 440 | 1415 | 147 | 1 | 9 | 4 | 1 | 9 | 145 | 1 | 13 | 161 | 1 | 9 | 3 | 1 | 9 | 160 | 1 | 13 | 481 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -7.8 | 17.96 | A | 7 | 0.75 | A | 7 | 993 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 1040 | A | 7 | 0.7 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 7 | 0
1976-01-10 | 1900-01-09 | 17:00 | 17 | 250 | 1415 | 69 | 1 | 13 | 2 | 1 | 9 | 68 | 1 | 13 | 76 | 1 | 13 | 1 | 1 | 9 | 75 | 1 | 13 | 223 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.72 | A | 7 | 991 | A | 7 | 140 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 980 | A | 7 | 0.7 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.46 | 7 | 0
1976-01-10 | 1900-01-09 | 18:00 | 18 | 43 | 884 | 16 | 1 | 13 | 0 | 1 | 9 | 16 | 1 | 13 | 18 | 1 | 13 | 0 | 1 | 9 | 18 | 1 | 13 | 54 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -7.2 | 19.04 | A | 7 | 0.69 | A | 7 | 991 | A | 7 | 160 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.7 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.04 | 7 | 0
1976-01-10 | 1900-01-09 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.72 | A | 7 | 990 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 790 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.34 | 7 | 0
1976-01-10 | 1900-01-09 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 989 | A | 7 | 150 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 760 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.44 | 7 | 0
1976-01-10 | 1900-01-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 989 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 760 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.92 | 7 | 0
1976-01-10 | 1900-01-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 989 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 980 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.92 | 7 | 0
1976-01-10 | 1900-01-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 988 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 940 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 7 | 0
1976-01-10 | 1900-01-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 987 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 940 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 7 | 0
1976-01-11 | 1900-01-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 986 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 980 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 1 | 0
1976-01-11 | 1900-01-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 820 | A | 7 | 1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.28 | 1 | 0
1976-01-11 | 1900-01-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.79 | A | 7 | 985 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 730 | A | 7 | 1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.54 | 1 | 0
1976-01-11 | 1900-01-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -0.6 | 30.92 | A | 7 | 0.79 | A | 7 | 985 | A | 7 | 220 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 730 | A | 7 | 1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.54 | 1 | 0
1976-01-11 | 1900-01-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 730 | A | 7 | 1.1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.84 | 1 | 0
1976-01-11 | 1900-01-10 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 0 | 32 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 230 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 1.1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.84 | 1 | 0
1976-01-11 | 1900-01-10 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.89 | A | 7 | 984 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 1.1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.74 | 1 | 0
1976-01-11 | 1900-01-10 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.89 | A | 7 | 984 | A | 7 | 240 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 370 | A | 7 | 1.1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.74 | 1 | 0
1976-01-11 | 1900-01-10 | 9:00 | 9 | 86 | 1238 | 23 | 1 | 13 | 0 | 1 | 9 | 23 | 1 | 13 | 26 | 1 | 13 | 0 | 1 | 9 | 26 | 1 | 13 | 77 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 260 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 310 | A | 7 | 1.2 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.04 | 1 | 0
1976-01-11 | 1900-01-10 | 10:00 | 10 | 303 | 1414 | 89 | 1 | 13 | 22 | 1 | 9 | 85 | 1 | 13 | 98 | 1 | 13 | 18 | 1 | 9 | 94 | 1 | 13 | 210 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 1.7 | 35.06 | A | 7 | 0 | 32 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 430 | A | 7 | 1.1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.76 | 1 | 0
1976-01-11 | 1900-01-10 | 11:00 | 11 | 482 | 1414 | 115 | 1 | 9 | 16 | 1 | 9 | 110 | 1 | 13 | 132 | 1 | 9 | 10 | 1 | 9 | 128 | 1 | 13 | 425 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.85 | A | 7 | 986 | A | 7 | 280 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 490 | A | 7 | 1 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.28 | 1 | 0
1976-01-11 | 1900-01-10 | 12:00 | 12 | 606 | 1414 | 232 | 1 | 9 | 7 | 1 | 9 | 228 | 1 | 13 | 255 | 1 | 9 | 6 | 1 | 9 | 252 | 1 | 13 | 769 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 280 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 790 | A | 7 | 0.9 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 1 | 0
1976-01-11 | 1900-01-10 | 13:00 | 13 | 666 | 1414 | 155 | 1 | 9 | 14 | 1 | 9 | 148 | 1 | 13 | 179 | 1 | 9 | 10 | 1 | 9 | 174 | 1 | 13 | 621 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 986 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 850 | A | 7 | 0.9 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 1 | 0
1976-01-11 | 1900-01-10 | 14:00 | 14 | 658 | 1414 | 189 | 1 | 9 | 9 | 1 | 9 | 186 | 1 | 13 | 216 | 1 | 9 | 7 | 1 | 9 | 212 | 1 | 13 | 725 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 986 | A | 7 | 280 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 0.9 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.22 | 1 | 0
1976-01-11 | 1900-01-10 | 15:00 | 15 | 582 | 1414 | 171 | 1 | 9 | 7 | 1 | 9 | 168 | 1 | 13 | 192 | 1 | 9 | 5 | 1 | 9 | 190 | 1 | 13 | 629 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 280 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 0.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 1 | 0
1976-01-11 | 1900-01-10 | 16:00 | 16 | 444 | 1414 | 130 | 1 | 9 | 5 | 1 | 9 | 128 | 1 | 13 | 144 | 1 | 9 | 3 | 1 | 9 | 143 | 1 | 13 | 450 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5 | 23 | A | 7 | 0.85 | A | 7 | 988 | A | 7 | 280 | A | 7 | 7.2 | A | 7 | 12900 | A | 7 | 550 | A | 7 | 0.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 1 | 0
1976-01-11 | 1900-01-10 | 17:00 | 17 | 254 | 1414 | 50 | 1 | 13 | 1 | 1 | 9 | 50 | 1 | 13 | 57 | 1 | 13 | 0 | 1 | 9 | 57 | 1 | 13 | 181 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -5 | 23 | A | 7 | 0.82 | A | 7 | 989 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 640 | A | 7 | 0.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 1 | 0
1976-01-11 | 1900-01-10 | 18:00 | 18 | 46 | 908 | 16 | 1 | 13 | 0 | 1 | 9 | 16 | 1 | 13 | 18 | 1 | 13 | 0 | 1 | 9 | 18 | 1 | 13 | 55 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5 | 23 | A | 7 | 0.85 | A | 7 | 990 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.137 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 1 | 0
1976-01-11 | 1900-01-10 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5 | 23 | A | 7 | 0.85 | A | 7 | 990 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 640 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 1 | 0
1976-01-11 | 1900-01-10 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 991 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.16 | 1 | 0
1976-01-11 | 1900-01-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 991 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 1 | 0
1976-01-11 | 1900-01-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 992 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 1 | 0
1976-01-11 | 1900-01-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 992 | A | 7 | 270 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 1 | 0
1976-01-11 | 1900-01-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 992 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 430 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 1 | 0
1976-01-12 | 1900-01-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 993 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 2 | 0
1976-01-12 | 1900-01-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 993 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 340 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 2 | 0
1976-01-12 | 1900-01-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 993 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 370 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 2 | 0
1976-01-12 | 1900-01-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 994 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 370 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 2 | 0
1976-01-12 | 1900-01-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.88 | A | 7 | 994 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 2 | 0
1976-01-12 | 1900-01-11 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.88 | A | 7 | 994 | A | 7 | 220 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 2 | 0
1976-01-12 | 1900-01-11 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.88 | A | 7 | 994 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 2 | 0
1976-01-12 | 1900-01-11 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 994 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 400 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22 | 2 | 0
1976-01-12 | 1900-01-11 | 9:00 | 9 | 87 | 1238 | 33 | 1 | 13 | 136 | 1 | 9 | 21 | 1 | 13 | 33 | 1 | 13 | 59 | 1 | 9 | 29 | 1 | 13 | 37 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 994 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22 | 2 | 0
1976-01-12 | 1900-01-11 | 10:00 | 10 | 304 | 1414 | 158 | 1 | 13 | 489 | 1 | 9 | 52 | 1 | 13 | 163 | 1 | 13 | 386 | 1 | 9 | 79 | 1 | 13 | 95 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 994 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 2 | 0
1976-01-12 | 1900-01-11 | 11:00 | 11 | 484 | 1414 | 284 | 1 | 9 | 609 | 1 | 9 | 75 | 1 | 13 | 297 | 1 | 9 | 560 | 1 | 9 | 104 | 1 | 13 | 145 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | -2.2 | 28.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.85 | A | 7 | 994 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 2 | 0
1976-01-12 | 1900-01-11 | 12:00 | 12 | 609 | 1414 | 365 | 1 | 9 | 549 | 1 | 9 | 128 | 1 | 13 | 389 | 1 | 9 | 536 | 1 | 9 | 158 | 1 | 13 | 253 | 1 | 18 | 5 | A | 7 | 2 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.78 | A | 7 | 993 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.62 | 2 | 0
1976-01-12 | 1900-01-11 | 13:00 | 13 | 669 | 1414 | 417 | 1 | 13 | 530 | 1 | 13 | 166 | 1 | 13 | 439 | 1 | 13 | 526 | 1 | 13 | 189 | 1 | 13 | 344 | 1 | 23 | 8 | A | 7 | 3 | A | 7 | 1.1 | 33.98 | A | 7 | -2.8 | 26.96 | A | 7 | 0.76 | A | 7 | 992 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.18 | 2 | 0
1976-01-12 | 1900-01-11 | 14:00 | 14 | 662 | 1414 | 410 | 1 | 13 | 518 | 1 | 13 | 167 | 1 | 13 | 430 | 1 | 13 | 513 | 1 | 13 | 189 | 1 | 13 | 345 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 2.2 | 35.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.73 | A | 7 | 990 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.76 | 2 | 0
1976-01-12 | 1900-01-11 | 15:00 | 15 | 586 | 1414 | 394 | 1 | 13 | 581 | 1 | 13 | 154 | 1 | 13 | 412 | 1 | 13 | 561 | 1 | 13 | 178 | 1 | 13 | 308 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 989 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.54 | 2 | 0
1976-01-12 | 1900-01-11 | 16:00 | 16 | 449 | 1414 | 198 | 1 | 13 | 186 | 1 | 13 | 139 | 1 | 13 | 214 | 1 | 13 | 172 | 1 | 13 | 160 | 1 | 13 | 313 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 3.3 | 37.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.67 | A | 7 | 989 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.84 | 2 | 0
1976-01-12 | 1900-01-11 | 17:00 | 17 | 258 | 1414 | 85 | 1 | 13 | 60 | 1 | 9 | 74 | 1 | 13 | 93 | 1 | 13 | 48 | 1 | 9 | 84 | 1 | 13 | 178 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 989 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.66 | 2 | 0
1976-01-12 | 1900-01-11 | 18:00 | 18 | 49 | 931 | 22 | 1 | 13 | 36 | 1 | 13 | 18 | 1 | 13 | 22 | 1 | 13 | 15 | 1 | 13 | 21 | 1 | 13 | 37 | 1 | 23 | 9 | A | 7 | 3 | A | 7 | 1.1 | 33.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.82 | A | 7 | 989 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 2 | 0
1976-01-12 | 1900-01-11 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.85 | A | 7 | 989 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.38 | 2 | 0
1976-01-12 | 1900-01-11 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 989 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 2 | 0
1976-01-12 | 1900-01-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 988 | A | 7 | 150 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 2 | 0
1976-01-12 | 1900-01-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 3 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 988 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 2 | 0
1976-01-12 | 1900-01-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | 0 | 32 | A | 7 | -2.8 | 26.96 | A | 7 | 0.82 | A | 7 | 987 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.1 | 2 | 0
1976-01-12 | 1900-01-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.79 | A | 7 | 986 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.68 | 2 | 0
1976-01-13 | 1900-01-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 3 | 0
1976-01-13 | 1900-01-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 3 | 0
1976-01-13 | 1900-01-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 6 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.92 | 3 | 0
1976-01-13 | 1900-01-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 984 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 3 | 0
1976-01-13 | 1900-01-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 983 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 0.9 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 3 | 0
1976-01-13 | 1900-01-12 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 240 | A | 7 | 1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 3 | 0
1976-01-13 | 1900-01-12 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 110 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 180 | A | 7 | 1.1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 3 | 0
1976-01-13 | 1900-01-12 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 600 | A | 7 | 90 | A | 7 | 1.1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 3 | 0
1976-01-13 | 1900-01-12 | 9:00 | 9 | 88 | 1261 | 10 | 1 | 13 | 2 | 1 | 9 | 10 | 1 | 13 | 12 | 1 | 13 | 0 | 1 | 9 | 12 | 1 | 13 | 39 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 1.1 | 33.98 | A | 7 | 1 | A | 7 | 979 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 200 | A | 7 | 60 | A | 7 | 1.1 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.88 | 3 | 0
1976-01-13 | 1900-01-12 | 10:00 | 10 | 306 | 1414 | 51 | 1 | 13 | 4 | 1 | 9 | 50 | 1 | 13 | 59 | 1 | 13 | 1 | 1 | 9 | 59 | 1 | 13 | 193 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 1.7 | 35.06 | A | 7 | 1 | A | 7 | 979 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1.2 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.96 | 3 | 0
1976-01-13 | 1900-01-12 | 11:00 | 11 | 486 | 1414 | 94 | 1 | 9 | 4 | 1 | 9 | 92 | 1 | 13 | 108 | 1 | 9 | 2 | 1 | 9 | 107 | 1 | 13 | 373 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 2.2 | 35.96 | A | 7 | 1 | A | 7 | 977 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 200 | A | 7 | 60 | A | 7 | 1.2 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.86 | 3 | 0
1976-01-13 | 1900-01-12 | 12:00 | 12 | 611 | 1414 | 109 | 1 | 9 | 6 | 1 | 9 | 106 | 1 | 13 | 128 | 1 | 9 | 4 | 1 | 9 | 126 | 1 | 13 | 459 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.8 | 37.04 | A | 7 | 1 | A | 7 | 974 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 1600 | A | 7 | 120 | A | 7 | 1.2 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.04 | 3 | 0
1976-01-13 | 1900-01-12 | 13:00 | 13 | 673 | 1414 | 115 | 1 | 9 | 7 | 1 | 9 | 112 | 1 | 13 | 136 | 1 | 9 | 5 | 1 | 9 | 134 | 1 | 13 | 500 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.9 | 39.02 | A | 7 | 3.9 | 39.02 | A | 7 | 1 | A | 7 | 970 | A | 7 | 150 | A | 7 | 6.7 | A | 7 | 2400 | A | 7 | 90 | A | 7 | 1.3 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.92 | 3 | 0
1976-01-13 | 1900-01-12 | 14:00 | 14 | 665 | 1414 | 146 | 1 | 9 | 8 | 1 | 9 | 142 | 1 | 13 | 169 | 1 | 9 | 6 | 1 | 9 | 166 | 1 | 13 | 601 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 4.4 | 39.92 | A | 7 | 1 | A | 7 | 968 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 600 | A | 7 | 90 | A | 7 | 1.4 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.92 | 3 | 0
1976-01-13 | 1900-01-12 | 15:00 | 15 | 590 | 1414 | 196 | 1 | 9 | 7 | 1 | 9 | 193 | 1 | 13 | 218 | 1 | 9 | 6 | 1 | 9 | 216 | 1 | 13 | 691 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 6.1 | 42.98 | A | 7 | 1 | A | 7 | 966 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 1.5 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.88 | 3 | 0
1976-01-13 | 1900-01-12 | 16:00 | 16 | 453 | 1414 | 94 | 1 | 9 | 3 | 1 | 9 | 93 | 1 | 13 | 108 | 1 | 9 | 2 | 1 | 9 | 107 | 1 | 13 | 364 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 4.4 | 39.92 | A | 7 | 1 | A | 7 | 968 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 4800 | A | 7 | 150 | A | 7 | 1.4 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.92 | 3 | 0
1976-01-13 | 1900-01-12 | 17:00 | 17 | 263 | 1414 | 78 | 1 | 13 | 2 | 1 | 9 | 77 | 1 | 13 | 85 | 1 | 13 | 1 | 1 | 9 | 85 | 1 | 13 | 246 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 1.1 | 33.98 | A | 7 | 1 | A | 7 | 970 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.88 | 3 | 0
1976-01-13 | 1900-01-12 | 18:00 | 18 | 51 | 955 | 21 | 1 | 13 | 0 | 1 | 9 | 21 | 1 | 13 | 23 | 1 | 13 | 0 | 1 | 9 | 23 | 1 | 13 | 68 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 975 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 1600 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | 0.035 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 3 | 0
1976-01-13 | 1900-01-12 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 6400 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 3 | 0
1976-01-13 | 1900-01-12 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | 0.6 | 33.08 | A | 7 | -1.1 | 30.02 | A | 7 | 0.89 | A | 7 | 983 | A | 7 | 310 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.78 | 3 | 0
1976-01-13 | 1900-01-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 300 | A | 7 | 9.8 | A | 7 | 24100 | A | 7 | 400 | A | 7 | 1 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.8 | 3 | 0
1976-01-13 | 1900-01-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 988 | A | 7 | 300 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 3 | 0
1976-01-13 | 1900-01-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 990 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 3 | 0
1976-01-13 | 1900-01-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.85 | A | 7 | 991 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 3 | 0
1976-01-14 | 1900-01-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -7.2 | 19.04 | A | 7 | 0.81 | A | 7 | 991 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 4 | 0
1976-01-14 | 1900-01-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 992 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 4 | 0
1976-01-14 | 1900-01-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 993 | A | 7 | 280 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 4 | 0
1976-01-14 | 1900-01-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 994 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 4 | 0
1976-01-14 | 1900-01-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.85 | A | 7 | 994 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 4 | 0
1976-01-14 | 1900-01-13 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.85 | A | 7 | 995 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.7 | 4 | 0
1976-01-14 | 1900-01-13 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.85 | A | 7 | 996 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 4 | 0
1976-01-14 | 1900-01-13 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 997 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 4 | 0
1976-01-14 | 1900-01-13 | 9:00 | 9 | 90 | 1261 | 27 | 1 | 13 | 8 | 1 | 9 | 26 | 1 | 13 | 29 | 1 | 13 | 5 | 1 | 9 | 29 | 1 | 13 | 62 | 1 | 21 | 8 | A | 7 | 8 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 998 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 400 | A | 7 | 0.6 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 4 | 0
1976-01-14 | 1900-01-13 | 10:00 | 10 | 308 | 1414 | 118 | 1 | 13 | 177 | 1 | 13 | 79 | 1 | 13 | 125 | 1 | 13 | 139 | 1 | 13 | 94 | 1 | 13 | 151 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.85 | A | 7 | 999 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 4 | 0
1976-01-14 | 1900-01-13 | 11:00 | 11 | 489 | 1414 | 292 | 1 | 9 | 589 | 1 | 9 | 88 | 1 | 13 | 302 | 1 | 9 | 539 | 1 | 9 | 115 | 1 | 13 | 166 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.85 | A | 7 | 1000 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.7 | 4 | 0
1976-01-14 | 1900-01-13 | 12:00 | 12 | 614 | 1414 | 400 | 1 | 9 | 677 | 1 | 9 | 105 | 1 | 13 | 417 | 1 | 9 | 652 | 1 | 9 | 133 | 1 | 13 | 211 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.78 | A | 7 | 1000 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 4 | 0
1976-01-14 | 1900-01-13 | 13:00 | 13 | 676 | 1414 | 451 | 1 | 9 | 706 | 1 | 9 | 113 | 1 | 13 | 473 | 1 | 9 | 691 | 1 | 9 | 141 | 1 | 13 | 236 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.72 | A | 7 | 999 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 4 | 0
1976-01-14 | 1900-01-13 | 14:00 | 14 | 669 | 1414 | 449 | 1 | 9 | 713 | 1 | 9 | 112 | 1 | 13 | 472 | 1 | 9 | 697 | 1 | 9 | 140 | 1 | 13 | 233 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.63 | A | 7 | 999 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.66 | 4 | 0
1976-01-14 | 1900-01-13 | 15:00 | 15 | 595 | 1414 | 381 | 1 | 9 | 665 | 1 | 9 | 102 | 1 | 13 | 399 | 1 | 9 | 637 | 1 | 9 | 130 | 1 | 13 | 203 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -10.6 | 12.92 | A | 7 | 0.53 | A | 7 | 999 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.44 | 4 | 0
1976-01-14 | 1900-01-13 | 16:00 | 16 | 457 | 1414 | 263 | 1 | 9 | 558 | 1 | 9 | 83 | 1 | 13 | 273 | 1 | 9 | 502 | 1 | 9 | 110 | 1 | 13 | 155 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -10.6 | 12.92 | A | 7 | 0.53 | A | 7 | 999 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.44 | 4 | 0
1976-01-14 | 1900-01-13 | 17:00 | 17 | 267 | 1414 | 120 | 1 | 13 | 342 | 1 | 9 | 56 | 1 | 13 | 127 | 1 | 13 | 251 | 1 | 9 | 80 | 1 | 13 | 101 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -10 | 14 | A | 7 | 0.56 | A | 7 | 999 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.74 | 4 | 0
1976-01-14 | 1900-01-13 | 18:00 | 18 | 54 | 978 | 22 | 1 | 13 | 35 | 1 | 9 | 19 | 1 | 13 | 23 | 1 | 13 | 15 | 1 | 9 | 22 | 1 | 13 | 39 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -10 | 14 | A | 7 | 0.6 | A | 7 | 999 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.16 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.36 | 4 | 0
1976-01-14 | 1900-01-13 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -10 | 14 | A | 7 | 0.63 | A | 7 | 999 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.68 | 4 | 0
1976-01-14 | 1900-01-13 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -9.4 | 15.08 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.28 | 4 | 0
1976-01-14 | 1900-01-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 998 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 4 | 0
1976-01-14 | 1900-01-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 998 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 4 | 0
1976-01-14 | 1900-01-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 998 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 4 | 0
1976-01-14 | 1900-01-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.85 | A | 7 | 998 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.075 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 4 | 0
1976-01-15 | 1900-01-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.85 | A | 7 | 998 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 5 | 0
1976-01-15 | 1900-01-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.85 | A | 7 | 998 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 5 | 0
1976-01-15 | 1900-01-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -8.3 | 17.06 | A | 7 | 0.88 | A | 7 | 998 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.04 | 5 | 0
1976-01-15 | 1900-01-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.92 | A | 7 | 997 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.46 | 5 | 0
1976-01-15 | 1900-01-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -8.9 | 15.98 | A | 7 | 0.92 | A | 7 | 997 | A | 7 | 200 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.36 | 5 | 0
1976-01-15 | 1900-01-14 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.92 | A | 7 | 996 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.46 | 5 | 0
1976-01-15 | 1900-01-14 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -9.4 | 15.08 | A | 7 | 0.92 | A | 7 | 996 | A | 7 | 200 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.46 | 5 | 0
1976-01-15 | 1900-01-14 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 3 | A | 7 | -7.2 | 19.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.88 | A | 7 | 996 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.14 | 5 | 0
1976-01-15 | 1900-01-14 | 9:00 | 9 | 91 | 1261 | 36 | 1 | 13 | 29 | 1 | 13 | 34 | 1 | 13 | 40 | 1 | 13 | 17 | 1 | 13 | 38 | 1 | 13 | 76 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | -6.1 | 21.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.96 | A | 7 | 996 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.62 | 5 | 0
1976-01-15 | 1900-01-14 | 10:00 | 10 | 310 | 1414 | 102 | 1 | 13 | 26 | 1 | 9 | 97 | 1 | 13 | 112 | 1 | 13 | 22 | 1 | 9 | 107 | 1 | 13 | 234 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -4.4 | 24.08 | A | 7 | -5.6 | 21.92 | A | 7 | 0.92 | A | 7 | 995 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.38 | 5 | 0
1976-01-15 | 1900-01-14 | 11:00 | 11 | 491 | 1414 | 175 | 1 | 9 | 46 | 1 | 9 | 159 | 1 | 13 | 192 | 1 | 9 | 43 | 1 | 9 | 176 | 1 | 13 | 417 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5 | 23 | A | 7 | 0.85 | A | 7 | 995 | A | 7 | 180 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 5 | 0
1976-01-15 | 1900-01-14 | 12:00 | 12 | 617 | 1414 | 177 | 1 | 9 | 6 | 1 | 9 | 174 | 1 | 13 | 200 | 1 | 9 | 5 | 1 | 9 | 198 | 1 | 13 | 667 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 994 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.22 | 5 | 0
1976-01-15 | 1900-01-14 | 13:00 | 13 | 680 | 1414 | 277 | 1 | 9 | 180 | 1 | 9 | 190 | 1 | 13 | 303 | 1 | 9 | 184 | 1 | 9 | 215 | 1 | 13 | 467 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -0.6 | 30.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.82 | A | 7 | 991 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.02 | 5 | 0
1976-01-15 | 1900-01-14 | 14:00 | 14 | 673 | 1414 | 241 | 1 | 9 | 53 | 1 | 9 | 216 | 1 | 13 | 265 | 1 | 9 | 53 | 1 | 9 | 240 | 1 | 13 | 626 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.75 | A | 7 | 988 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.28 | 5 | 0
1976-01-15 | 1900-01-14 | 15:00 | 15 | 599 | 1414 | 319 | 1 | 13 | 390 | 1 | 13 | 154 | 1 | 13 | 334 | 1 | 13 | 379 | 1 | 13 | 173 | 1 | 13 | 309 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 1.7 | 35.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 986 | A | 7 | 180 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.06 | 5 | 0
1976-01-15 | 1900-01-14 | 16:00 | 16 | 462 | 1414 | 142 | 1 | 9 | 39 | 1 | 9 | 129 | 1 | 13 | 155 | 1 | 9 | 36 | 1 | 9 | 144 | 1 | 13 | 346 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -3.3 | 26.06 | A | 7 | 0.67 | A | 7 | 984 | A | 7 | 170 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.86 | 5 | 0
1976-01-15 | 1900-01-14 | 17:00 | 17 | 272 | 1414 | 82 | 1 | 13 | 19 | 1 | 9 | 79 | 1 | 13 | 91 | 1 | 13 | 7 | 1 | 9 | 90 | 1 | 13 | 255 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 180 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.44 | 5 | 0
1976-01-15 | 1900-01-14 | 18:00 | 18 | 57 | 1002 | 15 | 1 | 13 | 3 | 1 | 9 | 15 | 1 | 13 | 17 | 1 | 13 | 0 | 1 | 9 | 17 | 1 | 13 | 53 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.44 | 5 | 0
1976-01-15 | 1900-01-14 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.65 | A | 7 | 982 | A | 7 | 230 | A | 7 | 11.3 | A | 7 | 24100 | A | 7 | 670 | A | 7 | 0.9 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.74 | 5 | 0
1976-01-15 | 1900-01-14 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.89 | A | 7 | 982 | A | 7 | 220 | A | 7 | 8.2 | A | 7 | 9700 | A | 7 | 310 | A | 7 | 1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 5 | 0
1976-01-15 | 1900-01-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 6400 | A | 7 | 370 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 5 | 0
1976-01-15 | 1900-01-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 270 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 5 | 0
1976-01-15 | 1900-01-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0.6 | 33.08 | A | 7 | 1 | A | 7 | 981 | A | 7 | 190 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 340 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.98 | 5 | 0
1976-01-15 | 1900-01-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0.6 | 33.08 | A | 7 | 1 | A | 7 | 980 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 210 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.98 | 5 | 0
1976-01-16 | 1900-01-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 200 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 460 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.48 | 6 | 0
1976-01-16 | 1900-01-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 270 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.48 | 6 | 0
1976-01-16 | 1900-01-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.92 | A | 7 | 979 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1130 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.16 | 6 | 0
1976-01-16 | 1900-01-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.89 | A | 7 | 979 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.66 | 6 | 0
1976-01-16 | 1900-01-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 0.6 | 33.08 | A | 7 | 0.92 | A | 7 | 979 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 640 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.16 | 6 | 0
1976-01-16 | 1900-01-15 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 520 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.48 | 6 | 0
1976-01-16 | 1900-01-15 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0.6 | 33.08 | A | 7 | 1 | A | 7 | 979 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.98 | 6 | 0
1976-01-16 | 1900-01-15 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 6 | 0
1976-01-16 | 1900-01-15 | 9:00 | 9 | 92 | 1284 | 29 | 1 | 13 | 2 | 1 | 9 | 29 | 1 | 13 | 32 | 1 | 13 | 0 | 1 | 9 | 32 | 1 | 13 | 91 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 982 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 400 | A | 7 | 1 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.1 | 6 | 0
1976-01-16 | 1900-01-15 | 10:00 | 10 | 312 | 1414 | 86 | 1 | 13 | 2 | 1 | 9 | 85 | 1 | 13 | 95 | 1 | 13 | 1 | 1 | 9 | 95 | 1 | 13 | 287 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 983 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 6400 | A | 7 | 340 | A | 7 | 1 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 6 | 0
1976-01-16 | 1900-01-15 | 11:00 | 11 | 494 | 1414 | 144 | 1 | 9 | 5 | 1 | 9 | 142 | 1 | 13 | 161 | 1 | 9 | 4 | 1 | 9 | 160 | 1 | 13 | 512 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.96 | A | 7 | 984 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 370 | A | 7 | 1 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.62 | 6 | 0
1976-01-16 | 1900-01-15 | 12:00 | 12 | 621 | 1414 | 229 | 1 | 9 | 6 | 1 | 9 | 227 | 1 | 13 | 254 | 1 | 9 | 5 | 1 | 9 | 252 | 1 | 13 | 783 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 340 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 6 | 0
1976-01-16 | 1900-01-15 | 13:00 | 13 | 683 | 1414 | 238 | 1 | 9 | 1 | 1 | 9 | 237 | 1 | 13 | 265 | 1 | 9 | 1 | 1 | 9 | 265 | 1 | 13 | 862 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 984 | A | 7 | 330 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 460 | A | 7 | 0.9 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 6 | 0
1976-01-16 | 1900-01-15 | 14:00 | 14 | 677 | 1414 | 228 | 1 | 9 | 1 | 1 | 9 | 228 | 1 | 13 | 256 | 1 | 9 | 1 | 1 | 9 | 255 | 1 | 13 | 838 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.78 | A | 7 | 984 | A | 7 | 330 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.62 | 6 | 0
1976-01-16 | 1900-01-15 | 15:00 | 15 | 603 | 1414 | 270 | 1 | 9 | 133 | 1 | 9 | 213 | 1 | 13 | 291 | 1 | 9 | 132 | 1 | 9 | 234 | 1 | 13 | 507 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | -1.1 | 30.02 | A | 7 | -5 | 23 | A | 7 | 0.75 | A | 7 | 985 | A | 7 | 320 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.42 | 6 | 0
1976-01-16 | 1900-01-15 | 16:00 | 16 | 467 | 1414 | 175 | 1 | 13 | 124 | 1 | 13 | 134 | 1 | 13 | 190 | 1 | 13 | 116 | 1 | 13 | 152 | 1 | 13 | 304 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 985 | A | 7 | 340 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.74 | 6 | 0
1976-01-16 | 1900-01-15 | 17:00 | 17 | 277 | 1414 | 125 | 1 | 13 | 286 | 1 | 13 | 70 | 1 | 13 | 130 | 1 | 13 | 212 | 1 | 13 | 88 | 1 | 13 | 129 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.78 | A | 7 | 987 | A | 7 | 340 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.06 | 6 | 0
1976-01-16 | 1900-01-15 | 18:00 | 18 | 60 | 1025 | 34 | 1 | 13 | 159 | 1 | 9 | 18 | 1 | 13 | 29 | 1 | 13 | 72 | 1 | 9 | 24 | 1 | 13 | 32 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.78 | A | 7 | 988 | A | 7 | 320 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.046 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 6 | 0
1976-01-16 | 1900-01-15 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -10.6 | 12.92 | A | 7 | 0.74 | A | 7 | 989 | A | 7 | 330 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.94 | 6 | 0
1976-01-16 | 1900-01-15 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 990 | A | 7 | 330 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 6 | 0
1976-01-16 | 1900-01-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.77 | A | 7 | 991 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.46 | 6 | 0
1976-01-16 | 1900-01-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.81 | A | 7 | 991 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.68 | 6 | 0
1976-01-16 | 1900-01-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | -9.4 | 15.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.8 | A | 7 | 991 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 6 | 0
1976-01-16 | 1900-01-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -9.4 | 15.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.8 | A | 7 | 991 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 6 | 0
1976-01-17 | 1900-01-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -13.3 | 8.06 | A | 7 | 0.77 | A | 7 | 991 | A | 7 | 330 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.6 | 7 | 0
1976-01-17 | 1900-01-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -10.6 | 12.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.84 | A | 7 | 991 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.92 | 7 | 0
1976-01-17 | 1900-01-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.84 | A | 7 | 992 | A | 7 | 330 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.12 | 7 | 0
1976-01-17 | 1900-01-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -11.1 | 12.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.84 | A | 7 | 992 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.12 | 7 | 0
1976-01-17 | 1900-01-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.88 | A | 7 | 993 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.24 | 7 | 0
1976-01-17 | 1900-01-16 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -11.7 | 10.94 | A | 7 | -13.9 | 6.98 | A | 7 | 0.84 | A | 7 | 993 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.04 | 7 | 0
1976-01-17 | 1900-01-16 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -14.4 | 6.08 | A | 7 | 0.84 | A | 7 | 993 | A | 7 | 360 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 7 | 0
1976-01-17 | 1900-01-16 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | -11.7 | 10.94 | A | 7 | -13.9 | 6.98 | A | 7 | 0.84 | A | 7 | 994 | A | 7 | 360 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 1490 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.04 | 7 | 0
1976-01-17 | 1900-01-16 | 9:00 | 9 | 94 | 1284 | 19 | 1 | 13 | 12 | 1 | 13 | 18 | 1 | 13 | 21 | 1 | 13 | 7 | 1 | 13 | 20 | 1 | 13 | 45 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | -10.6 | 12.92 | A | 7 | -13.3 | 8.06 | A | 7 | 0.8 | A | 7 | 995 | A | 7 | 10 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 1490 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.72 | 7 | 0
1976-01-17 | 1900-01-16 | 10:00 | 10 | 315 | 1414 | 152 | 1 | 13 | 370 | 1 | 9 | 69 | 1 | 13 | 159 | 1 | 13 | 292 | 1 | 9 | 94 | 1 | 13 | 125 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | -9.4 | 15.08 | A | 7 | -15 | 5 | A | 7 | 0.64 | A | 7 | 995 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.78 | 7 | 0
1976-01-17 | 1900-01-16 | 11:00 | 11 | 497 | 1414 | 300 | 1 | 9 | 604 | 1 | 9 | 87 | 1 | 13 | 311 | 1 | 9 | 556 | 1 | 9 | 115 | 1 | 13 | 166 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -14.4 | 6.08 | A | 7 | 0.59 | A | 7 | 996 | A | 7 | 20 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 7 | 0
1976-01-17 | 1900-01-16 | 12:00 | 12 | 624 | 1414 | 412 | 1 | 9 | 698 | 1 | 9 | 103 | 1 | 13 | 431 | 1 | 9 | 675 | 1 | 9 | 132 | 1 | 13 | 209 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.6 | A | 7 | 996 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.94 | 7 | 0
1976-01-17 | 1900-01-16 | 13:00 | 13 | 687 | 1414 | 468 | 1 | 9 | 734 | 1 | 9 | 111 | 1 | 13 | 493 | 1 | 9 | 722 | 1 | 9 | 140 | 1 | 13 | 234 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -15 | 5 | A | 7 | 0.5 | A | 7 | 995 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.12 | 7 | 0
1976-01-17 | 1900-01-16 | 14:00 | 14 | 682 | 1414 | 444 | 1 | 9 | 695 | 1 | 9 | 108 | 1 | 13 | 467 | 1 | 9 | 683 | 1 | 9 | 136 | 1 | 13 | 228 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | -6.1 | 21.02 | A | 7 | -13.9 | 6.98 | A | 7 | 0.55 | A | 7 | 994 | A | 7 | 20 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.52 | 7 | 0
1976-01-17 | 1900-01-16 | 15:00 | 15 | 608 | 1414 | 380 | 1 | 9 | 638 | 1 | 9 | 106 | 1 | 13 | 397 | 1 | 9 | 613 | 1 | 9 | 132 | 1 | 13 | 212 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | -6.1 | 21.02 | A | 7 | -14.4 | 6.08 | A | 7 | 0.52 | A | 7 | 994 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.22 | 7 | 0
1976-01-17 | 1900-01-16 | 16:00 | 16 | 471 | 1414 | 266 | 1 | 9 | 499 | 1 | 9 | 101 | 1 | 13 | 284 | 1 | 9 | 457 | 1 | 9 | 130 | 1 | 13 | 190 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -6.7 | 19.94 | A | 7 | -15 | 5 | A | 7 | 0.52 | A | 7 | 995 | A | 7 | 40 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.34 | 7 | 0
1976-01-17 | 1900-01-16 | 17:00 | 17 | 281 | 1414 | 118 | 1 | 13 | 224 | 1 | 9 | 74 | 1 | 13 | 125 | 1 | 13 | 168 | 1 | 9 | 92 | 1 | 13 | 142 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | -6.7 | 19.94 | A | 7 | -14.4 | 6.08 | A | 7 | 0.54 | A | 7 | 996 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.44 | 7 | 0
1976-01-17 | 1900-01-16 | 18:00 | 18 | 64 | 1048 | 20 | 1 | 13 | 31 | 1 | 9 | 17 | 1 | 13 | 21 | 1 | 13 | 14 | 1 | 9 | 20 | 1 | 13 | 35 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | -8.9 | 15.98 | A | 7 | -15 | 5 | A | 7 | 0.62 | A | 7 | 996 | A | 7 | 350 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.152 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.48 | 7 | 0
1976-01-17 | 1900-01-16 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -8.9 | 15.98 | A | 7 | -13.9 | 6.98 | A | 7 | 0.67 | A | 7 | 996 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 980 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 7 | 0
1976-01-17 | 1900-01-16 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 6 | A | 7 | -8.9 | 15.98 | A | 7 | -13.9 | 6.98 | A | 7 | 0.67 | A | 7 | 997 | A | 7 | 360 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 1040 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.78 | 7 | 0
1976-01-17 | 1900-01-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -13.9 | 6.98 | A | 7 | 0.65 | A | 7 | 997 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 940 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.66 | 7 | 0
1976-01-17 | 1900-01-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -13.3 | 8.06 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 820 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.86 | 7 | 0
1976-01-17 | 1900-01-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -9.4 | 15.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.84 | A | 7 | 998 | A | 7 | 300 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 940 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 7 | 0
1976-01-17 | 1900-01-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -10.6 | 12.92 | A | 7 | -12.8 | 8.96 | A | 7 | 0.84 | A | 7 | 998 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.92 | 7 | 0
1976-01-18 | 1900-01-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.88 | A | 7 | 998 | A | 7 | 290 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.24 | 1 | 0
1976-01-18 | 1900-01-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -13.9 | 6.98 | A | 7 | 0.84 | A | 7 | 999 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.04 | 1 | 0
1976-01-18 | 1900-01-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -14.4 | 6.08 | A | 7 | 0.84 | A | 7 | 999 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 1 | 0
1976-01-18 | 1900-01-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -14.4 | 6.08 | A | 7 | 0.87 | A | 7 | 1000 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.26 | 1 | 0
1976-01-18 | 1900-01-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -15 | 5 | A | 7 | 0.84 | A | 7 | 1000 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.16 | 1 | 0
1976-01-18 | 1900-01-17 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 1001 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.36 | 1 | 0
1976-01-18 | 1900-01-17 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 1002 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.36 | 1 | 0
1976-01-18 | 1900-01-17 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 1 | A | 7 | -13.3 | 8.06 | A | 7 | -15 | 5 | A | 7 | 0.87 | A | 7 | 1002 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.36 | 1 | 0
1976-01-18 | 1900-01-17 | 9:00 | 9 | 96 | 1284 | 41 | 1 | 13 | 155 | 1 | 9 | 27 | 1 | 13 | 41 | 1 | 13 | 69 | 1 | 9 | 35 | 1 | 13 | 48 | 1 | 21 | 4 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -14.4 | 6.08 | A | 7 | 0.84 | A | 7 | 1003 | A | 7 | 270 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 1 | 0
1976-01-18 | 1900-01-17 | 10:00 | 10 | 317 | 1413 | 174 | 1 | 13 | 547 | 1 | 9 | 51 | 1 | 13 | 181 | 1 | 13 | 441 | 1 | 9 | 81 | 1 | 13 | 94 | 1 | 21 | 1 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -12.2 | 10.04 | A | 7 | 0.84 | A | 7 | 1004 | A | 7 | 0 | A | 7 | 0 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13 | 1 | 0
1976-01-18 | 1900-01-17 | 11:00 | 11 | 500 | 1413 | 322 | 1 | 9 | 718 | 1 | 9 | 66 | 1 | 13 | 331 | 1 | 9 | 664 | 1 | 9 | 95 | 1 | 13 | 130 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -8.3 | 17.06 | A | 7 | -10.6 | 12.92 | A | 7 | 0.84 | A | 7 | 1004 | A | 7 | 90 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 1 | 0
1976-01-18 | 1900-01-17 | 12:00 | 12 | 628 | 1413 | 412 | 1 | 9 | 744 | 1 | 9 | 81 | 1 | 13 | 429 | 1 | 9 | 717 | 1 | 9 | 109 | 1 | 13 | 165 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 1004 | A | 7 | 180 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 1 | 0
1976-01-18 | 1900-01-17 | 13:00 | 13 | 691 | 1413 | 311 | 1 | 13 | 306 | 1 | 13 | 161 | 1 | 13 | 338 | 1 | 13 | 317 | 1 | 13 | 183 | 1 | 13 | 347 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 1003 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 1 | 0
1976-01-18 | 1900-01-17 | 14:00 | 14 | 686 | 1413 | 366 | 1 | 13 | 497 | 1 | 13 | 125 | 1 | 13 | 399 | 1 | 13 | 497 | 1 | 13 | 156 | 1 | 13 | 254 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | -5.6 | 21.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.62 | A | 7 | 1002 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 1 | 0
1976-01-18 | 1900-01-17 | 15:00 | 15 | 613 | 1413 | 405 | 1 | 9 | 746 | 1 | 9 | 82 | 1 | 13 | 420 | 1 | 9 | 715 | 1 | 9 | 109 | 1 | 13 | 163 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | -4.4 | 24.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.58 | A | 7 | 1003 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.48 | 1 | 0
1976-01-18 | 1900-01-17 | 16:00 | 16 | 476 | 1413 | 298 | 1 | 9 | 698 | 1 | 9 | 64 | 1 | 13 | 309 | 1 | 9 | 639 | 1 | 9 | 93 | 1 | 13 | 124 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.55 | A | 7 | 1002 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 1 | 0
1976-01-18 | 1900-01-17 | 17:00 | 17 | 286 | 1413 | 137 | 1 | 13 | 426 | 1 | 9 | 52 | 1 | 13 | 142 | 1 | 13 | 328 | 1 | 9 | 76 | 1 | 13 | 94 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | -3.9 | 24.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.55 | A | 7 | 1003 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 1 | 0
1976-01-18 | 1900-01-17 | 18:00 | 18 | 67 | 1095 | 29 | 1 | 13 | 46 | 1 | 9 | 24 | 1 | 13 | 30 | 1 | 13 | 20 | 1 | 9 | 28 | 1 | 13 | 50 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | -6.1 | 21.02 | A | 7 | -11.7 | 10.94 | A | 7 | 0.65 | A | 7 | 1002 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.32 | 1 | 0
1976-01-18 | 1900-01-17 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | -6.1 | 21.02 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 1002 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.52 | 1 | 0
1976-01-18 | 1900-01-17 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | -6.1 | 21.02 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 1002 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.52 | 1 | 0
1976-01-18 | 1900-01-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 1001 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.54 | 1 | 0
1976-01-18 | 1900-01-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 1001 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.54 | 1 | 0
1976-01-18 | 1900-01-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 1001 | A | 7 | 150 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.94 | 1 | 0
1976-01-18 | 1900-01-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 1000 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.076 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.94 | 1 | 0
1976-01-19 | 1900-01-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 1000 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.16 | 2 | 0
1976-01-19 | 1900-01-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 999 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.16 | 2 | 0
1976-01-19 | 1900-01-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 999 | A | 7 | 170 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 2 | 0
1976-01-19 | 1900-01-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 998 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.74 | 2 | 0
1976-01-19 | 1900-01-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 998 | A | 7 | 180 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.5 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 2 | 0
1976-01-19 | 1900-01-18 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 997 | A | 7 | 160 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.5 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 2 | 0
1976-01-19 | 1900-01-18 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 996 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 3350 | A | 7 | 0.5 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 2 | 0
1976-01-19 | 1900-01-18 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -11.7 | 10.94 | A | 7 | 0.6 | A | 7 | 996 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 2290 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.7 | 2 | 0
1976-01-19 | 1900-01-18 | 9:00 | 9 | 98 | 1307 | 17 | 1 | 13 | 0 | 1 | 9 | 17 | 1 | 13 | 20 | 1 | 13 | 0 | 1 | 9 | 20 | 1 | 13 | 62 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -9.4 | 15.08 | A | 7 | 0.66 | A | 7 | 996 | A | 7 | 170 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 0.6 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.98 | 2 | 0
1976-01-19 | 1900-01-18 | 10:00 | 10 | 320 | 1413 | 61 | 1 | 13 | 9 | 1 | 9 | 59 | 1 | 13 | 70 | 1 | 13 | 3 | 1 | 9 | 69 | 1 | 13 | 224 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.66 | A | 7 | 995 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 980 | A | 7 | 0.6 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.96 | 2 | 0
1976-01-19 | 1900-01-18 | 11:00 | 11 | 503 | 1413 | 88 | 1 | 9 | 10 | 1 | 9 | 85 | 1 | 13 | 103 | 1 | 9 | 6 | 1 | 9 | 101 | 1 | 13 | 355 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -7.2 | 19.04 | A | 7 | 0.75 | A | 7 | 995 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 790 | A | 7 | 0.7 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 2 | 0
1976-01-19 | 1900-01-18 | 12:00 | 12 | 631 | 1413 | 168 | 1 | 9 | 8 | 1 | 9 | 164 | 1 | 13 | 191 | 1 | 9 | 6 | 1 | 9 | 188 | 1 | 13 | 650 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.78 | A | 7 | 994 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 730 | A | 7 | 0.8 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 2 | 0
1976-01-19 | 1900-01-18 | 13:00 | 13 | 695 | 1413 | 177 | 1 | 9 | 2 | 1 | 9 | 177 | 1 | 13 | 204 | 1 | 9 | 2 | 1 | 9 | 203 | 1 | 13 | 724 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.78 | A | 7 | 993 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 760 | A | 7 | 0.8 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.72 | 2 | 0
1976-01-19 | 1900-01-18 | 14:00 | 14 | 690 | 1413 | 242 | 1 | 9 | 8 | 1 | 9 | 239 | 1 | 13 | 271 | 1 | 9 | 7 | 1 | 9 | 268 | 1 | 13 | 873 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -3.3 | 26.06 | A | 7 | 0.82 | A | 7 | 992 | A | 7 | 200 | A | 7 | 8.8 | A | 7 | 3200 | A | 7 | 730 | A | 7 | 0.9 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.02 | 2 | 0
1976-01-19 | 1900-01-18 | 15:00 | 15 | 617 | 1413 | 194 | 1 | 9 | 4 | 1 | 9 | 192 | 1 | 13 | 217 | 1 | 9 | 3 | 1 | 9 | 216 | 1 | 13 | 710 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 992 | A | 7 | 210 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 700 | A | 7 | 0.9 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 2 | 0
1976-01-19 | 1900-01-18 | 16:00 | 16 | 481 | 1413 | 152 | 1 | 9 | 2 | 1 | 9 | 151 | 1 | 13 | 168 | 1 | 9 | 1 | 1 | 9 | 168 | 1 | 13 | 523 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 992 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 0.9 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 2 | 0
1976-01-19 | 1900-01-18 | 17:00 | 17 | 291 | 1413 | 77 | 1 | 13 | 2 | 1 | 9 | 76 | 1 | 13 | 85 | 1 | 13 | 1 | 1 | 9 | 85 | 1 | 13 | 258 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.85 | A | 7 | 993 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 520 | A | 7 | 1 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.38 | 2 | 0
1976-01-19 | 1900-01-18 | 18:00 | 18 | 71 | 1119 | 22 | 1 | 13 | 0 | 1 | 9 | 22 | 1 | 13 | 25 | 1 | 13 | 0 | 1 | 9 | 25 | 1 | 13 | 73 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.89 | A | 7 | 993 | A | 7 | 220 | A | 7 | 5.7 | A | 7 | 4000 | A | 7 | 550 | A | 7 | 1 | E | 8 | 0.067 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.8 | 2 | 0
1976-01-19 | 1900-01-18 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 993 | A | 7 | 230 | A | 7 | 8.2 | A | 7 | 2400 | A | 7 | 180 | A | 7 | 1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 2 | 0
1976-01-19 | 1900-01-18 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 993 | A | 7 | 230 | A | 7 | 4.6 | A | 7 | 2000 | A | 7 | 180 | A | 7 | 1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 2 | 0
1976-01-19 | 1900-01-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 994 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 1600 | A | 7 | 150 | A | 7 | 1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 2 | 0
1976-01-19 | 1900-01-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 994 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 3200 | A | 7 | 150 | A | 7 | 1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 2 | 0
1976-01-19 | 1900-01-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 994 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 2 | 0
1976-01-19 | 1900-01-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | 0 | 32 | A | 7 | 1 | A | 7 | 994 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 910 | A | 7 | 1.1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.9 | 2 | 0
1976-01-20 | 1900-01-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 994 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 9700 | A | 7 | 3350 | A | 7 | 1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 3 | 0
1976-01-20 | 1900-01-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 994 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 240 | A | 7 | 1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 3 | 0
1976-01-20 | 1900-01-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 994 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 310 | A | 7 | 1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 3 | 0
1976-01-20 | 1900-01-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 994 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 310 | A | 7 | 1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 3 | 0
1976-01-20 | 1900-01-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.96 | A | 7 | 994 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 240 | A | 7 | 1 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.42 | 3 | 0
1976-01-20 | 1900-01-19 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 994 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 730 | A | 7 | 0.9 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 3 | 0
1976-01-20 | 1900-01-19 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 995 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 910 | A | 7 | 0.8 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.74 | 3 | 0
1976-01-20 | 1900-01-19 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.88 | A | 7 | 996 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 940 | A | 7 | 0.8 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.88 | 3 | 0
1976-01-20 | 1900-01-19 | 9:00 | 9 | 100 | 1307 | 28 | 1 | 13 | 0 | 1 | 9 | 28 | 1 | 13 | 31 | 1 | 13 | 0 | 1 | 9 | 31 | 1 | 13 | 91 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.88 | A | 7 | 997 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.14 | 3 | 0
1976-01-20 | 1900-01-19 | 10:00 | 10 | 323 | 1413 | 145 | 1 | 13 | 223 | 1 | 13 | 93 | 1 | 13 | 151 | 1 | 13 | 179 | 1 | 13 | 110 | 1 | 13 | 183 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.77 | A | 7 | 998 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.46 | 3 | 0
1976-01-20 | 1900-01-19 | 11:00 | 11 | 507 | 1413 | 298 | 1 | 9 | 568 | 1 | 9 | 94 | 1 | 13 | 308 | 1 | 9 | 523 | 1 | 9 | 120 | 1 | 13 | 178 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -8.9 | 15.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.81 | A | 7 | 999 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.68 | 3 | 0
1976-01-20 | 1900-01-19 | 12:00 | 12 | 635 | 1413 | 473 | 1 | 13 | 743 | 1 | 13 | 138 | 1 | 13 | 485 | 1 | 13 | 710 | 1 | 13 | 165 | 1 | 13 | 268 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.77 | A | 7 | 999 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.46 | 3 | 0
1976-01-20 | 1900-01-19 | 13:00 | 13 | 699 | 1413 | 447 | 1 | 13 | 453 | 1 | 13 | 222 | 1 | 13 | 475 | 1 | 13 | 468 | 1 | 13 | 242 | 1 | 13 | 510 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | -8.3 | 17.06 | A | 7 | -11.7 | 10.94 | A | 7 | 0.77 | A | 7 | 998 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 610 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.46 | 3 | 0
1976-01-20 | 1900-01-19 | 14:00 | 14 | 695 | 1413 | 422 | 1 | 13 | 294 | 1 | 13 | 277 | 1 | 13 | 452 | 1 | 13 | 298 | 1 | 13 | 305 | 1 | 13 | 687 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 997 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.16 | 3 | 0
1976-01-20 | 1900-01-19 | 15:00 | 15 | 622 | 1413 | 215 | 1 | 9 | 23 | 1 | 9 | 205 | 1 | 13 | 240 | 1 | 9 | 20 | 1 | 9 | 232 | 1 | 13 | 742 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 997 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 700 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 3 | 0
1976-01-20 | 1900-01-19 | 16:00 | 16 | 486 | 1413 | 119 | 1 | 9 | 19 | 1 | 9 | 112 | 1 | 13 | 135 | 1 | 9 | 12 | 1 | 9 | 131 | 1 | 13 | 432 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 997 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 910 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 3 | 0
1976-01-20 | 1900-01-19 | 17:00 | 17 | 296 | 1413 | 80 | 1 | 13 | 12 | 1 | 9 | 78 | 1 | 13 | 90 | 1 | 13 | 5 | 1 | 9 | 89 | 1 | 13 | 264 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 997 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 1130 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 3 | 0
1976-01-20 | 1900-01-19 | 18:00 | 18 | 74 | 1142 | 17 | 1 | 13 | 0 | 1 | 9 | 17 | 1 | 13 | 19 | 1 | 13 | 0 | 1 | 9 | 19 | 1 | 13 | 60 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.81 | A | 7 | 997 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 12900 | A | 7 | 550 | A | 7 | 0.6 | E | 8 | 0.07 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 3 | 0
1976-01-20 | 1900-01-19 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.84 | A | 7 | 997 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 520 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 3 | 0
1976-01-20 | 1900-01-19 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.84 | A | 7 | 996 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 400 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 3 | 0
1976-01-20 | 1900-01-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -8.9 | 15.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.88 | A | 7 | 995 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 370 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.18 | 3 | 0
1976-01-20 | 1900-01-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -10.6 | 12.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.92 | A | 7 | 995 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.42 | 3 | 0
1976-01-20 | 1900-01-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.88 | A | 7 | 993 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 5490 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.28 | 3 | 0
1976-01-20 | 1900-01-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.9 | 15.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.88 | A | 7 | 992 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 3350 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.18 | 3 | 0
1976-01-21 | 1900-01-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.88 | A | 7 | 991 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.06 | 4 | 0
1976-01-21 | 1900-01-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -8.9 | 15.98 | A | 7 | 0.88 | A | 7 | 988 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.14 | 4 | 0
1976-01-21 | 1900-01-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 3200 | A | 7 | 210 | A | 7 | 0.7 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 4 | 0
1976-01-21 | 1900-01-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.96 | A | 7 | 985 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 1300 | A | 7 | 150 | A | 7 | 0.7 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.62 | 4 | 0
1976-01-21 | 1900-01-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.96 | A | 7 | 984 | A | 7 | 240 | A | 7 | 7.7 | A | 7 | 800 | A | 7 | 150 | A | 7 | 0.7 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.52 | 4 | 0
1976-01-21 | 1900-01-20 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -5.6 | 21.92 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 240 | A | 7 | 7.7 | A | 7 | 1600 | A | 7 | 240 | A | 7 | 0.8 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.6 | 4 | 0
1976-01-21 | 1900-01-20 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5 | 23 | A | 7 | 0.92 | A | 7 | 983 | A | 7 | 240 | A | 7 | 7.2 | A | 7 | 9700 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.28 | 4 | 0
1976-01-21 | 1900-01-20 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 280 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 340 | A | 7 | 0.8 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.66 | 4 | 0
1976-01-21 | 1900-01-20 | 9:00 | 9 | 102 | 1330 | 26 | 1 | 13 | 2 | 1 | 9 | 26 | 1 | 13 | 29 | 1 | 13 | 0 | 1 | 9 | 29 | 1 | 13 | 86 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.1 | 21.02 | A | 7 | 0.88 | A | 7 | 985 | A | 7 | 320 | A | 7 | 10.3 | A | 7 | 11300 | A | 7 | 550 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 4 | 0
1976-01-21 | 1900-01-20 | 10:00 | 10 | 326 | 1413 | 100 | 1 | 13 | 2 | 1 | 9 | 100 | 1 | 13 | 111 | 1 | 13 | 1 | 1 | 9 | 110 | 1 | 13 | 324 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 8000 | A | 7 | 730 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 4 | 0
1976-01-21 | 1900-01-20 | 11:00 | 11 | 510 | 1413 | 381 | 1 | 13 | 692 | 1 | 13 | 131 | 1 | 13 | 385 | 1 | 13 | 625 | 1 | 13 | 158 | 1 | 13 | 230 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.84 | A | 7 | 989 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.72 | 4 | 0
1976-01-21 | 1900-01-20 | 12:00 | 12 | 639 | 1413 | 453 | 1 | 9 | 737 | 1 | 9 | 119 | 1 | 13 | 471 | 1 | 9 | 712 | 1 | 9 | 147 | 1 | 13 | 239 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 4 | 0
1976-01-21 | 1900-01-20 | 13:00 | 13 | 704 | 1413 | 502 | 1 | 9 | 738 | 1 | 9 | 135 | 1 | 13 | 523 | 1 | 9 | 722 | 1 | 9 | 162 | 1 | 13 | 280 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.78 | A | 7 | 990 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 4 | 0
1976-01-21 | 1900-01-20 | 14:00 | 14 | 700 | 1413 | 271 | 1 | 9 | 77 | 1 | 9 | 233 | 1 | 13 | 298 | 1 | 9 | 77 | 1 | 9 | 259 | 1 | 13 | 679 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 4 | 0
1976-01-21 | 1900-01-20 | 15:00 | 15 | 627 | 1413 | 483 | 1 | 13 | 729 | 1 | 13 | 160 | 1 | 13 | 491 | 1 | 13 | 688 | 1 | 13 | 184 | 1 | 13 | 297 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -5 | 23 | A | 7 | -8.9 | 15.98 | A | 7 | 0.74 | A | 7 | 991 | A | 7 | 300 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.8 | 4 | 0
1976-01-21 | 1900-01-20 | 16:00 | 16 | 491 | 1413 | 225 | 1 | 9 | 59 | 1 | 9 | 205 | 1 | 13 | 246 | 1 | 9 | 56 | 1 | 9 | 227 | 1 | 13 | 496 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | -5.6 | 21.92 | A | 7 | -9.4 | 15.08 | A | 7 | 0.74 | A | 7 | 992 | A | 7 | 310 | A | 7 | 8.8 | A | 7 | 16100 | A | 7 | 700 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.82 | 4 | 0
1976-01-21 | 1900-01-20 | 17:00 | 17 | 301 | 1413 | 94 | 1 | 13 | 3 | 1 | 9 | 93 | 1 | 13 | 103 | 1 | 13 | 1 | 1 | 9 | 103 | 1 | 13 | 296 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 992 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 610 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 4 | 0
1976-01-21 | 1900-01-20 | 18:00 | 18 | 78 | 1165 | 18 | 1 | 13 | 1 | 1 | 9 | 18 | 1 | 13 | 21 | 1 | 13 | 0 | 1 | 9 | 21 | 1 | 13 | 63 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 992 | A | 7 | 300 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 640 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 4 | 0
1976-01-21 | 1900-01-20 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.84 | A | 7 | 993 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 640 | A | 7 | 0.7 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.72 | 4 | 0
1976-01-21 | 1900-01-20 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 993 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 520 | A | 7 | 0.7 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 4 | 0
1976-01-21 | 1900-01-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 7 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 993 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 550 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 4 | 0
1976-01-21 | 1900-01-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.84 | A | 7 | 992 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 4 | 0
1976-01-21 | 1900-01-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -7.2 | 19.04 | A | 7 | -9.4 | 15.08 | A | 7 | 0.84 | A | 7 | 992 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.6 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.84 | 4 | 0
1976-01-21 | 1900-01-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.84 | A | 7 | 991 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 2740 | A | 7 | 0.7 | E | 8 | 0.077 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.72 | 4 | 0
1976-01-22 | 1900-01-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 991 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.7 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 5 | 0
1976-01-22 | 1900-01-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 991 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 790 | A | 7 | 0.7 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 5 | 0
1976-01-22 | 1900-01-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.92 | A | 7 | 990 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 790 | A | 7 | 0.7 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.22 | 5 | 0
1976-01-22 | 1900-01-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.92 | A | 7 | 990 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 0.7 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.22 | 5 | 0
1976-01-22 | 1900-01-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 991 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 880 | A | 7 | 0.7 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22 | 5 | 0
1976-01-22 | 1900-01-21 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -6.7 | 19.94 | A | 7 | 0.88 | A | 7 | 991 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.7 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22 | 5 | 0
1976-01-22 | 1900-01-21 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 992 | A | 7 | 340 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.7 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 5 | 0
1976-01-22 | 1900-01-21 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 992 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 730 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 5 | 0
1976-01-22 | 1900-01-21 | 9:00 | 9 | 105 | 1353 | 28 | 1 | 13 | 0 | 1 | 9 | 28 | 1 | 13 | 31 | 1 | 13 | 0 | 1 | 9 | 31 | 1 | 13 | 91 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -6.7 | 19.94 | A | 7 | -10 | 14 | A | 7 | 0.77 | A | 7 | 993 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 760 | A | 7 | 0.6 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 5 | 0
1976-01-22 | 1900-01-21 | 10:00 | 10 | 329 | 1412 | 172 | 1 | 13 | 412 | 1 | 9 | 76 | 1 | 13 | 180 | 1 | 13 | 331 | 1 | 9 | 102 | 1 | 13 | 139 | 1 | 21 | 2 | A | 7 | 1 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 994 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 5 | 0
1976-01-22 | 1900-01-21 | 11:00 | 11 | 514 | 1412 | 340 | 1 | 9 | 631 | 1 | 9 | 110 | 1 | 13 | 348 | 1 | 9 | 579 | 1 | 9 | 136 | 1 | 13 | 203 | 1 | 18 | 4 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 994 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.54 | 5 | 0
1976-01-22 | 1900-01-21 | 12:00 | 12 | 643 | 1412 | 424 | 1 | 13 | 404 | 1 | 13 | 239 | 1 | 13 | 443 | 1 | 13 | 410 | 1 | 13 | 256 | 1 | 13 | 555 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | -5.6 | 21.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.6 | A | 7 | 994 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.72 | 5 | 0
1976-01-22 | 1900-01-21 | 13:00 | 13 | 708 | 1412 | 455 | 1 | 13 | 358 | 1 | 13 | 275 | 1 | 13 | 476 | 1 | 13 | 370 | 1 | 13 | 290 | 1 | 13 | 666 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | -5.6 | 21.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.62 | A | 7 | 993 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 3350 | A | 7 | 0.6 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.82 | 5 | 0
1976-01-22 | 1900-01-21 | 14:00 | 14 | 704 | 1412 | 494 | 1 | 13 | 538 | 1 | 13 | 226 | 1 | 13 | 508 | 1 | 13 | 536 | 1 | 13 | 239 | 1 | 13 | 494 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -5 | 23 | A | 7 | -11.7 | 10.94 | A | 7 | 0.6 | A | 7 | 993 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.7 | 5 | 0
1976-01-22 | 1900-01-21 | 15:00 | 15 | 632 | 1412 | 442 | 1 | 13 | 601 | 1 | 13 | 174 | 1 | 13 | 461 | 1 | 13 | 589 | 1 | 13 | 196 | 1 | 13 | 358 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | -4.4 | 24.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.63 | A | 7 | 992 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.88 | 5 | 0
1976-01-22 | 1900-01-21 | 16:00 | 16 | 496 | 1412 | 242 | 1 | 13 | 207 | 1 | 13 | 169 | 1 | 13 | 260 | 1 | 13 | 197 | 1 | 13 | 191 | 1 | 13 | 387 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | -4.4 | 24.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.63 | A | 7 | 992 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 3350 | A | 7 | 0.6 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.88 | 5 | 0
1976-01-22 | 1900-01-21 | 17:00 | 17 | 306 | 1412 | 125 | 1 | 13 | 245 | 1 | 13 | 73 | 1 | 13 | 134 | 1 | 13 | 192 | 1 | 13 | 93 | 1 | 13 | 138 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | -4.4 | 24.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.6 | A | 7 | 993 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.68 | 5 | 0
1976-01-22 | 1900-01-21 | 18:00 | 18 | 82 | 1189 | 25 | 1 | 13 | 19 | 1 | 13 | 23 | 1 | 13 | 27 | 1 | 13 | 11 | 1 | 13 | 26 | 1 | 13 | 55 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | -6.1 | 21.02 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 992 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 5490 | A | 7 | 0.6 | E | 8 | 0.119 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.52 | 5 | 0
1976-01-22 | 1900-01-21 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.74 | A | 7 | 992 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 5 | 0
1976-01-22 | 1900-01-21 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 9 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.74 | A | 7 | 992 | A | 7 | 330 | A | 7 | 1 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 5 | 0
1976-01-22 | 1900-01-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | -5.6 | 21.92 | A | 7 | -10.6 | 12.92 | A | 7 | 0.68 | A | 7 | 991 | A | 7 | 20 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 5 | 0
1976-01-22 | 1900-01-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 5 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 991 | A | 7 | 190 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 5 | 0
1976-01-22 | 1900-01-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 4 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 990 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 5 | 0
1976-01-22 | 1900-01-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -7.2 | 19.04 | A | 7 | -10.6 | 12.92 | A | 7 | 0.77 | A | 7 | 990 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 5 | 0
1976-01-23 | 1900-01-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 989 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 6 | 0
1976-01-23 | 1900-01-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.77 | A | 7 | 988 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.48 | 6 | 0
1976-01-23 | 1900-01-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -12.8 | 8.96 | A | 7 | 0.8 | A | 7 | 987 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.8 | 6 | 0
1976-01-23 | 1900-01-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.77 | A | 7 | 985 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.58 | 6 | 0
1976-01-23 | 1900-01-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 983 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 6 | 0
1976-01-23 | 1900-01-22 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 982 | A | 7 | 130 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 6 | 0
1976-01-23 | 1900-01-22 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.16 | 6 | 0
1976-01-23 | 1900-01-22 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 979 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 6 | 0
1976-01-23 | 1900-01-22 | 9:00 | 9 | 107 | 1353 | 50 | 1 | 13 | 327 | 1 | 9 | 21 | 1 | 13 | 48 | 1 | 13 | 188 | 1 | 9 | 32 | 1 | 13 | 38 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -10 | 14 | A | 7 | 0.77 | A | 7 | 978 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 6 | 0
1976-01-23 | 1900-01-22 | 10:00 | 10 | 332 | 1412 | 198 | 1 | 13 | 669 | 1 | 9 | 40 | 1 | 13 | 206 | 1 | 13 | 562 | 1 | 9 | 73 | 1 | 13 | 82 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 6 | 0
1976-01-23 | 1900-01-22 | 11:00 | 11 | 517 | 1412 | 354 | 1 | 9 | 818 | 1 | 9 | 54 | 1 | 13 | 373 | 1 | 9 | 764 | 1 | 9 | 92 | 1 | 13 | 118 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 150 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.06 | 6 | 0
1976-01-23 | 1900-01-22 | 12:00 | 12 | 647 | 1412 | 464 | 1 | 9 | 872 | 1 | 9 | 63 | 1 | 13 | 487 | 1 | 9 | 841 | 1 | 9 | 100 | 1 | 13 | 142 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 6 | 0
1976-01-23 | 1900-01-22 | 13:00 | 13 | 713 | 1412 | 524 | 1 | 9 | 901 | 1 | 9 | 68 | 1 | 13 | 549 | 1 | 9 | 879 | 1 | 9 | 104 | 1 | 13 | 154 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.65 | A | 7 | 974 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.28 | 6 | 0
1976-01-23 | 1900-01-22 | 14:00 | 14 | 709 | 1412 | 519 | 1 | 9 | 897 | 1 | 9 | 68 | 1 | 13 | 545 | 1 | 9 | 874 | 1 | 9 | 104 | 1 | 13 | 154 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | 0 | 32 | A | 7 | 0.63 | A | 7 | 973 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.76 | 6 | 0
1976-01-23 | 1900-01-22 | 15:00 | 15 | 637 | 1412 | 455 | 1 | 9 | 871 | 1 | 9 | 63 | 1 | 13 | 480 | 1 | 9 | 839 | 1 | 9 | 100 | 1 | 13 | 140 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 7.8 | 46.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.63 | A | 7 | 972 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.44 | 6 | 0
1976-01-23 | 1900-01-22 | 16:00 | 16 | 501 | 1412 | 334 | 1 | 9 | 797 | 1 | 9 | 52 | 1 | 13 | 353 | 1 | 9 | 740 | 1 | 9 | 89 | 1 | 13 | 115 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.66 | A | 7 | 972 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.74 | 6 | 0
1976-01-23 | 1900-01-22 | 17:00 | 17 | 311 | 1412 | 179 | 1 | 13 | 649 | 1 | 9 | 38 | 1 | 13 | 188 | 1 | 13 | 535 | 1 | 9 | 70 | 1 | 13 | 77 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 8.3 | 46.94 | A | 7 | 2.2 | 35.96 | A | 7 | 0.66 | A | 7 | 973 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 41.74 | 6 | 0
1976-01-23 | 1900-01-22 | 18:00 | 18 | 86 | 1212 | 44 | 1 | 13 | 257 | 1 | 9 | 19 | 1 | 13 | 39 | 1 | 13 | 128 | 1 | 9 | 30 | 1 | 13 | 34 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | 2.2 | 35.96 | A | 7 | 0.74 | A | 7 | 973 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.049 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.36 | 6 | 0
1976-01-23 | 1900-01-22 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | 5 | 41 | A | 7 | 1.7 | 35.06 | A | 7 | 0.79 | A | 7 | 973 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.2 | 6 | 0
1976-01-23 | 1900-01-22 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 5.6 | 42.08 | A | 7 | 1.7 | 35.06 | A | 7 | 0.76 | A | 7 | 974 | A | 7 | 230 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 38.78 | 6 | 0
1976-01-23 | 1900-01-22 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | 5.6 | 42.08 | A | 7 | 2.2 | 35.96 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.18 | 6 | 0
1976-01-23 | 1900-01-22 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | 6.1 | 42.98 | A | 7 | 2.8 | 37.04 | A | 7 | 0.79 | A | 7 | 975 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.08 | 6 | 0
1976-01-23 | 1900-01-22 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 6 | A | 7 | 6.1 | 42.98 | A | 7 | 2.8 | 37.04 | A | 7 | 0.79 | A | 7 | 974 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 4880 | A | 7 | 1.2 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.08 | 6 | 0
1976-01-23 | 1900-01-22 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | 5 | 41 | A | 7 | 2.8 | 37.04 | A | 7 | 0.86 | A | 7 | 974 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 1.2 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.1 | 6 | 0
1976-01-24 | 1900-01-23 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | 3.9 | 39.02 | A | 7 | 1.7 | 35.06 | A | 7 | 0.86 | A | 7 | 974 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.22 | 7 | 0
1976-01-24 | 1900-01-23 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | 1.1 | 33.98 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.74 | 7 | 0
1976-01-24 | 1900-01-23 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.92 | A | 7 | 975 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.2 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.04 | 7 | 0
1976-01-24 | 1900-01-23 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | 1.7 | 35.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.96 | A | 7 | 975 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1.1 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.56 | 7 | 0
1976-01-24 | 1900-01-23 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 976 | A | 7 | 310 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 7 | 0
1976-01-24 | 1900-01-23 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 976 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 7 | 0
1976-01-24 | 1900-01-23 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -1.1 | 30.02 | A | 7 | -1.1 | 30.02 | A | 7 | 1 | A | 7 | 977 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.92 | 7 | 0
1976-01-24 | 1900-01-23 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -1.7 | 28.94 | A | 7 | -2.2 | 28.04 | A | 7 | 0.96 | A | 7 | 978 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.54 | 7 | 0
1976-01-24 | 1900-01-23 | 9:00 | 9 | 110 | 1376 | 24 | 1 | 13 | 18 | 1 | 13 | 23 | 1 | 13 | 27 | 1 | 13 | 11 | 1 | 13 | 26 | 1 | 13 | 57 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 0 | 32 | A | 7 | -1.1 | 30.02 | A | 7 | 0.92 | A | 7 | 978 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 3660 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.1 | 7 | 0
1976-01-24 | 1900-01-23 | 10:00 | 10 | 336 | 1412 | 117 | 1 | 13 | 71 | 1 | 13 | 100 | 1 | 13 | 128 | 1 | 13 | 61 | 1 | 13 | 113 | 1 | 13 | 248 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | 0.6 | 33.08 | A | 7 | -1.7 | 28.94 | A | 7 | 0.85 | A | 7 | 979 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 3960 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.38 | 7 | 0
1976-01-24 | 1900-01-23 | 11:00 | 11 | 521 | 1412 | 261 | 1 | 13 | 239 | 1 | 13 | 172 | 1 | 13 | 273 | 1 | 13 | 231 | 1 | 13 | 188 | 1 | 13 | 370 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 7 | 0
1976-01-24 | 1900-01-23 | 12:00 | 12 | 652 | 1412 | 331 | 1 | 9 | 239 | 1 | 9 | 221 | 1 | 13 | 359 | 1 | 9 | 241 | 1 | 9 | 247 | 1 | 13 | 537 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | 1.7 | 35.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.96 | 7 | 0
1976-01-24 | 1900-01-23 | 13:00 | 13 | 717 | 1412 | 250 | 1 | 9 | 70 | 1 | 9 | 215 | 1 | 13 | 275 | 1 | 9 | 70 | 1 | 9 | 240 | 1 | 13 | 649 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.66 | 7 | 0
1976-01-24 | 1900-01-23 | 14:00 | 14 | 714 | 1412 | 254 | 1 | 13 | 70 | 1 | 13 | 219 | 1 | 13 | 280 | 1 | 13 | 70 | 1 | 13 | 244 | 1 | 13 | 657 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 982 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.66 | 7 | 0
1976-01-24 | 1900-01-23 | 15:00 | 15 | 642 | 1412 | 252 | 1 | 13 | 145 | 1 | 13 | 186 | 1 | 13 | 275 | 1 | 13 | 147 | 1 | 13 | 208 | 1 | 13 | 450 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 983 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.34 | 7 | 0
1976-01-24 | 1900-01-23 | 16:00 | 16 | 506 | 1412 | 253 | 1 | 13 | 220 | 1 | 13 | 174 | 1 | 13 | 273 | 1 | 13 | 210 | 1 | 13 | 197 | 1 | 13 | 400 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | 3.3 | 37.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.7 | A | 7 | 984 | A | 7 | 300 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.24 | 7 | 0
1976-01-24 | 1900-01-23 | 17:00 | 17 | 316 | 1412 | 138 | 1 | 13 | 210 | 1 | 13 | 91 | 1 | 13 | 145 | 1 | 13 | 167 | 1 | 13 | 107 | 1 | 13 | 179 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 1.7 | 35.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.76 | A | 7 | 985 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.26 | 7 | 0
1976-01-24 | 1900-01-23 | 18:00 | 18 | 91 | 1235 | 32 | 1 | 13 | 39 | 1 | 13 | 28 | 1 | 13 | 34 | 1 | 13 | 19 | 1 | 13 | 32 | 1 | 13 | 58 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | 0 | 32 | A | 7 | -2.2 | 28.04 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.4 | 7 | 0
1976-01-24 | 1900-01-23 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 3 | A | 7 | -0.6 | 30.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.85 | A | 7 | 986 | A | 7 | 360 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.32 | 7 | 0
1976-01-24 | 1900-01-23 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | -2.2 | 28.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.92 | A | 7 | 987 | A | 7 | 10 | A | 7 | 2.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 7 | 0
1976-01-24 | 1900-01-23 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.92 | A | 7 | 987 | A | 7 | 40 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 7 | 0
1976-01-24 | 1900-01-23 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.8 | 26.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.92 | A | 7 | 988 | A | 7 | 40 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 7 | 0
1976-01-24 | 1900-01-23 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.96 | A | 7 | 988 | A | 7 | 50 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.66 | 7 | 0
1976-01-24 | 1900-01-23 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.9 | 24.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.96 | A | 7 | 988 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.58 | 7 | 0
1976-01-25 | 1900-01-24 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 4 | A | 7 | -3.9 | 24.98 | A | 7 | -4.4 | 24.08 | A | 7 | 0.96 | A | 7 | 987 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.58 | 1 | 0
1976-01-25 | 1900-01-24 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -2.8 | 26.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.92 | A | 7 | 987 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 6100 | A | 7 | 0.8 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 1 | 0
1976-01-25 | 1900-01-24 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 987 | A | 7 | 80 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 6100 | A | 7 | 0.9 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.94 | 1 | 0
1976-01-25 | 1900-01-24 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.96 | A | 7 | 987 | A | 7 | 40 | A | 7 | 5.7 | A | 7 | 3200 | A | 7 | 3660 | A | 7 | 0.8 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.66 | 1 | 0
1976-01-25 | 1900-01-24 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 60 | A | 7 | 5.7 | A | 7 | 3200 | A | 7 | 3350 | A | 7 | 0.8 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.16 | 1 | 0
1976-01-25 | 1900-01-24 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.89 | A | 7 | 985 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 3200 | A | 7 | 1130 | A | 7 | 0.9 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.94 | 1 | 0
1976-01-25 | 1900-01-24 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -3.3 | 26.06 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 3200 | A | 7 | 1220 | A | 7 | 0.9 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.24 | 1 | 0
1976-01-25 | 1900-01-24 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 983 | A | 7 | 50 | A | 7 | 6.7 | A | 7 | 3200 | A | 7 | 790 | A | 7 | 0.9 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 1 | 0
1976-01-25 | 1900-01-24 | 9:00 | 9 | 113 | 1400 | 15 | 1 | 13 | 3 | 1 | 9 | 15 | 1 | 13 | 18 | 1 | 13 | 0 | 1 | 9 | 18 | 1 | 13 | 56 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.1 | 30.02 | A | 7 | 0.96 | A | 7 | 982 | A | 7 | 80 | A | 7 | 6.2 | A | 7 | 2400 | A | 7 | 430 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.42 | 1 | 0
1976-01-25 | 1900-01-24 | 10:00 | 10 | 339 | 1411 | 53 | 1 | 13 | 12 | 1 | 9 | 50 | 1 | 13 | 58 | 1 | 13 | 10 | 1 | 9 | 56 | 1 | 13 | 140 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -0.6 | 30.92 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 70 | A | 7 | 5.2 | A | 7 | 2400 | A | 7 | 210 | A | 7 | 1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.5 | 1 | 0
1976-01-25 | 1900-01-24 | 11:00 | 11 | 525 | 1411 | 72 | 1 | 9 | 2 | 1 | 9 | 71 | 1 | 13 | 85 | 1 | 9 | 1 | 1 | 9 | 85 | 1 | 13 | 310 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 180 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 1 | 0
1976-01-25 | 1900-01-24 | 12:00 | 12 | 656 | 1411 | 99 | 1 | 9 | 6 | 1 | 9 | 96 | 1 | 13 | 118 | 1 | 9 | 4 | 1 | 9 | 116 | 1 | 13 | 436 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 100 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.48 | 1 | 0
1976-01-25 | 1900-01-24 | 13:00 | 13 | 722 | 1411 | 172 | 1 | 9 | 6 | 1 | 9 | 169 | 1 | 13 | 199 | 1 | 9 | 5 | 1 | 9 | 197 | 1 | 13 | 715 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.96 | A | 7 | 977 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 1300 | A | 7 | 90 | A | 7 | 1.1 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.56 | 1 | 0
1976-01-25 | 1900-01-24 | 14:00 | 14 | 719 | 1411 | 132 | 1 | 9 | 4 | 1 | 9 | 130 | 1 | 13 | 156 | 1 | 9 | 3 | 1 | 9 | 154 | 1 | 13 | 582 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.8 | 37.04 | A | 7 | 1 | A | 7 | 976 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 1300 | A | 7 | 60 | A | 7 | 1.2 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.04 | 1 | 0
1976-01-25 | 1900-01-24 | 15:00 | 15 | 648 | 1411 | 114 | 1 | 9 | 2 | 1 | 9 | 113 | 1 | 13 | 134 | 1 | 9 | 1 | 1 | 9 | 133 | 1 | 13 | 496 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | 5 | 41 | A | 7 | 1 | A | 7 | 974 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 1300 | A | 7 | 60 | A | 7 | 1.4 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.9 | 1 | 0
1976-01-25 | 1900-01-24 | 16:00 | 16 | 512 | 1411 | 88 | 1 | 9 | 1 | 1 | 9 | 87 | 1 | 13 | 102 | 1 | 9 | 1 | 1 | 9 | 102 | 1 | 13 | 364 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 6.7 | 44.06 | A | 7 | 6.7 | 44.06 | A | 7 | 1 | A | 7 | 974 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 60 | A | 7 | 1.6 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.06 | 1 | 0
1976-01-25 | 1900-01-24 | 17:00 | 17 | 322 | 1411 | 54 | 1 | 13 | 2 | 1 | 9 | 54 | 1 | 13 | 63 | 1 | 13 | 1 | 1 | 9 | 63 | 1 | 13 | 209 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 7.8 | 46.04 | A | 7 | 1 | A | 7 | 974 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 400 | A | 7 | 210 | A | 7 | 1.7 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.94 | 1 | 0
1976-01-25 | 1900-01-24 | 18:00 | 18 | 95 | 1282 | 14 | 1 | 13 | 0 | 1 | 9 | 14 | 1 | 13 | 16 | 1 | 13 | 0 | 1 | 9 | 16 | 1 | 13 | 52 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 976 | A | 7 | 220 | A | 7 | 4.1 | A | 7 | 4000 | A | 7 | 210 | A | 7 | 1.7 | E | 8 | 0.074 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.84 | 1 | 0
1976-01-25 | 1900-01-24 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 8.3 | 46.94 | A | 7 | 1 | A | 7 | 976 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 210 | A | 7 | 1.7 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.84 | 1 | 0
1976-01-25 | 1900-01-24 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 6.1 | 42.98 | A | 7 | 6.1 | 42.98 | A | 7 | 1 | A | 7 | 977 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 270 | A | 7 | 1.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.88 | 1 | 0
1976-01-25 | 1900-01-24 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | 4.4 | 39.92 | A | 7 | 1 | A | 7 | 978 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 180 | A | 7 | 1.4 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 39.92 | 1 | 0
1976-01-25 | 1900-01-24 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | 3.3 | 37.94 | A | 7 | 1 | A | 7 | 978 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 120 | A | 7 | 1.3 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.94 | 1 | 0
1976-01-25 | 1900-01-24 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 2.2 | 35.96 | A | 7 | 1 | A | 7 | 979 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 1680 | A | 7 | 1.2 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.86 | 1 | 0
1976-01-25 | 1900-01-24 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 1.1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.56 | 1 | 0
1976-01-26 | 1900-01-25 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 240 | A | 7 | 1.1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.48 | 2 | 0
1976-01-26 | 1900-01-25 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | 0 | 32 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.58 | 2 | 0
1976-01-26 | 1900-01-25 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -0.6 | 30.92 | A | 7 | 1 | A | 7 | 983 | A | 7 | 280 | A | 7 | 7.7 | A | 7 | 9700 | A | 7 | 120 | A | 7 | 1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.82 | 2 | 0
1976-01-26 | 1900-01-25 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -1.7 | 28.94 | A | 7 | 0.96 | A | 7 | 984 | A | 7 | 290 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 310 | A | 7 | 1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.62 | 2 | 0
1976-01-26 | 1900-01-25 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 280 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 340 | A | 7 | 1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 2 | 0
1976-01-26 | 1900-01-25 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 986 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 400 | A | 7 | 1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 2 | 0
1976-01-26 | 1900-01-25 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 987 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 370 | A | 7 | 1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 2 | 0
1976-01-26 | 1900-01-25 | 8:00 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -1.7 | 28.94 | A | 7 | 0.92 | A | 7 | 988 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 240 | A | 7 | 1 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.02 | 2 | 0
1976-01-26 | 1900-01-25 | 9:00 | 9 | 116 | 1399 | 33 | 1 | 13 | 0 | 1 | 9 | 33 | 1 | 13 | 36 | 1 | 13 | 0 | 1 | 9 | 36 | 1 | 13 | 104 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 987 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 4000 | A | 7 | 210 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1976-01-26 | 1900-01-25 | 10:00 | 10 | 343 | 1411 | 111 | 1 | 13 | 0 | 1 | 9 | 111 | 1 | 13 | 122 | 1 | 13 | 0 | 1 | 9 | 122 | 1 | 13 | 354 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 990 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 3200 | A | 7 | 120 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1976-01-26 | 1900-01-25 | 11:00 | 11 | 529 | 1411 | 200 | 1 | 9 | 1 | 1 | 9 | 200 | 1 | 13 | 220 | 1 | 9 | 1 | 1 | 9 | 219 | 1 | 13 | 649 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.92 | A | 7 | 991 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 4800 | A | 7 | 210 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.22 | 2 | 0
1976-01-26 | 1900-01-25 | 12:00 | 12 | 661 | 1411 | 255 | 1 | 9 | 1 | 1 | 9 | 254 | 1 | 13 | 281 | 1 | 9 | 1 | 1 | 9 | 281 | 1 | 13 | 871 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 992 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 310 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.92 | 2 | 0
1976-01-26 | 1900-01-25 | 13:00 | 13 | 727 | 1411 | 257 | 1 | 9 | 0 | 1 | 9 | 257 | 1 | 13 | 288 | 1 | 9 | 0 | 1 | 9 | 288 | 1 | 13 | 945 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.85 | A | 7 | 992 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.52 | 2 | 0
1976-01-26 | 1900-01-25 | 14:00 | 14 | 725 | 1411 | 244 | 1 | 9 | 1 | 1 | 9 | 244 | 1 | 13 | 275 | 1 | 9 | 1 | 1 | 9 | 274 | 1 | 13 | 916 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -3.3 | 26.06 | A | 7 | 0.85 | A | 7 | 992 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.52 | 2 | 0
1976-01-26 | 1900-01-25 | 15:00 | 15 | 653 | 1411 | 229 | 1 | 9 | 1 | 1 | 9 | 228 | 1 | 13 | 254 | 1 | 9 | 1 | 1 | 9 | 254 | 1 | 13 | 817 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 992 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 310 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.84 | 2 | 0
1976-01-26 | 1900-01-25 | 16:00 | 16 | 517 | 1411 | 181 | 1 | 9 | 1 | 1 | 9 | 180 | 1 | 13 | 199 | 1 | 9 | 1 | 1 | 9 | 199 | 1 | 13 | 606 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 993 | A | 7 | 320 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 340 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 2 | 0
1976-01-26 | 1900-01-25 | 17:00 | 17 | 327 | 1411 | 111 | 1 | 13 | 0 | 1 | 9 | 111 | 1 | 13 | 121 | 1 | 13 | 0 | 1 | 9 | 121 | 1 | 13 | 343 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -5 | 23 | A | 7 | 0.82 | A | 7 | 994 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 2 | 0
1976-01-26 | 1900-01-25 | 18:00 | 18 | 99 | 1305 | 32 | 1 | 13 | 11 | 1 | 9 | 31 | 1 | 13 | 35 | 1 | 13 | 7 | 1 | 9 | 34 | 1 | 13 | 72 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 995 | A | 7 | 320 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 460 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 2 | 0
1976-01-26 | 1900-01-25 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 5 | A | 7 | -3.3 | 26.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.81 | A | 7 | 996 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.36 | 2 | 0
1976-01-26 | 1900-01-25 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.85 | A | 7 | 997 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 2 | 0
1976-01-26 | 1900-01-25 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.88 | A | 7 | 997 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.92 | 2 | 0
1976-01-26 | 1900-01-25 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -7.8 | 17.96 | A | 7 | 0.88 | A | 7 | 998 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.02 | 2 | 0
1976-01-26 | 1900-01-25 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.81 | A | 7 | 999 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.54 | 2 | 0
1976-01-26 | 1900-01-25 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -10 | 14 | A | 7 | 0.77 | A | 7 | 999 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 2 | 0
1976-01-27 | 1900-01-26 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 999 | A | 7 | 320 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 3 | 0
1976-01-27 | 1900-01-26 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 1 | A | 7 | -8.3 | 17.06 | A | 7 | -11.1 | 12.02 | A | 7 | 0.81 | A | 7 | 1000 | A | 7 | 320 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.76 | 3 | 0
1976-01-27 | 1900-01-26 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.84 | A | 7 | 1000 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 3 | 0
1976-01-27 | 1900-01-26 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | -8.9 | 15.98 | A | 7 | -12.2 | 10.04 | A | 7 | 0.77 | A | 7 | 1000 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.48 | 3 | 0
1976-01-27 | 1900-01-26 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -13.3 | 8.06 | A | 7 | 0.77 | A | 7 | 1000 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.6 | 3 | 0
1976-01-27 | 1900-01-26 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 1 | A | 7 | -10.6 | 12.92 | A | 7 | -13.3 | 8.06 | A | 7 | 0.8 | A | 7 | 1001 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.72 | 3 | 0
1976-01-27 | 1900-01-26 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -10.6 | 12.92 | A | 7 | -13.9 | 6.98 | A | 7 | 0.77 | A | 7 | 1001 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.52 | 3 | 0
1976-01-27 | 1900-01-26 | 8:00 | 8 | 0 | 12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 3 | A | 7 | 1 | A | 7 | -11.1 | 12.02 | A | 7 | -13.9 | 6.98 | A | 7 | 0.8 | A | 7 | 1001 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.82 | 3 | 0
1976-01-27 | 1900-01-26 | 9:00 | 9 | 120 | 1411 | 36 | 1 | 13 | 96 | 1 | 9 | 27 | 1 | 13 | 37 | 1 | 13 | 41 | 1 | 9 | 34 | 1 | 13 | 48 | 1 | 21 | 3 | A | 7 | 2 | A | 7 | -11.1 | 12.02 | A | 7 | -13.9 | 6.98 | A | 7 | 0.8 | A | 7 | 1001 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.82 | 3 | 0
1976-01-27 | 1900-01-26 | 10:00 | 10 | 347 | 1411 | 173 | 1 | 13 | 422 | 1 | 9 | 69 | 1 | 13 | 184 | 1 | 13 | 348 | 1 | 9 | 98 | 1 | 13 | 125 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | -10 | 14 | A | 7 | -13.3 | 8.06 | A | 7 | 0.77 | A | 7 | 1002 | A | 7 | 350 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.6 | 3 | 0
1976-01-27 | 1900-01-26 | 11:00 | 11 | 534 | 1411 | 317 | 1 | 9 | 539 | 1 | 9 | 113 | 1 | 13 | 337 | 1 | 9 | 511 | 1 | 9 | 143 | 1 | 13 | 216 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | -8.3 | 17.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 1001 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 3 | 0
1976-01-27 | 1900-01-26 | 12:00 | 12 | 665 | 1411 | 443 | 1 | 9 | 704 | 1 | 9 | 111 | 1 | 13 | 465 | 1 | 9 | 688 | 1 | 9 | 139 | 1 | 13 | 230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 1001 | A | 7 | 310 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.94 | 3 | 0
1976-01-27 | 1900-01-26 | 13:00 | 13 | 732 | 1411 | 489 | 1 | 9 | 693 | 1 | 9 | 129 | 1 | 13 | 512 | 1 | 9 | 685 | 1 | 9 | 155 | 1 | 13 | 277 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 1001 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.74 | 3 | 0
1976-01-27 | 1900-01-26 | 14:00 | 14 | 730 | 1411 | 481 | 1 | 9 | 672 | 1 | 9 | 134 | 1 | 13 | 503 | 1 | 9 | 662 | 1 | 9 | 159 | 1 | 13 | 285 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | -6.1 | 21.02 | A | 7 | -11.1 | 12.02 | A | 7 | 0.68 | A | 7 | 1001 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.52 | 3 | 0
1976-01-27 | 1900-01-26 | 15:00 | 15 | 658 | 1411 | 373 | 1 | 9 | 498 | 1 | 9 | 141 | 1 | 13 | 399 | 1 | 9 | 494 | 1 | 9 | 168 | 1 | 13 | 286 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -5.6 | 21.92 | A | 7 | -10.6 | 12.92 | A | 7 | 0.68 | A | 7 | 1000 | A | 7 | 300 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 3 | 0
1976-01-27 | 1900-01-26 | 16:00 | 16 | 523 | 1411 | 296 | 1 | 9 | 466 | 1 | 9 | 125 | 1 | 13 | 313 | 1 | 9 | 439 | 1 | 9 | 149 | 1 | 13 | 241 | 1 | 18 | 3 | A | 7 | 2 | A | 7 | -5.6 | 21.92 | A | 7 | -11.1 | 12.02 | A | 7 | 0.65 | A | 7 | 1000 | A | 7 | 340 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.12 | 3 | 0
1976-01-27 | 1900-01-26 | 17:00 | 17 | 332 | 1411 | 144 | 1 | 13 | 196 | 1 | 13 | 98 | 1 | 13 | 151 | 1 | 13 | 160 | 1 | 13 | 114 | 1 | 13 | 195 | 1 | 23 | 4 | A | 7 | 4 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.74 | A | 7 | 1000 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 3 | 0
1976-01-27 | 1900-01-26 | 18:00 | 18 | 104 | 1328 | 29 | 1 | 13 | 31 | 1 | 13 | 26 | 1 | 13 | 31 | 1 | 13 | 16 | 1 | 13 | 30 | 1 | 13 | 54 | 1 | 23 | 5 | A | 7 | 5 | A | 7 | -7.2 | 19.04 | A | 7 | -10.6 | 12.92 | A | 7 | 0.77 | A | 7 | 1000 | A | 7 | 290 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 3 | 0
1976-01-27 | 1900-01-26 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 1000 | A | 7 | 310 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 3 | 0
1976-01-27 | 1900-01-26 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.84 | A | 7 | 1000 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 3 | 0
1976-01-27 | 1900-01-26 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.84 | A | 7 | 1000 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.88 | 3 | 0
1976-01-27 | 1900-01-26 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -11.1 | 12.02 | A | 7 | 0.88 | A | 7 | 999 | A | 7 | 0 | A | 7 | 0 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.28 | 3 | 0
1976-01-27 | 1900-01-26 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -11.1 | 12.02 | A | 7 | 0.92 | A | 7 | 998 | A | 7 | 250 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.5 | 3 | 0
1976-01-27 | 1900-01-26 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.92 | A | 7 | 998 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.079 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.42 | 3 | 0
1976-01-28 | 1900-01-27 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.92 | A | 7 | 997 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.52 | 4 | 0
1976-01-28 | 1900-01-27 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.88 | A | 7 | 996 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.32 | 4 | 0
1976-01-28 | 1900-01-27 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.92 | A | 7 | 996 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.52 | 4 | 0
1976-01-28 | 1900-01-27 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.88 | A | 7 | 995 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.32 | 4 | 0
1976-01-28 | 1900-01-27 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -12.8 | 8.96 | A | 7 | 0.88 | A | 7 | 995 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.32 | 4 | 0
1976-01-28 | 1900-01-27 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.88 | A | 7 | 994 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.22 | 4 | 0
1976-01-28 | 1900-01-27 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -12.2 | 10.04 | A | 7 | 0.88 | A | 7 | 993 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.22 | 4 | 0
1976-01-28 | 1900-01-27 | 8:00 | 8 | 0 | 35 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 3 | A | 7 | 1 | A | 7 | -9.4 | 15.08 | A | 7 | -11.7 | 10.94 | A | 7 | 0.84 | A | 7 | 991 | A | 7 | 170 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 4 | 0
1976-01-28 | 1900-01-27 | 9:00 | 9 | 123 | 1410 | 35 | 1 | 13 | 16 | 1 | 9 | 34 | 1 | 13 | 39 | 1 | 13 | 10 | 1 | 9 | 38 | 1 | 13 | 79 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -8.3 | 17.06 | A | 7 | -10 | 14 | A | 7 | 0.88 | A | 7 | 990 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.6 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.26 | 4 | 0
1976-01-28 | 1900-01-27 | 10:00 | 10 | 351 | 1410 | 156 | 1 | 13 | 194 | 1 | 13 | 108 | 1 | 13 | 164 | 1 | 13 | 162 | 1 | 13 | 123 | 1 | 13 | 218 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.84 | A | 7 | 989 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.72 | 4 | 0
1976-01-28 | 1900-01-27 | 11:00 | 11 | 538 | 1410 | 209 | 1 | 13 | 99 | 1 | 13 | 172 | 1 | 13 | 230 | 1 | 13 | 95 | 1 | 13 | 194 | 1 | 13 | 464 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | -3.9 | 24.98 | A | 7 | -7.8 | 17.96 | A | 7 | 0.75 | A | 7 | 988 | A | 7 | 200 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 4 | 0
1976-01-28 | 1900-01-27 | 12:00 | 12 | 670 | 1410 | 326 | 1 | 9 | 197 | 1 | 9 | 232 | 1 | 13 | 352 | 1 | 9 | 200 | 1 | 9 | 257 | 1 | 13 | 569 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 986 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.82 | 4 | 0
1976-01-28 | 1900-01-27 | 13:00 | 13 | 737 | 1410 | 375 | 1 | 13 | 292 | 1 | 13 | 221 | 1 | 13 | 400 | 1 | 13 | 305 | 1 | 13 | 240 | 1 | 13 | 513 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 984 | A | 7 | 190 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.4 | 4 | 0
1976-01-28 | 1900-01-27 | 14:00 | 14 | 735 | 1410 | 346 | 1 | 9 | 160 | 1 | 9 | 262 | 1 | 13 | 374 | 1 | 9 | 164 | 1 | 9 | 288 | 1 | 13 | 664 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 1.7 | 35.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 210 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.06 | 4 | 0
1976-01-28 | 1900-01-27 | 15:00 | 15 | 664 | 1410 | 219 | 1 | 9 | 119 | 1 | 9 | 163 | 1 | 13 | 242 | 1 | 9 | 121 | 1 | 9 | 185 | 1 | 13 | 398 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 2.2 | 35.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.16 | 4 | 0
1976-01-28 | 1900-01-27 | 16:00 | 16 | 528 | 1410 | 278 | 1 | 13 | 237 | 1 | 13 | 190 | 1 | 13 | 300 | 1 | 13 | 228 | 1 | 13 | 214 | 1 | 13 | 440 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | 2.8 | 37.04 | A | 7 | -3.9 | 24.98 | A | 7 | 0.62 | A | 7 | 982 | A | 7 | 230 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.44 | 4 | 0
1976-01-28 | 1900-01-27 | 17:00 | 17 | 338 | 1410 | 149 | 1 | 13 | 202 | 1 | 13 | 102 | 1 | 13 | 158 | 1 | 13 | 166 | 1 | 13 | 118 | 1 | 13 | 204 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | 2.2 | 35.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 982 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.46 | 4 | 0
1976-01-28 | 1900-01-27 | 18:00 | 18 | 109 | 1352 | 37 | 1 | 13 | 136 | 1 | 9 | 24 | 1 | 13 | 38 | 1 | 13 | 64 | 1 | 9 | 32 | 1 | 13 | 42 | 1 | 21 | 1 | A | 7 | 1 | A | 7 | 1.7 | 35.06 | A | 7 | -3.3 | 26.06 | A | 7 | 0.7 | A | 7 | 982 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.116 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.36 | 4 | 0
1976-01-28 | 1900-01-27 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.78 | 4 | 0
1976-01-28 | 1900-01-27 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.78 | 4 | 0
1976-01-28 | 1900-01-27 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.73 | A | 7 | 981 | A | 7 | 230 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.78 | 4 | 0
1976-01-28 | 1900-01-27 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.28 | 4 | 0
1976-01-28 | 1900-01-27 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.68 | 4 | 0
1976-01-28 | 1900-01-27 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | 1.1 | 33.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 4 | 0
1976-01-29 | 1900-01-28 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 250 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 1 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.66 | 5 | 0
1976-01-29 | 1900-01-28 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 1 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.96 | 5 | 0
1976-01-29 | 1900-01-28 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -1.1 | 30.02 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 1 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.96 | 5 | 0
1976-01-29 | 1900-01-28 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1130 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 5 | 0
1976-01-29 | 1900-01-28 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -2.2 | 28.04 | A | 7 | 0.79 | A | 7 | 981 | A | 7 | 290 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 1400 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.48 | 5 | 0
1976-01-29 | 1900-01-28 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -2.8 | 26.96 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 280 | A | 7 | 8.8 | A | 7 | 19300 | A | 7 | 1400 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.1 | 5 | 0
1976-01-29 | 1900-01-28 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -1.1 | 30.02 | A | 7 | -3.9 | 24.98 | A | 7 | 0.82 | A | 7 | 983 | A | 7 | 290 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 1400 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.22 | 5 | 0
1976-01-29 | 1900-01-28 | 8:00 | 8 | 0 | 59 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 6 | A | 7 | 4 | A | 7 | -2.2 | 28.04 | A | 7 | -5 | 23 | A | 7 | 0.82 | A | 7 | 984 | A | 7 | 310 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1400 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 5 | 0
1976-01-29 | 1900-01-28 | 9:00 | 9 | 127 | 1410 | 38 | 1 | 13 | 11 | 1 | 9 | 37 | 1 | 13 | 42 | 1 | 13 | 7 | 1 | 9 | 41 | 1 | 13 | 84 | 1 | 21 | 9 | A | 7 | 8 | A | 7 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.78 | A | 7 | 985 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 1250 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 5 | 0
1976-01-29 | 1900-01-28 | 10:00 | 10 | 355 | 1410 | 161 | 1 | 13 | 217 | 1 | 13 | 106 | 1 | 13 | 169 | 1 | 13 | 182 | 1 | 13 | 123 | 1 | 13 | 212 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.78 | A | 7 | 986 | A | 7 | 260 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 1190 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 5 | 0
1976-01-29 | 1900-01-28 | 11:00 | 11 | 543 | 1410 | 262 | 1 | 13 | 234 | 1 | 13 | 171 | 1 | 13 | 275 | 1 | 13 | 229 | 1 | 13 | 187 | 1 | 13 | 366 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 987 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1190 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 5 | 0
1976-01-29 | 1900-01-28 | 12:00 | 12 | 675 | 1410 | 438 | 1 | 13 | 652 | 1 | 13 | 126 | 1 | 13 | 456 | 1 | 13 | 635 | 1 | 13 | 151 | 1 | 13 | 258 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.66 | A | 7 | 988 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.32 | 5 | 0
1976-01-29 | 1900-01-28 | 13:00 | 13 | 742 | 1410 | 373 | 1 | 13 | 303 | 1 | 13 | 213 | 1 | 13 | 400 | 1 | 13 | 317 | 1 | 13 | 233 | 1 | 13 | 491 | 1 | 23 | 7 | A | 7 | 7 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 987 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 820 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 5 | 0
1976-01-29 | 1900-01-28 | 14:00 | 14 | 741 | 1410 | 338 | 1 | 13 | 277 | 1 | 13 | 193 | 1 | 13 | 367 | 1 | 13 | 290 | 1 | 13 | 214 | 1 | 13 | 436 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | 0 | 32 | A | 7 | -7.2 | 19.04 | A | 7 | 0.59 | A | 7 | 987 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 910 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.5 | 5 | 0
1976-01-29 | 1900-01-28 | 15:00 | 15 | 669 | 1410 | 309 | 1 | 13 | 326 | 1 | 13 | 155 | 1 | 13 | 337 | 1 | 13 | 336 | 1 | 13 | 177 | 1 | 13 | 330 | 1 | 23 | 6 | A | 7 | 6 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 987 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 940 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.52 | 5 | 0
1976-01-29 | 1900-01-28 | 16:00 | 16 | 534 | 1410 | 312 | 1 | 13 | 511 | 1 | 13 | 119 | 1 | 13 | 331 | 1 | 13 | 484 | 1 | 13 | 147 | 1 | 13 | 229 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | -1.7 | 28.94 | A | 7 | -7.2 | 19.04 | A | 7 | 0.66 | A | 7 | 987 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.54 | 5 | 0
1976-01-29 | 1900-01-28 | 17:00 | 17 | 343 | 1410 | 174 | 1 | 13 | 394 | 1 | 13 | 79 | 1 | 13 | 183 | 1 | 13 | 322 | 1 | 13 | 104 | 1 | 13 | 145 | 1 | 23 | 7 | A | 7 | 5 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 987 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.52 | 5 | 0
1976-01-29 | 1900-01-28 | 18:00 | 18 | 114 | 1375 | 32 | 1 | 13 | 51 | 1 | 13 | 27 | 1 | 13 | 35 | 1 | 13 | 26 | 1 | 13 | 32 | 1 | 13 | 56 | 1 | 23 | 8 | A | 7 | 5 | A | 7 | -1.7 | 28.94 | A | 7 | -7.2 | 19.04 | A | 7 | 0.66 | A | 7 | 987 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 1010 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.54 | 5 | 0
1976-01-29 | 1900-01-28 | 19:00 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 987 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 5 | 0
1976-01-29 | 1900-01-28 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 2 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 280 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 5 | 0
1976-01-29 | 1900-01-28 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 8 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 5490 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 5 | 0
1976-01-29 | 1900-01-28 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 210 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 5 | 0
1976-01-29 | 1900-01-28 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 3050 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 5 | 0
1976-01-29 | 1900-01-28 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3660 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.36 | 5 | 0
1976-01-30 | 1900-01-29 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 7 | A | 7 | -3.3 | 26.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.81 | A | 7 | 980 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.36 | 6 | 0
1976-01-30 | 1900-01-29 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 978 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 6 | 0
1976-01-30 | 1900-01-29 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.72 | A | 7 | 976 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 1130 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.34 | 6 | 0
1976-01-30 | 1900-01-29 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.75 | A | 7 | 975 | A | 7 | 160 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 490 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 6 | 0
1976-01-30 | 1900-01-29 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 974 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 1100 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.74 | 6 | 0
1976-01-30 | 1900-01-29 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.75 | A | 7 | 974 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.32 | 6 | 0
1976-01-30 | 1900-01-29 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 974 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 0.9 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 6 | 0
1976-01-30 | 1900-01-29 | 8:00 | 8 | 0 | 59 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.1 | 30.02 | A | 7 | 0.85 | A | 7 | 975 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 490 | A | 7 | 1 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.28 | 6 | 0
1976-01-30 | 1900-01-29 | 9:00 | 9 | 130 | 1410 | 28 | 1 | 13 | 2 | 1 | 9 | 28 | 1 | 13 | 32 | 1 | 13 | 0 | 1 | 9 | 32 | 1 | 13 | 95 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.82 | A | 7 | 976 | A | 7 | 300 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 820 | A | 7 | 1 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 6 | 0
1976-01-30 | 1900-01-29 | 10:00 | 10 | 359 | 1410 | 93 | 1 | 13 | 9 | 1 | 9 | 90 | 1 | 13 | 104 | 1 | 13 | 4 | 1 | 9 | 102 | 1 | 13 | 320 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -1.7 | 28.94 | A | 7 | 0.82 | A | 7 | 977 | A | 7 | 300 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 610 | A | 7 | 1 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.88 | 6 | 0
1976-01-30 | 1900-01-29 | 11:00 | 11 | 547 | 1410 | 149 | 1 | 9 | 6 | 1 | 9 | 147 | 1 | 13 | 169 | 1 | 9 | 4 | 1 | 9 | 167 | 1 | 13 | 557 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.2 | 28.04 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 290 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 1250 | A | 7 | 0.9 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.98 | 6 | 0
1976-01-30 | 1900-01-29 | 12:00 | 12 | 680 | 1410 | 198 | 1 | 9 | 3 | 1 | 9 | 197 | 1 | 13 | 225 | 1 | 9 | 2 | 1 | 9 | 224 | 1 | 13 | 769 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -2.8 | 26.96 | A | 7 | 0.79 | A | 7 | 980 | A | 7 | 320 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 730 | A | 7 | 0.9 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.68 | 6 | 0
1976-01-30 | 1900-01-29 | 13:00 | 13 | 748 | 1410 | 199 | 1 | 9 | 2 | 1 | 9 | 198 | 1 | 13 | 228 | 1 | 9 | 2 | 1 | 9 | 227 | 1 | 13 | 817 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -3.9 | 24.98 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 310 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.62 | 6 | 0
1976-01-30 | 1900-01-29 | 14:00 | 14 | 746 | 1410 | 232 | 1 | 9 | 4 | 1 | 9 | 230 | 1 | 13 | 263 | 1 | 9 | 4 | 1 | 9 | 261 | 1 | 13 | 902 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 310 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.72 | 6 | 0
1976-01-30 | 1900-01-29 | 15:00 | 15 | 675 | 1410 | 200 | 1 | 9 | 4 | 1 | 9 | 198 | 1 | 13 | 226 | 1 | 9 | 3 | 1 | 9 | 225 | 1 | 13 | 768 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -4.4 | 24.08 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.72 | 6 | 0
1976-01-30 | 1900-01-29 | 16:00 | 16 | 539 | 1410 | 180 | 1 | 9 | 0 | 1 | 9 | 180 | 1 | 13 | 200 | 1 | 9 | 0 | 1 | 9 | 200 | 1 | 13 | 625 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.82 | A | 7 | 983 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 430 | A | 7 | 0.8 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.14 | 6 | 0
1976-01-30 | 1900-01-29 | 17:00 | 17 | 349 | 1410 | 109 | 1 | 13 | 1 | 1 | 9 | 108 | 1 | 13 | 119 | 1 | 13 | 1 | 1 | 9 | 119 | 1 | 13 | 352 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 460 | A | 7 | 0.8 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 6 | 0
1976-01-30 | 1900-01-29 | 18:00 | 18 | 119 | 1410 | 35 | 1 | 13 | 1 | 1 | 9 | 35 | 1 | 13 | 38 | 1 | 13 | 0 | 1 | 9 | 38 | 1 | 13 | 106 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -4.4 | 24.08 | A | 7 | 0.88 | A | 7 | 986 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 550 | A | 7 | 0.8 | E | 8 | 0.059 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.86 | 6 | 0
1976-01-30 | 1900-01-29 | 19:00 | 19 | 0 | 12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 987 | A | 7 | 320 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.86 | 6 | 0
1976-01-30 | 1900-01-29 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 987 | A | 7 | 330 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 640 | A | 7 | 0.7 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.86 | 6 | 0
1976-01-30 | 1900-01-29 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.16 | 6 | 0
1976-01-30 | 1900-01-29 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 330 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.16 | 6 | 0
1976-01-30 | 1900-01-29 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 350 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 640 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.16 | 6 | 0
1976-01-30 | 1900-01-29 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 300 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 820 | A | 7 | 0.8 | E | 8 | 0.08 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 6 | 0
1976-01-31 | 1900-01-30 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5 | 23 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.96 | 7 | 0
1976-01-31 | 1900-01-30 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.16 | 7 | 0
1976-01-31 | 1900-01-30 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 987 | A | 7 | 20 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 640 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.16 | 7 | 0
1976-01-31 | 1900-01-30 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 7 | 0
1976-01-31 | 1900-01-30 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5 | 23 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 340 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.96 | 7 | 0
1976-01-31 | 1900-01-30 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5 | 23 | A | 7 | 0.88 | A | 7 | 987 | A | 7 | 300 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.96 | 7 | 0
1976-01-31 | 1900-01-30 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5 | 23 | A | 7 | 0.92 | A | 7 | 986 | A | 7 | 260 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.28 | 7 | 0
1976-01-31 | 1900-01-30 | 8:00 | 8 | 0 | 82 | 1 | 1 | 13 | 0 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -5 | 23 | A | 7 | 0.92 | A | 7 | 986 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 3050 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.28 | 7 | 0
1976-01-31 | 1900-01-30 | 9:00 | 9 | 134 | 1409 | 44 | 1 | 13 | 116 | 1 | 13 | 33 | 1 | 13 | 47 | 1 | 13 | 54 | 1 | 13 | 41 | 1 | 13 | 60 | 1 | 23 | 8 | A | 7 | 6 | A | 7 | -3.9 | 24.98 | A | 7 | -5 | 23 | A | 7 | 0.92 | A | 7 | 986 | A | 7 | 220 | A | 7 | 1.5 | A | 7 | 4000 | A | 7 | 7620 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.28 | 7 | 0
1976-01-31 | 1900-01-30 | 10:00 | 10 | 363 | 1409 | 177 | 1 | 13 | 346 | 1 | 13 | 88 | 1 | 13 | 185 | 1 | 13 | 289 | 1 | 13 | 110 | 1 | 13 | 163 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -3.3 | 26.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.92 | A | 7 | 986 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.26 | 7 | 0
1976-01-31 | 1900-01-30 | 11:00 | 11 | 552 | 1409 | 312 | 1 | 9 | 400 | 1 | 9 | 155 | 1 | 13 | 322 | 1 | 9 | 381 | 1 | 9 | 172 | 1 | 13 | 309 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 987 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 820 | A | 7 | 0.9 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.84 | 7 | 0
1976-01-31 | 1900-01-30 | 12:00 | 12 | 685 | 1409 | 240 | 1 | 9 | 33 | 1 | 9 | 224 | 1 | 13 | 263 | 1 | 9 | 33 | 1 | 9 | 247 | 1 | 13 | 652 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 986 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 820 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.44 | 7 | 0
1976-01-31 | 1900-01-30 | 13:00 | 13 | 753 | 1409 | 305 | 1 | 9 | 141 | 1 | 9 | 230 | 1 | 13 | 334 | 1 | 9 | 146 | 1 | 9 | 255 | 1 | 13 | 588 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 985 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 700 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.74 | 7 | 0
1976-01-31 | 1900-01-30 | 14:00 | 14 | 752 | 1409 | 353 | 1 | 9 | 147 | 1 | 9 | 274 | 1 | 13 | 381 | 1 | 9 | 151 | 1 | 9 | 300 | 1 | 13 | 700 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 984 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 640 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 7 | 0
1976-01-31 | 1900-01-30 | 15:00 | 15 | 681 | 1409 | 174 | 1 | 9 | 20 | 1 | 9 | 165 | 1 | 13 | 201 | 1 | 9 | 15 | 1 | 9 | 193 | 1 | 13 | 681 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 983 | A | 7 | 250 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 7 | 0
1976-01-31 | 1900-01-30 | 16:00 | 16 | 545 | 1409 | 202 | 1 | 9 | 12 | 1 | 9 | 198 | 1 | 13 | 223 | 1 | 9 | 10 | 1 | 9 | 219 | 1 | 13 | 662 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 983 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 670 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.44 | 7 | 0
1976-01-31 | 1900-01-30 | 17:00 | 17 | 354 | 1409 | 69 | 1 | 13 | 3 | 1 | 9 | 68 | 1 | 13 | 79 | 1 | 13 | 1 | 1 | 9 | 78 | 1 | 13 | 260 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 982 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 640 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.44 | 7 | 0
1976-01-31 | 1900-01-30 | 18:00 | 18 | 124 | 1409 | 30 | 1 | 13 | 4 | 1 | 9 | 29 | 1 | 13 | 33 | 1 | 13 | 0 | 1 | 9 | 33 | 1 | 13 | 96 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -5 | 23 | A | 7 | 0.82 | A | 7 | 982 | A | 7 | 230 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 490 | A | 7 | 0.8 | E | 8 | 0.068 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 7 | 0
1976-01-31 | 1900-01-30 | 19:00 | 19 | 0 | 35 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -5 | 23 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 7 | 0
1976-01-31 | 1900-01-30 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -5 | 23 | A | 7 | 0.82 | A | 7 | 981 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 7 | 0
1976-01-31 | 1900-01-30 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -5 | 23 | A | 7 | 0.82 | A | 7 | 980 | A | 7 | 230 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.34 | 7 | 0
1976-01-31 | 1900-01-30 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.8 | 25.16 | A | 7 | -6.8 | 19.76 | A | 7 | 0.82 | A | 7 | 979 | A | 7 | 230 | A | 7 | 7.3 | A | 7 | 16100 | A | 7 | 550 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.56 | 7 | 0
1976-01-31 | 1900-01-30 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.4 | 22.28 | A | 7 | -8.7 | 16.34 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 240 | A | 7 | 7.5 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.48 | 7 | 0
1976-01-31 | 1900-01-30 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.1 | 19.22 | A | 7 | -10.6 | 12.92 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 240 | A | 7 | 7.6 | A | 7 | 12900 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.081 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 7 | 0
1985-02-01 | 1900-01-31 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.8 | 16.16 | A | 7 | -12.5 | 9.5 | A | 7 | 0.67 | A | 7 | 992 | A | 7 | 340 | A | 7 | 7.8 | A | 7 | 16100 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.96 | 6 | 0
1985-02-01 | 1900-01-31 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.5 | 13.1 | A | 7 | -14.4 | 6.08 | A | 7 | 0.66 | A | 7 | 992 | A | 7 | 350 | A | 7 | 7.9 | A | 7 | 16100 | A | 7 | 3350 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.1 | 6 | 0
1985-02-01 | 1900-01-31 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.1 | 10.22 | A | 7 | -16.3 | 2.66 | A | 7 | 0.66 | A | 7 | 992 | A | 7 | 340 | A | 7 | 8.1 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.42 | 6 | 0
1985-02-01 | 1900-01-31 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -13.9 | 6.98 | A | 7 | -18.3 | -0.94 | A | 7 | 0.69 | A | 7 | 992 | A | 7 | 340 | A | 7 | 8.2 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.48 | 6 | 0
1985-02-01 | 1900-01-31 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.73 | A | 7 | 993 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 6 | 0
1985-02-01 | 1900-01-31 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.73 | A | 7 | 994 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 1040 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 6 | 0
1985-02-01 | 1900-01-31 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.73 | A | 7 | 994 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 910 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 6 | 0
1985-02-01 | 1900-01-31 | 8:00 | 8 | 1 | 129 | 1 | 1 | 13 | 0 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -18.9 | -2.02 | A | 7 | 0.69 | A | 7 | 994 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 910 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.68 | 6 | 0
1985-02-01 | 1900-01-31 | 9:00 | 9 | 142 | 1409 | 43 | 1 | 13 | 1 | 1 | 9 | 43 | 1 | 13 | 4700 | 1 | 13 | 0 | 1 | 9 | 4700 | 1 | 13 | 1290 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.73 | A | 7 | 994 | A | 7 | 350 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 1830 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.88 | 6 | 0
1985-02-01 | 1900-01-31 | 10:00 | 10 | 372 | 1409 | 126 | 1 | 9 | 0 | 1 | 9 | 126 | 1 | 13 | 13800 | 1 | 9 | 0 | 1 | 9 | 13800 | 1 | 13 | 3990 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -13.9 | 6.98 | A | 7 | -17.8 | -0.04 | A | 7 | 0.73 | A | 7 | 994 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 2440 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.68 | 6 | 0
1985-02-01 | 1900-01-31 | 11:00 | 11 | 561 | 1409 | 215 | 1 | 9 | 1 | 1 | 9 | 214 | 1 | 13 | 23600 | 1 | 9 | 100 | 1 | 9 | 23500 | 1 | 13 | 7030 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -13.3 | 8.06 | A | 7 | -17.2 | 1.04 | A | 7 | 0.73 | A | 7 | 994 | A | 7 | 350 | A | 7 | 6.2 | A | 7 | 14500 | A | 7 | 2440 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 6 | 0
1985-02-01 | 1900-01-31 | 12:00 | 12 | 695 | 1409 | 276 | 1 | 9 | 1 | 1 | 9 | 275 | 1 | 13 | 30500 | 1 | 9 | 100 | 1 | 9 | 30400 | 1 | 13 | 9440 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -17.2 | 1.04 | A | 7 | 0.67 | A | 7 | 994 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 6 | 0
1985-02-01 | 1900-01-31 | 13:00 | 13 | 763 | 1409 | 298 | 1 | 9 | 0 | 1 | 9 | 297 | 1 | 13 | 33100 | 1 | 9 | 0 | 1 | 9 | 33100 | 1 | 13 | 10610 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -17.2 | 1.04 | A | 7 | 0.67 | A | 7 | 994 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 6 | 0
1985-02-01 | 1900-01-31 | 14:00 | 14 | 762 | 1409 | 291 | 1 | 9 | 1 | 1 | 9 | 290 | 1 | 13 | 32400 | 1 | 9 | 100 | 1 | 9 | 32300 | 1 | 13 | 10470 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -16.7 | 1.94 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.44 | 6 | 0
1985-02-01 | 1900-01-31 | 15:00 | 15 | 691 | 1409 | 267 | 1 | 9 | 2 | 1 | 9 | 266 | 1 | 13 | 29600 | 1 | 9 | 200 | 1 | 9 | 29500 | 1 | 13 | 9260 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -16.7 | 1.94 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 350 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.44 | 6 | 0
1985-02-01 | 1900-01-31 | 16:00 | 16 | 555 | 1409 | 226 | 1 | 9 | 54 | 1 | 9 | 205 | 1 | 13 | 24800 | 1 | 9 | 5300 | 1 | 9 | 22700 | 1 | 13 | 5370 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 993 | A | 7 | 340 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 6 | 0
1985-02-01 | 1900-01-31 | 17:00 | 17 | 364 | 1409 | 93 | 1 | 13 | 29 | 1 | 9 | 85 | 1 | 13 | 10200 | 1 | 13 | 2500 | 1 | 9 | 9500 | 1 | 13 | 2260 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -11.1 | 12.02 | A | 7 | -16.1 | 3.02 | A | 7 | 0.67 | A | 7 | 993 | A | 7 | 340 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.12 | 6 | 0
1985-02-01 | 1900-01-31 | 18:00 | 18 | 133 | 1409 | 44 | 1 | 13 | 46 | 1 | 13 | 40 | 1 | 13 | 4800 | 1 | 13 | 2500 | 1 | 13 | 4600 | 1 | 13 | 830 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | -10.6 | 12.92 | A | 7 | -16.1 | 3.02 | A | 7 | 0.64 | A | 7 | 993 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.073 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.82 | 6 | 0
1985-02-01 | 1900-01-31 | 19:00 | 19 | 0 | 82 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 9 | A | 7 | 4 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 994 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 6 | 0
1985-02-01 | 1900-01-31 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -12.2 | 10.04 | A | 7 | -17.8 | -0.04 | A | 7 | 0.64 | A | 7 | 994 | A | 7 | 350 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.14 | 6 | 0
1985-02-01 | 1900-01-31 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | -13.3 | 8.06 | A | 7 | -18.9 | -2.02 | A | 7 | 0.63 | A | 7 | 993 | A | 7 | 360 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.26 | 6 | 0
1985-02-01 | 1900-01-31 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 5 | A | 7 | -13.3 | 8.06 | A | 7 | -18.9 | -2.02 | A | 7 | 0.63 | A | 7 | 993 | A | 7 | 10 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 5790 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.26 | 6 | 0
1985-02-01 | 1900-01-31 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 6 | A | 7 | -13.3 | 8.06 | A | 7 | -18.9 | -2.02 | A | 7 | 0.63 | A | 7 | 993 | A | 7 | 10 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 5180 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.26 | 6 | 0
1985-02-01 | 1900-01-31 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -18.9 | -2.02 | A | 7 | 0.61 | A | 7 | 994 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 3960 | A | 7 | 0.4 | E | 8 | 0.091 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.96 | 6 | 0
1985-02-02 | 1900-02-01 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -18.3 | -0.94 | A | 7 | 0.64 | A | 7 | 993 | A | 7 | 30 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 3960 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.16 | 7 | 0
1985-02-02 | 1900-02-01 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -17.8 | -0.04 | A | 7 | 0.67 | A | 7 | 993 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.26 | 7 | 0
1985-02-02 | 1900-02-01 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -17.2 | 1.04 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 10 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 1980 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.46 | 7 | 0
1985-02-02 | 1900-02-01 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -17.2 | 1.04 | A | 7 | 0.7 | A | 7 | 993 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1310 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.46 | 7 | 0
1985-02-02 | 1900-02-01 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.73 | A | 7 | 994 | A | 7 | 10 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 910 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.56 | 7 | 0
1985-02-02 | 1900-02-01 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -15.6 | 3.92 | A | 7 | 0.8 | A | 7 | 994 | A | 7 | 10 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 550 | A | 7 | 0.5 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.96 | 7 | 0
1985-02-02 | 1900-02-01 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -14.4 | 6.08 | A | 7 | 0.88 | A | 7 | 993 | A | 7 | 10 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 550 | A | 7 | 0.5 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.36 | 7 | 0
1985-02-02 | 1900-02-01 | 8:00 | 8 | 1 | 153 | 1 | 1 | 13 | 0 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -15.6 | 3.92 | A | 7 | 0.8 | A | 7 | 993 | A | 7 | 40 | A | 7 | 6.7 | A | 7 | 4000 | A | 7 | 400 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.96 | 7 | 0
1985-02-02 | 1900-02-01 | 9:00 | 9 | 146 | 1408 | 49 | 1 | 13 | 6 | 1 | 9 | 48 | 1 | 13 | 5300 | 1 | 13 | 0 | 1 | 9 | 5300 | 1 | 13 | 1390 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -12.8 | 8.96 | A | 7 | -15.6 | 3.92 | A | 7 | 0.8 | A | 7 | 992 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 3200 | A | 7 | 1520 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.96 | 7 | 0
1985-02-02 | 1900-02-01 | 10:00 | 10 | 377 | 1408 | 125 | 1 | 9 | 6 | 1 | 9 | 123 | 1 | 13 | 13700 | 1 | 9 | 400 | 1 | 9 | 13600 | 1 | 13 | 3980 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -12.2 | 10.04 | A | 7 | -15.6 | 3.92 | A | 7 | 0.77 | A | 7 | 993 | A | 7 | 20 | A | 7 | 5.2 | A | 7 | 2400 | A | 7 | 910 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 7 | 0
1985-02-02 | 1900-02-01 | 11:00 | 11 | 566 | 1408 | 212 | 1 | 9 | 2 | 1 | 9 | 212 | 1 | 13 | 23400 | 1 | 9 | 200 | 1 | 9 | 23400 | 1 | 13 | 7050 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -15.6 | 3.92 | A | 7 | 0.7 | A | 7 | 994 | A | 7 | 360 | A | 7 | 5.2 | A | 7 | 2400 | A | 7 | 910 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 7 | 0
1985-02-02 | 1900-02-01 | 12:00 | 12 | 700 | 1408 | 271 | 1 | 9 | 11 | 1 | 9 | 265 | 1 | 13 | 30000 | 1 | 9 | 1000 | 1 | 9 | 29500 | 1 | 13 | 9340 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -11.1 | 12.02 | A | 7 | -15 | 5 | A | 7 | 0.73 | A | 7 | 994 | A | 7 | 360 | A | 7 | 4.6 | A | 7 | 1600 | A | 7 | 1220 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 7 | 0
1985-02-02 | 1900-02-01 | 13:00 | 13 | 769 | 1408 | 360 | 1 | 13 | 85 | 1 | 13 | 314 | 1 | 13 | 39500 | 1 | 13 | 8700 | 1 | 13 | 34800 | 1 | 13 | 9030 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | -9.4 | 15.08 | A | 7 | -15 | 5 | A | 7 | 0.64 | A | 7 | 994 | A | 7 | 340 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 2740 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.78 | 7 | 0
1985-02-02 | 1900-02-01 | 14:00 | 14 | 768 | 1408 | 486 | 1 | 9 | 296 | 1 | 9 | 326 | 1 | 13 | 52200 | 1 | 9 | 30400 | 1 | 9 | 35600 | 1 | 13 | 8420 | 1 | 18 | 8 | A | 7 | 8 | A | 7 | -8.9 | 15.98 | A | 7 | -14.4 | 6.08 | A | 7 | 0.65 | A | 7 | 994 | A | 7 | 330 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 610 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.68 | 7 | 0
1985-02-02 | 1900-02-01 | 15:00 | 15 | 697 | 1408 | 333 | 1 | 13 | 148 | 1 | 13 | 261 | 1 | 13 | 36000 | 1 | 13 | 15100 | 1 | 13 | 28500 | 1 | 13 | 6490 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | -8.9 | 15.98 | A | 7 | -15 | 5 | A | 7 | 0.62 | A | 7 | 995 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 760 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.48 | 7 | 0
1985-02-02 | 1900-02-01 | 16:00 | 16 | 561 | 1408 | 278 | 1 | 13 | 322 | 1 | 13 | 152 | 1 | 13 | 30000 | 1 | 13 | 31800 | 1 | 13 | 17200 | 1 | 13 | 3170 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | -8.9 | 15.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.59 | A | 7 | 995 | A | 7 | 330 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.28 | 7 | 0
1985-02-02 | 1900-02-01 | 17:00 | 17 | 370 | 1408 | 244 | 1 | 13 | 641 | 1 | 13 | 79 | 1 | 13 | 25200 | 1 | 13 | 53600 | 1 | 13 | 11100 | 1 | 13 | 1400 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | -8.9 | 15.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.59 | A | 7 | 996 | A | 7 | 340 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.28 | 7 | 0
1985-02-02 | 1900-02-01 | 18:00 | 18 | 138 | 1408 | 58 | 1 | 13 | 198 | 1 | 13 | 39 | 1 | 13 | 6000 | 1 | 13 | 10000 | 1 | 13 | 5000 | 1 | 13 | 710 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -11.1 | 12.02 | A | 7 | -15.6 | 3.92 | A | 7 | 0.7 | A | 7 | 997 | A | 7 | 300 | A | 7 | 4.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.042 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 7 | 0
1985-02-02 | 1900-02-01 | 19:00 | 19 | 1 | 106 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 1 | 7 | A | 7 | 3 | A | 7 | -13.3 | 8.06 | A | 7 | -17.2 | 1.04 | A | 7 | 0.73 | A | 7 | 997 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 7 | 0
1985-02-02 | 1900-02-01 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -16.7 | 1.94 | A | 7 | 0.76 | A | 7 | 998 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.86 | 7 | 0
1985-02-02 | 1900-02-01 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -18.3 | -0.94 | A | 7 | 0.76 | A | 7 | 998 | A | 7 | 330 | A | 7 | 2.1 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.9 | 7 | 0
1985-02-02 | 1900-02-01 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -18.3 | -0.94 | A | 7 | 0.83 | A | 7 | 999 | A | 7 | 280 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.32 | 7 | 0
1985-02-02 | 1900-02-01 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -18.3 | -0.94 | A | 7 | 0.96 | A | 7 | 999 | A | 7 | 270 | A | 7 | 1.5 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.24 | 7 | 0
1985-02-02 | 1900-02-01 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -20.6 | -5.08 | A | 7 | 0.79 | A | 7 | 1000 | A | 7 | 310 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.84 | 7 | 0
1985-02-03 | 1900-02-02 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -18.9 | -2.02 | A | 7 | -26.1 | -14.98 | A | 7 | 0.53 | A | 7 | 1000 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.52 | 1 | 0
1985-02-03 | 1900-02-02 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -21.1 | -5.98 | A | 7 | -26.1 | -14.98 | A | 7 | 0.64 | A | 7 | 1000 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.98 | 1 | 0
1985-02-03 | 1900-02-02 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -21.7 | -7.06 | A | 7 | -26.1 | -14.98 | A | 7 | 0.68 | A | 7 | 1001 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -7.86 | 1 | 0
1985-02-03 | 1900-02-02 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -21.1 | -5.98 | A | 7 | -24.4 | -11.92 | A | 7 | 0.75 | A | 7 | 1001 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.68 | 1 | 0
1985-02-03 | 1900-02-02 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -21.7 | -7.06 | A | 7 | -25.6 | -14.08 | A | 7 | 0.71 | A | 7 | 1002 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -7.86 | 1 | 0
1985-02-03 | 1900-02-02 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -23.3 | -9.94 | A | 7 | -26.7 | -16.06 | A | 7 | 0.74 | A | 7 | 1003 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -10.54 | 1 | 0
1985-02-03 | 1900-02-02 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -20.6 | -5.08 | A | 7 | -24.4 | -11.92 | A | 7 | 0.71 | A | 7 | 1003 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.88 | 1 | 0
1985-02-03 | 1900-02-02 | 8:00 | 8 | 2 | 176 | 1 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | -22.8 | -9.04 | A | 7 | -26.7 | -16.06 | A | 7 | 0.71 | A | 7 | 1004 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -9.74 | 1 | 0
1985-02-03 | 1900-02-02 | 9:00 | 9 | 150 | 1408 | 52 | 1 | 13 | 159 | 1 | 9 | 36 | 1 | 13 | 5500 | 1 | 13 | 8500 | 1 | 9 | 4600 | 1 | 13 | 650 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | -22.2 | -7.96 | A | 7 | -26.1 | -14.98 | A | 7 | 0.71 | A | 7 | 1004 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -8.66 | 1 | 0
1985-02-03 | 1900-02-02 | 10:00 | 10 | 381 | 1408 | 208 | 1 | 13 | 286 | 1 | 13 | 131 | 1 | 13 | 21700 | 1 | 13 | 24700 | 1 | 13 | 14900 | 1 | 13 | 2730 | 1 | 23 | 5 | A | 7 | 4 | A | 7 | -16.7 | 1.94 | A | 7 | -17.8 | -0.04 | A | 7 | 0.91 | A | 7 | 1003 | A | 7 | 360 | A | 7 | 1.5 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.54 | 1 | 0
1985-02-03 | 1900-02-02 | 11:00 | 11 | 571 | 1408 | 369 | 1 | 9 | 695 | 1 | 9 | 89 | 1 | 13 | 39000 | 1 | 9 | 66400 | 1 | 9 | 12000 | 1 | 13 | 1780 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -13.3 | 8.06 | A | 7 | 0.96 | A | 7 | 1003 | A | 7 | 50 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.76 | 1 | 0
1985-02-03 | 1900-02-02 | 12:00 | 12 | 706 | 1408 | 507 | 1 | 9 | 806 | 1 | 9 | 106 | 1 | 13 | 54000 | 1 | 9 | 79800 | 1 | 9 | 13900 | 1 | 13 | 2290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -20.6 | -5.08 | A | 7 | 0.44 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.62 | 1 | 0
1985-02-03 | 1900-02-02 | 13:00 | 13 | 775 | 1408 | 575 | 1 | 9 | 843 | 1 | 9 | 114 | 1 | 13 | 59600 | 1 | 9 | 82700 | 1 | 9 | 13900 | 1 | 13 | 2340 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -18.9 | -2.02 | A | 7 | 0.45 | A | 7 | 1003 | A | 7 | 170 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.38 | 1 | 0
1985-02-03 | 1900-02-02 | 14:00 | 14 | 774 | 1408 | 570 | 1 | 9 | 836 | 1 | 9 | 113 | 1 | 13 | 59100 | 1 | 9 | 82100 | 1 | 9 | 13800 | 1 | 13 | 2320 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -17.8 | -0.04 | A | 7 | 0.45 | A | 7 | 1003 | A | 7 | 190 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.06 | 1 | 0
1985-02-03 | 1900-02-02 | 15:00 | 15 | 703 | 1408 | 505 | 1 | 9 | 807 | 1 | 9 | 105 | 1 | 13 | 52200 | 1 | 9 | 78400 | 1 | 9 | 12900 | 1 | 13 | 2050 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.49 | A | 7 | 1003 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.36 | 1 | 0
1985-02-03 | 1900-02-02 | 16:00 | 16 | 567 | 1408 | 383 | 1 | 9 | 726 | 1 | 9 | 94 | 1 | 13 | 40400 | 1 | 9 | 69000 | 1 | 9 | 12500 | 1 | 13 | 1860 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.49 | A | 7 | 1003 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.36 | 1 | 0
1985-02-03 | 1900-02-02 | 17:00 | 17 | 376 | 1408 | 216 | 1 | 9 | 577 | 1 | 9 | 65 | 1 | 13 | 22700 | 1 | 9 | 49100 | 1 | 9 | 9500 | 1 | 13 | 1200 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -17.2 | 1.04 | A | 7 | 0.47 | A | 7 | 1003 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.26 | 1 | 0
1985-02-03 | 1900-02-02 | 18:00 | 18 | 144 | 1408 | 49 | 1 | 13 | 151 | 1 | 9 | 35 | 1 | 13 | 5200 | 1 | 13 | 7900 | 1 | 9 | 4400 | 1 | 13 | 630 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | -9.4 | 15.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.49 | A | 7 | 1003 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.88 | 1 | 0
1985-02-03 | 1900-02-02 | 19:00 | 19 | 1 | 129 | 1 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 4 | A | 7 | 1 | A | 7 | -11.7 | 10.94 | A | 7 | -18.9 | -2.02 | A | 7 | 0.55 | A | 7 | 1003 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.44 | 1 | 0
1985-02-03 | 1900-02-02 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -18.3 | -0.94 | A | 7 | 0.64 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.16 | 1 | 0
1985-02-03 | 1900-02-02 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -18.3 | -0.94 | A | 7 | 0.64 | A | 7 | 1003 | A | 7 | 60 | A | 7 | 2.1 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.16 | 1 | 0
1985-02-03 | 1900-02-02 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -18.9 | -2.02 | A | 7 | 0.73 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.8 | 1 | 0
1985-02-03 | 1900-02-02 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -15.6 | 3.92 | A | 7 | -18.9 | -2.02 | A | 7 | 0.76 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.92 | 1 | 0
1985-02-03 | 1900-02-02 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -20 | -4 | A | 7 | 0.76 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.092 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.04 | 1 | 0
1985-02-04 | 1900-02-03 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -17.2 | 1.04 | A | 7 | -21.1 | -5.98 | A | 7 | 0.72 | A | 7 | 1004 | A | 7 | 360 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.04 | 2 | 0
1985-02-04 | 1900-02-03 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -18.3 | -0.94 | A | 7 | -21.1 | -5.98 | A | 7 | 0.79 | A | 7 | 1004 | A | 7 | 340 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.64 | 2 | 0
1985-02-04 | 1900-02-03 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -19.4 | -2.92 | A | 7 | -22.8 | -9.04 | A | 7 | 0.75 | A | 7 | 1004 | A | 7 | 350 | A | 7 | 1.5 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.72 | 2 | 0
1985-02-04 | 1900-02-03 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -18.3 | -0.94 | A | 7 | -21.7 | -7.06 | A | 7 | 0.75 | A | 7 | 1004 | A | 7 | 30 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.84 | 2 | 0
1985-02-04 | 1900-02-03 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | -17.2 | 1.04 | A | 7 | -20.6 | -5.08 | A | 7 | 0.76 | A | 7 | 1003 | A | 7 | 60 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.14 | 2 | 0
1985-02-04 | 1900-02-03 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 2 | A | 7 | -17.2 | 1.04 | A | 7 | -20.6 | -5.08 | A | 7 | 0.76 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.14 | 2 | 0
1985-02-04 | 1900-02-03 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -20 | -4 | A | 7 | -23.9 | -11.02 | A | 7 | 0.71 | A | 7 | 1004 | A | 7 | 340 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -4.9 | 2 | 0
1985-02-04 | 1900-02-03 | 8:00 | 8 | 2 | 199 | 2 | 1 | 13 | 4 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -18.3 | -0.94 | A | 7 | -21.1 | -5.98 | A | 7 | 0.79 | A | 7 | 1004 | A | 7 | 30 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.64 | 2 | 0
1985-02-04 | 1900-02-03 | 9:00 | 9 | 155 | 1408 | 55 | 1 | 13 | 179 | 1 | 13 | 35 | 1 | 13 | 5700 | 1 | 13 | 9800 | 1 | 13 | 4600 | 1 | 13 | 630 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -15.6 | 3.92 | A | 7 | -19.4 | -2.92 | A | 7 | 0.72 | A | 7 | 1004 | A | 7 | 60 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.72 | 2 | 0
1985-02-04 | 1900-02-03 | 10:00 | 10 | 386 | 1408 | 236 | 1 | 9 | 645 | 1 | 9 | 60 | 1 | 13 | 24800 | 1 | 9 | 55700 | 1 | 9 | 9400 | 1 | 13 | 1130 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -17.2 | 1.04 | A | 7 | 0.67 | A | 7 | 1003 | A | 7 | 70 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 2 | 0
1985-02-04 | 1900-02-03 | 11:00 | 11 | 577 | 1408 | 396 | 1 | 9 | 776 | 1 | 9 | 81 | 1 | 13 | 41100 | 1 | 9 | 73500 | 1 | 9 | 10900 | 1 | 13 | 1570 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -18.3 | -0.94 | A | 7 | 0.49 | A | 7 | 1003 | A | 7 | 100 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.88 | 2 | 0
1985-02-04 | 1900-02-03 | 12:00 | 12 | 711 | 1408 | 504 | 1 | 13 | 618 | 1 | 13 | 194 | 1 | 13 | 52900 | 1 | 13 | 61900 | 1 | 13 | 21500 | 1 | 13 | 4180 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | -7.2 | 19.04 | A | 7 | -17.2 | 1.04 | A | 7 | 0.45 | A | 7 | 1003 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 6100 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.04 | 2 | 0
1985-02-04 | 1900-02-03 | 13:00 | 13 | 780 | 1408 | 583 | 1 | 9 | 873 | 1 | 9 | 102 | 1 | 13 | 61300 | 1 | 9 | 86300 | 1 | 9 | 13300 | 1 | 13 | 2220 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -18.3 | -0.94 | A | 7 | 0.39 | A | 7 | 1002 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.34 | 2 | 0
1985-02-04 | 1900-02-03 | 14:00 | 14 | 779 | 1408 | 564 | 1 | 9 | 804 | 1 | 9 | 122 | 1 | 13 | 60100 | 1 | 9 | 80500 | 1 | 9 | 15400 | 1 | 13 | 2770 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | -5.6 | 21.92 | A | 7 | -18.3 | -0.94 | A | 7 | 0.36 | A | 7 | 1001 | A | 7 | 90 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.72 | 2 | 0
1985-02-04 | 1900-02-03 | 15:00 | 15 | 709 | 1408 | 505 | 1 | 9 | 751 | 1 | 9 | 130 | 1 | 13 | 53100 | 1 | 9 | 73800 | 1 | 9 | 15800 | 1 | 13 | 2730 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -5 | 23 | A | 7 | -17.8 | -0.04 | A | 7 | 0.36 | A | 7 | 1000 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.6 | 2 | 0
1985-02-04 | 1900-02-03 | 16:00 | 16 | 573 | 1408 | 374 | 1 | 13 | 495 | 1 | 13 | 175 | 1 | 13 | 38600 | 1 | 13 | 47500 | 1 | 13 | 19200 | 1 | 13 | 3560 | 1 | 23 | 4 | A | 7 | 3 | A | 7 | -4.4 | 24.08 | A | 7 | -17.2 | 1.04 | A | 7 | 0.37 | A | 7 | 999 | A | 7 | 80 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.58 | 2 | 0
1985-02-04 | 1900-02-03 | 17:00 | 17 | 381 | 1408 | 150 | 1 | 9 | 106 | 1 | 9 | 122 | 1 | 13 | 16300 | 1 | 9 | 9300 | 1 | 9 | 13700 | 1 | 13 | 2700 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -4.4 | 24.08 | A | 7 | -17.2 | 1.04 | A | 7 | 0.37 | A | 7 | 996 | A | 7 | 90 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.58 | 2 | 0
1985-02-04 | 1900-02-03 | 18:00 | 18 | 149 | 1408 | 42 | 1 | 13 | 12 | 1 | 9 | 41 | 1 | 13 | 4600 | 1 | 13 | 800 | 1 | 9 | 4500 | 1 | 13 | 960 | 1 | 21 | 10 | A | 7 | 8 | A | 7 | -5.6 | 21.92 | A | 7 | -17.8 | -0.04 | A | 7 | 0.38 | A | 7 | 998 | A | 7 | 90 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.92 | 2 | 0
1985-02-04 | 1900-02-03 | 19:00 | 19 | 2 | 176 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -17.2 | 1.04 | A | 7 | 0.4 | A | 7 | 996 | A | 7 | 90 | A | 7 | 7.2 | A | 7 | 16100 | A | 7 | 3660 | A | 7 | 0.4 | E | 8 | 0.088 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.02 | 2 | 0
1985-02-04 | 1900-02-03 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -17.2 | 1.04 | A | 7 | 0.38 | A | 7 | 996 | A | 7 | 90 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 0.4 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.8 | 2 | 0
1985-02-04 | 1900-02-03 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -17.2 | 1.04 | A | 7 | 0.4 | A | 7 | 996 | A | 7 | 80 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 0.4 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.02 | 2 | 0
1985-02-04 | 1900-02-03 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.42 | A | 7 | 995 | A | 7 | 70 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 1680 | A | 7 | 0.4 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.22 | 2 | 0
1985-02-04 | 1900-02-03 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -16.7 | 1.94 | A | 7 | 0.42 | A | 7 | 994 | A | 7 | 90 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 1190 | A | 7 | 0.4 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.22 | 2 | 0
1985-02-04 | 1900-02-03 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -13.9 | 6.98 | A | 7 | 0.52 | A | 7 | 994 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 610 | A | 7 | 0.5 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 2 | 0
1985-02-05 | 1900-02-04 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 993 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 3200 | A | 7 | 760 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.74 | 3 | 0
1985-02-05 | 1900-02-04 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -10 | 14 | A | 7 | 0.78 | A | 7 | 992 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 610 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 3 | 0
1985-02-05 | 1900-02-04 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.81 | A | 7 | 991 | A | 7 | 70 | A | 7 | 4.6 | A | 7 | 3200 | A | 7 | 400 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.54 | 3 | 0
1985-02-05 | 1900-02-04 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 990 | A | 7 | 90 | A | 7 | 4.1 | A | 7 | 1600 | A | 7 | 210 | A | 7 | 0.6 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 3 | 0
1985-02-05 | 1900-02-04 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -8.3 | 17.06 | A | 7 | 0.85 | A | 7 | 989 | A | 7 | 70 | A | 7 | 3.1 | A | 7 | 1600 | A | 7 | 210 | A | 7 | 0.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.82 | 3 | 0
1985-02-05 | 1900-02-04 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 988 | A | 7 | 80 | A | 7 | 3.1 | A | 7 | 1600 | A | 7 | 270 | A | 7 | 0.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 3 | 0
1985-02-05 | 1900-02-04 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.85 | A | 7 | 987 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 3200 | A | 7 | 1130 | A | 7 | 0.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.72 | 3 | 0
1985-02-05 | 1900-02-04 | 8:00 | 8 | 3 | 223 | 1 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.88 | A | 7 | 986 | A | 7 | 100 | A | 7 | 3.1 | A | 7 | 1600 | A | 7 | 240 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.92 | 3 | 0
1985-02-05 | 1900-02-04 | 9:00 | 9 | 159 | 1407 | 40 | 1 | 13 | 5 | 1 | 9 | 39 | 1 | 13 | 4400 | 1 | 13 | 0 | 1 | 9 | 4400 | 1 | 13 | 1280 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.88 | A | 7 | 986 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 1600 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.92 | 3 | 0
1985-02-05 | 1900-02-04 | 10:00 | 10 | 391 | 1407 | 120 | 1 | 9 | 4 | 1 | 9 | 119 | 1 | 13 | 13300 | 1 | 9 | 200 | 1 | 9 | 13200 | 1 | 13 | 4000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.85 | A | 7 | 985 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 3200 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 3 | 0
1985-02-05 | 1900-02-04 | 11:00 | 11 | 582 | 1407 | 211 | 1 | 9 | 1 | 1 | 9 | 211 | 1 | 13 | 23400 | 1 | 9 | 100 | 1 | 9 | 23300 | 1 | 13 | 7200 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.85 | A | 7 | 984 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 3200 | A | 7 | 210 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 3 | 0
1985-02-05 | 1900-02-04 | 12:00 | 12 | 717 | 1407 | 258 | 1 | 9 | 4 | 1 | 9 | 256 | 1 | 13 | 28800 | 1 | 9 | 400 | 1 | 9 | 28600 | 1 | 13 | 9350 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 3200 | A | 7 | 210 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.16 | 3 | 0
1985-02-05 | 1900-02-04 | 13:00 | 13 | 786 | 1407 | 303 | 1 | 9 | 2 | 1 | 9 | 302 | 1 | 13 | 33800 | 1 | 9 | 200 | 1 | 9 | 33700 | 1 | 13 | 10970 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 0 | A | 7 | 0 | A | 7 | 3200 | A | 7 | 210 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.16 | 3 | 0
1985-02-05 | 1900-02-04 | 14:00 | 14 | 785 | 1407 | 352 | 1 | 9 | 4 | 1 | 9 | 350 | 1 | 13 | 38800 | 1 | 9 | 400 | 1 | 9 | 38600 | 1 | 13 | 11700 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 0 | A | 7 | 0 | A | 7 | 4800 | A | 7 | 520 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.94 | 3 | 0
1985-02-05 | 1900-02-04 | 15:00 | 15 | 715 | 1407 | 315 | 1 | 9 | 4 | 1 | 9 | 314 | 1 | 13 | 34700 | 1 | 9 | 400 | 1 | 9 | 34500 | 1 | 13 | 10250 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 0 | A | 7 | 0 | A | 7 | 4800 | A | 7 | 370 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.74 | 3 | 0
1985-02-05 | 1900-02-04 | 16:00 | 16 | 579 | 1407 | 248 | 1 | 9 | 0 | 1 | 9 | 248 | 1 | 13 | 27000 | 1 | 9 | 0 | 1 | 9 | 27000 | 1 | 13 | 7680 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 6400 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.74 | 3 | 0
1985-02-05 | 1900-02-04 | 17:00 | 17 | 387 | 1407 | 150 | 1 | 9 | 1 | 1 | 9 | 150 | 1 | 13 | 16300 | 1 | 9 | 100 | 1 | 9 | 16300 | 1 | 13 | 4450 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 980 | A | 7 | 320 | A | 7 | 2.6 | A | 7 | 6400 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.74 | 3 | 0
1985-02-05 | 1900-02-04 | 18:00 | 18 | 154 | 1407 | 46 | 1 | 13 | 1 | 1 | 9 | 46 | 1 | 13 | 5000 | 1 | 13 | 0 | 1 | 9 | 5000 | 1 | 13 | 1400 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 310 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 550 | A | 7 | 0.8 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.44 | 3 | 0
1985-02-05 | 1900-02-04 | 19:00 | 19 | 2 | 199 | 2 | 1 | 13 | 0 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.72 | A | 7 | 981 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 400 | A | 7 | 0.7 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.14 | 3 | 0
1985-02-05 | 1900-02-04 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.75 | A | 7 | 981 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 3 | 0
1985-02-05 | 1900-02-04 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.1 | 21.02 | A | 7 | 0.78 | A | 7 | 981 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.86 | 3 | 0
1985-02-05 | 1900-02-04 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 982 | A | 7 | 290 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 820 | A | 7 | 0.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 3 | 0
1985-02-05 | 1900-02-04 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -6.7 | 19.94 | A | 7 | 0.75 | A | 7 | 982 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 580 | A | 7 | 0.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 3 | 0
1985-02-05 | 1900-02-04 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.78 | A | 7 | 982 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 340 | A | 7 | 0.7 | E | 8 | 0.093 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.06 | 3 | 0
1985-02-06 | 1900-02-05 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 982 | A | 7 | 300 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 270 | A | 7 | 0.7 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 4 | 0
1985-02-06 | 1900-02-05 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.78 | A | 7 | 983 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 370 | A | 7 | 0.7 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.18 | 4 | 0
1985-02-06 | 1900-02-05 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.75 | A | 7 | 983 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 610 | A | 7 | 0.7 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 4 | 0
1985-02-06 | 1900-02-05 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -9.4 | 15.08 | A | 7 | 0.71 | A | 7 | 984 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 460 | A | 7 | 0.6 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.6 | 4 | 0
1985-02-06 | 1900-02-05 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 984 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 400 | A | 7 | 0.6 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 4 | 0
1985-02-06 | 1900-02-05 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.74 | A | 7 | 984 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 980 | A | 7 | 0.6 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 4 | 0
1985-02-06 | 1900-02-05 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 980 | A | 7 | 0.6 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.74 | 4 | 0
1985-02-06 | 1900-02-05 | 8:00 | 8 | 4 | 246 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 986 | A | 7 | 290 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 910 | A | 7 | 0.6 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 4 | 0
1985-02-06 | 1900-02-05 | 9:00 | 9 | 164 | 1407 | 50 | 1 | 13 | 0 | 1 | 9 | 50 | 1 | 13 | 5500 | 1 | 13 | 0 | 1 | 9 | 5500 | 1 | 13 | 1510 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 987 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 910 | A | 7 | 0.6 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.16 | 4 | 0
1985-02-06 | 1900-02-05 | 10:00 | 10 | 397 | 1407 | 174 | 1 | 13 | 100 | 1 | 13 | 146 | 1 | 13 | 19000 | 1 | 13 | 9100 | 1 | 13 | 16500 | 1 | 13 | 3520 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | -8.3 | 17.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 987 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 4 | 0
1985-02-06 | 1900-02-05 | 11:00 | 11 | 588 | 1407 | 383 | 1 | 13 | 401 | 1 | 13 | 216 | 1 | 13 | 40100 | 1 | 13 | 39900 | 1 | 13 | 23400 | 1 | 13 | 4890 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | -7.8 | 17.96 | A | 7 | -12.8 | 8.96 | A | 7 | 0.68 | A | 7 | 988 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.66 | 4 | 0
1985-02-06 | 1900-02-05 | 12:00 | 12 | 723 | 1407 | 396 | 1 | 13 | 250 | 1 | 13 | 268 | 1 | 13 | 42800 | 1 | 13 | 25600 | 1 | 13 | 29600 | 1 | 13 | 6750 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | -7.2 | 19.04 | A | 7 | -12.8 | 8.96 | A | 7 | 0.65 | A | 7 | 989 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 8000 | A | 7 | 670 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.44 | 4 | 0
1985-02-06 | 1900-02-05 | 13:00 | 13 | 792 | 1407 | 472 | 1 | 13 | 378 | 1 | 13 | 261 | 1 | 13 | 50500 | 1 | 13 | 39800 | 1 | 13 | 28000 | 1 | 13 | 6400 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | -6.7 | 19.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.6 | A | 7 | 989 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 670 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.94 | 4 | 0
1985-02-06 | 1900-02-05 | 14:00 | 14 | 791 | 1407 | 556 | 1 | 13 | 663 | 1 | 13 | 185 | 1 | 13 | 57400 | 1 | 13 | 65100 | 1 | 13 | 20700 | 1 | 13 | 3960 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 988 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 4 | 0
1985-02-06 | 1900-02-05 | 15:00 | 15 | 721 | 1407 | 497 | 1 | 9 | 786 | 1 | 9 | 98 | 1 | 13 | 52000 | 1 | 9 | 76900 | 1 | 9 | 12500 | 1 | 13 | 2030 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 4 | 0
1985-02-06 | 1900-02-05 | 16:00 | 16 | 584 | 1407 | 395 | 1 | 9 | 763 | 1 | 9 | 82 | 1 | 13 | 41200 | 1 | 9 | 72500 | 1 | 9 | 10900 | 1 | 13 | 1590 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 240 | A | 7 | 5.7 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 4 | 0
1985-02-06 | 1900-02-05 | 17:00 | 17 | 393 | 1407 | 234 | 1 | 9 | 623 | 1 | 9 | 64 | 1 | 13 | 24800 | 1 | 9 | 54000 | 1 | 9 | 9600 | 1 | 13 | 1200 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 989 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 4 | 0
1985-02-06 | 1900-02-05 | 18:00 | 18 | 160 | 1407 | 72 | 1 | 13 | 426 | 1 | 9 | 26 | 1 | 13 | 7500 | 1 | 13 | 27500 | 1 | 9 | 4300 | 1 | 13 | 480 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -13.3 | 8.06 | A | 7 | 0.62 | A | 7 | 990 | A | 7 | 280 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.24 | 4 | 0
1985-02-06 | 1900-02-05 | 19:00 | 19 | 3 | 223 | 5 | 1 | 13 | 13 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 990 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12 | 4 | 0
1985-02-06 | 1900-02-05 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 990 | A | 7 | 290 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.32 | 4 | 0
1985-02-06 | 1900-02-05 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -14.4 | 6.08 | A | 7 | 0.77 | A | 7 | 990 | A | 7 | 0 | A | 7 | 0 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.72 | 4 | 0
1985-02-06 | 1900-02-05 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -14.4 | 6.08 | A | 7 | 0.84 | A | 7 | 991 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 4 | 0
1985-02-06 | 1900-02-05 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -15.6 | 3.92 | A | 7 | 0.87 | A | 7 | 992 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.38 | 4 | 0
1985-02-06 | 1900-02-05 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.83 | A | 7 | 992 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.28 | 4 | 0
1985-02-07 | 1900-02-06 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.83 | A | 7 | 992 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.28 | 5 | 0
1985-02-07 | 1900-02-06 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -16.1 | 3.02 | A | 7 | -18.3 | -0.94 | A | 7 | 0.83 | A | 7 | 992 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 4800 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.32 | 5 | 0
1985-02-07 | 1900-02-06 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -15.6 | 3.92 | A | 7 | -17.2 | 1.04 | A | 7 | 0.87 | A | 7 | 993 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.32 | 5 | 0
1985-02-07 | 1900-02-06 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.83 | A | 7 | 993 | A | 7 | 270 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.28 | 5 | 0
1985-02-07 | 1900-02-06 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -17.8 | -0.04 | A | 7 | 0.8 | A | 7 | 994 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.1 | 5 | 0
1985-02-07 | 1900-02-06 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -19.4 | -2.92 | A | 7 | 0.76 | A | 7 | 994 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.02 | 5 | 0
1985-02-07 | 1900-02-06 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -18.9 | -2.02 | A | 7 | 0.83 | A | 7 | 995 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.24 | 5 | 0
1985-02-07 | 1900-02-06 | 8:00 | 8 | 4 | 270 | 2 | 1 | 13 | 2 | 1 | 9 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -19.4 | -2.92 | A | 7 | 0.79 | A | 7 | 995 | A | 7 | 260 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.14 | 5 | 0
1985-02-07 | 1900-02-06 | 9:00 | 9 | 169 | 1406 | 67 | 1 | 13 | 235 | 1 | 9 | 40 | 1 | 13 | 7100 | 1 | 13 | 13500 | 1 | 9 | 5500 | 1 | 13 | 720 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -17.2 | 1.04 | A | 7 | -18.9 | -2.02 | A | 7 | 0.87 | A | 7 | 996 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.54 | 5 | 0
1985-02-07 | 1900-02-06 | 10:00 | 10 | 402 | 1406 | 235 | 1 | 9 | 564 | 1 | 9 | 75 | 1 | 13 | 24300 | 1 | 9 | 48900 | 1 | 9 | 10300 | 1 | 13 | 1380 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -18.3 | -0.94 | A | 7 | 0.8 | A | 7 | 997 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.12 | 5 | 0
1985-02-07 | 1900-02-06 | 11:00 | 11 | 593 | 1406 | 403 | 1 | 9 | 719 | 1 | 9 | 101 | 1 | 13 | 42300 | 1 | 9 | 68900 | 1 | 9 | 13100 | 1 | 13 | 2010 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -17.8 | -0.04 | A | 7 | 0.76 | A | 7 | 997 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.98 | 5 | 0
1985-02-07 | 1900-02-06 | 12:00 | 12 | 728 | 1406 | 524 | 1 | 9 | 786 | 1 | 9 | 119 | 1 | 13 | 55500 | 1 | 9 | 77900 | 1 | 9 | 14900 | 1 | 13 | 2580 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -13.3 | 8.06 | A | 7 | -17.2 | 1.04 | A | 7 | 0.73 | A | 7 | 997 | A | 7 | 260 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 5 | 0
1985-02-07 | 1900-02-06 | 13:00 | 13 | 798 | 1406 | 592 | 1 | 9 | 822 | 1 | 9 | 128 | 1 | 13 | 62900 | 1 | 9 | 82400 | 1 | 9 | 16000 | 1 | 13 | 2940 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -16.7 | 1.94 | A | 7 | 0.7 | A | 7 | 998 | A | 7 | 280 | A | 7 | 6.2 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.44 | 5 | 0
1985-02-07 | 1900-02-06 | 14:00 | 14 | 797 | 1406 | 556 | 1 | 13 | 614 | 1 | 13 | 210 | 1 | 13 | 58800 | 1 | 13 | 62500 | 1 | 13 | 23300 | 1 | 13 | 4800 | 1 | 23 | 3 | A | 7 | 3 | A | 7 | -10.6 | 12.92 | A | 7 | -16.1 | 3.02 | A | 7 | 0.64 | A | 7 | 998 | A | 7 | 280 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.82 | 5 | 0
1985-02-07 | 1900-02-06 | 15:00 | 15 | 727 | 1406 | 512 | 1 | 13 | 638 | 1 | 13 | 186 | 1 | 13 | 54300 | 1 | 13 | 64200 | 1 | 13 | 21000 | 1 | 13 | 4020 | 1 | 23 | 7 | A | 7 | 4 | A | 7 | -10 | 14 | A | 7 | -15.6 | 3.92 | A | 7 | 0.64 | A | 7 | 999 | A | 7 | 310 | A | 7 | 5.7 | A | 7 | 12900 | A | 7 | 640 | A | 7 | 0.5 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.8 | 5 | 0
1985-02-07 | 1900-02-06 | 16:00 | 16 | 590 | 1406 | 376 | 1 | 9 | 637 | 1 | 9 | 112 | 1 | 13 | 39300 | 1 | 9 | 60700 | 1 | 9 | 13800 | 1 | 13 | 2190 | 1 | 18 | 3 | A | 7 | 1 | A | 7 | -9.4 | 15.08 | A | 7 | -15.6 | 3.92 | A | 7 | 0.62 | A | 7 | 1000 | A | 7 | 310 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.68 | 5 | 0
1985-02-07 | 1900-02-06 | 17:00 | 17 | 398 | 1406 | 223 | 1 | 9 | 536 | 1 | 9 | 74 | 1 | 13 | 23300 | 1 | 9 | 46300 | 1 | 9 | 10100 | 1 | 13 | 1360 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -9.4 | 15.08 | A | 7 | -15.6 | 3.92 | A | 7 | 0.62 | A | 7 | 1001 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.68 | 5 | 0
1985-02-07 | 1900-02-06 | 18:00 | 18 | 165 | 1406 | 67 | 1 | 13 | 171 | 1 | 9 | 48 | 1 | 13 | 7100 | 1 | 13 | 9200 | 1 | 9 | 6000 | 1 | 13 | 910 | 1 | 21 | 6 | A | 7 | 0 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 1001 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 5 | 0
1985-02-07 | 1900-02-06 | 19:00 | 19 | 4 | 246 | 1 | 1 | 13 | 1 | 1 | 9 | 1 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 6 | A | 7 | 2 | A | 7 | -13.3 | 8.06 | A | 7 | -17.2 | 1.04 | A | 7 | 0.73 | A | 7 | 1001 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.131 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.76 | 5 | 0
1985-02-07 | 1900-02-06 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -13.9 | 6.98 | A | 7 | -16.7 | 1.94 | A | 7 | 0.8 | A | 7 | 1002 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.98 | 5 | 0
1985-02-07 | 1900-02-06 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -15 | 5 | A | 7 | -17.2 | 1.04 | A | 7 | 0.83 | A | 7 | 1002 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.2 | 5 | 0
1985-02-07 | 1900-02-06 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -15.6 | 3.92 | A | 7 | -18.3 | -0.94 | A | 7 | 0.8 | A | 7 | 1002 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.12 | 5 | 0
1985-02-07 | 1900-02-06 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -15 | 5 | A | 7 | -17.2 | 1.04 | A | 7 | 0.83 | A | 7 | 1002 | A | 7 | 260 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.2 | 5 | 0
1985-02-07 | 1900-02-06 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15.6 | 3.92 | A | 7 | -17.2 | 1.04 | A | 7 | 0.87 | A | 7 | 1002 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.094 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.32 | 5 | 0
1985-02-08 | 1900-02-07 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -18.3 | -0.94 | A | 7 | 0.87 | A | 7 | 1002 | A | 7 | 270 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.44 | 6 | 0
1985-02-08 | 1900-02-07 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.2 | 1.04 | A | 7 | -19.4 | -2.92 | A | 7 | 0.83 | A | 7 | 1002 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 0.34 | 6 | 0
1985-02-08 | 1900-02-07 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -19.4 | -2.92 | A | 7 | 0.87 | A | 7 | 1002 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.54 | 6 | 0
1985-02-08 | 1900-02-07 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -17.8 | -0.04 | A | 7 | -18.9 | -2.02 | A | 7 | 0.91 | A | 7 | 1002 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -0.44 | 6 | 0
1985-02-08 | 1900-02-07 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -19.4 | -2.92 | A | 7 | -20.6 | -5.08 | A | 7 | 0.91 | A | 7 | 1002 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -3.22 | 6 | 0
1985-02-08 | 1900-02-07 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -21.1 | -5.98 | A | 7 | -22.8 | -9.04 | A | 7 | 0.87 | A | 7 | 1002 | A | 7 | 240 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.38 | 6 | 0
1985-02-08 | 1900-02-07 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -20.6 | -5.08 | A | 7 | -22.2 | -7.96 | A | 7 | 0.87 | A | 7 | 1003 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.48 | 6 | 0
1985-02-08 | 1900-02-07 | 8:00 | 8 | 5 | 293 | 5 | 1 | 13 | 12 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -21.1 | -5.98 | A | 7 | -23.3 | -9.94 | A | 7 | 0.82 | A | 7 | 1003 | A | 7 | 250 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.3 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -6.48 | 6 | 0
1985-02-08 | 1900-02-07 | 9:00 | 9 | 174 | 1406 | 78 | 1 | 13 | 371 | 1 | 9 | 34 | 1 | 13 | 8200 | 1 | 13 | 23000 | 1 | 9 | 5300 | 1 | 13 | 600 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -20.6 | -5.08 | A | 7 | -21.7 | -7.06 | A | 7 | 0.91 | A | 7 | 1004 | A | 7 | 0 | A | 7 | 0 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -5.38 | 6 | 0
1985-02-08 | 1900-02-07 | 10:00 | 10 | 407 | 1406 | 253 | 1 | 9 | 666 | 1 | 9 | 62 | 1 | 13 | 26700 | 1 | 9 | 58600 | 1 | 9 | 9600 | 1 | 13 | 1180 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | -18.3 | -0.94 | A | 7 | -22.2 | -7.96 | A | 7 | 0.72 | A | 7 | 1004 | A | 7 | 220 | A | 7 | 1.5 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | -1.94 | 6 | 0
1985-02-08 | 1900-02-07 | 11:00 | 11 | 599 | 1406 | 419 | 1 | 9 | 808 | 1 | 9 | 78 | 1 | 13 | 43900 | 1 | 9 | 77300 | 1 | 9 | 10800 | 1 | 13 | 1570 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -18.3 | -0.94 | A | 7 | 0.76 | A | 7 | 1005 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.9 | 6 | 0
1985-02-08 | 1900-02-07 | 12:00 | 12 | 734 | 1406 | 546 | 1 | 9 | 876 | 1 | 9 | 92 | 1 | 13 | 57700 | 1 | 9 | 86200 | 1 | 9 | 12400 | 1 | 13 | 1990 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -18.3 | -0.94 | A | 7 | 0.56 | A | 7 | 1005 | A | 7 | 270 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.52 | 6 | 0
1985-02-08 | 1900-02-07 | 13:00 | 13 | 804 | 1406 | 608 | 1 | 9 | 897 | 1 | 9 | 98 | 1 | 13 | 64500 | 1 | 9 | 89200 | 1 | 9 | 13300 | 1 | 13 | 2230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -14.4 | 6.08 | A | 7 | 0.65 | A | 7 | 1004 | A | 7 | 200 | A | 7 | 2.6 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.68 | 6 | 0
1985-02-08 | 1900-02-07 | 14:00 | 14 | 803 | 1406 | 608 | 1 | 9 | 898 | 1 | 9 | 98 | 1 | 13 | 64500 | 1 | 9 | 89200 | 1 | 9 | 13300 | 1 | 13 | 2230 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -13.3 | 8.06 | A | 7 | 0.57 | A | 7 | 1003 | A | 7 | 300 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.62 | 6 | 0
1985-02-08 | 1900-02-07 | 15:00 | 15 | 733 | 1406 | 527 | 1 | 9 | 826 | 1 | 9 | 100 | 1 | 13 | 55100 | 1 | 9 | 81000 | 1 | 9 | 12800 | 1 | 13 | 2080 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | -5.6 | 21.92 | A | 7 | -13.9 | 6.98 | A | 7 | 0.52 | A | 7 | 1003 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 6 | 0
1985-02-08 | 1900-02-07 | 16:00 | 16 | 596 | 1406 | 390 | 1 | 9 | 692 | 1 | 9 | 100 | 1 | 13 | 41200 | 1 | 9 | 66400 | 1 | 9 | 12900 | 1 | 13 | 2000 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | -6.1 | 21.02 | A | 7 | -13.9 | 6.98 | A | 7 | 0.55 | A | 7 | 1003 | A | 7 | 290 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.52 | 6 | 0
1985-02-08 | 1900-02-07 | 17:00 | 17 | 404 | 1406 | 248 | 1 | 9 | 661 | 1 | 9 | 61 | 1 | 13 | 26300 | 1 | 9 | 58000 | 1 | 9 | 9500 | 1 | 13 | 1160 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -14.4 | 6.08 | A | 7 | 0.54 | A | 7 | 1003 | A | 7 | 280 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.44 | 6 | 0
1985-02-08 | 1900-02-07 | 18:00 | 18 | 170 | 1406 | 70 | 1 | 13 | 220 | 1 | 13 | 45 | 1 | 13 | 7400 | 1 | 13 | 12700 | 1 | 13 | 5800 | 1 | 13 | 820 | 1 | 23 | 5 | A | 7 | 3 | A | 7 | -9.4 | 15.08 | A | 7 | -16.1 | 3.02 | A | 7 | 0.59 | A | 7 | 1004 | A | 7 | 320 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.48 | 6 | 0
1985-02-08 | 1900-02-07 | 19:00 | 19 | 4 | 269 | 2 | 1 | 13 | 4 | 1 | 13 | 2 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 7 | A | 7 | 3 | A | 7 | -10 | 14 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 1003 | A | 7 | 330 | A | 7 | 1.5 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.078 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12 | 6 | 0
1985-02-08 | 1900-02-07 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -10 | 14 | A | 7 | -15 | 5 | A | 7 | 0.67 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12 | 6 | 0
1985-02-08 | 1900-02-07 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | -11.1 | 12.02 | A | 7 | -15 | 5 | A | 7 | 0.73 | A | 7 | 1003 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.52 | 6 | 0
1985-02-08 | 1900-02-07 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 1003 | A | 7 | 60 | A | 7 | 2.6 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.32 | 6 | 0
1985-02-08 | 1900-02-07 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -13.3 | 8.06 | A | 7 | -16.1 | 3.02 | A | 7 | 0.8 | A | 7 | 1002 | A | 7 | 0 | A | 7 | 0 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.06 | 6 | 0
1985-02-08 | 1900-02-07 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -16.7 | 1.94 | A | 7 | 0.83 | A | 7 | 1002 | A | 7 | 0 | A | 7 | 0 | A | 7 | 11300 | A | 7 | 7010 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.28 | 6 | 0
1985-02-09 | 1900-02-08 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -14.4 | 6.08 | A | 7 | -17.2 | 1.04 | A | 7 | 0.8 | A | 7 | 1003 | A | 7 | 320 | A | 7 | 1.5 | A | 7 | 11300 | A | 7 | 4570 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.18 | 7 | 0
1985-02-09 | 1900-02-08 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -16.7 | 1.94 | A | 7 | -19.4 | -2.92 | A | 7 | 0.79 | A | 7 | 1003 | A | 7 | 230 | A | 7 | 1.5 | A | 7 | 9700 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.14 | 7 | 0
1985-02-09 | 1900-02-08 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -16.1 | 3.02 | A | 7 | 0.84 | A | 7 | 1003 | A | 7 | 80 | A | 7 | 2.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.18 | 7 | 0
1985-02-09 | 1900-02-08 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 3 | A | 7 | -13.9 | 6.98 | A | 7 | -16.1 | 3.02 | A | 7 | 0.84 | A | 7 | 1002 | A | 7 | 110 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 6.18 | 7 | 0
1985-02-09 | 1900-02-08 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -13.9 | 6.98 | A | 7 | -20 | -4 | A | 7 | 0.6 | A | 7 | 1002 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 7010 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.08 | 7 | 0
1985-02-09 | 1900-02-08 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | -15.6 | 3.92 | A | 7 | -17.8 | -0.04 | A | 7 | 0.83 | A | 7 | 1003 | A | 7 | 0 | A | 7 | 0 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.22 | 7 | 0
1985-02-09 | 1900-02-08 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 1 | A | 7 | -16.1 | 3.02 | A | 7 | -18.3 | -0.94 | A | 7 | 0.83 | A | 7 | 1003 | A | 7 | 10 | A | 7 | 1.5 | A | 7 | 6400 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.32 | 7 | 0
1985-02-09 | 1900-02-08 | 8:00 | 8 | 6 | 316 | 4 | 1 | 13 | 4 | 1 | 13 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | -14.4 | 6.08 | A | 7 | -17.8 | -0.04 | A | 7 | 0.76 | A | 7 | 1003 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.98 | 7 | 0
1985-02-09 | 1900-02-08 | 9:00 | 9 | 179 | 1405 | 54 | 1 | 13 | 21 | 1 | 13 | 51 | 1 | 13 | 5900 | 1 | 13 | 1500 | 1 | 13 | 5700 | 1 | 13 | 1190 | 1 | 23 | 10 | A | 7 | 6 | A | 7 | -13.3 | 8.06 | A | 7 | -15.6 | 3.92 | A | 7 | 0.84 | A | 7 | 1003 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 8000 | A | 7 | 6400 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.26 | 7 | 0
1985-02-09 | 1900-02-08 | 10:00 | 10 | 413 | 1405 | 177 | 1 | 9 | 95 | 1 | 9 | 149 | 1 | 13 | 19300 | 1 | 9 | 8700 | 1 | 9 | 16800 | 1 | 13 | 3640 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -11.1 | 12.02 | A | 7 | -14.4 | 6.08 | A | 7 | 0.77 | A | 7 | 1003 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 6100 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.72 | 7 | 0
1985-02-09 | 1900-02-08 | 11:00 | 11 | 605 | 1405 | 389 | 1 | 13 | 338 | 1 | 13 | 245 | 1 | 13 | 40500 | 1 | 13 | 33800 | 1 | 13 | 25900 | 1 | 13 | 5730 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | -8.9 | 15.98 | A | 7 | -13.3 | 8.06 | A | 7 | 0.71 | A | 7 | 1003 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 6400 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.08 | 7 | 0
1985-02-09 | 1900-02-08 | 12:00 | 12 | 740 | 1405 | 422 | 1 | 9 | 132 | 1 | 9 | 353 | 1 | 13 | 46200 | 1 | 9 | 13500 | 1 | 9 | 39100 | 1 | 13 | 9470 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -7.2 | 19.04 | A | 7 | -12.8 | 8.96 | A | 7 | 0.65 | A | 7 | 1003 | A | 7 | 140 | A | 7 | 5.7 | A | 7 | 11300 | A | 7 | 6100 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.44 | 7 | 0
1985-02-09 | 1900-02-08 | 13:00 | 13 | 810 | 1405 | 399 | 1 | 9 | 200 | 1 | 9 | 284 | 1 | 13 | 43300 | 1 | 9 | 20800 | 1 | 9 | 31300 | 1 | 13 | 7520 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -6.7 | 19.94 | A | 7 | -13.3 | 8.06 | A | 7 | 0.6 | A | 7 | 1002 | A | 7 | 130 | A | 7 | 6.7 | A | 7 | 11300 | A | 7 | 6100 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.94 | 7 | 0
1985-02-09 | 1900-02-08 | 14:00 | 14 | 810 | 1405 | 420 | 1 | 9 | 115 | 1 | 9 | 355 | 1 | 13 | 46200 | 1 | 9 | 11800 | 1 | 9 | 39300 | 1 | 13 | 10270 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -5 | 23 | A | 7 | -14.4 | 6.08 | A | 7 | 0.48 | A | 7 | 1001 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 6100 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.7 | 7 | 0
1985-02-09 | 1900-02-08 | 15:00 | 15 | 739 | 1405 | 393 | 1 | 13 | 276 | 1 | 13 | 250 | 1 | 13 | 41900 | 1 | 13 | 28800 | 1 | 13 | 26700 | 1 | 13 | 5960 | 1 | 23 | 10 | A | 7 | 5 | A | 7 | -4.4 | 24.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.55 | A | 7 | 1001 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.18 | 7 | 0
1985-02-09 | 1900-02-08 | 16:00 | 16 | 602 | 1405 | 207 | 1 | 9 | 5 | 1 | 9 | 205 | 1 | 13 | 23000 | 1 | 9 | 400 | 1 | 9 | 22900 | 1 | 13 | 7280 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.5 | A | 7 | 1000 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.78 | 7 | 0
1985-02-09 | 1900-02-08 | 17:00 | 17 | 410 | 1405 | 105 | 1 | 9 | 2 | 1 | 9 | 105 | 1 | 13 | 11900 | 1 | 9 | 100 | 1 | 9 | 11800 | 1 | 13 | 3800 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.5 | A | 7 | 1000 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.78 | 7 | 0
1985-02-09 | 1900-02-08 | 18:00 | 18 | 176 | 1405 | 40 | 1 | 13 | 6 | 1 | 9 | 39 | 1 | 13 | 4500 | 1 | 13 | 0 | 1 | 9 | 4500 | 1 | 13 | 1330 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.55 | A | 7 | 1000 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.18 | 7 | 0
1985-02-09 | 1900-02-08 | 19:00 | 19 | 5 | 293 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -12.2 | 10.04 | A | 7 | 0.55 | A | 7 | 999 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 2290 | A | 7 | 0.5 | E | 8 | 0.051 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.18 | 7 | 0
1985-02-09 | 1900-02-08 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.53 | A | 7 | 999 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1980 | A | 7 | 0.5 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.98 | 7 | 0
1985-02-09 | 1900-02-08 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.55 | A | 7 | 999 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 0.6 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 7 | 0
1985-02-09 | 1900-02-08 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.55 | A | 7 | 998 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 0.6 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 7 | 0
1985-02-09 | 1900-02-08 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.58 | A | 7 | 997 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 0.6 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.28 | 7 | 0
1985-02-09 | 1900-02-08 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.55 | A | 7 | 997 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 1220 | A | 7 | 0.6 | E | 8 | 0.095 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 7 | 0
1985-02-10 | 1900-02-09 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.55 | A | 7 | 997 | A | 7 | 110 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 0.6 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 1 | 0
1985-02-10 | 1900-02-09 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.58 | A | 7 | 997 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 0.6 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.28 | 1 | 0
1985-02-10 | 1900-02-09 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.6 | A | 7 | 997 | A | 7 | 110 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 910 | A | 7 | 0.6 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.48 | 1 | 0
1985-02-10 | 1900-02-09 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -8.9 | 15.98 | A | 7 | 0.69 | A | 7 | 997 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 1600 | A | 7 | 150 | A | 7 | 0.7 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.28 | 1 | 0
1985-02-10 | 1900-02-09 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.78 | A | 7 | 996 | A | 7 | 100 | A | 7 | 6.2 | A | 7 | 1200 | A | 7 | 120 | A | 7 | 0.7 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.18 | 1 | 0
1985-02-10 | 1900-02-09 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.81 | A | 7 | 996 | A | 7 | 100 | A | 7 | 5.2 | A | 7 | 1600 | A | 7 | 180 | A | 7 | 0.7 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.4 | 1 | 0
1985-02-10 | 1900-02-09 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.81 | A | 7 | 996 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 1600 | A | 7 | 150 | A | 7 | 0.7 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.4 | 1 | 0
1985-02-10 | 1900-02-09 | 8:00 | 8 | 7 | 339 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.2 | 19.04 | A | 7 | 0.85 | A | 7 | 995 | A | 7 | 110 | A | 7 | 7.7 | A | 7 | 6400 | A | 7 | 1280 | A | 7 | 0.7 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.7 | 1 | 0
1985-02-10 | 1900-02-09 | 9:00 | 9 | 185 | 1405 | 50 | 1 | 13 | 4 | 1 | 9 | 49 | 1 | 13 | 5500 | 1 | 13 | 0 | 1 | 9 | 5500 | 1 | 13 | 1580 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.85 | A | 7 | 994 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 1600 | A | 7 | 1010 | A | 7 | 0.7 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.78 | 1 | 0
1985-02-10 | 1900-02-09 | 10:00 | 10 | 419 | 1405 | 140 | 1 | 9 | 2 | 1 | 9 | 139 | 1 | 13 | 15400 | 1 | 9 | 100 | 1 | 9 | 15300 | 1 | 13 | 4560 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.1 | 21.02 | A | 7 | 0.85 | A | 7 | 993 | A | 7 | 120 | A | 7 | 7.7 | A | 7 | 1200 | A | 7 | 270 | A | 7 | 0.8 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.68 | 1 | 0
1985-02-10 | 1900-02-09 | 11:00 | 11 | 611 | 1405 | 208 | 1 | 9 | 4 | 1 | 9 | 206 | 1 | 13 | 23100 | 1 | 9 | 300 | 1 | 9 | 23000 | 1 | 13 | 7370 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -5.6 | 21.92 | A | 7 | 0.85 | A | 7 | 993 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 1200 | A | 7 | 270 | A | 7 | 0.8 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.66 | 1 | 0
1985-02-10 | 1900-02-09 | 12:00 | 12 | 746 | 1405 | 285 | 1 | 9 | 3 | 1 | 9 | 284 | 1 | 13 | 31800 | 1 | 9 | 300 | 1 | 9 | 31700 | 1 | 13 | 10210 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5 | 23 | A | 7 | 0.85 | A | 7 | 992 | A | 7 | 130 | A | 7 | 7.2 | A | 7 | 1600 | A | 7 | 270 | A | 7 | 0.8 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.56 | 1 | 0
1985-02-10 | 1900-02-09 | 13:00 | 13 | 816 | 1405 | 333 | 1 | 9 | 2 | 1 | 9 | 332 | 1 | 13 | 37100 | 1 | 9 | 200 | 1 | 9 | 37000 | 1 | 13 | 11870 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.85 | A | 7 | 991 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 1000 | A | 7 | 150 | A | 7 | 0.8 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.54 | 1 | 0
1985-02-10 | 1900-02-09 | 14:00 | 14 | 816 | 1405 | 351 | 1 | 9 | 1 | 1 | 9 | 351 | 1 | 13 | 39000 | 1 | 9 | 100 | 1 | 9 | 38900 | 1 | 13 | 12160 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -1.1 | 30.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.89 | A | 7 | 990 | A | 7 | 140 | A | 7 | 5.2 | A | 7 | 1200 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.92 | 1 | 0
1985-02-10 | 1900-02-09 | 15:00 | 15 | 745 | 1405 | 306 | 1 | 9 | 1 | 1 | 9 | 306 | 1 | 13 | 33900 | 1 | 9 | 100 | 1 | 9 | 33900 | 1 | 13 | 10560 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -2.2 | 28.04 | A | 7 | 0.89 | A | 7 | 990 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 1200 | A | 7 | 180 | A | 7 | 0.9 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.72 | 1 | 0
1985-02-10 | 1900-02-09 | 16:00 | 16 | 608 | 1405 | 154 | 1 | 9 | 1 | 1 | 9 | 153 | 1 | 13 | 17500 | 1 | 9 | 100 | 1 | 9 | 17500 | 1 | 13 | 6080 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 989 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 240 | A | 7 | 1 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.18 | 1 | 0
1985-02-10 | 1900-02-09 | 17:00 | 17 | 416 | 1405 | 103 | 1 | 9 | 1 | 1 | 9 | 103 | 1 | 13 | 11600 | 1 | 9 | 100 | 1 | 9 | 11600 | 1 | 13 | 3780 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 989 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 4800 | A | 7 | 180 | A | 7 | 1 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.18 | 1 | 0
1985-02-10 | 1900-02-09 | 18:00 | 18 | 181 | 1405 | 32 | 1 | 13 | 1 | 1 | 9 | 32 | 1 | 13 | 3700 | 1 | 13 | 0 | 1 | 9 | 3700 | 1 | 13 | 1160 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 989 | A | 7 | 120 | A | 7 | 5.2 | A | 7 | 4800 | A | 7 | 120 | A | 7 | 1 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.18 | 1 | 0
1985-02-10 | 1900-02-09 | 19:00 | 19 | 7 | 339 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.89 | A | 7 | 988 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 150 | A | 7 | 1 | E | 8 | 0.054 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 1 | 0
1985-02-10 | 1900-02-09 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 988 | A | 7 | 120 | A | 7 | 6.2 | A | 7 | 4800 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.08 | 1 | 0
1985-02-10 | 1900-02-09 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.89 | A | 7 | 987 | A | 7 | 120 | A | 7 | 7.2 | A | 7 | 4800 | A | 7 | 150 | A | 7 | 1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 1 | 0
1985-02-10 | 1900-02-09 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.89 | A | 7 | 986 | A | 7 | 120 | A | 7 | 6.7 | A | 7 | 8000 | A | 7 | 210 | A | 7 | 1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 1 | 0
1985-02-10 | 1900-02-09 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 986 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 6400 | A | 7 | 180 | A | 7 | 1.1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.08 | 1 | 0
1985-02-10 | 1900-02-09 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 985 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 180 | A | 7 | 1.1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.08 | 1 | 0
1985-02-11 | 1900-02-10 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0 | 32 | A | 7 | 0.92 | A | 7 | 984 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 150 | A | 7 | 1.1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.08 | 2 | 0
1985-02-11 | 1900-02-10 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 984 | A | 7 | 130 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 490 | A | 7 | 1.1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.48 | 2 | 0
1985-02-11 | 1900-02-10 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 983 | A | 7 | 140 | A | 7 | 6.7 | A | 7 | 2400 | A | 7 | 310 | A | 7 | 1.1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.48 | 2 | 0
1985-02-11 | 1900-02-10 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | 0.6 | 33.08 | A | 7 | 0.96 | A | 7 | 982 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 2400 | A | 7 | 180 | A | 7 | 1.1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.48 | 2 | 0
1985-02-11 | 1900-02-10 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.96 | A | 7 | 982 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 120 | A | 7 | 1.1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.56 | 2 | 0
1985-02-11 | 1900-02-10 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | 1.1 | 33.98 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 800 | A | 7 | 90 | A | 7 | 1.1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.56 | 2 | 0
1985-02-11 | 1900-02-10 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 400 | A | 7 | 120 | A | 7 | 1.2 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.46 | 2 | 0
1985-02-11 | 1900-02-10 | 8:00 | 8 | 9 | 386 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.96 | A | 7 | 981 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 200 | A | 7 | 150 | A | 7 | 1.2 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.46 | 2 | 0
1985-02-11 | 1900-02-10 | 9:00 | 9 | 190 | 1404 | 42 | 1 | 13 | 0 | 1 | 9 | 42 | 1 | 13 | 4700 | 1 | 13 | 0 | 1 | 9 | 4700 | 1 | 13 | 1440 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 800 | A | 7 | 210 | A | 7 | 1.2 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.46 | 2 | 0
1985-02-11 | 1900-02-10 | 10:00 | 10 | 424 | 1404 | 108 | 1 | 9 | 1 | 1 | 9 | 108 | 1 | 13 | 12200 | 1 | 9 | 100 | 1 | 9 | 12200 | 1 | 13 | 3950 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.96 | A | 7 | 980 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 1400 | A | 7 | 210 | A | 7 | 1.2 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.46 | 2 | 0
1985-02-11 | 1900-02-10 | 11:00 | 11 | 616 | 1404 | 146 | 1 | 9 | 0 | 1 | 9 | 146 | 1 | 13 | 16700 | 1 | 9 | 0 | 1 | 9 | 16700 | 1 | 13 | 5930 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 1.7 | 35.06 | A | 7 | 0.96 | A | 7 | 979 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 1400 | A | 7 | 60 | A | 7 | 1.2 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.46 | 2 | 0
1985-02-11 | 1900-02-10 | 12:00 | 12 | 752 | 1404 | 212 | 1 | 9 | 1 | 1 | 9 | 211 | 1 | 13 | 24200 | 1 | 9 | 100 | 1 | 9 | 24100 | 1 | 13 | 8590 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.93 | A | 7 | 979 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 1600 | A | 7 | 460 | A | 7 | 1.2 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.14 | 2 | 0
1985-02-11 | 1900-02-10 | 13:00 | 13 | 822 | 1404 | 218 | 1 | 9 | 1 | 1 | 9 | 217 | 1 | 13 | 25100 | 1 | 9 | 100 | 1 | 9 | 25100 | 1 | 13 | 9230 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 2.2 | 35.96 | A | 7 | 0.96 | A | 7 | 978 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 3200 | A | 7 | 460 | A | 7 | 1.2 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.54 | 2 | 0
1985-02-11 | 1900-02-10 | 14:00 | 14 | 822 | 1404 | 234 | 1 | 9 | 2 | 1 | 9 | 233 | 1 | 13 | 26900 | 1 | 9 | 200 | 1 | 9 | 26800 | 1 | 13 | 9690 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.93 | A | 7 | 977 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 400 | A | 7 | 1.2 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.14 | 2 | 0
1985-02-11 | 1900-02-10 | 15:00 | 15 | 751 | 1404 | 205 | 1 | 9 | 1 | 1 | 9 | 205 | 1 | 13 | 23500 | 1 | 9 | 100 | 1 | 9 | 23500 | 1 | 13 | 8410 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.93 | A | 7 | 976 | A | 7 | 120 | A | 7 | 4.6 | A | 7 | 3200 | A | 7 | 340 | A | 7 | 1.2 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.14 | 2 | 0
1985-02-11 | 1900-02-10 | 16:00 | 16 | 614 | 1404 | 164 | 1 | 9 | 1 | 1 | 9 | 164 | 1 | 13 | 18700 | 1 | 9 | 100 | 1 | 9 | 18600 | 1 | 13 | 6420 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.93 | A | 7 | 975 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 340 | A | 7 | 1.2 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.14 | 2 | 0
1985-02-11 | 1900-02-10 | 17:00 | 17 | 421 | 1404 | 104 | 1 | 9 | 0 | 1 | 9 | 104 | 1 | 13 | 11700 | 1 | 9 | 0 | 1 | 9 | 11700 | 1 | 13 | 3830 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 180 | A | 7 | 1.1 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.66 | 2 | 0
1985-02-11 | 1900-02-10 | 18:00 | 18 | 187 | 1404 | 36 | 1 | 13 | 0 | 1 | 9 | 36 | 1 | 13 | 4100 | 1 | 13 | 0 | 1 | 9 | 4100 | 1 | 13 | 1280 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | 0.6 | 33.08 | A | 7 | 0.89 | A | 7 | 975 | A | 7 | 120 | A | 7 | 3.6 | A | 7 | 4800 | A | 7 | 180 | A | 7 | 1.1 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.66 | 2 | 0
1985-02-11 | 1900-02-10 | 19:00 | 19 | 8 | 363 | 5 | 1 | 13 | 0 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -0.6 | 30.92 | A | 7 | 0.89 | A | 7 | 974 | A | 7 | 10 | A | 7 | 2.1 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 1 | E | 8 | 0.062 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.68 | 2 | 0
1985-02-11 | 1900-02-10 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 974 | A | 7 | 350 | A | 7 | 4.1 | A | 7 | 1000 | A | 7 | 90 | A | 7 | 1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.18 | 2 | 0
1985-02-11 | 1900-02-10 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -0.6 | 30.92 | A | 7 | 0.92 | A | 7 | 973 | A | 7 | 330 | A | 7 | 4.1 | A | 7 | 1600 | A | 7 | 90 | A | 7 | 1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.18 | 2 | 0
1985-02-11 | 1900-02-10 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -1.7 | 28.94 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 330 | A | 7 | 6.7 | A | 7 | 2400 | A | 7 | 180 | A | 7 | 1 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.8 | 2 | 0
1985-02-11 | 1900-02-10 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.3 | 26.06 | A | 7 | 0.89 | A | 7 | 973 | A | 7 | 330 | A | 7 | 7.7 | A | 7 | 2400 | A | 7 | 310 | A | 7 | 0.9 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.84 | 2 | 0
1985-02-11 | 1900-02-10 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -4.4 | 24.08 | A | 7 | 0.82 | A | 7 | 973 | A | 7 | 330 | A | 7 | 8.8 | A | 7 | 2400 | A | 7 | 550 | A | 7 | 0.8 | E | 8 | 0.096 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.14 | 2 | 0
1985-02-12 | 1900-02-11 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 972 | A | 7 | 330 | A | 7 | 9.3 | A | 7 | 2400 | A | 7 | 340 | A | 7 | 0.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 3 | 0
1985-02-12 | 1900-02-11 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 972 | A | 7 | 330 | A | 7 | 11.3 | A | 7 | 2400 | A | 7 | 340 | A | 7 | 0.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 3 | 0
1985-02-12 | 1900-02-11 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 972 | A | 7 | 330 | A | 7 | 9.8 | A | 7 | 8000 | A | 7 | 370 | A | 7 | 0.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 3 | 0
1985-02-12 | 1900-02-11 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 972 | A | 7 | 320 | A | 7 | 10.8 | A | 7 | 8000 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 3 | 0
1985-02-12 | 1900-02-11 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -3.9 | 24.98 | A | 7 | 0.85 | A | 7 | 973 | A | 7 | 320 | A | 7 | 10.3 | A | 7 | 14500 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.44 | 3 | 0
1985-02-12 | 1900-02-11 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -1.7 | 28.94 | A | 7 | -5 | 23 | A | 7 | 0.78 | A | 7 | 973 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 11300 | A | 7 | 400 | A | 7 | 0.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.74 | 3 | 0
1985-02-12 | 1900-02-11 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -5.6 | 21.92 | A | 7 | 0.81 | A | 7 | 973 | A | 7 | 310 | A | 7 | 10.3 | A | 7 | 11300 | A | 7 | 340 | A | 7 | 0.8 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.16 | 3 | 0
1985-02-12 | 1900-02-11 | 8:00 | 8 | 10 | 409 | 5 | 1 | 13 | 0 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.3 | 26.06 | A | 7 | -6.7 | 19.94 | A | 7 | 0.78 | A | 7 | 973 | A | 7 | 310 | A | 7 | 9.8 | A | 7 | 6400 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.06 | 3 | 0
1985-02-12 | 1900-02-11 | 9:00 | 9 | 195 | 1404 | 64 | 1 | 13 | 0 | 1 | 9 | 64 | 1 | 13 | 7000 | 1 | 13 | 0 | 1 | 9 | 7000 | 1 | 13 | 1890 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 973 | A | 7 | 310 | A | 7 | 9.8 | A | 7 | 4800 | A | 7 | 270 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 3 | 0
1985-02-12 | 1900-02-11 | 10:00 | 10 | 430 | 1404 | 169 | 1 | 9 | 1 | 1 | 9 | 169 | 1 | 13 | 18400 | 1 | 9 | 100 | 1 | 9 | 18400 | 1 | 13 | 5110 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.81 | A | 7 | 973 | A | 7 | 310 | A | 7 | 10.8 | A | 7 | 3200 | A | 7 | 310 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.28 | 3 | 0
1985-02-12 | 1900-02-11 | 11:00 | 11 | 623 | 1404 | 272 | 1 | 9 | 0 | 1 | 9 | 272 | 1 | 13 | 29700 | 1 | 9 | 0 | 1 | 9 | 29700 | 1 | 13 | 8530 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.78 | A | 7 | 974 | A | 7 | 310 | A | 7 | 9.3 | A | 7 | 3200 | A | 7 | 370 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 3 | 0
1985-02-12 | 1900-02-11 | 12:00 | 12 | 758 | 1404 | 326 | 1 | 9 | 0 | 1 | 9 | 325 | 1 | 13 | 35900 | 1 | 9 | 0 | 1 | 9 | 35900 | 1 | 13 | 11020 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.78 | A | 7 | 973 | A | 7 | 310 | A | 7 | 10.8 | A | 7 | 3200 | A | 7 | 490 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.18 | 3 | 0
1985-02-12 | 1900-02-11 | 13:00 | 13 | 829 | 1404 | 382 | 1 | 9 | 1 | 1 | 9 | 382 | 1 | 13 | 42200 | 1 | 9 | 100 | 1 | 9 | 42200 | 1 | 13 | 12770 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.78 | A | 7 | 974 | A | 7 | 300 | A | 7 | 11.3 | A | 7 | 3200 | A | 7 | 610 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.18 | 3 | 0
1985-02-12 | 1900-02-11 | 14:00 | 14 | 828 | 1404 | 345 | 1 | 9 | 0 | 1 | 9 | 345 | 1 | 13 | 38400 | 1 | 9 | 0 | 1 | 9 | 38400 | 1 | 13 | 12240 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 300 | A | 7 | 10.3 | A | 7 | 4800 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.4 | 3 | 0
1985-02-12 | 1900-02-11 | 15:00 | 15 | 757 | 1404 | 313 | 1 | 9 | 0 | 1 | 9 | 312 | 1 | 13 | 34600 | 1 | 9 | 0 | 1 | 9 | 34600 | 1 | 13 | 10810 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.81 | A | 7 | 974 | A | 7 | 310 | A | 7 | 11.3 | A | 7 | 4800 | A | 7 | 460 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.4 | 3 | 0
1985-02-12 | 1900-02-11 | 16:00 | 16 | 620 | 1404 | 259 | 1 | 9 | 1 | 1 | 9 | 259 | 1 | 13 | 28400 | 1 | 9 | 100 | 1 | 9 | 28400 | 1 | 13 | 8350 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -7.8 | 17.96 | A | 7 | 0.81 | A | 7 | 975 | A | 7 | 300 | A | 7 | 11.3 | A | 7 | 2000 | A | 7 | 520 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.4 | 3 | 0
1985-02-12 | 1900-02-11 | 17:00 | 17 | 427 | 1404 | 176 | 1 | 9 | 1 | 1 | 9 | 176 | 1 | 13 | 19100 | 1 | 9 | 100 | 1 | 9 | 19000 | 1 | 13 | 5150 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 975 | A | 7 | 290 | A | 7 | 10.3 | A | 7 | 3200 | A | 7 | 490 | A | 7 | 0.7 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 3 | 0
1985-02-12 | 1900-02-11 | 18:00 | 18 | 192 | 1404 | 63 | 1 | 13 | 0 | 1 | 9 | 63 | 1 | 13 | 6800 | 1 | 13 | 0 | 1 | 9 | 6800 | 1 | 13 | 1860 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 976 | A | 7 | 300 | A | 7 | 10.3 | A | 7 | 3200 | A | 7 | 580 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 3 | 0
1985-02-12 | 1900-02-11 | 19:00 | 19 | 9 | 386 | 6 | 1 | 13 | 0 | 1 | 9 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 290 | A | 7 | 10.3 | A | 7 | 9700 | A | 7 | 550 | A | 7 | 0.6 | E | 8 | 0.055 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 3 | 0
1985-02-12 | 1900-02-11 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 310 | A | 7 | 11.8 | A | 7 | 11300 | A | 7 | 550 | A | 7 | 0.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 3 | 0
1985-02-12 | 1900-02-11 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 977 | A | 7 | 310 | A | 7 | 11.3 | A | 7 | 16100 | A | 7 | 580 | A | 7 | 0.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 3 | 0
1985-02-12 | 1900-02-11 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 300 | A | 7 | 10.3 | A | 7 | 19300 | A | 7 | 640 | A | 7 | 0.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 3 | 0
1985-02-12 | 1900-02-11 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -9.4 | 15.08 | A | 7 | 0.78 | A | 7 | 978 | A | 7 | 300 | A | 7 | 10.8 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.32 | 3 | 0
1985-02-12 | 1900-02-11 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.1 | 21.02 | A | 7 | -10.6 | 12.92 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 310 | A | 7 | 12.9 | A | 7 | 19300 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | 0.097 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.72 | 3 | 0
1985-02-13 | 1900-02-12 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -10.6 | 12.92 | A | 7 | 0.74 | A | 7 | 978 | A | 7 | 300 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 700 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.94 | 4 | 0
1985-02-13 | 1900-02-12 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -11.1 | 12.02 | A | 7 | 0.71 | A | 7 | 978 | A | 7 | 280 | A | 7 | 9.3 | A | 7 | 12900 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.74 | 4 | 0
1985-02-13 | 1900-02-12 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 280 | A | 7 | 10.3 | A | 7 | 14500 | A | 7 | 670 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.94 | 4 | 0
1985-02-13 | 1900-02-12 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 280 | A | 7 | 7.7 | A | 7 | 14500 | A | 7 | 910 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.94 | 4 | 0
1985-02-13 | 1900-02-12 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 979 | A | 7 | 280 | A | 7 | 8.2 | A | 7 | 12900 | A | 7 | 820 | A | 7 | 0.5 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 4 | 0
1985-02-13 | 1900-02-12 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -11.7 | 10.94 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 280 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.16 | 4 | 0
1985-02-13 | 1900-02-12 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.74 | A | 7 | 980 | A | 7 | 280 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 0.5 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.26 | 4 | 0
1985-02-13 | 1900-02-12 | 8:00 | 8 | 11 | 433 | 8 | 1 | 13 | 0 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.74 | A | 7 | 981 | A | 7 | 290 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 820 | A | 7 | 0.5 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.38 | 4 | 0
1985-02-13 | 1900-02-12 | 9:00 | 9 | 201 | 1403 | 67 | 1 | 13 | 1 | 1 | 9 | 67 | 1 | 13 | 7300 | 1 | 13 | 0 | 1 | 9 | 7300 | 1 | 13 | 1970 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.74 | A | 7 | 982 | A | 7 | 280 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 730 | A | 7 | 0.5 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.38 | 4 | 0
1985-02-13 | 1900-02-12 | 10:00 | 10 | 436 | 1403 | 170 | 1 | 9 | 1 | 1 | 9 | 170 | 1 | 13 | 18500 | 1 | 9 | 100 | 1 | 9 | 18500 | 1 | 13 | 5180 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -12.8 | 8.96 | A | 7 | 0.77 | A | 7 | 982 | A | 7 | 260 | A | 7 | 8.2 | A | 7 | 11300 | A | 7 | 820 | A | 7 | 0.5 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.58 | 4 | 0
1985-02-13 | 1900-02-12 | 11:00 | 11 | 629 | 1403 | 288 | 1 | 9 | 1 | 1 | 9 | 287 | 1 | 13 | 31300 | 1 | 9 | 100 | 1 | 9 | 31200 | 1 | 13 | 8770 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -9.4 | 15.08 | A | 7 | -13.3 | 8.06 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 270 | A | 7 | 9.8 | A | 7 | 11300 | A | 7 | 640 | A | 7 | 0.5 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.38 | 4 | 0
1985-02-13 | 1900-02-12 | 12:00 | 12 | 765 | 1403 | 462 | 1 | 13 | 406 | 1 | 13 | 242 | 1 | 13 | 49500 | 1 | 13 | 42600 | 1 | 13 | 26200 | 1 | 13 | 5780 | 1 | 23 | 9 | A | 7 | 7 | A | 7 | -8.3 | 17.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 984 | A | 7 | 270 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 580 | A | 7 | 0.5 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 4 | 0
1985-02-13 | 1900-02-12 | 13:00 | 13 | 835 | 1403 | 658 | 1 | 13 | 665 | 1 | 13 | 265 | 1 | 13 | 68400 | 1 | 13 | 67800 | 1 | 13 | 27900 | 1 | 13 | 6410 | 1 | 23 | 7 | A | 7 | 6 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 983 | A | 7 | 270 | A | 7 | 9.3 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 0.5 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.74 | 4 | 0
1985-02-13 | 1900-02-12 | 14:00 | 14 | 834 | 1403 | 643 | 1 | 9 | 810 | 1 | 9 | 166 | 1 | 13 | 67600 | 1 | 9 | 80700 | 1 | 9 | 19400 | 1 | 13 | 3820 | 1 | 18 | 2 | A | 7 | 2 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 270 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 4 | 0
1985-02-13 | 1900-02-12 | 15:00 | 15 | 763 | 1403 | 633 | 1 | 9 | 813 | 1 | 9 | 194 | 1 | 13 | 65000 | 1 | 9 | 79100 | 1 | 9 | 21800 | 1 | 13 | 3980 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | -6.1 | 21.02 | A | 7 | -12.2 | 10.04 | A | 7 | 0.62 | A | 7 | 983 | A | 7 | 290 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.02 | 4 | 0
1985-02-13 | 1900-02-12 | 16:00 | 16 | 626 | 1403 | 289 | 1 | 9 | 125 | 1 | 9 | 234 | 1 | 13 | 31800 | 1 | 9 | 12400 | 1 | 9 | 26200 | 1 | 13 | 6370 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -5.6 | 21.92 | A | 7 | -11.7 | 10.94 | A | 7 | 0.63 | A | 7 | 984 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 7620 | A | 7 | 0.6 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.92 | 4 | 0
1985-02-13 | 1900-02-12 | 17:00 | 17 | 433 | 1403 | 213 | 1 | 9 | 145 | 1 | 9 | 169 | 1 | 13 | 22800 | 1 | 9 | 13200 | 1 | 9 | 18700 | 1 | 13 | 3800 | 1 | 18 | 9 | A | 7 | 8 | A | 7 | -5.6 | 21.92 | A | 7 | -11.1 | 12.02 | A | 7 | 0.65 | A | 7 | 984 | A | 7 | 260 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 6400 | A | 7 | 0.6 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.12 | 4 | 0
1985-02-13 | 1900-02-12 | 18:00 | 18 | 197 | 1403 | 66 | 1 | 13 | 46 | 1 | 9 | 60 | 1 | 13 | 7300 | 1 | 13 | 3400 | 1 | 9 | 6800 | 1 | 13 | 1390 | 1 | 21 | 9 | A | 7 | 9 | A | 7 | -4.4 | 24.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.63 | A | 7 | 984 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 1980 | A | 7 | 0.6 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.88 | 4 | 0
1985-02-13 | 1900-02-12 | 19:00 | 19 | 10 | 409 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.58 | A | 7 | 984 | A | 7 | 260 | A | 7 | 7.7 | A | 7 | 40200 | A | 7 | 1980 | A | 7 | 0.6 | E | 8 | 0.053 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.28 | 4 | 0
1985-02-13 | 1900-02-12 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.7 | 10.94 | A | 7 | 0.55 | A | 7 | 984 | A | 7 | 260 | A | 7 | 6.2 | A | 7 | 40200 | A | 7 | 1830 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.98 | 4 | 0
1985-02-13 | 1900-02-12 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 9 | A | 7 | 7 | A | 7 | -4.4 | 24.08 | A | 7 | -10.6 | 12.92 | A | 7 | 0.63 | A | 7 | 985 | A | 7 | 260 | A | 7 | 6.2 | A | 7 | 40200 | A | 7 | 1830 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.88 | 4 | 0
1985-02-13 | 1900-02-12 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -11.1 | 12.02 | A | 7 | 0.58 | A | 7 | 985 | A | 7 | 280 | A | 7 | 8.8 | A | 7 | 40200 | A | 7 | 1680 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.28 | 4 | 0
1985-02-13 | 1900-02-12 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -10.6 | 12.92 | A | 7 | 0.6 | A | 7 | 985 | A | 7 | 270 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 2440 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.48 | 4 | 0
1985-02-13 | 1900-02-12 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -9.4 | 15.08 | A | 7 | 0.66 | A | 7 | 984 | A | 7 | 270 | A | 7 | 6.2 | A | 7 | 16100 | A | 7 | 1830 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.98 | 4 | 0
1985-02-14 | 1900-02-13 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.72 | A | 7 | 984 | A | 7 | 260 | A | 7 | 5.7 | A | 7 | 6400 | A | 7 | 670 | A | 7 | 0.7 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 5 | 0
1985-02-14 | 1900-02-13 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -8.3 | 17.06 | A | 7 | 0.72 | A | 7 | 984 | A | 7 | 260 | A | 7 | 6.7 | A | 7 | 6400 | A | 7 | 550 | A | 7 | 0.7 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.48 | 5 | 0
1985-02-14 | 1900-02-13 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -8.9 | 15.98 | A | 7 | 0.75 | A | 7 | 984 | A | 7 | 270 | A | 7 | 9.3 | A | 7 | 4800 | A | 7 | 760 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.9 | 5 | 0
1985-02-14 | 1900-02-13 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -8.3 | 17.06 | A | 7 | 0.81 | A | 7 | 984 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 4800 | A | 7 | 550 | A | 7 | 0.7 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.42 | 5 | 0
1985-02-14 | 1900-02-13 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -5.6 | 21.92 | A | 7 | -9.4 | 15.08 | A | 7 | 0.74 | A | 7 | 983 | A | 7 | 270 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 1830 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.82 | 5 | 0
1985-02-14 | 1900-02-13 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -10 | 14 | A | 7 | 0.78 | A | 7 | 983 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 4800 | A | 7 | 1680 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.24 | 5 | 0
1985-02-14 | 1900-02-13 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 3 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 984 | A | 7 | 260 | A | 7 | 7.2 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 5 | 0
1985-02-14 | 1900-02-13 | 8:00 | 8 | 13 | 456 | 3 | 1 | 13 | 0 | 1 | 9 | 3 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -11.1 | 12.02 | A | 7 | 0.77 | A | 7 | 984 | A | 7 | 260 | A | 7 | 6.7 | A | 7 | 4800 | A | 7 | 610 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.36 | 5 | 0
1985-02-14 | 1900-02-13 | 9:00 | 9 | 207 | 1403 | 85 | 1 | 13 | 161 | 1 | 9 | 62 | 1 | 13 | 8900 | 1 | 13 | 10100 | 1 | 9 | 7400 | 1 | 13 | 1200 | 1 | 21 | 5 | A | 7 | 2 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 250 | A | 7 | 7.7 | A | 7 | 8000 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 5 | 0
1985-02-14 | 1900-02-13 | 10:00 | 10 | 442 | 1403 | 231 | 1 | 13 | 101 | 1 | 13 | 199 | 1 | 13 | 25200 | 1 | 13 | 9500 | 1 | 13 | 22200 | 1 | 13 | 4570 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 260 | A | 7 | 8.8 | A | 7 | 8000 | A | 7 | 910 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 5 | 0
1985-02-14 | 1900-02-13 | 11:00 | 11 | 635 | 1403 | 188 | 1 | 9 | 7 | 1 | 9 | 185 | 1 | 13 | 21300 | 1 | 9 | 600 | 1 | 9 | 21000 | 1 | 13 | 7100 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 270 | A | 7 | 7.2 | A | 7 | 4000 | A | 7 | 550 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 5 | 0
1985-02-14 | 1900-02-13 | 12:00 | 12 | 771 | 1403 | 252 | 1 | 9 | 3 | 1 | 9 | 250 | 1 | 13 | 28500 | 1 | 9 | 300 | 1 | 9 | 28300 | 1 | 13 | 9740 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 986 | A | 7 | 250 | A | 7 | 8.2 | A | 7 | 3200 | A | 7 | 550 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.74 | 5 | 0
1985-02-14 | 1900-02-13 | 13:00 | 13 | 841 | 1403 | 552 | 1 | 9 | 265 | 1 | 9 | 394 | 1 | 13 | 59000 | 1 | 9 | 27400 | 1 | 9 | 42500 | 1 | 13 | 10670 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -7.2 | 19.04 | A | 7 | -11.7 | 10.94 | A | 7 | 0.71 | A | 7 | 986 | A | 7 | 270 | A | 7 | 8.2 | A | 7 | 3200 | A | 7 | 550 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.94 | 5 | 0
1985-02-14 | 1900-02-13 | 14:00 | 14 | 841 | 1403 | 304 | 1 | 9 | 69 | 1 | 9 | 263 | 1 | 13 | 33500 | 1 | 9 | 7000 | 1 | 9 | 29300 | 1 | 13 | 8490 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | -7.2 | 19.04 | A | 7 | -11.1 | 12.02 | A | 7 | 0.74 | A | 7 | 986 | A | 7 | 250 | A | 7 | 6.7 | A | 7 | 3200 | A | 7 | 460 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.14 | 5 | 0
1985-02-14 | 1900-02-13 | 15:00 | 15 | 769 | 1403 | 273 | 1 | 9 | 1 | 1 | 9 | 273 | 1 | 13 | 30700 | 1 | 9 | 100 | 1 | 9 | 30700 | 1 | 13 | 10240 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -6.7 | 19.94 | A | 7 | -11.7 | 10.94 | A | 7 | 0.68 | A | 7 | 986 | A | 7 | 240 | A | 7 | 6.7 | A | 7 | 3200 | A | 7 | 610 | A | 7 | 0.6 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.54 | 5 | 0
1985-02-14 | 1900-02-13 | 16:00 | 16 | 632 | 1403 | 348 | 1 | 13 | 233 | 1 | 13 | 245 | 1 | 13 | 37600 | 1 | 13 | 23300 | 1 | 13 | 27000 | 1 | 13 | 5920 | 1 | 23 | 10 | A | 7 | 7 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 986 | A | 7 | 270 | A | 7 | 8.8 | A | 7 | 11300 | A | 7 | 700 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.74 | 5 | 0
1985-02-14 | 1900-02-13 | 17:00 | 17 | 438 | 1403 | 178 | 1 | 9 | 43 | 1 | 9 | 165 | 1 | 13 | 19500 | 1 | 9 | 4000 | 1 | 9 | 18200 | 1 | 13 | 4040 | 1 | 18 | 10 | A | 7 | 8 | A | 7 | -7.2 | 19.04 | A | 7 | -12.2 | 10.04 | A | 7 | 0.68 | A | 7 | 987 | A | 7 | 280 | A | 7 | 6.7 | A | 7 | 16100 | A | 7 | 700 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 16.74 | 5 | 0
1985-02-14 | 1900-02-13 | 18:00 | 18 | 203 | 1403 | 52 | 1 | 13 | 11 | 1 | 9 | 50 | 1 | 13 | 5700 | 1 | 13 | 200 | 1 | 9 | 5700 | 1 | 13 | 1670 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | -7.8 | 17.96 | A | 7 | -12.8 | 8.96 | A | 7 | 0.68 | A | 7 | 987 | A | 7 | 280 | A | 7 | 7.7 | A | 7 | 16100 | A | 7 | 6400 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.66 | 5 | 0
1985-02-14 | 1900-02-13 | 19:00 | 19 | 12 | 432 | 8 | 1 | 13 | 0 | 1 | 13 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | -8.3 | 17.06 | A | 7 | -12.8 | 8.96 | A | 7 | 0.71 | A | 7 | 988 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.158 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.06 | 5 | 0
1985-02-14 | 1900-02-13 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 2 | A | 7 | -8.9 | 15.98 | A | 7 | -13.9 | 6.98 | A | 7 | 0.68 | A | 7 | 988 | A | 7 | 280 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.88 | 5 | 0
1985-02-14 | 1900-02-13 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 2 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 988 | A | 7 | 290 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.2 | 5 | 0
1985-02-14 | 1900-02-13 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10 | 14 | A | 7 | -14.4 | 6.08 | A | 7 | 0.7 | A | 7 | 988 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 14500 | A | 7 | 700 | A | 7 | 0.5 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.2 | 5 | 0
1985-02-14 | 1900-02-13 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10 | 14 | A | 7 | -13.9 | 6.98 | A | 7 | 0.74 | A | 7 | 989 | A | 7 | 300 | A | 7 | 5.7 | A | 7 | 12900 | A | 7 | 670 | A | 7 | 0.5 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.4 | 5 | 0
1985-02-14 | 1900-02-13 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 2 | A | 7 | -11.1 | 12.02 | A | 7 | -15.6 | 3.92 | A | 7 | 0.7 | A | 7 | 989 | A | 7 | 290 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.098 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 10.32 | 5 | 0
1985-02-15 | 1900-02-14 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 1 | A | 7 | -12.8 | 8.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.73 | A | 7 | 989 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.56 | 6 | 0
1985-02-15 | 1900-02-14 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.73 | A | 7 | 988 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.56 | 6 | 0
1985-02-15 | 1900-02-14 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -16.7 | 1.94 | A | 7 | 0.8 | A | 7 | 988 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.98 | 6 | 0
1985-02-15 | 1900-02-14 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -17.2 | 1.04 | A | 7 | 0.8 | A | 7 | 988 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.18 | 6 | 0
1985-02-15 | 1900-02-14 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -14.4 | 6.08 | A | 7 | -17.8 | -0.04 | A | 7 | 0.76 | A | 7 | 988 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 4.98 | 6 | 0
1985-02-15 | 1900-02-14 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -15 | 5 | A | 7 | -18.3 | -0.94 | A | 7 | 0.76 | A | 7 | 989 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 3.9 | 6 | 0
1985-02-15 | 1900-02-14 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -16.1 | 3.02 | A | 7 | -18.9 | -2.02 | A | 7 | 0.79 | A | 7 | 989 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 2.12 | 6 | 0
1985-02-15 | 1900-02-14 | 8:00 | 8 | 15 | 502 | 8 | 1 | 13 | 8 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | -16.7 | 1.94 | A | 7 | -19.4 | -2.92 | A | 7 | 0.79 | A | 7 | 988 | A | 7 | 250 | A | 7 | 2.6 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.14 | 6 | 0
1985-02-15 | 1900-02-14 | 9:00 | 9 | 213 | 1402 | 93 | 1 | 13 | 252 | 1 | 9 | 56 | 1 | 13 | 9700 | 1 | 13 | 16400 | 1 | 9 | 7200 | 1 | 13 | 1030 | 1 | 21 | 3 | A | 7 | 1 | A | 7 | -16.1 | 3.02 | A | 7 | -20 | -4 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 250 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 1.92 | 6 | 0
1985-02-15 | 1900-02-14 | 10:00 | 10 | 448 | 1402 | 277 | 1 | 9 | 608 | 1 | 9 | 85 | 1 | 13 | 28800 | 1 | 9 | 54400 | 1 | 9 | 11400 | 1 | 13 | 1580 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -13.9 | 6.98 | A | 7 | -18.3 | -0.94 | A | 7 | 0.69 | A | 7 | 990 | A | 7 | 260 | A | 7 | 3.1 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 5.48 | 6 | 0
1985-02-15 | 1900-02-14 | 11:00 | 11 | 641 | 1402 | 449 | 1 | 9 | 740 | 1 | 9 | 113 | 1 | 13 | 47200 | 1 | 9 | 71800 | 1 | 9 | 14200 | 1 | 13 | 2300 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -12.2 | 10.04 | A | 7 | -17.8 | -0.04 | A | 7 | 0.64 | A | 7 | 990 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.14 | 6 | 0
1985-02-15 | 1900-02-14 | 12:00 | 12 | 777 | 1402 | 579 | 1 | 9 | 811 | 1 | 9 | 133 | 1 | 13 | 61300 | 1 | 9 | 80900 | 1 | 9 | 16300 | 1 | 13 | 2980 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -17.2 | 1.04 | A | 7 | 0.61 | A | 7 | 990 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.82 | 6 | 0
1985-02-15 | 1900-02-14 | 13:00 | 13 | 847 | 1402 | 642 | 1 | 9 | 833 | 1 | 9 | 142 | 1 | 13 | 68300 | 1 | 9 | 83800 | 1 | 9 | 17400 | 1 | 13 | 3400 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -10 | 14 | A | 7 | -16.7 | 1.94 | A | 7 | 0.59 | A | 7 | 990 | A | 7 | 260 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.5 | 6 | 0
1985-02-15 | 1900-02-14 | 14:00 | 14 | 847 | 1402 | 638 | 1 | 9 | 827 | 1 | 9 | 141 | 1 | 13 | 67800 | 1 | 9 | 83300 | 1 | 9 | 17300 | 1 | 13 | 3380 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -8.9 | 15.98 | A | 7 | -15 | 5 | A | 7 | 0.62 | A | 7 | 990 | A | 7 | 270 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 13.48 | 6 | 0
1985-02-15 | 1900-02-14 | 15:00 | 15 | 775 | 1402 | 574 | 1 | 9 | 806 | 1 | 9 | 132 | 1 | 13 | 60800 | 1 | 9 | 80400 | 1 | 9 | 16200 | 1 | 13 | 2960 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -15 | 5 | A | 7 | 0.57 | A | 7 | 990 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.96 | 6 | 0
1985-02-15 | 1900-02-14 | 16:00 | 16 | 638 | 1402 | 445 | 1 | 9 | 737 | 1 | 9 | 113 | 1 | 13 | 46800 | 1 | 9 | 71400 | 1 | 9 | 14200 | 1 | 13 | 2290 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -15.6 | 3.92 | A | 7 | 0.52 | A | 7 | 989 | A | 7 | 260 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.54 | 6 | 0
1985-02-15 | 1900-02-14 | 17:00 | 17 | 444 | 1402 | 272 | 1 | 9 | 601 | 1 | 9 | 84 | 1 | 13 | 28300 | 1 | 9 | 53600 | 1 | 9 | 11200 | 1 | 13 | 1560 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -16.1 | 3.02 | A | 7 | 0.5 | A | 7 | 989 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.34 | 6 | 0
1985-02-15 | 1900-02-14 | 18:00 | 18 | 208 | 1402 | 91 | 1 | 13 | 300 | 1 | 9 | 48 | 1 | 13 | 9600 | 1 | 13 | 19400 | 1 | 9 | 6800 | 1 | 13 | 870 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -7.8 | 17.96 | A | 7 | -16.1 | 3.02 | A | 7 | 0.52 | A | 7 | 989 | A | 7 | 250 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.56 | 6 | 0
1985-02-15 | 1900-02-14 | 19:00 | 19 | 13 | 479 | 9 | 1 | 13 | 8 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 2 | A | 7 | 0 | A | 7 | -11.1 | 12.02 | A | 7 | -17.8 | -0.04 | A | 7 | 0.58 | A | 7 | 989 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.132 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.62 | 6 | 0
1985-02-15 | 1900-02-14 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 1 | A | 7 | -11.7 | 10.94 | A | 7 | -17.8 | -0.04 | A | 7 | 0.61 | A | 7 | 988 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.84 | 6 | 0
1985-02-15 | 1900-02-14 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 3 | A | 7 | -12.2 | 10.04 | A | 7 | -17.2 | 1.04 | A | 7 | 0.67 | A | 7 | 988 | A | 7 | 240 | A | 7 | 2.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 6 | 0
1985-02-15 | 1900-02-14 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 8 | A | 7 | -11.7 | 10.94 | A | 7 | -16.7 | 1.94 | A | 7 | 0.67 | A | 7 | 988 | A | 7 | 0 | A | 7 | 0 | A | 7 | 19300 | A | 7 | 1070 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 9.14 | 6 | 0
1985-02-15 | 1900-02-14 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -12.2 | 10.04 | A | 7 | -17.2 | 1.04 | A | 7 | 0.67 | A | 7 | 987 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 8.34 | 6 | 0
1985-02-15 | 1900-02-14 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.73 | A | 7 | 987 | A | 7 | 190 | A | 7 | 2.6 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.56 | 6 | 0
1985-02-16 | 1900-02-15 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | -12.8 | 8.96 | A | 7 | -16.7 | 1.94 | A | 7 | 0.73 | A | 7 | 987 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.56 | 7 | 0
1985-02-16 | 1900-02-15 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -12.8 | 8.96 | A | 7 | -16.1 | 3.02 | A | 7 | 0.76 | A | 7 | 986 | A | 7 | 210 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.4 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 7.76 | 7 | 0
1985-02-16 | 1900-02-15 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -10.6 | 12.92 | A | 7 | -14.4 | 6.08 | A | 7 | 0.73 | A | 7 | 986 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.5 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 11.32 | 7 | 0
1985-02-16 | 1900-02-15 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -10 | 14 | A | 7 | -13.9 | 6.98 | A | 7 | 0.74 | A | 7 | 985 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 4570 | A | 7 | 0.5 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 12.4 | 7 | 0
1985-02-16 | 1900-02-15 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -8.9 | 15.98 | A | 7 | -12.8 | 8.96 | A | 7 | 0.74 | A | 7 | 985 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 2130 | A | 7 | 0.5 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 14.28 | 7 | 0
1985-02-16 | 1900-02-15 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -8.3 | 17.06 | A | 7 | -12.2 | 10.04 | A | 7 | 0.74 | A | 7 | 985 | A | 7 | 170 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.5 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.26 | 7 | 0
1985-02-16 | 1900-02-15 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -7.8 | 17.96 | A | 7 | -12.2 | 10.04 | A | 7 | 0.71 | A | 7 | 985 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 0.5 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 15.96 | 7 | 0
1985-02-16 | 1900-02-15 | 8:00 | 8 | 17 | 526 | 6 | 1 | 13 | 1 | 1 | 13 | 6 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 8 | A | 7 | 4 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 985 | A | 7 | 190 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 7 | 0
1985-02-16 | 1900-02-15 | 9:00 | 9 | 218 | 1401 | 82 | 1 | 13 | 83 | 1 | 13 | 70 | 1 | 13 | 8900 | 1 | 13 | 5700 | 1 | 13 | 8000 | 1 | 13 | 1490 | 1 | 23 | 10 | A | 7 | 4 | A | 7 | -6.7 | 19.94 | A | 7 | -12.2 | 10.04 | A | 7 | 0.65 | A | 7 | 984 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.5 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.34 | 7 | 0
1985-02-16 | 1900-02-15 | 10:00 | 10 | 454 | 1401 | 80 | 1 | 9 | 2 | 1 | 9 | 80 | 1 | 13 | 9400 | 1 | 9 | 100 | 1 | 9 | 9300 | 1 | 13 | 3260 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | -5 | 23 | A | 7 | -10.6 | 12.92 | A | 7 | 0.65 | A | 7 | 983 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 1980 | A | 7 | 0.6 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.1 | 7 | 0
1985-02-16 | 1900-02-15 | 11:00 | 11 | 647 | 1401 | 402 | 1 | 9 | 565 | 1 | 9 | 143 | 1 | 13 | 43100 | 1 | 9 | 55900 | 1 | 9 | 17100 | 1 | 13 | 2900 | 1 | 18 | 1 | A | 7 | 1 | A | 7 | -2.8 | 26.96 | A | 7 | -9.4 | 15.08 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 200 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.26 | 7 | 0
1985-02-16 | 1900-02-15 | 12:00 | 12 | 784 | 1401 | 544 | 1 | 9 | 660 | 1 | 9 | 178 | 1 | 13 | 56400 | 1 | 9 | 64900 | 1 | 9 | 20000 | 1 | 13 | 3820 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.59 | A | 7 | 982 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.62 | 7 | 0
1985-02-16 | 1900-02-15 | 13:00 | 13 | 854 | 1401 | 615 | 1 | 9 | 684 | 1 | 9 | 201 | 1 | 13 | 63700 | 1 | 9 | 67600 | 1 | 9 | 22400 | 1 | 13 | 4580 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -6.7 | 19.94 | A | 7 | 0.57 | A | 7 | 982 | A | 7 | 230 | A | 7 | 8.8 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.98 | 7 | 0
1985-02-16 | 1900-02-15 | 14:00 | 14 | 853 | 1401 | 603 | 1 | 9 | 683 | 1 | 9 | 190 | 1 | 13 | 62700 | 1 | 9 | 67800 | 1 | 9 | 21300 | 1 | 13 | 4370 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.57 | A | 7 | 981 | A | 7 | 230 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.86 | 7 | 0
1985-02-16 | 1900-02-15 | 15:00 | 15 | 781 | 1401 | 547 | 1 | 9 | 651 | 1 | 9 | 187 | 1 | 13 | 58500 | 1 | 9 | 66200 | 1 | 9 | 21500 | 1 | 13 | 4190 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -5 | 23 | A | 7 | 0.62 | A | 7 | 981 | A | 7 | 220 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.46 | 7 | 0
1985-02-16 | 1900-02-15 | 16:00 | 16 | 644 | 1401 | 419 | 1 | 9 | 573 | 1 | 9 | 159 | 1 | 13 | 44500 | 1 | 9 | 56600 | 1 | 9 | 18400 | 1 | 13 | 3260 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 2.2 | 35.96 | A | 7 | -5 | 23 | A | 7 | 0.59 | A | 7 | 981 | A | 7 | 230 | A | 7 | 10.3 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.86 | 7 | 0
1985-02-16 | 1900-02-15 | 17:00 | 17 | 450 | 1401 | 162 | 1 | 9 | 24 | 1 | 9 | 155 | 1 | 13 | 17900 | 1 | 9 | 1800 | 1 | 9 | 17300 | 1 | 13 | 5090 | 1 | 18 | 9 | A | 7 | 9 | A | 7 | 2.2 | 35.96 | A | 7 | -3.9 | 24.98 | A | 7 | 0.64 | A | 7 | 981 | A | 7 | 240 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 0.8 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.46 | 7 | 0
1985-02-16 | 1900-02-15 | 18:00 | 18 | 214 | 1401 | 59 | 1 | 13 | 1 | 1 | 9 | 58 | 1 | 13 | 6400 | 1 | 13 | 0 | 1 | 9 | 6400 | 1 | 13 | 1880 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 982 | A | 7 | 230 | A | 7 | 8.2 | A | 7 | 24100 | A | 7 | 3960 | A | 7 | 0.8 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.06 | 7 | 0
1985-02-16 | 1900-02-15 | 19:00 | 19 | 15 | 502 | 5 | 1 | 13 | 0 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -3.9 | 24.98 | A | 7 | 0.67 | A | 7 | 983 | A | 7 | 230 | A | 7 | 6.7 | A | 7 | 14500 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | 0.229 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.06 | 7 | 0
1985-02-16 | 1900-02-15 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 3 | A | 7 | 1.1 | 33.98 | A | 7 | -3.9 | 24.98 | A | 7 | 0.7 | A | 7 | 984 | A | 7 | 230 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.48 | 7 | 0
1985-02-16 | 1900-02-15 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.73 | A | 7 | 984 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 910 | A | 7 | 0.9 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.08 | 7 | 0
1985-02-16 | 1900-02-15 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.73 | A | 7 | 985 | A | 7 | 250 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 850 | A | 7 | 0.9 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.78 | 7 | 0
1985-02-16 | 1900-02-15 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.73 | A | 7 | 987 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 850 | A | 7 | 0.9 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.78 | 7 | 0
1985-02-16 | 1900-02-15 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 987 | A | 7 | 260 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.099 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.62 | 7 | 0
1985-02-17 | 1900-02-16 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 988 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.62 | 1 | 0
1985-02-17 | 1900-02-16 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 2 | A | 7 | -1.1 | 30.02 | A | 7 | -6.1 | 21.02 | A | 7 | 0.69 | A | 7 | 988 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.82 | 1 | 0
1985-02-17 | 1900-02-16 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | A | 7 | 1 | A | 7 | -1.7 | 28.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.14 | 1 | 0
1985-02-17 | 1900-02-16 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 989 | A | 7 | 240 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 1 | 0
1985-02-17 | 1900-02-16 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.69 | A | 7 | 990 | A | 7 | 250 | A | 7 | 4.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.84 | 1 | 0
1985-02-17 | 1900-02-16 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -7.2 | 19.04 | A | 7 | 0.75 | A | 7 | 990 | A | 7 | 240 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.76 | 1 | 0
1985-02-17 | 1900-02-16 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -8.9 | 15.98 | A | 7 | 0.81 | A | 7 | 991 | A | 7 | 240 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.52 | 1 | 0
1985-02-17 | 1900-02-16 | 8:00 | 8 | 19 | 549 | 8 | 1 | 13 | 2 | 1 | 9 | 8 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -6.7 | 19.94 | A | 7 | -9.4 | 15.08 | A | 7 | 0.81 | A | 7 | 992 | A | 7 | 220 | A | 7 | 3.1 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 18.54 | 1 | 0
1985-02-17 | 1900-02-16 | 9:00 | 9 | 224 | 1401 | 88 | 1 | 13 | 200 | 1 | 9 | 57 | 1 | 13 | 9400 | 1 | 13 | 13200 | 1 | 9 | 7300 | 1 | 13 | 1070 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -6.1 | 21.02 | A | 7 | 0.81 | A | 7 | 993 | A | 7 | 240 | A | 7 | 4.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.36 | 1 | 0
1985-02-17 | 1900-02-16 | 10:00 | 10 | 460 | 1401 | 257 | 1 | 9 | 475 | 1 | 9 | 103 | 1 | 13 | 27400 | 1 | 9 | 43300 | 1 | 9 | 13100 | 1 | 13 | 1940 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -5 | 23 | A | 7 | 0.72 | A | 7 | 993 | A | 7 | 230 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.02 | 1 | 0
1985-02-17 | 1900-02-16 | 11:00 | 11 | 654 | 1401 | 425 | 1 | 9 | 618 | 1 | 9 | 139 | 1 | 13 | 44100 | 1 | 9 | 59600 | 1 | 9 | 16200 | 1 | 13 | 2750 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 0.6 | 33.08 | A | 7 | -4.4 | 24.08 | A | 7 | 0.7 | A | 7 | 994 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.68 | 1 | 0
1985-02-17 | 1900-02-16 | 12:00 | 12 | 790 | 1401 | 554 | 1 | 9 | 687 | 1 | 9 | 170 | 1 | 13 | 57700 | 1 | 9 | 67800 | 1 | 9 | 19400 | 1 | 13 | 3710 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 1.7 | 35.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.64 | A | 7 | 995 | A | 7 | 270 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.66 | 1 | 0
1985-02-17 | 1900-02-16 | 13:00 | 13 | 860 | 1401 | 621 | 1 | 9 | 720 | 1 | 9 | 183 | 1 | 13 | 65000 | 1 | 9 | 71700 | 1 | 9 | 20800 | 1 | 13 | 4280 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -4.4 | 24.08 | A | 7 | 0.59 | A | 7 | 995 | A | 7 | 250 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.04 | 1 | 0
1985-02-17 | 1900-02-16 | 14:00 | 14 | 859 | 1401 | 633 | 1 | 9 | 552 | 1 | 9 | 297 | 1 | 13 | 65300 | 1 | 9 | 56300 | 1 | 9 | 30600 | 1 | 13 | 7440 | 1 | 18 | 7 | A | 7 | 2 | A | 7 | 3.3 | 37.94 | A | 7 | -5 | 23 | A | 7 | 0.55 | A | 7 | 995 | A | 7 | 280 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.24 | 1 | 0
1985-02-17 | 1900-02-16 | 15:00 | 15 | 788 | 1401 | 549 | 1 | 9 | 681 | 1 | 9 | 169 | 1 | 13 | 57200 | 1 | 9 | 67200 | 1 | 9 | 19200 | 1 | 13 | 3680 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.53 | A | 7 | 996 | A | 7 | 300 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.74 | 1 | 0
1985-02-17 | 1900-02-16 | 16:00 | 16 | 650 | 1401 | 421 | 1 | 9 | 603 | 1 | 9 | 144 | 1 | 13 | 45200 | 1 | 9 | 59700 | 1 | 9 | 17400 | 1 | 13 | 2920 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -5 | 23 | A | 7 | 0.53 | A | 7 | 997 | A | 7 | 290 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.92 | 1 | 0
1985-02-17 | 1900-02-16 | 17:00 | 17 | 456 | 1401 | 254 | 1 | 9 | 473 | 1 | 9 | 102 | 1 | 13 | 27000 | 1 | 9 | 43000 | 1 | 9 | 13000 | 1 | 13 | 1920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 3.3 | 37.94 | A | 7 | -5.6 | 21.92 | A | 7 | 0.53 | A | 7 | 997 | A | 7 | 270 | A | 7 | 4.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.74 | 1 | 0
1985-02-17 | 1900-02-16 | 18:00 | 18 | 219 | 1401 | 85 | 1 | 13 | 190 | 1 | 9 | 56 | 1 | 13 | 9100 | 1 | 13 | 12400 | 1 | 9 | 7100 | 1 | 13 | 1050 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -5.6 | 21.92 | A | 7 | 0.55 | A | 7 | 998 | A | 7 | 280 | A | 7 | 4.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.24 | 1 | 0
1985-02-17 | 1900-02-16 | 19:00 | 19 | 17 | 525 | 8 | 1 | 13 | 2 | 1 | 9 | 7 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.54 | A | 7 | 998 | A | 7 | 270 | A | 7 | 3.6 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.208 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.58 | 1 | 0
1985-02-17 | 1900-02-16 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -7.8 | 17.96 | A | 7 | 0.59 | A | 7 | 999 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 40200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.62 | 1 | 0
1985-02-17 | 1900-02-16 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -8.3 | 17.06 | A | 7 | 0.63 | A | 7 | 999 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 40200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.44 | 1 | 0
1985-02-17 | 1900-02-16 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -1.7 | 28.94 | A | 7 | -7.8 | 17.96 | A | 7 | 0.64 | A | 7 | 999 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 40200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.34 | 1 | 0
1985-02-17 | 1900-02-16 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -8.9 | 15.98 | A | 7 | 0.72 | A | 7 | 1000 | A | 7 | 220 | A | 7 | 2.6 | A | 7 | 40200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.68 | 1 | 0
1985-02-17 | 1900-02-16 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -4.4 | 24.08 | A | 7 | -8.3 | 17.06 | A | 7 | 0.75 | A | 7 | 1000 | A | 7 | 230 | A | 7 | 3.1 | A | 7 | 40200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.1 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.88 | 1 | 0
1985-02-18 | 1900-02-17 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.78 | A | 7 | 1000 | A | 7 | 240 | A | 7 | 1.5 | A | 7 | 40200 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.18 | 2 | 0
1985-02-18 | 1900-02-17 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 2 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.78 | A | 7 | 999 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 2 | 0
1985-02-18 | 1900-02-17 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | A | 7 | 5 | A | 7 | -5 | 23 | A | 7 | -8.3 | 17.06 | A | 7 | 0.78 | A | 7 | 1000 | A | 7 | 210 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 7010 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 21.2 | 2 | 0
1985-02-18 | 1900-02-17 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | -4.4 | 24.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.78 | A | 7 | 999 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 6100 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.18 | 2 | 0
1985-02-18 | 1900-02-17 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -3.9 | 24.98 | A | 7 | -7.2 | 19.04 | A | 7 | 0.78 | A | 7 | 1000 | A | 7 | 180 | A | 7 | 1.5 | A | 7 | 32200 | A | 7 | 3660 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.08 | 2 | 0
1985-02-18 | 1900-02-17 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.8 | 26.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.72 | A | 7 | 1000 | A | 7 | 140 | A | 7 | 2.1 | A | 7 | 32200 | A | 7 | 3350 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.36 | 2 | 0
1985-02-18 | 1900-02-17 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -2.2 | 28.04 | A | 7 | -6.1 | 21.02 | A | 7 | 0.75 | A | 7 | 1000 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 0.8 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.64 | 2 | 0
1985-02-18 | 1900-02-17 | 8:00 | 8 | 21 | 572 | 18 | 1 | 13 | 34 | 1 | 13 | 14 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 23 | 9 | A | 7 | 4 | A | 7 | -1.7 | 28.94 | A | 7 | -6.1 | 21.02 | A | 7 | 0.72 | A | 7 | 1000 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.14 | 2 | 0
1985-02-18 | 1900-02-17 | 9:00 | 9 | 231 | 1400 | 95 | 1 | 13 | 85 | 1 | 13 | 81 | 1 | 13 | 10200 | 1 | 13 | 6000 | 1 | 13 | 9200 | 1 | 13 | 1720 | 1 | 23 | 8 | A | 7 | 7 | A | 7 | -1.1 | 30.02 | A | 7 | -5.6 | 21.92 | A | 7 | 0.72 | A | 7 | 1000 | A | 7 | 140 | A | 7 | 2.6 | A | 7 | 14500 | A | 7 | 2440 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 2 | 0
1985-02-18 | 1900-02-17 | 10:00 | 10 | 467 | 1400 | 202 | 1 | 9 | 108 | 1 | 9 | 166 | 1 | 13 | 22100 | 1 | 9 | 10200 | 1 | 9 | 18700 | 1 | 13 | 4200 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 0.6 | 33.08 | A | 7 | -3.9 | 24.98 | A | 7 | 0.73 | A | 7 | 1000 | A | 7 | 130 | A | 7 | 2.1 | A | 7 | 14500 | A | 7 | 2440 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.08 | 2 | 0
1985-02-18 | 1900-02-17 | 11:00 | 11 | 660 | 1400 | 386 | 1 | 13 | 459 | 1 | 13 | 172 | 1 | 13 | 40700 | 1 | 13 | 45500 | 1 | 13 | 19200 | 1 | 13 | 3580 | 1 | 23 | 6 | A | 7 | 4 | A | 7 | 1.7 | 35.06 | A | 7 | -4.4 | 24.08 | A | 7 | 0.64 | A | 7 | 999 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 1980 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.66 | 2 | 0
1985-02-18 | 1900-02-17 | 12:00 | 12 | 796 | 1400 | 564 | 1 | 9 | 826 | 1 | 9 | 97 | 1 | 13 | 59800 | 1 | 9 | 82100 | 1 | 9 | 12900 | 1 | 13 | 2200 | 1 | 18 | 4 | A | 7 | 1 | A | 7 | 3.9 | 39.02 | A | 7 | -5 | 23 | A | 7 | 0.53 | A | 7 | 999 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 32200 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.92 | 2 | 0
1985-02-18 | 1900-02-17 | 13:00 | 13 | 867 | 1400 | 317 | 1 | 9 | 11 | 1 | 9 | 310 | 1 | 13 | 35800 | 1 | 9 | 1100 | 1 | 9 | 35100 | 1 | 13 | 12040 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -4.4 | 24.08 | A | 7 | 0.53 | A | 7 | 998 | A | 7 | 200 | A | 7 | 5.7 | A | 7 | 32200 | A | 7 | 1520 | A | 7 | 0.8 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.72 | 2 | 0
1985-02-18 | 1900-02-17 | 14:00 | 14 | 866 | 1400 | 363 | 1 | 9 | 5 | 1 | 9 | 360 | 1 | 13 | 40500 | 1 | 9 | 500 | 1 | 9 | 40200 | 1 | 13 | 13000 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -3.9 | 24.98 | A | 7 | 0.53 | A | 7 | 996 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 3050 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.6 | 2 | 0
1985-02-18 | 1900-02-17 | 15:00 | 15 | 794 | 1400 | 228 | 1 | 9 | 2 | 1 | 9 | 227 | 1 | 13 | 26100 | 1 | 9 | 200 | 1 | 9 | 26000 | 1 | 13 | 9340 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -3.9 | 24.98 | A | 7 | 0.53 | A | 7 | 996 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 1400 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.6 | 2 | 0
1985-02-18 | 1900-02-17 | 16:00 | 16 | 656 | 1400 | 239 | 1 | 9 | 3 | 1 | 9 | 238 | 1 | 13 | 26600 | 1 | 9 | 300 | 1 | 9 | 26500 | 1 | 13 | 8430 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5 | 41 | A | 7 | -3.3 | 26.06 | A | 7 | 0.55 | A | 7 | 995 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 32200 | A | 7 | 1190 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.9 | 2 | 0
1985-02-18 | 1900-02-17 | 17:00 | 17 | 461 | 1400 | 146 | 1 | 9 | 5 | 1 | 9 | 144 | 1 | 13 | 16200 | 1 | 9 | 400 | 1 | 9 | 16000 | 1 | 13 | 4970 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 4.4 | 39.92 | A | 7 | -2.8 | 26.96 | A | 7 | 0.6 | A | 7 | 995 | A | 7 | 240 | A | 7 | 6.2 | A | 7 | 32200 | A | 7 | 1100 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.72 | 2 | 0
1985-02-18 | 1900-02-17 | 18:00 | 18 | 224 | 1400 | 61 | 1 | 13 | 0 | 1 | 9 | 61 | 1 | 13 | 6700 | 1 | 13 | 0 | 1 | 9 | 6700 | 1 | 13 | 1980 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -2.8 | 26.96 | A | 7 | 0.65 | A | 7 | 995 | A | 7 | 240 | A | 7 | 5.2 | A | 7 | 24100 | A | 7 | 850 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.54 | 2 | 0
1985-02-18 | 1900-02-17 | 19:00 | 19 | 19 | 548 | 10 | 1 | 13 | 0 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -2.2 | 28.04 | A | 7 | 0.7 | A | 7 | 995 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 850 | A | 7 | 0.9 | E | 8 | 0.043 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.34 | 2 | 0
1985-02-18 | 1900-02-17 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 995 | A | 7 | 220 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 1070 | A | 7 | 1 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.16 | 2 | 0
1985-02-18 | 1900-02-17 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.73 | A | 7 | 995 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 1130 | A | 7 | 1 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.74 | 2 | 0
1985-02-18 | 1900-02-17 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.79 | A | 7 | 995 | A | 7 | 250 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 940 | A | 7 | 1 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.46 | 2 | 0
1985-02-18 | 1900-02-17 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -0.6 | 30.92 | A | 7 | 0.82 | A | 7 | 996 | A | 7 | 270 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 550 | A | 7 | 1 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.86 | 2 | 0
1985-02-18 | 1900-02-17 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -3.3 | 26.06 | A | 7 | 0.73 | A | 7 | 997 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 30.78 | 2 | 0
1985-02-19 | 1900-02-18 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | 0 | 32 | A | 7 | -5.6 | 21.92 | A | 7 | 0.67 | A | 7 | 997 | A | 7 | 310 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.4 | 3 | 0
1985-02-19 | 1900-02-18 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | A | 7 | 0 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.67 | A | 7 | 998 | A | 7 | 310 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.42 | 3 | 0
1985-02-19 | 1900-02-18 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -2.2 | 28.04 | A | 7 | -7.8 | 17.96 | A | 7 | 0.66 | A | 7 | 998 | A | 7 | 300 | A | 7 | 5.2 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.74 | 3 | 0
1985-02-19 | 1900-02-18 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.66 | A | 7 | 998 | A | 7 | 310 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.96 | 3 | 0
1985-02-19 | 1900-02-18 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -3.3 | 26.06 | A | 7 | -8.9 | 15.98 | A | 7 | 0.66 | A | 7 | 998 | A | 7 | 320 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 22.96 | 3 | 0
1985-02-19 | 1900-02-18 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -5 | 23 | A | 7 | -9.4 | 15.08 | A | 7 | 0.71 | A | 7 | 999 | A | 7 | 320 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.6 | 3 | 0
1985-02-19 | 1900-02-18 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | A | 7 | 0 | A | 7 | -6.1 | 21.02 | A | 7 | -10 | 14 | A | 7 | 0.74 | A | 7 | 999 | A | 7 | 340 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 19.02 | 3 | 0
1985-02-19 | 1900-02-18 | 8:00 | 8 | 23 | 618 | 16 | 1 | 13 | 20 | 1 | 9 | 14 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 7 | A | 7 | 0 | A | 7 | -7.2 | 19.04 | A | 7 | -10 | 14 | A | 7 | 0.81 | A | 7 | 1000 | A | 7 | 260 | A | 7 | 2.1 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 17.64 | 3 | 0
1985-02-19 | 1900-02-18 | 9:00 | 9 | 237 | 1400 | 115 | 1 | 13 | 268 | 1 | 9 | 71 | 1 | 13 | 11800 | 1 | 13 | 18400 | 1 | 9 | 8700 | 1 | 13 | 1330 | 1 | 21 | 10 | A | 7 | 0 | A | 7 | -5.6 | 21.92 | A | 7 | -8.9 | 15.98 | A | 7 | 0.78 | A | 7 | 1000 | A | 7 | 220 | A | 7 | 2.1 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.6 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 20.12 | 3 | 0
1985-02-19 | 1900-02-18 | 10:00 | 10 | 473 | 1400 | 295 | 1 | 9 | 451 | 1 | 9 | 145 | 1 | 13 | 30400 | 1 | 9 | 41200 | 1 | 9 | 16400 | 1 | 13 | 2850 | 1 | 18 | 10 | A | 7 | 2 | A | 7 | -3.3 | 26.06 | A | 7 | -7.8 | 17.96 | A | 7 | 0.72 | A | 7 | 1000 | A | 7 | 200 | A | 7 | 1.5 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 23.46 | 3 | 0
1985-02-19 | 1900-02-18 | 11:00 | 11 | 666 | 1400 | 455 | 1 | 9 | 579 | 1 | 9 | 182 | 1 | 13 | 47800 | 1 | 9 | 57400 | 1 | 9 | 20300 | 1 | 13 | 3820 | 1 | 18 | 10 | A | 7 | 1 | A | 7 | -2.2 | 28.04 | A | 7 | -7.2 | 19.04 | A | 7 | 0.69 | A | 7 | 1000 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 12900 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.04 | 3 | 0
1985-02-19 | 1900-02-18 | 12:00 | 12 | 803 | 1400 | 569 | 1 | 9 | 783 | 1 | 9 | 123 | 1 | 13 | 60800 | 1 | 9 | 78700 | 1 | 9 | 15500 | 1 | 13 | 2860 | 1 | 18 | 2 | A | 7 | 1 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 1000 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.52 | 3 | 0
1985-02-19 | 1900-02-18 | 13:00 | 13 | 873 | 1400 | 574 | 1 | 9 | 552 | 1 | 9 | 233 | 1 | 13 | 61000 | 1 | 9 | 56700 | 1 | 9 | 25500 | 1 | 13 | 5760 | 1 | 18 | 9 | A | 7 | 1 | A | 7 | -1.1 | 30.02 | A | 7 | -7.2 | 19.04 | A | 7 | 0.64 | A | 7 | 999 | A | 7 | 190 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.32 | 3 | 0
1985-02-19 | 1900-02-18 | 14:00 | 14 | 872 | 1400 | 647 | 1 | 13 | 617 | 1 | 13 | 265 | 1 | 13 | 67700 | 1 | 13 | 63200 | 1 | 13 | 28100 | 1 | 13 | 6630 | 1 | 23 | 10 | A | 7 | 3 | A | 7 | 0 | 32 | A | 7 | -7.2 | 19.04 | A | 7 | 0.59 | A | 7 | 998 | A | 7 | 180 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.5 | 3 | 0
1985-02-19 | 1900-02-18 | 15:00 | 15 | 800 | 1400 | 297 | 1 | 9 | 1 | 1 | 9 | 297 | 1 | 13 | 33400 | 1 | 9 | 100 | 1 | 9 | 33300 | 1 | 13 | 11070 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0 | 32 | A | 7 | -7.8 | 17.96 | A | 7 | 0.56 | A | 7 | 997 | A | 7 | 190 | A | 7 | 3.1 | A | 7 | 24100 | A | 7 | 5180 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.2 | 3 | 0
1985-02-19 | 1900-02-18 | 16:00 | 16 | 662 | 1400 | 232 | 1 | 9 | 3 | 1 | 9 | 230 | 1 | 13 | 25800 | 1 | 9 | 300 | 1 | 9 | 25700 | 1 | 13 | 8340 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -7.8 | 17.96 | A | 7 | 0.54 | A | 7 | 996 | A | 7 | 140 | A | 7 | 2.1 | A | 7 | 24100 | A | 7 | 3350 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.88 | 3 | 0
1985-02-19 | 1900-02-18 | 17:00 | 17 | 467 | 1400 | 172 | 1 | 9 | 4 | 1 | 9 | 170 | 1 | 13 | 18800 | 1 | 9 | 300 | 1 | 9 | 18700 | 1 | 13 | 5480 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 0.6 | 33.08 | A | 7 | -7.2 | 19.04 | A | 7 | 0.56 | A | 7 | 996 | A | 7 | 240 | A | 7 | 1.5 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.08 | 3 | 0
1985-02-19 | 1900-02-18 | 18:00 | 18 | 230 | 1400 | 40 | 1 | 13 | 27 | 1 | 9 | 36 | 1 | 13 | 4500 | 1 | 13 | 2000 | 1 | 9 | 4100 | 1 | 13 | 960 | 1 | 21 | 10 | A | 7 | 9 | A | 7 | 0.6 | 33.08 | A | 7 | -6.7 | 19.94 | A | 7 | 0.59 | A | 7 | 996 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 19300 | A | 7 | 3050 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 28.48 | 3 | 0
1985-02-19 | 1900-02-18 | 19:00 | 19 | 21 | 571 | 5 | 1 | 13 | 1 | 1 | 9 | 5 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -5.6 | 21.92 | A | 7 | 0.69 | A | 7 | 996 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 2740 | A | 7 | 0.8 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.62 | 3 | 0
1985-02-19 | 1900-02-18 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 996 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 2440 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 3 | 0
1985-02-19 | 1900-02-18 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 995 | A | 7 | 110 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 3 | 0
1985-02-19 | 1900-02-18 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 995 | A | 7 | 120 | A | 7 | 2.6 | A | 7 | 14500 | A | 7 | 1680 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 3 | 0
1985-02-19 | 1900-02-18 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -6.7 | 19.94 | A | 7 | 0.64 | A | 7 | 995 | A | 7 | 120 | A | 7 | 1.5 | A | 7 | 14500 | A | 7 | 1340 | A | 7 | 0.7 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.12 | 3 | 0
1985-02-19 | 1900-02-18 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.67 | A | 7 | 995 | A | 7 | 100 | A | 7 | 2.6 | A | 7 | 14500 | A | 7 | 1830 | A | 7 | 0.8 | E | 8 | 0.101 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.42 | 3 | 0
1985-02-20 | 1900-02-19 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.67 | A | 7 | 995 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 0.8 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.42 | 4 | 0
1985-02-20 | 1900-02-19 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | -0.6 | 30.92 | A | 7 | -6.1 | 21.02 | A | 7 | 0.67 | A | 7 | 995 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 0.8 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 27.42 | 4 | 0
1985-02-20 | 1900-02-19 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -0.6 | 30.92 | A | 7 | -7.2 | 19.04 | A | 7 | 0.61 | A | 7 | 995 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.82 | 4 | 0
1985-02-20 | 1900-02-19 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -2.2 | 28.04 | A | 7 | -7.8 | 17.96 | A | 7 | 0.66 | A | 7 | 995 | A | 7 | 110 | A | 7 | 2.6 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.74 | 4 | 0
1985-02-20 | 1900-02-19 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -1.7 | 28.94 | A | 7 | -6.7 | 19.94 | A | 7 | 0.69 | A | 7 | 994 | A | 7 | 130 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 2130 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.84 | 4 | 0
1985-02-20 | 1900-02-19 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | A | 7 | 4 | A | 7 | -2.8 | 26.96 | A | 7 | -7.8 | 17.96 | A | 7 | 0.69 | A | 7 | 995 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.06 | 4 | 0
1985-02-20 | 1900-02-19 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 6 | A | 7 | 6 | A | 7 | -2.2 | 28.04 | A | 7 | -6.7 | 19.94 | A | 7 | 0.72 | A | 7 | 995 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 1520 | A | 7 | 0.7 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 25.34 | 4 | 0
1985-02-20 | 1900-02-19 | 8:00 | 8 | 26 | 641 | 8 | 1 | 13 | 3 | 1 | 9 | 7 | 1 | 13 | 800 | 1 | 13 | 100 | 1 | 9 | 800 | 1 | 13 | 180 | 1 | 21 | 2 | A | 7 | 2 | A | 7 | -2.8 | 26.96 | A | 7 | -7.2 | 19.04 | A | 7 | 0.72 | A | 7 | 995 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 24.36 | 4 | 0
1985-02-20 | 1900-02-19 | 9:00 | 9 | 243 | 1399 | 95 | 1 | 13 | 212 | 1 | 9 | 59 | 1 | 13 | 10200 | 1 | 13 | 14700 | 1 | 9 | 7600 | 1 | 13 | 1100 | 1 | 21 | 0 | A | 7 | 0 | A | 7 | -1.1 | 30.02 | A | 7 | -6.7 | 19.94 | A | 7 | 0.66 | A | 7 | 996 | A | 7 | 160 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 77777 | A | 7 | 0.7 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 26.52 | 4 | 0
1985-02-20 | 1900-02-19 | 10:00 | 10 | 479 | 1399 | 276 | 1 | 9 | 512 | 1 | 9 | 102 | 1 | 13 | 29500 | 1 | 9 | 47300 | 1 | 9 | 13200 | 1 | 13 | 1920 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 1.1 | 33.98 | A | 7 | -5.6 | 21.92 | A | 7 | 0.62 | A | 7 | 996 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 29.58 | 4 | 0
1985-02-20 | 1900-02-19 | 11:00 | 11 | 673 | 1399 | 451 | 1 | 9 | 633 | 1 | 9 | 149 | 1 | 13 | 46600 | 1 | 9 | 61100 | 1 | 9 | 17100 | 1 | 13 | 2960 | 1 | 18 | 2 | A | 7 | 0 | A | 7 | 2.8 | 37.04 | A | 7 | -5 | 23 | A | 7 | 0.57 | A | 7 | 997 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 14500 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.44 | 4 | 0
1985-02-20 | 1900-02-19 | 12:00 | 12 | 809 | 1399 | 576 | 1 | 9 | 624 | 1 | 9 | 218 | 1 | 13 | 60900 | 1 | 9 | 63600 | 1 | 9 | 24000 | 1 | 13 | 5070 | 1 | 18 | 7 | A | 7 | 1 | A | 7 | 4.4 | 39.92 | A | 7 | -5 | 23 | A | 7 | 0.51 | A | 7 | 997 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.8 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.42 | 4 | 0
1985-02-20 | 1900-02-19 | 13:00 | 13 | 879 | 1399 | 596 | 1 | 9 | 662 | 1 | 9 | 183 | 1 | 13 | 62400 | 1 | 9 | 66100 | 1 | 9 | 20700 | 1 | 13 | 4390 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 5.6 | 42.08 | A | 7 | -3.3 | 26.06 | A | 7 | 0.53 | A | 7 | 996 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 35.58 | 4 | 0
1985-02-20 | 1900-02-19 | 14:00 | 14 | 878 | 1399 | 635 | 1 | 9 | 737 | 1 | 9 | 176 | 1 | 13 | 66800 | 1 | 9 | 73800 | 1 | 9 | 20300 | 1 | 13 | 4250 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -3.3 | 26.06 | A | 7 | 0.49 | A | 7 | 996 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 36.66 | 4 | 0
1985-02-20 | 1900-02-19 | 15:00 | 15 | 806 | 1399 | 560 | 1 | 9 | 705 | 1 | 9 | 158 | 1 | 13 | 58900 | 1 | 9 | 70100 | 1 | 9 | 18300 | 1 | 13 | 3560 | 1 | 18 | 0 | A | 7 | 0 | A | 7 | 6.7 | 44.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.56 | A | 7 | 995 | A | 7 | 130 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.66 | 4 | 0
1985-02-20 | 1900-02-19 | 16:00 | 16 | 668 | 1399 | 439 | 1 | 9 | 631 | 1 | 9 | 141 | 1 | 13 | 45600 | 1 | 9 | 61000 | 1 | 9 | 16400 | 1 | 13 | 2820 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.52 | A | 7 | 995 | A | 7 | 120 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.86 | 4 | 0
1985-02-20 | 1900-02-19 | 17:00 | 17 | 473 | 1399 | 269 | 1 | 9 | 490 | 1 | 9 | 105 | 1 | 13 | 28600 | 1 | 9 | 45000 | 1 | 9 | 13300 | 1 | 13 | 1980 | 1 | 18 | 1 | A | 7 | 0 | A | 7 | 7.2 | 44.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.52 | A | 7 | 995 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.86 | 4 | 0
1985-02-20 | 1900-02-19 | 18:00 | 18 | 235 | 1399 | 98 | 1 | 13 | 181 | 1 | 9 | 68 | 1 | 13 | 10300 | 1 | 13 | 12300 | 1 | 9 | 8200 | 1 | 13 | 1310 | 1 | 21 | 7 | A | 7 | 1 | A | 7 | 6.7 | 44.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.56 | A | 7 | 994 | A | 7 | 130 | A | 7 | 4.6 | A | 7 | 24100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.66 | 4 | 0
1985-02-20 | 1900-02-19 | 19:00 | 19 | 23 | 595 | 10 | 1 | 13 | 4 | 1 | 9 | 10 | 1 | 13 | 0 | 1 | 13 | 0 | 1 | 9 | 0 | 1 | 13 | 0 | 1 | 21 | 6 | A | 7 | 1 | A | 7 | 3.9 | 39.02 | A | 7 | -2.2 | 28.04 | A | 7 | 0.65 | A | 7 | 994 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 20900 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.196 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.52 | 4 | 0
1985-02-20 | 1900-02-19 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | A | 7 | 0 | A | 7 | 3.9 | 39.02 | A | 7 | -2.8 | 26.96 | A | 7 | 0.62 | A | 7 | 995 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.12 | 4 | 0
1985-02-20 | 1900-02-19 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | A | 7 | 2 | A | 7 | 1.7 | 35.06 | A | 7 | -2.8 | 26.96 | A | 7 | 0.73 | A | 7 | 995 | A | 7 | 120 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 31.76 | 4 | 0
1985-02-20 | 1900-02-19 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 7 | A | 7 | 3 | A | 7 | 1.7 | 35.06 | A | 7 | -2.2 | 28.04 | A | 7 | 0.76 | A | 7 | 995 | A | 7 | 130 | A | 7 | 4.1 | A | 7 | 19300 | A | 7 | 77777 | A | 7 | 0.9 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.26 | 4 | 0
1985-02-20 | 1900-02-19 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -1.7 | 28.94 | A | 7 | 0.7 | A | 7 | 995 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 19300 | A | 7 | 7010 | A | 7 | 1 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.24 | 4 | 0
1985-02-20 | 1900-02-19 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 2.8 | 37.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.73 | A | 7 | 995 | A | 7 | 140 | A | 7 | 3.6 | A | 7 | 19300 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.102 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.74 | 4 | 0
1985-02-21 | 1900-02-20 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 2.8 | 37.04 | A | 7 | -1.7 | 28.94 | A | 7 | 0.73 | A | 7 | 995 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.74 | 5 | 0
1985-02-21 | 1900-02-20 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 4 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 995 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.16 | 5 | 0
1985-02-21 | 1900-02-20 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 5 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 995 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 77777 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.16 | 5 | 0
1985-02-21 | 1900-02-20 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 7 | A | 7 | 2.2 | 35.96 | A | 7 | -2.2 | 28.04 | A | 7 | 0.73 | A | 7 | 995 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 0.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.76 | 5 | 0
1985-02-21 | 1900-02-20 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 9 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 994 | A | 7 | 130 | A | 7 | 5.7 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.16 | 5 | 0
1985-02-21 | 1900-02-20 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 8 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 994 | A | 7 | 140 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.16 | 5 | 0
1985-02-21 | 1900-02-20 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 6 | A | 7 | 2.2 | 35.96 | A | 7 | -1.7 | 28.94 | A | 7 | 0.76 | A | 7 | 994 | A | 7 | 150 | A | 7 | 3.6 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.16 | 5 | 0
1985-02-21 | 1900-02-20 | 8:00 | 8 | 29 | 664 | 11 | 1 | 13 | 1 | 1 | 9 | 11 | 1 | 13 | 1300 | 1 | 13 | 0 | 1 | 9 | 1300 | 1 | 13 | 390 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 1.7 | 35.06 | A | 7 | -1.7 | 28.94 | A | 7 | 0.79 | A | 7 | 994 | A | 7 | 120 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 7620 | A | 7 | 1 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 32.66 | 5 | 0
1985-02-21 | 1900-02-20 | 9:00 | 9 | 249 | 1398 | 60 | 1 | 13 | 7 | 1 | 9 | 59 | 1 | 13 | 6700 | 1 | 13 | 200 | 1 | 9 | 6700 | 1 | 13 | 2030 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 2.2 | 35.96 | A | 7 | -1.1 | 30.02 | A | 7 | 0.79 | A | 7 | 995 | A | 7 | 140 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 1 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 33.46 | 5 | 0
1985-02-21 | 1900-02-20 | 10:00 | 10 | 486 | 1398 | 182 | 1 | 9 | 9 | 1 | 9 | 179 | 1 | 13 | 20000 | 1 | 9 | 700 | 1 | 9 | 19700 | 1 | 13 | 5800 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 3.3 | 37.94 | A | 7 | -0.6 | 30.92 | A | 7 | 0.76 | A | 7 | 994 | A | 7 | 150 | A | 7 | 3.1 | A | 7 | 11300 | A | 7 | 3050 | A | 7 | 1 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 34.94 | 5 | 0
1985-02-21 | 1900-02-20 | 11:00 | 11 | 679 | 1398 | 235 | 1 | 9 | 10 | 1 | 9 | 230 | 1 | 13 | 26300 | 1 | 9 | 900 | 1 | 9 | 25900 | 1 | 13 | 8500 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 5.6 | 42.08 | A | 7 | 0 | 32 | A | 7 | 0.68 | A | 7 | 994 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 16100 | A | 7 | 3050 | A | 7 | 1.1 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 37.68 | 5 | 0
1985-02-21 | 1900-02-20 | 12:00 | 12 | 816 | 1398 | 255 | 1 | 9 | 7 | 1 | 9 | 252 | 1 | 13 | 29200 | 1 | 9 | 600 | 1 | 9 | 28800 | 1 | 13 | 10190 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 1.7 | 35.06 | A | 7 | 0.66 | A | 7 | 993 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 19300 | A | 7 | 1520 | A | 7 | 1.2 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 40.94 | 5 | 0
1985-02-21 | 1900-02-20 | 13:00 | 13 | 886 | 1398 | 295 | 1 | 9 | 7 | 1 | 9 | 291 | 1 | 13 | 33700 | 1 | 9 | 700 | 1 | 9 | 33300 | 1 | 13 | 11790 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 2.2 | 35.96 | A | 7 | 0.63 | A | 7 | 993 | A | 7 | 180 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 1340 | A | 7 | 1.2 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 42.22 | 5 | 0
1985-02-21 | 1900-02-20 | 14:00 | 14 | 885 | 1398 | 180 | 1 | 9 | 6 | 1 | 9 | 177 | 1 | 13 | 21400 | 1 | 9 | 500 | 1 | 9 | 21100 | 1 | 13 | 8220 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 3.9 | 39.02 | A | 7 | 0.69 | A | 7 | 992 | A | 7 | 210 | A | 7 | 5.2 | A | 7 | 17700 | A | 7 | 1340 | A | 7 | 1.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.02 | 5 | 0
1985-02-21 | 1900-02-20 | 15:00 | 15 | 812 | 1398 | 168 | 1 | 9 | 5 | 1 | 9 | 165 | 1 | 13 | 19800 | 1 | 9 | 400 | 1 | 9 | 19600 | 1 | 13 | 7470 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 4.4 | 39.92 | A | 7 | 0.74 | A | 7 | 991 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 11300 | A | 7 | 1460 | A | 7 | 1.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.02 | 5 | 0
1985-02-21 | 1900-02-20 | 16:00 | 16 | 673 | 1398 | 134 | 1 | 9 | 2 | 1 | 9 | 133 | 1 | 13 | 15700 | 1 | 9 | 100 | 1 | 9 | 15600 | 1 | 13 | 5780 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 990 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 8000 | A | 7 | 2290 | A | 7 | 1.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.42 | 5 | 0
1985-02-21 | 1900-02-20 | 17:00 | 17 | 478 | 1398 | 172 | 1 | 9 | 1 | 1 | 9 | 171 | 1 | 13 | 18800 | 1 | 9 | 100 | 1 | 9 | 18800 | 1 | 13 | 5600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 5 | 41 | A | 7 | 0.8 | A | 7 | 990 | A | 7 | 150 | A | 7 | 4.6 | A | 7 | 16100 | A | 7 | 1340 | A | 7 | 1.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 43.94 | 5 | 0
1985-02-21 | 1900-02-20 | 18:00 | 18 | 240 | 1398 | 42 | 1 | 13 | 1 | 1 | 9 | 41 | 1 | 13 | 4700 | 1 | 13 | 0 | 1 | 9 | 4700 | 1 | 13 | 1530 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 5 | 41 | A | 7 | 0.77 | A | 7 | 989 | A | 7 | 160 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 1040 | A | 7 | 1.4 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.42 | 5 | 0
1985-02-21 | 1900-02-20 | 19:00 | 19 | 25 | 618 | 12 | 1 | 13 | 0 | 1 | 9 | 12 | 1 | 13 | 1400 | 1 | 13 | 0 | 1 | 9 | 1400 | 1 | 13 | 420 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.8 | A | 7 | 989 | A | 7 | 160 | A | 7 | 5.2 | A | 7 | 19300 | A | 7 | 1100 | A | 7 | 1.5 | E | 8 | 0.058 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.92 | 5 | 0
1985-02-21 | 1900-02-20 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.8 | A | 7 | 989 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 12900 | A | 7 | 1100 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.92 | 5 | 0
1985-02-21 | 1900-02-20 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 5.6 | 42.08 | A | 7 | 0.8 | A | 7 | 989 | A | 7 | 180 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 1250 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.92 | 5 | 0
1985-02-21 | 1900-02-20 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 6.1 | 42.98 | A | 7 | 0.8 | A | 7 | 988 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 12900 | A | 7 | 1250 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.82 | 5 | 0
1985-02-21 | 1900-02-20 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 6.1 | 42.98 | A | 7 | 0.77 | A | 7 | 988 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 19300 | A | 7 | 1520 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.3 | 5 | 0
1985-02-21 | 1900-02-20 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 6.1 | 42.98 | A | 7 | 0.83 | A | 7 | 989 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 9700 | A | 7 | 1400 | A | 7 | 1.5 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.42 | 5 | 0
1985-02-22 | 1900-02-21 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 989 | A | 7 | 230 | A | 7 | 2.6 | A | 7 | 8000 | A | 7 | 1040 | A | 7 | 1.6 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.94 | 6 | 0
1985-02-22 | 1900-02-21 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 7.2 | 44.96 | A | 7 | 0.89 | A | 7 | 989 | A | 7 | 210 | A | 7 | 4.1 | A | 7 | 12900 | A | 7 | 3350 | A | 7 | 1.6 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.32 | 6 | 0
1985-02-22 | 1900-02-21 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 6.7 | 44.06 | A | 7 | 0.83 | A | 7 | 989 | A | 7 | 220 | A | 7 | 8.2 | A | 7 | 19300 | A | 7 | 3350 | A | 7 | 1.6 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.22 | 6 | 0
1985-02-22 | 1900-02-21 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.2 | 44.96 | A | 7 | 0.86 | A | 7 | 989 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1680 | A | 7 | 1.6 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 46.72 | 6 | 0
1985-02-22 | 1900-02-21 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 7.8 | 46.04 | A | 7 | 0.9 | A | 7 | 990 | A | 7 | 210 | A | 7 | 7.2 | A | 7 | 19300 | A | 7 | 3660 | A | 7 | 1.7 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.32 | 6 | 0
1985-02-22 | 1900-02-21 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 8.3 | 46.94 | A | 7 | 0.93 | A | 7 | 991 | A | 7 | 220 | A | 7 | 6.2 | A | 7 | 8000 | A | 7 | 1490 | A | 7 | 1.8 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 47.82 | 6 | 0
1985-02-22 | 1900-02-21 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 6.7 | 44.06 | A | 7 | 0.89 | A | 7 | 991 | A | 7 | 230 | A | 7 | 2.1 | A | 7 | 9700 | A | 7 | 760 | A | 7 | 1.6 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.24 | 6 | 0
1985-02-22 | 1900-02-21 | 8:00 | 8 | 32 | 710 | 7 | 1 | 13 | 0 | 1 | 9 | 7 | 1 | 13 | 800 | 1 | 13 | 0 | 1 | 9 | 800 | 1 | 13 | 270 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 7.8 | 46.04 | A | 7 | 6.7 | 44.06 | A | 7 | 0.93 | A | 7 | 991 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 9700 | A | 7 | 520 | A | 7 | 1.6 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 44.94 | 6 | 0
1985-02-22 | 1900-02-21 | 9:00 | 9 | 256 | 1398 | 43 | 1 | 13 | 1 | 1 | 9 | 43 | 1 | 13 | 5000 | 1 | 13 | 0 | 1 | 9 | 5000 | 1 | 13 | 1620 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 8.3 | 46.94 | A | 7 | 7.2 | 44.96 | A | 7 | 0.93 | A | 7 | 992 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 6400 | A | 7 | 310 | A | 7 | 1.6 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 45.84 | 6 | 0
1985-02-22 | 1900-02-21 | 10:00 | 10 | 493 | 1398 | 84 | 1 | 9 | 0 | 1 | 9 | 84 | 1 | 13 | 9800 | 1 | 9 | 0 | 1 | 9 | 9800 | 1 | 13 | 3500 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 8.9 | 48.02 | A | 7 | 1 | A | 7 | 992 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 6400 | A | 7 | 370 | A | 7 | 1.8 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.02 | 6 | 0
1985-02-22 | 1900-02-21 | 11:00 | 11 | 686 | 1398 | 136 | 1 | 9 | 1 | 1 | 9 | 135 | 1 | 13 | 15900 | 1 | 9 | 100 | 1 | 9 | 15800 | 1 | 13 | 5900 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 8.9 | 48.02 | A | 7 | 8.9 | 48.02 | A | 7 | 1 | A | 7 | 992 | A | 7 | 200 | A | 7 | 4.1 | A | 7 | 4000 | A | 7 | 310 | A | 7 | 1.8 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.02 | 6 | 0
1985-02-22 | 1900-02-21 | 12:00 | 12 | 822 | 1398 | 160 | 1 | 9 | 1 | 1 | 9 | 160 | 1 | 13 | 19000 | 1 | 9 | 100 | 1 | 9 | 18900 | 1 | 13 | 7340 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 9.4 | 48.92 | A | 7 | 1 | A | 7 | 992 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 370 | A | 7 | 1.9 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.82 | 6 | 0
1985-02-22 | 1900-02-21 | 13:00 | 13 | 892 | 1398 | 191 | 1 | 9 | 1 | 1 | 9 | 190 | 1 | 13 | 22500 | 1 | 9 | 100 | 1 | 9 | 22400 | 1 | 13 | 8730 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.96 | A | 7 | 992 | A | 7 | 200 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 580 | A | 7 | 1.8 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 6 | 0
1985-02-22 | 1900-02-21 | 14:00 | 14 | 891 | 1398 | 191 | 1 | 9 | 1 | 1 | 9 | 190 | 1 | 13 | 22500 | 1 | 9 | 100 | 1 | 9 | 22400 | 1 | 13 | 8730 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 460 | A | 7 | 1.9 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 6 | 0
1985-02-22 | 1900-02-21 | 15:00 | 15 | 818 | 1398 | 298 | 1 | 9 | 1 | 1 | 9 | 298 | 1 | 13 | 33600 | 1 | 9 | 100 | 1 | 9 | 33500 | 1 | 13 | 11300 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 210 | A | 7 | 6.2 | A | 7 | 9700 | A | 7 | 460 | A | 7 | 1.9 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 6 | 0
1985-02-22 | 1900-02-21 | 16:00 | 16 | 679 | 1398 | 145 | 1 | 9 | 1 | 1 | 9 | 145 | 1 | 13 | 16900 | 1 | 9 | 100 | 1 | 9 | 16900 | 1 | 13 | 6200 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 200 | A | 7 | 4.6 | A | 7 | 4800 | A | 7 | 310 | A | 7 | 1.9 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 6 | 0
1985-02-22 | 1900-02-21 | 17:00 | 17 | 484 | 1398 | 86 | 1 | 9 | 0 | 1 | 9 | 86 | 1 | 13 | 10000 | 1 | 9 | 0 | 1 | 9 | 10000 | 1 | 13 | 3540 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 9.4 | 48.92 | A | 7 | 8.9 | 48.02 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 160 | A | 7 | 3.6 | A | 7 | 3200 | A | 7 | 310 | A | 7 | 1.8 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 48.22 | 6 | 0
1985-02-22 | 1900-02-21 | 18:00 | 18 | 246 | 1398 | 35 | 1 | 13 | 0 | 1 | 9 | 35 | 1 | 13 | 4100 | 1 | 13 | 0 | 1 | 9 | 4100 | 1 | 13 | 1350 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 190 | A | 7 | 6.2 | A | 7 | 3200 | A | 7 | 400 | A | 7 | 1.9 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 6 | 0
1985-02-22 | 1900-02-21 | 19:00 | 19 | 27 | 664 | 10 | 1 | 13 | 0 | 1 | 9 | 10 | 1 | 13 | 1200 | 1 | 13 | 0 | 1 | 9 | 1200 | 1 | 13 | 360 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 991 | A | 7 | 180 | A | 7 | 3.6 | A | 7 | 8000 | A | 7 | 400 | A | 7 | 1.9 | E | 8 | 0.11 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 6 | 0
1985-02-22 | 1900-02-21 | 20:00 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 990 | A | 7 | 140 | A | 7 | 4.1 | A | 7 | 6400 | A | 7 | 340 | A | 7 | 1.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 6 | 0
1985-02-22 | 1900-02-21 | 21:00 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 10 | 50 | A | 7 | 1 | A | 7 | 990 | A | 7 | 170 | A | 7 | 3.1 | A | 7 | 4800 | A | 7 | 210 | A | 7 | 1.9 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50 | 6 | 0
1985-02-22 | 1900-02-21 | 22:00 | 22 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.96 | A | 7 | 990 | A | 7 | 180 | A | 7 | 5.7 | A | 7 | 4800 | A | 7 | 210 | A | 7 | 2 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.28 | 6 | 0
1985-02-22 | 1900-02-21 | 23:00 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 11.1 | 51.98 | A | 7 | 1 | A | 7 | 990 | A | 7 | 190 | A | 7 | 5.2 | A | 7 | 9700 | A | 7 | 1130 | A | 7 | 2.1 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.88 | 6 | 0
1985-02-22 | 1900-02-21 | 24:00 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 10.6 | 51.08 | A | 7 | 0.96 | A | 7 | 989 | A | 7 | 130 | A | 7 | 2.6 | A | 7 | 9700 | A | 7 | 1340 | A | 7 | 2 | E | 8 | 0.103 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.28 | 6 | 0
1985-02-23 | 1900-02-22 | 1:00 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 11.1 | 51.98 | A | 7 | 11.1 | 51.98 | A | 7 | 1 | A | 7 | 988 | A | 7 | 140 | A | 7 | 6.2 | A | 7 | 11300 | A | 7 | 1520 | A | 7 | 2.1 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.88 | 7 | 0
1985-02-23 | 1900-02-22 | 2:00 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10.6 | 51.08 | A | 7 | 10 | 50 | A | 7 | 0.96 | A | 7 | 988 | A | 7 | 120 | A | 7 | 2.1 | A | 7 | 6400 | A | 7 | 1340 | A | 7 | 1.9 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 50.38 | 7 | 0
1985-02-23 | 1900-02-22 | 3:00 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 10 | 50 | A | 7 | 9.4 | 48.92 | A | 7 | 0.96 | A | 7 | 987 | A | 7 | 130 | A | 7 | 3.6 | A | 7 | 9700 | A | 7 | 1190 | A | 7 | 1.9 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 49.3 | 7 | 0
1985-02-23 | 1900-02-22 | 4:00 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 12.2 | 53.96 | A | 7 | 10 | 50 | A | 7 | 0.86 | A | 7 | 986 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 24100 | A | 7 | 1520 | A | 7 | 1.9 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 51.56 | 7 | 0
1985-02-23 | 1900-02-22 | 5:00 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 10 | 50 | A | 7 | 0.8 | A | 7 | 986 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 32200 | A | 7 | 1680 | A | 7 | 1.9 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.34 | 7 | 0
1985-02-23 | 1900-02-22 | 6:00 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.9 | 57.02 | A | 7 | 10 | 50 | A | 7 | 0.78 | A | 7 | 986 | A | 7 | 190 | A | 7 | 7.2 | A | 7 | 32200 | A | 7 | 1830 | A | 7 | 1.9 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 53.02 | 7 | 0
1985-02-23 | 1900-02-22 | 7:00 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 10 | 50 | A | 7 | 0.8 | A | 7 | 987 | A | 7 | 230 | A | 7 | 3.6 | A | 7 | 24100 | A | 7 | 1490 | A | 7 | 1.9 | E | 8 | 0.104 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.34 | 7 | 0
1985-02-23 | 1900-02-22 | 8:00 | 8 | 35 | 733 | 9 | 1 | 13 | 0 | 1 | 9 | 9 | 1 | 13 | 1100 | 1 | 13 | 0 | 1 | 9 | 1100 | 1 | 13 | 340 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 12.8 | 55.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.87 | A | 7 | 987 | A | 7 | 200 | A | 7 | 3.6 | A | 7 | 11300 | A | 7 | 1490 | A | 7 | 2 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.74 | 7 | 0
1985-02-23 | 1900-02-22 | 9:00 | 9 | 262 | 1397 | 68 | 1 | 13 | 1 | 1 | 9 | 68 | 1 | 13 | 7600 | 1 | 13 | 0 | 1 | 9 | 7600 | 1 | 13 | 2290 | 1 | 21 | 10 | A | 7 | 10 | A | 7 | 12.8 | 55.04 | A | 7 | 10.6 | 51.08 | A | 7 | 0.87 | A | 7 | 987 | A | 7 | 170 | A | 7 | 3.6 | A | 7 | 14500 | A | 7 | 1490 | A | 7 | 2 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.74 | 7 | 0
1985-02-23 | 1900-02-22 | 10:00 | 10 | 499 | 1397 | 160 | 1 | 9 | 0 | 1 | 9 | 160 | 1 | 13 | 17800 | 1 | 9 | 0 | 1 | 9 | 17800 | 1 | 13 | 5580 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 13.3 | 55.94 | A | 7 | 10.6 | 51.08 | A | 7 | 0.83 | A | 7 | 987 | A | 7 | 170 | A | 7 | 4.6 | A | 7 | 14500 | A | 7 | 1490 | A | 7 | 2 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 52.94 | 7 | 0
1985-02-23 | 1900-02-22 | 11:00 | 11 | 693 | 1397 | 228 | 1 | 9 | 0 | 1 | 9 | 227 | 1 | 13 | 25500 | 1 | 9 | 0 | 1 | 9 | 25500 | 1 | 13 | 8560 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 15 | 59 | A | 7 | 11.1 | 51.98 | A | 7 | 0.78 | A | 7 | 986 | A | 7 | 190 | A | 7 | 6.7 | A | 7 | 19300 | A | 7 | 1400 | A | 7 | 2.1 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 54.9 | 7 | 0
1985-02-23 | 1900-02-22 | 12:00 | 12 | 829 | 1397 | 290 | 1 | 9 | 1 | 1 | 9 | 289 | 1 | 13 | 32700 | 1 | 9 | 100 | 1 | 9 | 32700 | 1 | 13 | 11210 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 16.1 | 60.98 | A | 7 | 11.1 | 51.98 | A | 7 | 0.72 | A | 7 | 986 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 19300 | A | 7 | 1400 | A | 7 | 2.1 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 55.48 | 7 | 0
1985-02-23 | 1900-02-22 | 13:00 | 13 | 899 | 1397 | 303 | 1 | 9 | 1 | 1 | 9 | 302 | 1 | 13 | 34500 | 1 | 9 | 100 | 1 | 9 | 34400 | 1 | 13 | 12180 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 18.3 | 64.94 | A | 7 | 11.7 | 53.06 | A | 7 | 0.65 | A | 7 | 986 | A | 7 | 210 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 2290 | A | 7 | 2.1 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 57.54 | 7 | 0
1985-02-23 | 1900-02-22 | 14:00 | 14 | 897 | 1397 | 306 | 1 | 9 | 0 | 1 | 9 | 305 | 1 | 13 | 34700 | 1 | 9 | 0 | 1 | 9 | 34700 | 1 | 13 | 12240 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 19.4 | 66.92 | A | 7 | 12.8 | 55.04 | A | 7 | 0.66 | A | 7 | 984 | A | 7 | 190 | A | 7 | 7.7 | A | 7 | 24100 | A | 7 | 1400 | A | 7 | 2.3 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 59.52 | 7 | 0
1985-02-23 | 1900-02-22 | 15:00 | 15 | 824 | 1397 | 266 | 1 | 9 | 2 | 1 | 9 | 265 | 1 | 13 | 30300 | 1 | 9 | 200 | 1 | 9 | 30200 | 1 | 13 | 10600 | 1 | 18 | 10 | A | 7 | 10 | A | 7 | 20.6 | 69.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 190 | A | 7 | 9.3 | A | 7 | 24100 | A | 7 | 1830 | A | 7 | 2.3 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 7 | 0
1985-02-23 | 1900-02-22 | 16:00 | 16 | 685 | 1397 | 212 | 1 | 9 | 57 | 1 | 9 | 184 | 1 | 13 | 23300 | 1 | 9 | 5600 | 1 | 9 | 20500 | 1 | 13 | 5610 | 1 | 18 | 10 | A | 7 | 9 | A | 7 | 20.6 | 69.08 | A | 7 | 12.8 | 55.04 | A | 7 | 0.61 | A | 7 | 983 | A | 7 | 180 | A | 7 | 6.7 | A | 7 | 24100 | A | 7 | 2440 | A | 7 | 2.3 | E | 8 | 0.121 | F | 8 | -9900 | ? | 0 | -9900 | -9900 | ? | 0 | 60.18 | 7 | 0