## Instructions
AES Indiana Business Rebates & Incentives Program
Lighting New Construction Savings Calculator
Welcome. This document has been prepared by CLEAResult.
The purpose of this spreadsheet is to determine the savings from replacing an existing lighting system with a more efficient lighting system.
1. Enter all initial parameters on the "Lighting Calculator" tab. The necessary items are highlighted in Green.
2. All required fields must be filled in for savings to be properly displayed.
3. For technical support on this tool contact custom@aesindianarebates.com.
Please Note: This calculator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this calculator is deemed acceptable for the AES Indiana Custom Incentives program. However, the assumptions used by the applicant to calculate the annual savings will be reviewed by the AES Indiana Custom Incentives program, which is solely responsible for the final determination of the annual energy savings to be used in calculating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities.
Incentive amount is calculated based on first year energy savings. The incentives are earned at $0.07 kWh saved. Incentives are limited to a maximum cap of $1,000,000 per project at a service ID and/or building behind a master meter. Total combined custom and prescriptive incentives are capped at $1,000,000 per customer per calendar year.

## Methodology
AES Indiana Business Rebates & Incentives Program
Lighting New Construction Savings Methodology
The methodology of this calculator is based on the Indiana Technical Resource Manual, Version 1.0, Lighting Power Density Reduction (New Construction) Section and Lighting Controls Section.
Where:
LPDBase is the allowed lighting power density (watts per square foot) based on energy code requirements for building or space type. See ASHRAE 90.1 2007 code tables below.
Area is the area of the lighted space.
WattsEE is the actual wattage of the efficient equipment.
WattsControlled is the total actual lighting load connected to the controls.
Hours is the annual operating hours of lighting. Site-specific operating hours (estimate from customer or determined from data logging) should be used if available. If not, assume default values dependent on building type below.
WHF_E is the lighting-HVAC interaction factor for energy. This factor represents the reduced electric space cooling requirements due to the reduction of waste heat rejected by the efficient lighting. Consider default values dependent on HVAC system type below.
1/1000 is the conversion factor from watts to kilowatts.
CF is the summer peak coincidence factor. Site-specific CF (estimate from customer or determined from data logging) should be used if available. If not, assume default values dependent on building type below.
WHF_D is the lighting-HVAC interaction factor for demand. This factor represents the reduced electric space cooling requirements due to the reduction of waste heat rejected by the efficient lighting. Consider default values dependent on HVAC system type below.
ESF is the energy savings factor. This factor represents the percent operating hours or wattage reduced due to the installation of the occupancy lighting controls, timeclocks, dimming lighting controls, or multilevel switching. Site-specific factor should be determined from data logging if possible. If not, assume default values dependent on control type below.
CFControlled is the summer peak coincidence factor. Site-specific factor should be determined from data logging if possible. If not, assume default values dependent on control type below.
Table 9.5.1 Lighting Power Densities Using the Buldign Area Method |  |  | Table 9.4.5 Lighting Power Densities for Building Exteriors
Tradeable Surfaces (LPDs for uncovered parking areas, building grounds, building entrances and exists, canopies and overhangs, and outdoor sales areas may be traded.)
Building Area Type* | LPD (W/ft2)
Automotive facility | 0.9 |  | Uncovered Parking Areas
Convention center | 1.2 |  | Parking lots and drives |  |  |  |  | 0.15 W/ft2
Courthouse | 1.2 |  | Building Grounds
Dining: bar lounge/leisure | 1.3 |  | Walkways less than 10 ft wide |  |  |  |  | 1.0 W/linear foot
Dining: cafeteria/fast food | 1.4 |  | Walkways 10 ft wide or greater |  |  |  |  | 0.2 W/ft2
Dining: family | 1.6 |  | Plaza areas
Dormatory | 1 |  | Special feature areas
Exercise center | 1 |  | Stairways |  |  |  |  | 1.0 W/ft2
Gymnasium | 1.1 |  | Building Entrances and Exits
Health-care clinic | 1 |  | Main entries |  |  |  |  | 30 W/linear foot of door width
Hospital | 1.2 |  | Other doors |  |  |  |  | 20 W/linear foot of door width
Library | 1.3 |  | Canopies and Overhangs
Manufacturing facility | 1.3 |  | Canopies (free standing and attached and overhangs) |  |  |  |  | 1.25 W/ft2
Motel | 1 |  | Outdoor Sales
Motion picture theater | 1.2 |  | Open areas (including vehicle sales lots) |  |  |  |  | 0.5 W/ft2
Multifamily | 0.7 |  | Street frontage for vehicle sales lots in addition to "open area" allowance |  |  |  |  | 20 W/linear foot
Museum | 1.1
Office | 1 |  | Nontradeable Surfaces (LPD calculations for the following applications can only be used for the specific application and cannot be traded between surfaces or with other exterior lighting. The following allowances are in addition to any allowance otherwise permitted in the "Tradeable Surfaces" section of this table.)
Parking garage | 0.3
Penitentiary | 1
Performing arts theater | 1.6
Police/fire station | 1 |  | Building facades |  |  |  |  | 0.2 W/ft2 for each illuminated wall or surface or 5.0 W/linear foot for each illuminated wall or surface length
Post office | 1.1
Religious building | 1.3
Retail | 1.5
School/university | 1.2 |  | Automated teller machines and night depositories |  |  |  |  | 270 W per location plus 90 W per additional ATM per location
Sports arena | 1.1
Town hall | 1.1 |  | Loading areas for law enforcement, fire, ambulance, and other emergency service vehicles |  |  |  |  | 1.25 W/ft2 of uncovered area (covered areas are included in the "Canopies and Overhangs" section of "Tradeable Surfaces")
Transportation | 1
Warehouse | 0.8
Workshop | 1.4
*In cases where both a general building area type and a specific building area type are listed, the specific building area type shall apply. |  |  | Drive-through windows at fast food restaurants |  |  |  |  | 400 W per drive-through
|  |  | Parking near 24-hour retail entrances |  |  |  |  | 800 W per main entry
Building Type | Hours | CF | Control Type |  |  | ESF | CF Controlled
Food sales/grocery | 5544 | 0.92 | Wall- or ceiling-mounted occupancy |  |  | 30% | 0.15
Food service - fast food | 3357 | 0.83 | Fixture-mounted occupancy sensors |  |  | 30% | 0.15
Food sesrvice - restaurant | 3357 | 0.83 | Remote-mounted daylight dimming |  |  | 30% | 0.9
Health care | 6802 | 0.78 | Fixture-mounted daylight dimming sensors |  |  | 30% | 0.9
Hotel/motel | 3754 | 0.37 | Switch controls for multi-level lighting |  |  | 30% | 0.77
Office | 3253 | 0.76 | Central lighting controls (timeclocks) |  |  | 10% | -
Public assembly | 2867 | 0.65
Public services (non-food) | 3299 | 0.64 | WHF vary by building type
Retail - big box | 4984 | 0.84 | (Other building type is below)
Small retail | 4984 | 0.84 | HVAC Sytem Type | WHF_E | WHF_D
Warehouse | 3824 | 0.79 | A/C with gas heat | 0.115 | 0.2
School | 2379 | 0.5 | Heat pump | -0.15 | 0.2
College | 3749 | 0.68 | A/C with electric heat | -0.357 | 0.19
Industrial - 1 shift | 2857 | 0.76 | Electric heat only | -0.487 | -
Industrial - 2 shifts | 4730 | 0.76 | Gas heat only | - | -
Industrial - 3 shifts | 6631 | 0.76
Other | 4408 | 0.65
Exterior | 4300 | -
〖𝑘𝑊ℎ〗_(𝐴𝑛𝑛𝑢𝑎𝑙 𝑆𝑎𝑣𝑖𝑛𝑔𝑠)=(〖(𝐿𝑃𝐷〗_𝐵𝑎𝑠𝑒×𝐴𝑟𝑒𝑎−〖𝑊𝑎𝑡𝑡𝑠〗_𝐸𝐸)×𝐻𝑜𝑢𝑟𝑠×(1+〖𝑊𝐻𝐹〗_𝐸)" " )/1,000
〖𝑘𝑊〗_(𝑆𝑢𝑚𝑚𝑒𝑟 𝑃𝑒𝑎𝑘 𝑆𝑎𝑣𝑖𝑛𝑔𝑠)=((〖𝐿𝑃𝐷〗_𝐵𝑎𝑠𝑒×𝐴𝑟𝑒𝑎−〖𝑊𝑎𝑡𝑡𝑠〗_𝐸𝐸)×𝐶𝐹×(1+〖𝑊𝐻𝐹〗_𝐷)" " )/1,000
〖𝑘𝑊ℎ〗_(𝐴𝑛𝑛𝑢𝑎𝑙 𝑆𝑎𝑣𝑖𝑛𝑔𝑠, 𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑠)=(〖𝑊𝑎𝑡𝑡𝑠〗_𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑑×𝐻𝑜𝑢𝑟𝑠×(1+〖𝑊𝐻𝐹〗_𝐸)×𝐸𝑆𝐹)/1,000
〖𝑘𝑊〗_(𝑆𝑢𝑚𝑚𝑒𝑟 𝑃𝑒𝑎𝑘 𝑆𝑎𝑣𝑖𝑛𝑔𝑠, 𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑠)=(〖𝑊𝑎𝑡𝑡𝑠〗_𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑑×〖𝐶𝐹〗_𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑑×(1+〖𝑊𝐻𝐹〗_𝐷)×𝐸𝑆𝐹)/1,000

## Lighting Calculator
AES Indiana Business Rebates & Incentives Program
New Construction Lighting Savings Calculator
Color Legend Highlighting
Input
Results
Note: If project includes some exterior areas, select "Exterior" for Area Type for the fixture types in that area.
Site Information
Building Name:
Area Description:
Building Type:
HVAC System Type:
Electricity Rate ($/kWh, Example: $0.08/kWh): | 0.08
Project Cost:
Operating Hours and Summer Coincidence Factor
Default Operating Hours for Building Type:
Default Summer Coincidence Factor for Building Type:
Annual Operating Hours Type:
If Custom, Customer Operating Hours:
Baseline Conditions
Baseline Conditions | 1 | 2 | 3 | 4 | 5
Area Type:
Building Exteriors Type:
Area Size (Units should match row below):
LPD Unit (W/Unit):
Baseline Lighting Power Density:
Proposed Conditions
Proposed Conditions | 1 | 2 | 3 | 4 | 5
Fixture Type:
Fixture Qty:
Installed Watts / Fixture (W)
Occupancy Sensors Required by Code? See ASHRAE 90.1 2007.
Installed Control Type (Use "Custom" if ESF and CF are known):
Proposed Lighting Power Density: | [5 empty] | Hide Row
Proposed Controls Energy Savings Factor and Controlled Summer Coincidence Factor
Default Controls ESF
Default Controls CF
Controls Factors to Use:
If Custom Controls, Controls ESF (%)
If Custom Baseline Controls, Controls CF
Energy and Demand Savings Calculations | [5 empty] | Hide Row
Hide Row
Hours Used | [5 empty] | Hide Row
CF | [5 empty] | Hide Row
WHF_Energy | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
WHF_Demand | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
ESF_Proposed | [5 empty] | Hide Row
CF_Controls_Proposed | [5 empty] | Hide Row
Baseline Energy | 0 | 0 | 0 | 0 | 0 | Hide Row
Baseline Controls Energy Savings | 0 | 0 | 0 | 0 | 0 | Hide Row
Baseline Demand | 0 | 0 | 0 | 0 | 0 | Hide Row
Proposed Energy | 0 | 0 | 0 | 0 | 0 | Hide Row
Proposed Controls Energy Savings | 0 | 0 | 0 | 0 | 0 | Hide Row
Proposed Demand | 0 | 0 | 0 | 0 | 0 | Hide Row
Lighting Energy Savings | 0 | 0 | 0 | 0 | 0 | Hide Row
Controls Energy Savings | 0 | 0 | 0 | 0 | 0 | Hide Row
Total Lighting & Controls Energy Savings | 0 | 0 | 0 | 0 | 0
Lighting Demand Savings | 0 | 0 | 0 | 0 | 0 | Hide Row
Controls Demand Savings | 0 | 0 | 0 | 0 | 0 | Hide Row
Total Lighting & Controls Demand Savings | 0 | 0 | 0 | 0 | 0
Hide Row
Incentive Calculations | [5 empty] | Hide Row
Hide Row
Capped Incentive | 0 |  |  |  |  | Hide Row
Incentive at $0.07 per kWh savings | 0 |  |  |  |  | Hide Row
Incentive Amount Approved | 0 |  |  |  |  | Hide Row
Hide Row
Savings Summary
Baseline Energy Consumption (kWh/Yr.) | 0
Proposed Energy Consumption (kWh/Yr.) | 0
Energy Savings (kWh/Yr.) | 0
Demand Reduction (kW) | 0
Eligible Custom Incentive | Need Project Cost
Incentive Calculation Method
Energy Cost Savings ($/Yr.) | Need Total Annual kWh Saved
Simple Payback Period without Incentive (Yrs.) | Need Project Cost
Simple Payback Period with Incentive (Yrs.) | Need Project Cost
Note on B17: Use $0.08 if unknown
Note on B22: Default will use the average hours based on the building type. Custom allows you to enter in your own hours. You may be asked to provide justification for the entered hours.

## Project Notes
This is an optional sheet that is not password protected where you can put any notes about the project (if needed).

## SF Estimator
This page is optional and is meant as a tool to help estimate the associated square footage for custom lights when they are mixed in spaces that have either lights that qualify for the prescriptive incentive program or don't qualify for any incentive. Essentially, the percentage of total custom watts versus total watts is used to approximate what portion of that space should be allocated to the custom fixtures. 3 example rows are included for your reference.
Example | Total Area of Affected Space (in square feet) | 25000 |  |  |  |  | Sum | Sum
| Custom Building Area (sf) | 13923.0769 |  |  |  |  | 16250 | 9050
Fixture Code | Fixture Description | Fixture Qty. | Fixture Wattage | Incentive Category | Interior or Exterior | Is this fixture part of the interior LPD Calculation? | Total LPD Watts | Custom LPD Watts
A | 4' 2-lamp 18W LED | 200 | 36 | Prescriptive | Interior | Yes | 7200 | 0
B | 400W Metal Halide | 10 | 458 | Does not Qualify | Exterior | No | 0 | 0
C | 4' 54W 3-lamp T5HO | 50 | 181 | Custom | Interior | Yes | 9050 | 9050
Complete this table. The total area and the columns in Green are the required inputs. Add more rows to the table if needed.
| Total Area of Affected Space (in square feet) | [5 empty] | Sum | Sum
| Custom Building Area (sf) | #DIV/0! |  |  |  |  | 0 | 0
Fixture Code | Fixture Description | Fixture Qty. | Fixture Wattage | Incentive Category | Interior or Exterior | Is this fixture part of the interior LPD Calculation? | Total LPD Watts | Custom LPD Watts
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
Note on C14: This is the square footage of the space containing the mix of prescriptive, custom, and non-qualified lights listed in the table below.
Note on G17: Some lights including exit signs and emergency only lights do not count against code LPD requirements.

## LPD LookUp Tables
AES Indiana Business Rebates & Incentives Program
Lighting Calculator LPD
ASHRAE 90.1 2007, Table 9.5.1, Lighting Power Densities Using the Building Area Method | [8 empty] | ASHRAE 90.1 2007, Table 9.4.5, Lighting Power Densities for Building Exteriors
Area Type |  | LPD (W/ft2) |  | 1 | 2 | 3 | 4 | 5 | Area Type |  | Unit | LPD (Unit) |  | 1 | 2 | 3 | 4 | 5
1 | Automotive Facility | 0.9 | Area Type | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | Uncovered Parking Areas | W/ft2 | 0.15 | Area Type | #N/A | #N/A | #N/A | #N/A | #N/A
2 | Convention Center | 1.2 | LPD | #N/A | #N/A | #N/A | #N/A | #N/A | 2 | Walkways (< 10 ft wide) | W/linear foot | 1 | Unit | #N/A | #N/A | #N/A | #N/A | #N/A
3 | Courthouse | 1.2 | [6 empty] | 3 | Walkways (≥ 10ft wide), Plaza Areas, Special Feature Areas | W/ft2 | 0.2 | LPD | #N/A | #N/A | #N/A | #N/A | #N/A
4 | Dining: Bar Lounge/Leisure | 1.3 | [6 empty] | 4 | Stairways | W/ft2 | 1
5 | Dining: Cafeteria/Fast Food | 1.4 | [6 empty] | 5 | Building Main Entrance/Exit | W/linear foot of door width | 30
6 | Dining: Family | 1.6 | [6 empty] | 6 | Other Building Doors | W/linear foot of door width | 20
7 | Dormitory | 1 | [6 empty] | 7 | Canopies (Free Standing, Attached, Overhangs) | W/ft2 | 1.25
8 | Exercise Center | 1 | [6 empty] | 8 | Outdoor Sales Open Areas | W/ft2 | 0.5
9 | Gymnasium | 1.1 | [6 empty] | 9 | Outdoor Sales Street Frontage | W/linear foot | 20
10 | Health care clinic | 1 | [6 empty] | 10 | Building Facades | W/ft2 | 0.2
11 | Hospital | 1.2 | [6 empty] | 11 | Automated Teller Machines | W/location | 270
12 | Hotel | 1 | [6 empty] | 12 | Entrances and Gatehouse Inspection Stations | W/ft2 | 1.25
13 | Library | 1.3 | [6 empty] | 13 | Emergency Service Loading Areas | W/ft2 | 0.5
14 | Manufacturing facility | 1.3 | [6 empty] | 14 | Drive-Through Windows | W/drive-through | 400
15 | Motel | 1 | [6 empty] | 15 | Parking Near 24-Hour Retail Entrance | W/main-entry | 800
16 | Motion Picture Theater | 1.2
17 | Multifamily | 0.7
18 | Museum | 1.1
19 | Office | 1
20 | Parking Garage | 0.3
21 | Penitentiary | 1
22 | Performing Arts Theater | 1.6
23 | Police/Fire Station | 1
24 | Post Office | 1.1
25 | Religious Building | 1.3
26 | Retail | 1.5
27 | School/University | 1.2
28 | Sports Arena | 1.1
29 | Town Hall | 1.1
30 | Transportation | 1
31 | Warehouse | 0.8
32 | Workshop | 1.4
Exterior

## LookUp Tables
AES Indiana Business Rebates & Incentives Program
Lighting Calculator Look-Up Tables
Building Type | IN TRM Name | Hours | CF |  | Control Type | ESF | CF Controlled | [5 empty] | Yes | Fixture Types
Food Sales / Grocery | Food Sales | 5544 | 0.92 |  | Wall- or Ceiling-Mounted Occupancy | 30% | 0.15 | [5 empty] | No | LED
Food Service - Fast Food | Food Service | 3357 | 0.83 |  | Fixture-Mounted Occupancy Sensors | 30% | 0.15 | [6 empty] | CFL
Food Service - Restaurant | Food Service | 3357 | 0.83 |  | Remote-Mounted Daylight Dimming | 30% | 0.9 | [6 empty] | Circular Lamp
Health Care | Health Care | 6802 | 0.78 |  | Fixture-Mounted Daylight Dimming Sensors | 30% | 0.9 | [6 empty] | Halogen
Hotel/Motel | Hotel/Motel | 3754 | 0.37 |  | Switching Controls for Multi-Level Lighting | 30% | 0.77 | [6 empty] | High Pressure Sodium
Office | Office | 3253 | 0.76 |  | Central Lighting Controls (Timeclocks) | 10% | 0 | [6 empty] | Incandescent
Public Assembly | Public Assembly | 2867 | 0.65 |  | Custom | [8 empty] | Low Wattage T8
Public Services (non-food) | Public Services (non-food) | 3299 | 0.64 |  | None | 0% | 0 | [6 empty] | Mercury Vapor
Retail - Big Box | Retail | 4984 | 0.84 | [10 empty] | Metal Halide
Small Retail | Retail | 4984 | 0.84 | [10 empty] | T12
Warehouse | Warehouse | 3824 | 0.79 | [10 empty] | T5
School | School | 2379 | 0.5 |  | HVAC System Type | WHF_E | WHF_D | [6 empty] | T8
College | College | 3749 | 0.68 |  | AC with Gas Heat | 0.115 | 0.2 | [6 empty] | U-Tube T8
Industrial - 1 Shift | Industrial - 1 Shift | 2857 | 0.76 |  | Heat Pump | -0.15 | 0.2 | [6 empty] | U-Tube T12
Industrial - 2 Shifts | Industrial - 2 Shift | 4730 | 0.76 |  | AC with Electric Heat | -0.357 | 0.185 | [6 empty] | Custom
Industrial - 3 Shifts | Industrial - 3 Shift | 6631 | 0.76 |  | Electric Heat Only | -0.487 | 0
Other | Other | 4408 | 0.65 |  | Gas Heat Only | 0 | 0
Exterior | Exterior | 4300 | 0
Custom | Custom
Occupied 24/7 | Occupied 24/7 | 8760 | 1
Location: | Indianapolis |  |  |  | Based on IN TRM v2.2
|  | AC with Gas Heat |  |  | Heat Pump |  |  | AC with Electric Heat |  |  | Electric Heat Only |  |  | Gas Heat Only |  |  | Avg. from Old Version
IPL Calculator Name | IN TRM Name | WHFe | WHFd | WHFg | WHFe | WHFd | WHFg | WHFe | WHFd | WHFg | WHFe | WHFd | WHFg | WHFe | WHFd | WHFg | HVAC System Type | WHF_E | WHF_D
Public Assembly | Assembly | 0.155 | 0.2 | -0.0029 | -0.174 | 0.2 | 0 | -0.434 | 0.2 | 0 | -0.591 | 0 | 0 | 0 | 0 | -0.0029 | AC with Gas Heat | 0.115 | 0.2 | 1
Retail - Big Box | Big Box | 0.146 | 0.2 | -0.0017 | -0.086 | 0.2 | 0 | -0.193 | 0.2 | 0 | -0.604 | 0 | 0 | 0 | 0 | -0.0017 | Heat Pump | -0.15 | 0.2 | 2
School | Elementary School | 0.096 | 0.2 | -0.0033 | -0.278 | 0.2 | 0 | -0.605 | 0.2 | 0 | -0.743 | 0 | 0 | 0 | 0 | -0.0033 | AC with Electric Heat | -0.357 | 0.185 | 3
College | Other | 0.115 | 0.2 | -0.0023 | -0.15 | 0.2 | 0 | -0.357 | 0.185 | 0 | -0.487 | 0 | 0 | 0 | 0 | -0.0022 | Electric Heat Only | -0.487 | 0 | 4
Food Service - Fast Food | Fast Food | 0.109 | 0.2 | -0.0029 | -0.023 | 0.2 | 0 | -0.53 | 0.2 | 0 | -0.661 | 0 | 0 | 0 | 0 | -0.0032 | Gas Heat Only | 0 | 0 | 5
Food Service - Restaurant | Full Service Restaurant | 0.108 | 0.2 | -0.0033 | -0.023 | 0.2 | 0 | -0.556 | 0 | 0 | -0.872 | 0 | 0 | 0 | 0 | -0.0042
Food Sales / Grocery | Grocery | 0.146 | 0.2 | -0.0017 | -0.086 | 0.2 | 0 | -0.193 | 0.2 | 0 | -0.318 | 0 | 0 | 0 | 0 | -0.0017
Industrial - 1 Shift | Light Industrial | 0.096 | 0.2 | -0.0022 | -0.145 | 0.2 | 0 | -0.332 | 0.2 | 0 | -0.433 | 0 | 0 | 0 | 0 | -0.0021
Industrial - 2 Shifts | Light Industrial | 0.096 | 0.2 | -0.0022 | -0.145 | 0.2 | 0 | -0.332 | 0.2 | 0 | -0.433 | 0 | 0 | 0 | 0 | -0.0021
Industrial - 3 Shifts | Light Industrial | 0.096 | 0.2 | -0.0022 | -0.145 | 0.2 | 0 | -0.332 | 0.2 | 0 | -0.433 | 0 | 0 | 0 | 0 | -0.0021
Office | Small Office | 0.119 | 0.2 | -0.0016 | -0.027 | 0.2 | 0 | -0.182 | 0.2 | 0 | -0.182 | 0 | 0 | 0 | 0 | -0.0015
Small Retail | Small Retail | 0.124 | 0.2 | -0.0023 | -0.083 | 0.2 | 0 | -0.315 | 0.2 | 0 | -0.437 | 0 | 0 | 0 | 0 | -0.0022
Warehouse | Warehouse | 0.096 | 0.2 | -0.0022 | -0.145 | 0.2 | 0 | -0.332 | 0.2 | 0 | -0.433 | 0 | 0 | 0 | 0 | -0.0021
Other | Other | 0.115 | 0.2 | -0.0023 | -0.15 | 0.2 | 0 | -0.357 | 0.185 | 0 | -0.487 | 0 | 0 | 0 | 0 | -0.0022
Public Services (non-food) | Other | 0.115 | 0.2 | -0.0023 | -0.15 | 0.2 | 0 | -0.357 | 0.185 | 0 | -0.487 | 0 | 0 | 0 | 0 | -0.0022
Health Care | Other | 0.115 | 0.2 | -0.0023 | -0.15 | 0.2 | 0 | -0.357 | 0.185 | 0 | -0.487 | 0 | 0 | 0 | 0 | -0.0022
Hotel/Motel | Other | 0.115 | 0.2 | -0.0023 | -0.15 | 0.2 | 0 | -0.357 | 0.185 | 0 | -0.487 | 0 | 0 | 0 | 0 | -0.0022
Exterior | Exterior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Custom | Other | 0.115 | 0.2 | -0.0023 | -0.15 | 0.2 | 0 | -0.357 | 0.185 | 0 | -0.487 | 0 | 0 | 0 | 0 | -0.0022

## Fixture Wattage Reference
Below is a list of the most commonly seen fixtures and their associated fixture wattage:
T12 Fluorescent Fixtures
Lamps per fixture: | 1-Lamp | 2-Lamps | 3-Lamps | 4-Lamps | 5-Lamps | 6-Lamps | 8-Lamps | 10-Lamps | 12-Lamps
2' 20W T12 Lamp, Magnetic Ballast | 24 | 56 | 62 | 112 | 118 | 146 | 224 | 236 | 292
3' 30W T12 Lamp, Magnetic Ballast | 46 | 81 | 127 | 162 | 208 | 342 | 324 | 416 | 684
4' 34W T12 Lamp, Magnetic Ballast | 43 | 72 | 115 | 144 | 187 | 216 | 288 | 374 | 432
4' 40W T12 Lamp, Magnetic Ballast | 51 | 82 | 133 | 164 | 215 | 266 | 328 | 430 | 532
5' 50W T12 Lamp, Magnetic Ballast | 63 | 128 | 191 | 256 | 319 | 382 | 512 | 638 | 764
6' 55W T12 Lamp, Magnetic Ballast | 76 | 122 | 202 | 244 | 324 | 404 | 488 | 648 | 808
8' 60W T12 Lamp, Magnetic Ballast | 75 | 123 | 203 | 246 | 369 | 406 | 492 | 738 | 812
8' 75W T12 Lamp, Magnetic Ballast | 100 | 173 | 237 | 346 | 410 | 474 | 692 | 820 | 948
2' 35W T12/HO Lamp, Magnetic Ballast | 64 | 95 | 148 | 183 | 243 | 296 | 366 | 486 | 592
3' 50W T12/HO Lamp, Magnetic Ballast | 72 | 110 | 166 | 212 | 276 | 332 | 424 | 552 | 664
4' 60W T12/HO Lamp, Magnetic Ballast | 85 | 145 | 230 | 290 | 375 | 460 | 580 | 750 | 920
5' 75W T12/HO Lamp, Magnetic Ballast | 92 | 168 | 260 | 336 | 428 | 520 | 672 | 856 | 1040
6' 85W T12/HO Lamp, Magnetic Ballast | 120 | 194 | 314 | 388 | 508 | 628 | 776 | 1016 | 1256
8' 95W T12/HO Lamp, Magnetic Ballast | 112 | 227 | 380 | 454 | 721 | 760 | 908 | 1442 | 1520
8' 110W T12/VHO Lamp, Magnetic Ballast | 145 | 257 | 392 | 514 | 649 | 784 | 1028 | 1298 | 1568
8' 185W T12/VHO Lamp, Magnetic Ballast | 205 | 380 | 585 | 760 | 965 | 1170 | 1520 | 1930 | 2340
34W U-Bend T12 Lamp, Magnetic Ballast | 34 | 67 | 101 | 134 | 168 | 202 | 268 | 336 | 404
40W U-Bend T12 Lamp, Magnetic Ballast | 43 | 72 | 115 | 144 | 187 | 230 | 288 | 374 | 460
T8 Fluorescent Fixtures
Lamps per fixture: | 1-Lamp | 2-Lamps | 3-Lamps | 4-Lamps | 5-Lamps | 6-Lamps | 8-Lamps | 10-Lamps | 12-Lamps
18" 15W T8 Lamp, Electronic Ballast | 16 | 28 | 44 | 57 | 72 | 88 | 115 | 145 | 176
2' 17W T8 Lamp, Electronic Ballast | 18 | 32 | 50 | 65 | 82 | 100 | 130 | 164 | 200
3' 25W T8 Lamp, Electronic Ballast | 25 | 46 | 70 | 88 | 116 | 140 | 176 | 232 | 280
4' 25W RW T8 Lamp, Electronic Ballast | 22 | 41 | 61.3 | 80.5 | 102.3 | 122.6 | 161 | 204.6 | 245.2
4' 28W RW T8 Lamp, Electronic Ballast | 23 | 47 | 69.9 | 92.6 | 116.9 | 139.8 | 185.2 | 233.8 | 279.6
4' 30W ES T8 Lamp, Electronic Ballast | 27 | 51 | 77 | 102 | 128 | 153 | 204 | 256 | 306
4' 32W HP T8 Lamp, Electronic Ballast | 25 | 48 | 73 | 96 | 121 | 156 | 204 | 242 | 312
4' 32W Std T8 Lamp, Electronic Ballast | 31 | 59 | 89 | 112 | 148 | 175 | 224 | 296 | 350
5' 40W T8 Lamp, Electronic Ballast | 36 | 72 | 106 | 134 | 178 | 212 | 268 | 356 | 424
6' 46W T8 Lamp, Electronic Ballast | 50 | 88 | 138 | 176 | 226 | 276 | 352 | 452 | 552
8' 59W T8 Lamp, Electronic Ballast | 58 | 109 | 167 | 219 | 328 | 334 | 438 | 656 | 668
4' 25W T8/HO Lamp, Electronic Ballast | 28 | 51 | 73 | 102 | 123 | 145 | 203 | 247 | 291
Lamps per fixture: | 1-Lamp | 2-Lamps | 3-Lamps | 4-Lamps | 5-Lamps | 6-Lamps | 8-Lamps | 10-Lamps | 12-Lamps
4' 28W T8/HO Lamp, Electronic Ballast | 32 | 57 | 81 | 114 | 138 | 163 | 228 | 277 | 326
4' 32W T8/HO Lamp, Electronic Ballast | 36 | 65 | 93 | 130 | 158 | 186 | 260 | 316 | 372
4' 32W T8/VHO Lamp, Electronic Ballast | 41 | 79 | 112 | 151 | 189 | 226 | 302 | 378 | 452
4' 44W T8/HO Lamp, Electronic Ballast | 59 | 98 | 157 | 196 | 255 | 314 | 392 | 510 | 628
5' 55W T8/HO Lamp, Electronic Ballast | 70 | 118 | 188 | 236 | 306 | 376 | 472 | 612 | 752
6' 66W T8/HO Lamp, Electronic Ballast | 81 | 135 | 216 | 270 | 351 | 432 | 540 | 702 | 864
8' 86W T8/HO Lamp, Electronic Ballast | 80 | 160 | 240 | 320 | 400 | 480 | 640 | 800 | 960
28W U-Bend T8 Lamp, Electronic Ballast | 25 | 48 | 71 | 96 | 119 | 142 | 193 | 238 | 284
31W U-Bend T8 Lamp, Electronic Ballast | 28 | 53 | 78 | 107 | 132 | 157 | 213 | 264 | 314
32W U-Bend T8 Lamp, Electronic Ballast | 29 | 55 | 81 | 110 | 136 | 162 | 220 | 272 | 324
T5 Fluorescent Fixtures
Lamps per fixture: | 1-Lamp | 2-Lamps | 3-Lamps | 4-Lamps | 5-Lamps | 6-Lamps | 8-Lamps | 10-Lamps | 12-Lamps
2' 14W T5 Lamp, Electronic Ballast | 18 | 33 | 50 | 66 | 83 | 100 | 132 | 166 | 200
2' 24W T5/HO Lamp, Electronic Ballast | 27 | 52 | 79 | 104 | 131 | 158 | 208 | 262 | 316
3' 21W T5 Lamp, Electronic Ballast | 25 | 48 | 73 | 96 | 121 | 146 | 192 | 242 | 292
3' 39W T5/HO Lamp, Electronic Ballast | 42 | 85 | 127 | 170 | 212 | 254 | 340 | 424 | 508
4' 28W T5 Lamp, Electronic Ballast | 33 | 64 | 97 | 128 | 161 | 192 | 256 | 322 | 384
4' 39W T5/HO Lamp, Electronic Ballast | 42 | 85 | 127 | 170 | 212 | 254 | 340 | 424 | 508
4' 50W T5/HO Lamp, Electronic Ballast | 55 | 108 | 168 | 217 | 276 | 325 | 433 | 552 | 650
4' 54W T5/HO Lamp, Electronic Ballast | 59 | 117 | 181 | 234 | 298 | 351 | 468 | 596 | 702
5' 35W T5 Lamp, Electronic Ballast | 40 | 78 | 118 | 156 | 196 | 234 | 312 | 392 | 468
Other Fluorescent Fixtures |  |  |  |  | Pin-Based CFL Fixtures
Lamps per fixture: | 1-Lamp | 2-Lamps | 3-Lamps |  | Lamps per fixture: |  |  | 1-Lamp | 2-Lamps | 3-Lamps
4' 40W T10 | 41 | 77 | 114 |  | 9W Pinned-Based CFL |  |  | 10.3846 | 19.3846 | 29.7692
32W FC12T9 Circline | 31 | 62 | 93 |  | 13W Pinned-Based CFL |  |  | 15 | 28 | 43
22W FC8T9 Circline | 26 | 52 | 78 |  | 18W Pinned-Based CFL |  |  | 20 | 38 | 58
[5 empty] | 26W Pinned-Based CFL |  |  | 27 | 50 | 77
[5 empty] | 28W Pinned-Based CFL |  |  | 29.75 | 54.25 | 84
[5 empty] | 32W Pinned-Based CFL |  |  | 34 | 62 | 96
[5 empty] | 38W Pinned-Based CFL |  |  | 40 | 74 | 114
[5 empty] | 40W Pinned-Based CFL |  |  | 43 | 72 | 105
[5 empty] | 42W Pinned-Based CFL |  |  | 44 | 93 | 137
High Pressure Sodium | W / Fixture |  |  | Metal Halide Fixtures (Std/Probe-Start) |  |  |  | W / Fixture
35W High Pressure Sodium | 46 |  |  | 20W Metal Halide |  |  |  | 23
50W High Pressure Sodium | 66 |  |  | 32W Metal Halide |  |  |  | 43
70W High Pressure Sodium | 95 |  |  | 50W Metal Halide |  |  |  | 77
100W High Pressure Sodium | 138 |  |  | 70W Metal Halide |  |  |  | 95
150W High Pressure Sodium | 188 |  |  | 100W Metal Halide |  |  |  | 128
200W High Pressure Sodium | 250 |  |  | 150W Metal Halide |  |  |  | 190
250W High Pressure Sodium | 295 |  |  | 175W Metal Halide |  |  |  | 208
310W High Pressure Sodium | 365 |  |  | 200W Metal Halide |  |  |  | 232
400W High Pressure Sodium | 465 |  |  | 250W Metal Halide |  |  |  | 295
750W High Pressure Sodium | 835 |  |  | 360W Metal Halide |  |  |  | 418
1,000W High Pressure Sodium | 1100 |  |  | 400W Metal Halide |  |  |  | 458
|  |  |  | 750W Metal Halide |  |  |  | 850
|  |  |  | 1,000W Metal Halide |  |  |  | 1080
Mercury Vapor | W / Fixture |  |  | 1,500W Metal Halide |  |  |  | 1610
40W Mercury Vapor | 50
50W Mercury Vapor | 74
75W Mercury Vapor | 93 |  |  | Pulse-Start Metal Halide Fixtures |  |  |  | W / Fixture
100W Mercury Vapor | 125 |  |  | 100W Pulse-Start Metal Halide |  |  |  | 110
175W Mercury Vapor | 205 |  |  | 150W Pulse-Start Metal Halide |  |  |  | 183
250W Mercury Vapor | 290 |  |  | 175W Pulse-Start Metal Halide |  |  |  | 208
400W Mercury Vapor | 455 |  |  | 200W Pulse-Start Metal Halide |  |  |  | 232
700W Mercury Vapor | 780 |  |  | 250W Pulse-Start Metal Halide |  |  |  | 288
1,000W Mercury Vapor | 1075 |  |  | 320W Pulse-Start Metal Halide |  |  |  | 365
|  |  |  | 350W Pulse-Start Metal Halide |  |  |  | 400
|  |  |  | 400W Pulse-Start Metal Halide |  |  |  | 456
Ceramic Metal Halide Fixtures | W / Fixture |  |  | 500W Pulse-Start Metal Halide |  |  |  | 506
20W Ceramic Metal Halide | 26 |  |  | 750W Pulse-Start Metal Halide |  |  |  | 818
39W Ceramic Metal Halide | 45 |  |  | 1,000W Pulse-Start Metal Halide |  |  |  | 1080
50W Ceramic Metal Halide | 55
70W Ceramic Metal Halide | 79
100W Ceramic Metal Halide | 110
150W Ceramic Metal Halide | 163

## Updates (hidden)
Version # | Date | Editing Engineer | Reviewing Engineer | Updates Made
1 | 2017-01-01 | Ben Reinhart | Will Nichols | Updated for 2017 program rules, inlcuding incentive caps
2 | 2017-04-03 | Ben Reinhart | Will Nichols | Fixed errors in how the control savings were calculating. Updated fixture wattage reference table. Added optional tool for splitting building floor area between prescriptive, custom, and non-qualified lighting.
3 | 2018-01-08 | Ben Reinhart | Will Nichols | Updated for 2018 program rules, specifically changing the incentive rate to $0.06 per annual kWh saved.
4 | 2018-06-08 | Ben Reinhart | Will Nichols | The formulas in cells F36 & F37 got accidently deleted making this column unusable to customers. This was corrected.
5 | 2019-01-14 | Ben Reinhart | Will Nichols | Updated for 2018 program rules, specifically changing the incentive rate to $0.07 per annual kWh saved.
6 | 2022-08-15 | Ben Reinhart |  | Updated for 2022 Project Cost cap of $,1000,000 per project and per building per year.