## Instructions
AES Indiana Business Rebates & Incentives Program
Lighting Retrofit Savings Calculator
Welcome. This document has been prepared by CLEAResult.
The purpose of this spreadsheet is to determine the savings from replacing an existing lighting system with a more efficient lighting system.
1. Enter all initial parameters on the "Lighting Calculator" tab. The necessary items are highlighted in Green.
2. All required fields must be filled in for savings to be properly displayed.
3. For technical support on this tool contact custom@aesindianarebates.com.
Please Note: This calculator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this calculator is deemed acceptable for the AES Indiana Custom Incentives program. However, the assumptions used by the applicant to calculate the annual savings will be reviewed by the AES Indiana Custom Incentives program, which is solely responsible for the final determination of the annual energy savings to be used in calculating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities.
Incentive amount is calculated based on first year energy savings. The incentives are earned at $0.07 per kWh saved. Total combined custom and prescriptive incentives are capped at $1,000,000 per customer per calendar year.

## Methodology
AES Indiana Business Rebates & Incentives Program
Lighting Calculator Methodology for Retrofit Projects
The methodology of this calculator is based on the Illinois Technical Resource Manual, Version 12.
Where:
WattsBase is the actual connected wattage of the existing equipment.
WattsEE is the actual wattage of the efficient equipment.
WattsControlled is the total actual lighting load connected to the controls.
Hours is the annual operating hours of lighting. Site-specific operating hours (estimate from customer or determined from data logging) should be used if available. If not, assume default values dependent on building type.
WHF_E is the lighting cooling HVAC interaction factor for energy. This factor represents the reduced electric space cooling requirements due to the reduction of waste heat rejected by the efficient lighting. Values are dependent on whether the affected space is air conditioned and the building type.
IFkWH is the lighting heating HVAC interaction factor for energy. This factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficient lighting. Values are dependent on the building type and the heating HVAC system type and are only counted if the space has electric heating.
1/1000 is the conversion factor from watts to kilowatts.
CF is the summer peak coincidence factor. Site-specific CF (estimate from customer or determined from data logging) should be used if available. If not, assume default values dependent on building type.
WHF_D is the lighting-HVAC interaction factor for demand. This factor represents the reduced electric space cooling requirements due to the reduction of waste heat rejected by the efficient lighting. Values are dependent on whether the affected space is air conditioned and the building type.
ESF is the energy savings factor. This factor represents the percent operating hours or wattage reduced due to the installation of the occupancy lighting controls, timeclocks, dimming lighting controls, or multilevel switching. Site-specific factor should be determined from data logging if possible. If not, assume default values dependent on control type.
CFControlled is the summer peak coincidence factor. Site-specific factor should be determined from data logging if possible. If not, assume default values dependent on control type.
〖𝑘𝑊ℎ〗_(𝐴𝑛𝑛𝑢𝑎𝑙 𝑆𝑎𝑣𝑖𝑛𝑔𝑠)=(〖(𝑊𝑎𝑡𝑡𝑠〗_𝐵𝑎𝑠𝑒−〖𝑊𝑎𝑡𝑡𝑠〗_𝐸𝐸)×𝐻𝑜𝑢𝑟𝑠×(〖𝑊𝐻𝐹〗_𝐸 −𝐼𝐹𝑘𝑊ℎ)" " )/1,000
〖𝑘𝑊〗_(𝑆𝑢𝑚𝑚𝑒𝑟 𝑃𝑒𝑎𝑘 𝑆𝑎𝑣𝑖𝑛𝑔𝑠)=((〖𝑊𝑎𝑡𝑡𝑠〗_𝐵𝑎𝑠𝑒−〖𝑊𝑎𝑡𝑡𝑠〗_𝐸𝐸)×𝐶𝐹×(〖𝑊𝐻𝐹〗_𝐷)" " )/1,000
〖𝑘𝑊ℎ〗_(𝐴𝑛𝑛𝑢𝑎𝑙 𝑆𝑎𝑣𝑖𝑛𝑔𝑠, 𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑠)=(〖𝑊𝑎𝑡𝑡𝑠〗_𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑑×𝐻𝑜𝑢𝑟𝑠×(〖𝑊𝐻𝐹〗_(𝐸 )−𝐼𝐹𝑘𝑊ℎ)×𝐸𝑆𝐹)/1,000
〖𝑘𝑊〗_(𝑆𝑢𝑚𝑚𝑒𝑟 𝑃𝑒𝑎𝑘 𝑆𝑎𝑣𝑖𝑛𝑔𝑠, 𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑠)=(〖𝑊𝑎𝑡𝑡𝑠〗_𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑑×〖𝐶𝐹〗_𝐶𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑑×(〖𝑊𝐻𝐹〗_𝐷)×𝐸𝑆𝐹)/1,000

## Lighting Calculator
AES Indiana Business Rebates & Incentives Program
Lighting Savings Calculator Retrofit
Color Legend Highlighting
Input
Results
Site Information
Building Name:
Area Description:
Building Type:
HVAC Heating System Type:
Electricity Rate ($/kWh, Example: $0.08/kWh): | 0.08
Project Cost:
Operating Hours and Summer Coincidence Factor
Default Operating Hours for Building Type:
Default Summer Coincidence Factor for Building Type:
Annual Operating Hours Type:
If Custom, Customer Operating Hours:
Baseline Conditions
Fixture Description (optional) (ex. 4-lamp 4' 54W T5HO):
Baseline Conditions | 1 | 2 | 3 | 4 | 5
Is the space with the lights air conditioned:
Are these exterior fixtures:
Fixture Type:
Fixture Qty:
Watts / Fixture (W)
Pre Control Type (Use "Custom" if ESF and CF are known):
Baseline Controls Energy Savings Factor and Controlled Summer Coincidence Factor
Default Baseline Controls ESF
Default Baseline Controls CF
Baseline Controls Factors to Use:
If Custom Controls, Baseline Controls ESF (%)
If Custom Baseline Controls, Baseline Controls CF
Proposed Conditions
Fixture Description (optional), (ex. 1-lamp 4' 18W LED):
Proposed Conditions | 1 | 2 | 3 | 4 | 5
Fixture Type:
Post Fixture Qty:
Installed Watts / Fixture (W)
Installed Control Type (Use "Custom" if ESF and CF are known):
Proposed Controls Energy Savings Factor and Controlled Summer Coincidence Factor
Default Baseline Controls ESF
Default Baseline Controls CF
Baseline Controls Factors to Use:
If Custom Controls, Baseline Controls ESF (%)
If Custom Baseline Controls, Baseline Controls CF
Hide Row
Energy and Demand Savings Calculations | [5 empty] | Hide Row
Hide Row
Hours | 0 | 0 | 0 | 0 | 0 | Hide Row
CF | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
WHF_Energy | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
WHF_Demand | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
IFkWh | #N/A | #N/A | #N/A | #N/A | #N/A
ESF_Baseline | 0% | 0% | 0% | 0% | 0% | Hide Row
ESF_Proposed | 0% | 0% | 0% | 0% | 0% | Hide Row
CF_Controls_Baseline | 0 | 0 | 0 | 0 | 0 | Hide Row
CF_Controls_Proposed | 0 | 0 | 0 | 0 | 0 | Hide Row
Baseline Lighting Energy | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Baseline Controls Energy Savings | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Net Baseline Energy | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Proposed Energy | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Proposed Controls Energy Savings | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Net Proposed Energy | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Lighting Energy Savings | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Controls Energy Savings | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Net Energy Savings | 0 | 0 | 0 | 0 | 0 | Hide Row
Lighting Demand Savings | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Controls Demand Savings | #N/A | #N/A | #N/A | #N/A | #N/A | Hide Row
Net Demand Savings | 0 | 0 | 0 | 0 | 0 | Hide Row
Hide Row
Incentive Calculations | [5 empty] | Hide Row
Hide Row
Capped Incentive | 0 |  |  |  |  | Hide Row
Incentive at $0.07 per kWh savings | 0 |  |  |  |  | Hide Row
Incentive Amount Approved | 0 |  |  |  |  | Hide Row
Savings Summary
Baseline Energy Consumption (kWh/Yr.) | 0
Proposed Energy Consumption (kWh/Yr.) | 0
Energy Savings (kWh/Yr.) | 0
Demand Reduction (kW) | 0
Eligible Custom Incentive | Need Project Cost
Incentive Based on:
Energy Cost Savings ($/Yr.) | Need Total Annual kWh Saved
Simple Payback Period without Incentive (Yrs.) | Need Project Cost
Simple Payback Period with Incentive (Yrs.) | Need Project Cost
Note on B15: If unknown use $0.08
Note on B20: Default will use the average hours based on the building type. Custom allows you to enter in your own hours. You may be asked to provide justification for the entered hours.
Note on B29: See "Fixture Wattage Reference" tab for guidance.

## Project Notes
This is an optional sheet that is not password protected where you can put any notes about the project or additional calculations (if needed).

## LookUp Tables
AES Indiana Business Rebates & Incentives Program
Lighting Calculator Look-Up Tables
Heating System
[5 empty] | 0 | 1 | 2
[5 empty] | Electric Resistance | Heat Pump | Natural Gas, None, or Other | Control Type | ESF | CF Controlled | Fixture Types
Building Type | Hrs/yr | CF | WHFe | WHFd | IFkWh | IFkWh | IFkWh | Interior Occupancy Sensor (automatic on / automatic off) | 24% | 0.15 | LED
Exterior | 4303 | 0 | 1 | 1 | 0 | 0 | 0 | Interior Vacancy Sensor (manual on / automatic off) | 31% | 0.15 | CFL
Arena /Auditorium /Convention | 3379 | 0.67 | 1.08 | 1.3 | 0.354 | 0.154 | 0 | Interior Daylight Sensor | 28% | 0.15 | Circular Lamp
Assisted living | 7862 | 0.66 | 1.14 | 1.3 | 0.823 | 0.358 | 0 | Interior Dual Occupancy and Daylighting Sensor | 38% | 0.15 | Halogen
Auto Dealership | 4099 | 0.97 | 1.16 | 1.24 | 0.315 | 0.137 | 0 | Interior Networked Luminaire Level Lighting Controls (LLLCs) | 61% | 0.15 | High Pressure Sodium
Daycare | 2860 | 0.72 | 1.17 | 1.29 | 0.42 | 0.183 | 0 | Interior Networked Lighting Controls Only with no LLLCs | 35% | 0.15 | Incandescent
College/University | 3395 | 0.63 | 1.02 | 1.54 | 0.548 | 0.238 | 0 | Interior Networked Lighting Controls (unknown or mixed LLLCs) | 49% | 0.15 | Low Wattage T8
Convenience Store | 4672 | 0.76 | 1.09 | 1.26 | 0.828 | 0.36 | 0 | Refrigerated Case Occupancy Sensor – Freezer and Cooler | 27% | 0.15 | Mercury Vapor
Drug Store | 4093 | 1 | 1.05 | 1.34 | 0.394 | 0.171 | 0 | Exterior Occupancy Sensor | 27% | 0 | Metal Halide
School (Elementary) | 3038 | 0.65 | 1.04 | 1.51 | 0.455 | 0.198 | 0 | Exterior Networked Lighting Controls | 48% | 0 | T12
Police/Fire Station | 2698 | 0.65 | 1.06 | 1.09 | 0.014 | 0.006 | 0 | Interior High End Trim | 13% | 0.15 | T5
Parking Garage | 3401 | 0.92 | 1 | 1 | 0 | 0 | 0 | Custom |  |  | T8
Grocery | 5468 | 0.82 | 1.05 | 1.22 | 0.23 | 0.1 | 0 | None | 0% | 0 | U-Tube T8
Healthcare clinic | 3890 | 0.67 | 1.14 | 1.04 | 0.463 | 0.201 | 0 |  |  |  | U-Tube T12
School (High/Middle) | 3038 | 0.65 | 1.15 | 1.4 | 0.249 | 0.108 | 0 |  |  |  | Custom
Hospital | 7616 | 0.56 | 1.13 | 1.35 | 0.148 | 0.064 | 0
Manufacturing facility | 4618 | 0.81 | 1.02 | 1.04 | 0.27 | 0.117 | 0
Multi-Family (Common Areas) | 5216 | 0.62 | 1.11 | 1.16 | 0.484 | 0.211 | 0 | HVAC Heating System Type | IFkWh
Lodging - Common Areas | 6138 | 0.85 | 1.09 | 1.26 | 0.406 | 0.176 | 0 | Electric Resistance
Lodging Hotel (Guest Rooms) | 2390 | 0.46 | 1.17 | 1.21 | 0.468 | 0.204 | 0 | Heat Pump
Office - Large | 2886 | 0.6 | 1.21 | 1.17 | 0.153 | 0.067 | 0 | Natural Gas, None, or Other
Office - Low Rise | 2698 | 0.52 | 1.1 | 1.26 | 0.231 | 0.1 | 0
Office - Mid Rise | 3266 | 0.6 | 1.1 | 1.36 | 0.378 | 0.164 | 0
Religious/Worship | 2085 | 0.48 | 1.12 | 1.37 | 0.356 | 0.155 | 0
Restaurant | 5571 | 1 | 1.08 | 1.1 | 0.208 | 0.09 | 0
Retail - Department Store | 4099 | 0.94 | 1.06 | 1.06 | 0.346 | 0.15 | 0
Retail - Strip Mall | 4093 | 0.71 | 1.12 | 1.29 | 0.45 | 0.196 | 0
Warehouse | 3135 | 0.85 | 1.02 | 1.17 | 0.378 | 0.164 | 0
Other | 3379 | 0.67 | 1.08 | 1.3 | 0.354 | 0.154 | 0
Low-Use Small Business | 2954 | 0.66 | 1.31 | 1.53 | 0.524 | 0.262 | 0
Refrigerated Cases | 5802 | 1 | 1.29 | 1.29 | 0 | 0 | 0
Freezer Cases | 5802 | 1 | 1.5 | 1.5 | 0 | 0 | 0

## Fixture Wattage Reference
Source | IL TRM v12 |  | Table developed using a constant ballast factor of .77 for troffers/linear HPT8 and 1.15 for HPT8 highbay, and 0.88 for standard T8.
Below is a list of the most commonly seen fixtures and their associated fixture wattage:
T12 Fluorescent Fixtures
Note that T12s are no longer allowed to be used as the baseline fixture. Instead use the T8 equivalent wattage for the baseline calculations if T12 fixtures are being replaced.
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 8 | 10 | 12
T8 Fluorescent Fixtures
Lamps per fixture: | Lamp W | BF | 1-Lamp | 2-Lamps | 3-Lamps | 4-Lamps | 5-Lamps | 6-Lamps | 8-Lamps | 10-Lamps | 12-Lamps
18" 15W T8 Lamp, Electronic Ballast | 15 | 0.88 | 13.2 | 26.4 | 39.6 | 52.8 | 66 | 79.2 | 105.6 | 132 | 158.4
2' RW F17T8 Lamp, Electronic Ballast | 16 | 0.88 | 14.08 | 28.16 | 42.24 | 56.32 | 70.4 | 84.48 | 112.64 | 140.8 | 168.96
2' 17W T8 Lamp, Electronic Ballast | 17 | 0.88 | 14.96 | 29.92 | 44.88 | 59.84 | 74.8 | 89.76 | 119.68 | 149.6 | 179.52
3' RW F25T8 Lamp, Electronic Ballast | 23 | 0.88 | 20.24 | 40.48 | 60.72 | 80.96 | 101.2 | 121.44 | 161.92 | 202.4 | 242.88
3' 25W T8 Lamp, Electronic Ballast | 25 | 0.88 | 22 | 44 | 66 | 88 | 110 | 132 | 176 | 220 | 264
4' 25W RW T8 Lamp, Electronic Ballast | 25 | 0.88 | 22 | 44 | 66 | 88 | 110 | 132 | 176 | 220 | 264
4' 28W RW T8 Lamp, Electronic Ballast | 28 | 0.88 | 24.64 | 49.28 | 73.92 | 98.56 | 123.2 | 147.84 | 197.12 | 246.4 | 295.68
4' 30W ES T8 Lamp, Electronic Ballast | 30 | 0.88 | 26.4 | 52.8 | 79.2 | 105.6 | 132 | 158.4 | 211.2 | 264 | 316.8
4' 32W HP T8 Lamp, Electronic Ballast | 32 | 0.77 | 24.64 | 49.28 | 73.92 | 98.56 | 123.2 | 147.84 | 197.12 | 246.4 | 295.68
4' 32W Std T8 Lamp, Electronic Ballast Lamps | 32 | 0.88 | 28.16 | 56.32 | 84.48 | 112.64 | 140.8 | 168.96 | 225.28 | 281.6 | 337.92
4' 32W Std T8 Lamp, Electronic Ballast Troffer | 32 | 0.885 | 29.1 | 57 | 84.5 | 112.6 | 141.6 | 169.92 | 226.56 | 283.2 | 339.84
5' 40W T8 Lamp, Electronic Ballast | 40 | 0.88 | 35.2 | 70.4 | 105.6 | 140.8 | 176 | 211.2 | 281.6 | 352 | 422.4
6' 46W T8 Lamp, Electronic Ballast | 46 | 0.88 | 40.48 | 80.96 | 121.44 | 161.92 | 202.4 | 242.88 | 323.84 | 404.8 | 485.76
8' RW F96T8 Lamp, Electronic Ballast | 65 | 0.88 | 57.2 | 114.4 | 171.6 | 228.8 | 286 | 343.2 | 457.6 | 572 | 686.4
8' Std F96T8 Lamp, Electronic Ballast | 70 | 0.88 | 61.6 | 123.2 | 184.8 | 246.4 | 308 | 369.6 | 492.8 | 616 | 739.2
4' 25W T8/HO Lamp, Electronic Ballast | 25 | 1.15 | 28.75 | 57.5 | 86.25 | 115 | 143.75 | 172.5 | 230 | 287.5 | 345
Lamps per fixture: | Lamp W | BF | 1-Lamp | 2-Lamps | 3-Lamps | 4-Lamps | 5-Lamps | 6-Lamps | 8-Lamps | 10-Lamps | 12-Lamps
4' 28W T8/HO Lamp, Electronic Ballast | 28 | 1.15 | 32.2 | 64.4 | 96.6 | 128.8 | 161 | 193.2 | 257.6 | 322 | 386.4
4' 32W T8/HO Lamp, Electronic Ballast | 32 | 1.15 | 36.8 | 73.6 | 110.4 | 147.2 | 184 | 220.8 | 294.4 | 368 | 441.6
4' 32W T8/VHO Lamp, Electronic Ballast | 32 | 1.25 | 41.8 | 80 | 120 | 160 | 200 | 240 | 320 | 400 | 480
4' 44W T8/HO Lamp, Electronic Ballast | 44 | 1.1245 | 49.48 | 98.95 | 157 | 196 | 247.38 | 294 | 392 | 494.76 | 593.71
5' 55W T8/HO Lamp, Electronic Ballast | 55 | 1.15 | 63.25 | 126.5 | 189.75 | 253 | 316.25 | 379.5 | 506 | 632.5 | 759
6' 66W T8/HO Lamp, Electronic Ballast | 66 | 1.15 | 75.9 | 151.8 | 227.7 | 303.6 | 379.5 | 455.4 | 607.2 | 759 | 910.8
8' 86W T8/HO Lamp, Electronic Ballast | 86 | 1.15 | 98.9 | 197.8 | 296.7 | 395.6 | 494.5 | 593.4 | 791.2 | 989 | 1186.8
RW F29T8 U-Bend Lamp, Electronic Ballast | 29 | 0.88 | 25.52 | 51.04 | 76.56 | 102.08 | 127.6 | 153.12 | 204.16 | 255.2 | 306.24
RW F30T8 U-Bend Lamp, Electronic Ballast | 30 | 0.88 | 26.4 | 52.8 | 79.2 | 105.6 | 132 | 158.4 | 211.2 | 264 | 316.8
32W U-Bend T8 Lamp, Electronic Ballast | 32 | 0.88 | 28.16 | 56.32 | 84.48 | 112.64 | 140.8 | 168.96 | 225.28 | 281.6 | 337.92
T5 Fluorescent Fixtures
Lamps per fixture: | Lamp W | BF | 1-Lamp | 2-Lamps | 3-Lamps | 4-Lamps | 5-Lamps | 6-Lamps | 8-Lamps | 10-Lamps | 12-Lamps
2' 14W T5 Lamp, Electronic Ballast | 14 | 1.14 | 15.96 | 31.92 | 47.88 | 63.84 | 79.8 | 95.76 | 127.68 | 159.6 | 191.52
2' 24W T5/HO Lamp, Electronic Ballast | 24 | 1.1111 | 26.67 | 53.33 | 80 | 106.67 | 133.33 | 160 | 213.33 | 266.67 | 320
3' 21W T5 Lamp, Electronic Ballast | 21 | 1.14 | 23.94 | 47.88 | 71.82 | 95.76 | 119.7 | 143.64 | 191.52 | 239.4 | 287.28
3' 39W T5/HO Lamp, Electronic Ballast | 39 | 1.1111 | 43.33 | 86.67 | 130 | 173.33 | 216.67 | 260 | 346.67 | 433.33 | 520
4' 28W T5 Lamp, Electronic Ballast | 28 | 1.1429 | 32 | 64 | 96 | 128 | 160 | 192 | 256 | 320 | 384
4' 39W T5/HO Lamp, Electronic Ballast | 39 | 1.1111 | 43.33 | 86.67 | 130 | 173.33 | 216.67 | 260 | 346.67 | 433.33 | 520
4' 50W T5/HO Lamp, Electronic Ballast | 50 | 1.1111 | 55.56 | 111.11 | 166.67 | 222.22 | 277.78 | 333.33 | 444.44 | 555.56 | 666.67
4' 54W T5/HO Lamp, Electronic Ballast | 54 | 1.1111 | 60 | 120 | 180 | 240 | 300 | 360 | 480 | 600 | 720
5' 35W T5 Lamp, Electronic Ballast | 35 | 1.11 | 38.85 | 77.7 | 116.55 | 155.4 | 194.25 | 233.1 | 310.8 | 388.5 | 466.2
Other Fluorescent Fixtures | [5 empty] | Pin-Based CFL Fixtures
Lamps per fixture: | 1-Lamp | 2-Lamps | 3-Lamps |  |  | Lamps per fixture: |  |  | 1-Lamp | 2-Lamps | 3-Lamps
4' 40W T10 | 41 | 77 | 114 |  |  | 9W Pinned-Based CFL |  |  | 10.3846 | 19.3846 | 29.7692
32W FC12T9 Circline | 31 | 62 | 93 |  |  | 13W Pinned-Based CFL |  |  | 15 | 28 | 43
22W FC8T9 Circline | 26 | 52 | 78 |  |  | 18W Pinned-Based CFL |  |  | 20 | 38 | 58
[6 empty] | 26W Pinned-Based CFL |  |  | 27 | 50 | 77
[6 empty] | 28W Pinned-Based CFL |  |  | 29.75 | 54.25 | 84
[6 empty] | 32W Pinned-Based CFL |  |  | 34 | 62 | 96
[6 empty] | 38W Pinned-Based CFL |  |  | 40 | 74 | 114
[6 empty] | 40W Pinned-Based CFL |  |  | 43 | 72 | 105
[6 empty] | 42W Pinned-Based CFL |  |  | 44 | 93 | 137
High Pressure Sodium | W / Fixture |  |  |  |  | Metal Halide Fixtures (Std/Probe-Start) |  |  |  | W / Fixture
35W High Pressure Sodium | 46 |  |  |  |  | 20W Metal Halide |  |  |  | 23
50W High Pressure Sodium | 66 |  |  |  |  | 32W Metal Halide |  |  |  | 43
70W High Pressure Sodium | 95 |  |  |  |  | 50W Metal Halide |  |  |  | 77
100W High Pressure Sodium | 138 |  |  |  |  | 70W Metal Halide |  |  |  | 95
150W High Pressure Sodium | 188 |  |  |  |  | 100W Metal Halide |  |  |  | 113.6
200W High Pressure Sodium | 250 |  |  |  |  | 150W Metal Halide |  |  |  | 190
250W High Pressure Sodium | 295 |  |  |  |  | 175W Metal Halide |  |  |  | 208
310W High Pressure Sodium | 365 |  |  |  |  | 200W Metal Halide |  |  |  | 232
400W High Pressure Sodium | 465 |  |  |  |  | 250W Metal Halide |  |  |  | 295
750W High Pressure Sodium | 835 |  |  |  |  | 360W Metal Halide |  |  |  | 418
1,000W High Pressure Sodium | 1100 |  |  |  |  | 400W Metal Halide |  |  |  | 455
[6 empty] | 750W Metal Halide |  |  |  | 850
[6 empty] | 1,000W Metal Halide |  |  |  | 1080
Mercury Vapor | W / Fixture |  |  |  |  | 1,500W Metal Halide |  |  |  | 1610
40W Mercury Vapor | 50
50W Mercury Vapor | 74
75W Mercury Vapor | 93 |  |  |  |  | Pulse-Start Metal Halide Fixtures |  |  |  | W / Fixture
100W Mercury Vapor | 125 |  |  |  |  | 100W Pulse-Start Metal Halide |  |  |  | 110
175W Mercury Vapor | 205 |  |  |  |  | 150W Pulse-Start Metal Halide |  |  |  | 183
250W Mercury Vapor | 290 |  |  |  |  | 175W Pulse-Start Metal Halide |  |  |  | 198.9
400W Mercury Vapor | 455 |  |  |  |  | 200W Pulse-Start Metal Halide |  |  |  | 227.3
700W Mercury Vapor | 780 |  |  |  |  | 250W Pulse-Start Metal Halide |  |  |  | 284.1
1,000W Mercury Vapor | 1075 |  |  |  |  | 320W Pulse-Start Metal Halide |  |  |  | 363.6
[6 empty] | 350W Pulse-Start Metal Halide |  |  |  | 397.7
[6 empty] | 400W Pulse-Start Metal Halide |  |  |  | 454.5
Ceramic Metal Halide Fixtures | W / Fixture |  |  |  |  | 500W Pulse-Start Metal Halide |  |  |  | 506
20W Ceramic Metal Halide | 26 |  |  |  |  | 750W Pulse-Start Metal Halide |  |  |  | 818
39W Ceramic Metal Halide | 45 |  |  |  |  | 1,000W Pulse-Start Metal Halide |  |  |  | 1080
50W Ceramic Metal Halide | 55
70W Ceramic Metal Halide | 79
100W Ceramic Metal Halide | 110
150W Ceramic Metal Halide | 163

## Updates (hidden)
Version # | Date | Editing Engineer | Reviewing Engineer | Updates Made
1 | 2017-01-01 | Ben Reinhart | Will Nichols | Updated for 2017 program rules, inlcuding incentive caps
2 | 2017-02-01 | Ben Reinhart | Will Nichols | Fixed calculation issue with different quantities of existing and proposed columns.
3 | 2017-04-03 | Ben Reinhart | Will Nichols | Added more fixture types to wattage reference.
4 | 2018-01-08 | Ben Reinhart | Will Nichols | Updated for 2018 program rules, inlcuding the new $0.06 per kWh saved rate.
5 | 2018-01-14 | Ben Reinhart | Will Nichols | Updated for 2019 program rules, inlcuding the new $0.07 per kWh saved rate.
6 | 2024-06-28 | Ben Reinhart | Will Nichols | Updated to use the IL TRM v12 methodology including WHF, hours, CF, IFkWh values, and ESFs.
7
8
9
10