## Application
AES Indiana Business Rebates & Incentives Program
Electric Chiller Replacement
Customer Information
Customer/Business Name: |  |  | Account Holder:
Phone Number: |  |  | Email Address:
AES Indiana Account Number (As shown on utility bill): |  |  | Business Rate Class: |  | Site ID:
Installation Street Address: |  |  | City |  | State | Zip Code
IN
Building Type:
Heating Type: |  |  | Cooling Type:
Mailing Address for Incentive Check
Payee Legal Name (as shown on income tax return): |  |  | Payee Business Name (if different than payee legal name):
Payee Legal Address: |  |  | City |  | State | Zip Code
Payee Contact Name: |  |  | Payee Phone: |  | Payee Email:
Payee Federal Tax Classification (choose from list):
Payee Taxpayer Identification Number (TIN) (Complete ONE only. Must match payee legal name above)
FEIN #: | (XX-XXXXXXX) |  | OR SSN: | (XX-XX-XXXX)
Installing Trade Ally Information
Business Name: |  |  | Contact Name:
Phone Number: |  |  | Email Address:
Address: |  |  | City |  | State | Zip Code
Sign Application
I hereby certify that: 1. The information contained in this final application is accurate and complete. 2. All rules of this incentive application have been followed. 3. I have read and understood the terms and conditions of this document. I agree to verification of equipment installation which may include a site inspection by a program or utility representative. I understand that I am not allowed to receive more than one incentive from this program on any piece of equipment. I hereby agree to indemnify, hold harmless, and release the utility from any actions or claims in regard to the installation, operation, or disposal of equipment (and related materials) covered herein, including liability from any incidental or consequential damages.
Signature |  | Print Name |  |  | Date
If Trade Ally is receiving the incentive payment, Trade Ally signature is required below.
Signature |  | Print Name |  |  | Date
Program Rules
In order to qualify for an incentive, the following must occur:
1. Customer must exceed the minimum chiller efficiency requirements specified by path A
or path B in IECC 2018, and indicate which path was used for the rated efficiencies.
2. Customer must submit spec sheets on all chillers verifying the inputs used in this calculator.
3. Customer must submit this workbook and invoices for both the material and external labor cost
of this project. A W-9 for the payee must also be submitted.
4. Incentives are earned at $0.08 per kWh saved in the first year post install.
5. Incentives will not exceed 50% of the total project cost.
6. Total combined custom and prescriptive incentives are capped at $1,000,000 per customer
per calendar year.

## Instructions
AES Indiana Business Rebates & Incentives Program
Chiller Replacement Savings Calculator
Welcome. This document has been prepared by CLEAResult.
The purpose of this spreadsheet is to determine the savings from replacing an existing HVAC electric chiller with a more efficient chiller. The baseline chiller is a minimum code efficient chiller.
1. Enter all initial parameters on the "Calculator" tab. The necessary items are highlighted in Green.
2. All required fields must be filled in for savings to be properly displayed.
3. For technical support on this tool contact custom@aesindianarebates.com.
4. Submit a spec sheet for each chiller showing the rated full load efficiency, IPLV, rated path, and tons.
Please Note: This calculator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this calculator is deemed acceptable for the AES Indiana Custom Incentives program. However, the assumptions used by the applicant to calculate the annual savings will be reviewed by the AES Indiana Custom Incentives program, which is solely responsible for the final determination of the annual energy savings to be used in calculating the incentive
amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities.
Incentive amount is calculated based on first year energy savings. The incentives are earned at $0.08 per kWh saved. Incentives are limited to a maximum cap of $1,000,000 per project at a service ID and/or building behind a master meter.
Total combined custom and prescriptive incentives are capped at $1,000,000 per customer per calendar year.

## Calculator
AES Indiana Business Rebates & Incentives Program
Chiller Savings Calculator
Color Legend Highlighting
Input
Calculated
Header / Example
| Site Information |  | Building Type Notes: |  | Useful Conversions:
| Facility Name: | High School example | CAV = Constant Air Volume |  | kW / ton = 12 / EER
| Building Type: | School (High/Middle) | VAV = Variable Air Volume |  | EER = COP * 3.412
| Total Project Cost: | 1000000 | FCU - Fan Coil Unit |  | 1 ton = 12,000 Btu/hr
| Potential Custom Incentive: | 11112.8058 | no econ - no economizer
| Total kWh/yr Savings | 138910.0727 | econ = economizer
| Total kW Savings | 17.0242
Note: This methodology only applies to HVAC chillers. Process chillers will be calculated using a different custom methodology.
| Air-Cooled Chillers | [17 empty] | kWh/yr Savings | kW Savings | Eligible Incentive
[18 empty] | Total | 22672.3667 | 1.5032 | 1813.7893
| Chiller Tag / ID Number | Model Number | Serial Number | Manufacturer | Size Category (Drop Down List) | Tons | Efficiency Rating Path (Drop Down List) | Rated Full Load EER | Rated IPLV (in EER) | Is only an NPLV rating available? | If Yes, then rated NPLV (in EER) | NPLV Adj Factor | Is this a backup Chiller Only? | Baseline Full Load EER | Baseline IPLV /NPLV (in EER) | Meets EER Requirement | Meets IPLV Requirement | EFLH | kWh/yr Savings | kW Savings | Eligible Incentive
example | Chiller #1 | XXXX-XXXX-XXXX | XXXX-XXXX-XXXX | Carrier | < 150 Tons | 120 | Path A | 10.2 | 15 | No | N/A | N/A | No | 10.1 | 13.7 | Yes | Yes | 1066 | 9710.7153 | 1.2762 | 776.8572
1 | CH-1 | 30RCB0926S016-D09 | 4925Q901748 | Carrier | ≥ 150 tons | 156.9 | Path A | 10.19 | 16.63 | No | N/A | N/A | No | 10.1 | 14 | Yes | Yes | 1066 | 22672.3667 | 1.5032 | 1813.7893
2 | CH-2 | 30RCB0926S016-D09 | 4925Q901749 | Carrier | ≥ 150 tons | 156.9 | Path A | 10.19 | 16.63 | No | N/A | N/A | Yes | 10.1 | 14 | Yes | Yes | 1066 | 0 | 0 | 0
3 | [17 empty] | 1066 | 0 | 0 | 0
4 | [17 empty] | 1066 | 0 | 0 | 0
5 | [17 empty] | 1066 | 0 | 0 | 0
6 | [17 empty] | 1066 | 0 | 0 | 0
7 | [17 empty] | 1066 | 0 | 0 | 0
8 | [17 empty] | 1066 | 0 | 0 | 0
9 | [17 empty] | 1066 | 0 | 0 | 0
10 | [17 empty] | 1066 | 0 | 0 | 0
| Water-Cooled Chillers (Positive Displacement: screw, scroll, reciprocating, and rotary vane) | [17 empty] | kWh/yr Savings | kW Savings | Eligible Incentive
[18 empty] | Total | 21017.256 | 15.521 | 1681.3805
| Chiller Tag # / ID | Model Number | Serial Number | Manufacturer | Size Category (Drop Down List) | Tons | Efficiency Rating Path (Drop Down List) | Rated Full Load kW/ton | Rated IPLV (in kW/ton) | Is only an NPLV rating available? | If Yes, then rated NPLV (in EER) | NPLV Adj Factor | Is this a backup Chiller Only? | Baseline Full Load kW/ton | Baseline IPLV / NPLV (in kW/ton) | Meets EER Requirement | Meets IPLV Requirement | EFLH | kWh/yr Savings | kW Savings | Eligible Incentive
example | CH-2 | XXXX-XXXX-XXXX | XXXX-XXXX-XXXX | Trane | ≥ 75 & <150 tons | 120 | Path A | 0.7 | 0.5 | No | N/A | N/A | No | 0.72 | 0.56 | Yes | Yes | 1066 | 7675.2 | 2.1912 | 614.016
1 | CH-3 | Fictional Screw Chiller | XXXX-XXXX-XXXX | Trane | ≥ 75 & <150 tons | 100 | Path A | 0.67 | 0.52 | No | N/A | N/A | No | 0.72 | 0.56 | Yes | Yes | 1066 | 4264 | 4.565 | 341.12
2 | CH-4 | Fictional Screw Chiller | XXXX-XXXX-XXXX | Trane | ≥ 150 & <300 tons | 200 | Path A | 0.6 | N/A | Yes | 0.53 | 1.127 | No | 0.66 | 0.60858 | Yes | Yes | 1066 | 16753.256 | 10.956 | 1340.2605
3 | [17 empty] | 1066 | 0 | 0 | 0
4 | [17 empty] | 1066 | 0 | 0 | 0
5 | [17 empty] | 1066 | 0 | 0 | 0
6 | [17 empty] | 1066 | 0 | 0 | 0
7 | [17 empty] | 1066 | 0 | 0 | 0
8 | [17 empty] | 1066 | 0 | 0 | 0
9 | [17 empty] | 1066 | 0 | 0 | 0
10 | [17 empty] | 1066 | 0 | 0 | 0
| Water-Cooled Chillers (Centrifugal) | [17 empty] | kWh/yr Savings | kW Savings | Eligible Incentive
[18 empty] | Total | 95220.45 | 0 | 7617.636
| Chiller Tag # / ID | Model Number | Serial Number | Manufacturer | Size Category (Drop Down List) | Tons | Efficiency Rating Path (Drop Down List) | Rated Full Load kW/ton | Rated IPLV (in kW/ton) | Is only an NPLV rating available? | If Yes, then rated NPLV (in EER) | NPLV Adj Factor | Is this a backup Chiller Only? | Baseline Full Load kW/ton | Baseline IPLV / NPLV (in kW/ton) | Meets EER Requirement | Meets IPLV Requirement | EFLH | kWh/yr Savings | kW Savings | Eligible Incentive
example | Chiller #3 | XXXX-XXXX-XXXX | XXXX-XXXX-XXXX | Daikin | ≥ 150 & <300 tons | 200 | Path B | 0.6 | 0.35 | No | N/A | N/A | No | 0.635 | 0.4 | Yes | Yes | 1066 | 10660 | 6.391 | 852.8
1 | CH-5 | YKH3FLH9_EWH | XXXX-XXXX-XXXX | York | ≥ 600 tons | 750 | Path A | 0.665 | N/A | Yes | 0.4219 | 1.082 | No | 0.56 | 0.541 | No | Yes | 1066 | 95220.45 | 0 | 7617.636
2 | CH-6 | YKH3FLH9_EWH | XXXX-XXXX-XXXX | York | ≥ 600 tons | 750 | Path A | 0.665 | N/A | Yes | 0.4219 | 1.082 | Yes | 0.56 | 0.541 | No | Yes | 1066 | 0 | 0 | 0
3 | [17 empty] | 1066 | 0 | 0 | 0
4 | [17 empty] | 1066 | 0 | 0 | 0
5 | [17 empty] | 1066 | 0 | 0 | 0
6 | [17 empty] | 1066 | 0 | 0 | 0
7 | [17 empty] | 1066 | 0 | 0 | 0
8 | [17 empty] | 1066 | 0 | 0 | 0
9 | [17 empty] | 1066 | 0 | 0 | 0
10 | [17 empty] | 1066 | 0 | 0 | 0
Note on K25: IPLV Ratings preferred over NPLV thus only use NPLV if IPLV rating not listed.
Note on L25: Mark as N/A if IPLV if previous column is listed as "No".
Note on M25: See the NPLV Adj factors tab for the appropriate value if NPLV is being used; otherwise use N/A
Note on K43: IPLV Ratings preferred over NPLV thus only use NPLV if IPLV rating not listed.
Note on L43: Mark as N/A if IPLV if previous column is listed as "No".
Note on M43: See the NPLV Adj factors tab for the appropriate value if NPLV is being used; otherwise use N/A
Note on K61: IPLV Ratings preferred over NPLV thus only use NPLV if IPLV rating not listed.
Note on L61: Mark as N/A if IPLV if previous column is listed as "No".
Note on M61: See the NPLV Adj factors tab for the appropriate value if NPLV is being used; otherwise use N/A

## NPLV Adj Factors
Water-Cooled Chillers
ILadj Factors to IPLV (Path A) Baseline
Space Type (occupancy schedule assumption) | Water-Cooled Chiller Type
| Centrifugal | Screw/Scroll
Office (or unknown) (12hr, 5 days/week) | 1.143 | 1.178
Hospital (24hr, 7 days/week, high occupancy during day) | 1.043 | 1.067
High-Rise Apartments (24hr, 7 days/week, lighter occupancy during day) | 1.117 | 1.155
Primary School (12hr, 5 days/week, seasonal) | 1.082 | 1.127
Hotel (24hr, 7days/week) | 1.159 | 1.186
Air-Cooled Chillers
ILadj Factors to IPLV (Path A) Baseline
Space Type | Air-Cooled Chiller
Office (or unknown) | 0.86
Hospital | 0.925
High-Rise Apartments | 0.866
Primary School | 0.85
Hotel | 0.929

## Lists
| Existing Building - Cooling EFLH | [6 empty] | Air-Cooled Chillers |  |  | Reference | 2018 IECC |  |  | Building Types: | Heating Types: | Cooling Types:
AES IN Building Type | IL TRM Building Type | Zone 1 Rockford | Zone 2 Chicago | Zone 3 Springfield | Zone 4 Belleville | Zone 5 Marion | Model Source | Size Category | Path A FL EER | Path B FL EER | Path A IPLV | Path B IPLV |  |  | Arena/Audtorium/Convention | Natural Gas | Electric
Assembly (theater, hall, arena) | Assembly (theater, hall, arena) | 725 | 796 | 937 | 1183 | 932 | eQuest | < 150 Tons | 10.1 | 9.7 | 13.7 | 15.8 | Path A | 1 | Assisted Living | Electric Heat Pump | Other
Assisted Living | Assisted Living | 1475 | 1457 | 1773 | 2110 | 1811 | eQuest | ≥ 150 tons | 10.1 | 9.7 | 14 | 16.1 | Path B | 2 | Auto Dealership | Electric Resistance | Unknown
Auto Dealership | Auto Dealership | 996 | 1051 | 1343 | 1582 | 1414 | OpenStudio | [7 empty] | Daycare | Unknown | None
Daycare | Other | 1003 | 1019 | 1230 | 1403 | 1236 | n/a | [7 empty] | College/University
College/University | College/University | 572 | 564 | 676 | 776 | 613 | OpenStudio | Water-Cooled Chillers (positive displacement) | [6 empty] | Convenience Store
Convenience Store | Convenience Store | 1088 | 1067 | 1368 | 1541 | 1371 | eQuest |  |  |  | Reference | 2018 IECC |  |  | Drug Store
Drug Store | Drug Store | 858 | 943 | 1133 | 1279 | 1092 | OpenStudio | Size Category | Path A FL kW / ton | Path B FL kW / ton | Path A IPLV (kW / ton) | Path B IPLV (kW / ton) |  |  | Grocery
School (Elementary) | School (Elementary) | 834 | 837 | 999 | 1264 | 967 | OpenStudio | < 75 Tons | 0.75 | 0.78 | 0.6 | 0.5 |  |  | Healthcare Clinic
Emergency Services | Emergency Services | 2983 | 3009 | 3762 | 4030 | 3740 | OpenStudio | ≥ 75 & <150 tons | 0.72 | 0.75 | 0.56 | 0.49 |  |  | Hospital
Parking Garage | Parking Garage | 934 | 974 | 1226 | 1582 | 1383 | eQuest | ≥ 150 & <300 tons | 0.66 | 0.68 | 0.54 | 0.44 |  |  | Lodging (Common Areas)
Grocery | Grocery | 826 | 914 | 1151 | 1329 | 1240 | OpenStudio | ≥ 300 & <600 tons | 0.61 | 0.625 | 0.52 | 0.41 |  |  | Lodging Hotel (Guest Rooms)
Healthcare clinic | Healthcare Clinic | 1220 | 1294 | 1505 | 1658 | 1534 | OpenStudio | ≥ 600 tons | 0.56 | 0.585 | 0.5 | 0.38 |  |  | Manufacturing Facility
School (High/Middle) | School (High/Middle) | 892 | 883 | 1066 | 1397 | 1018 | OpenStudio | [7 empty] | Multi-Family (Common Areas)
Hospital | Hospital - CAV no econ | 1719 | 1799 | 2068 | 2238 | 2066 | OpenStudio | [7 empty] | Office (Large)
Hospital | Hospital - CAV econ | 1267 | 1302 | 1604 | 1798 | 1592 | OpenStudio | Water-Cooled Chillers (centrifigual) | [6 empty] | Office (Low Rise)
Hospital | Hospital - VAV econ | 3313 | 3332 | 3458 | 3546 | 3311 | OpenStudio |  |  |  | Reference | 2018 IECC |  |  | Office (Small)
Hospital | Hospital - FCU | 1575 | 1562 | 1921 | 1979 | 1812 | OpenStudio | Size Category | Path A FL kW / ton | Path B FL kW / ton | Path A IPLV (kW / ton) | Path B IPLV (kW / ton) |  |  | Police/Fire Station
Hotel/Motel - Common | Hotel/Motel | 1106 | 1148 | 1453 | 1605 | 1435 | OpenStudio | < 150 Tons | 0.61 | 0.695 | 0.55 | 0.44 |  |  | Parking Garage
Hotel/Motel - Common | Hotel/Motel - Common | 1108 | 1168 | 1430 | 1574 | 1406 | OpenStudio | ≥ 150 & <300 tons | 0.61 | 0.635 | 0.55 | 0.4 |  |  | Religious/Worship
Hotel/Motel - Guest | Hotel/Motel - Guest | 1061 | 1106 | 1391 | 1509 | 1401 | OpenStudio | ≥ 300 & <400 tons | 0.56 | 0.595 | 0.52 | 0.39 |  |  | Restaurant
Manufacturing facility | Manufacturing Facility | 1010 | 1055 | 1209 | 1453 | 1273 | eQuest | ≥ 400 & <600 tons | 0.56 | 0.585 | 0.5 | 0.38 |  |  | Retail (Department Store)
Multi-Family (Common Areas) | MF - High Rise | 928 | 920 | 1059 | 1360 | 1205 | OpenStudio | ≥ 600 tons | 0.56 | 0.585 | 0.5 | 0.38 |  |  | Retail (Strip Mall)
Multi-Family (Common Areas) | MF - High Rise - Common | 1405 | 1383 | 1479 | 1527 | 1466 | OpenStudio | [7 empty] | School (Elementary)
Multi-Family (Common Areas) | MF - High Rise - Residential | 764 | 807 | 976 | 1216 | 1147 | OpenStudio | [7 empty] | School (High/Middle)
Multi-Family (Common Areas) | MF - Mid Rise | 787 | 855 | 1099 | 1198 | 1082 | OpenStudio | [7 empty] | Warehouse
Other | Movie Theater | 876 | 745 | 1036 | 1178 | 1010 | eQuest
Office - Large | Office - High Rise - CAV no econ | 1357 | 1404 | 1587 | 1753 | 1468 | OpenStudio
Office - Large | Office - High Rise - CAV econ | 922 | 937 | 1138 | 1274 | 1000 | OpenStudio
Office - Large | Office - High Rise - VAV econ | 847 | 887 | 991 | 1092 | 893 | OpenStudio
Office - Large | Office - High Rise - FCU | 1083 | 1116 | 1269 | 1348 | 1266 | OpenStudio
Office - Low Rise | Office - Low Rise | 1796 | 1790 | 2233 | 2342 | 2219 | OpenStudio
Office - Mid Rise | Office - Mid Rise | 1128 | 1153 | 1360 | 1461 | 1356 | OpenStudio
Religious/Worship | Religious/Worship | 861 | 817 | 967 | 1159 | 1067 | eQuest
Restaurant | Restaurant | 990 | 1021 | 1273 | 1411 | 1290 | OpenStudio
Retail - Department Store | Retail - Department Store | 639 | 640 | 775 | 936 | 812 | OpenStudio
Retail - Strip Mall | Retail - Strip Mall | 697 | 720 | 915 | 998 | 930 | OpenStudio
Warehouse | Warehouse | 252 | 265 | 363 | 377 | 379 | OpenStudio
Other | Other | 1003 | 1019 | 1230 | 1403 | 1236 | n/a

## Version History
Version | Date | Engineer | QC Engineer | Description | Future Consideration
1 | 2023-12-19 | Ben Reinhart | Will Nichols | Initial Release | Review for code or program changes.
2 | 2024-01-10 | Ben Reinhart | Will Nichols | Added fields for Make, Model #, and Serial # per program team request.
2.1 | 2025-02-05 | Mary Cox (Program Team) | None | Updated application page; did not change any calculations.
3 | 2026-06-17 | Ben Reinhart |  | Created an example calculator. Added option to use NPLV if IPLV is not available and included the baseline adjustment from the IL TRM v14. Also, added option to select unit as backup only and not count towards savings. | Review for code, TRM, or program changes.
4
5
6
7
8
9