## Application
AES Indiana Business Rebates & Incentives Program
Compressed Air Leak Repair Application
Customer Information
Customer/Business Name: |  |  | Account Holder:
Phone Number: |  |  | Email Address:
AES Indiana Account Number (As shown on utility bill): |  |  | Business Rate Class: |  | Electric Meter Number:
Installation Street Address: |  |  | City |  | State | Zip Code
Building Type:
Heating Type: |  |  | Cooling Type:
Mailing Address for Incentive Check
Payee Legal Name (as shown on income tax return): |  |  | Payee Business Name (if different than payee legal name):
Payee Legal Address: |  |  | City |  | State | Zip Code
Payee Contact Name: |  |  | Payee Phone: |  | Payee Email:
Payee Federal Tax Classification (choose from list):
Payee Taxpayer Identification Number (TIN) (Complete ONE only. Must match payee legal name above)
FEIN #: | (XX-XXXXXXX) |  | OR SSN: | (XX-XX-XXXX)
Installing Trade Ally Information
Business Name: |  |  | Contact Name:
Phone Number: |  |  | Email Address:
Address: |  |  | City |  | State | Zip Code
Sign Application
I hereby certify that: 1. The information contained in this final application is accurate and complete. 2. All rules of this incentive application have been followed. 3. I have read and understood the terms and conditions of this document. I agree to verification of equipment installation which may include a site inspection by a program or utility representative. I understand that I am not allowed to receive more than one incentive from this program on any piece of equipment. I hereby agree to indemnify, hold harmless, and release the utility from any actions or claims in regard to the installation, operation, or disposal of equipment (and related materials) covered herein, including liability from any incidental or consequential damages.
Signature |  | Print Name |  |  | Date
If Trade Ally is receiving the incentive payment, Trade Ally signature is required below.
Signature |  | Print Name |  |  | Date
Program Rules
In order to qualify for a leak repair incentive, the following must occur:
1. Customer must have an ultrasonic leak audit performed by a qualified contractor.
2. Leak audit data must be entered into this workbook.
3. Leak repair cost (material and labor) must be entered for each leak repaired. Note that
internal labor does not count towards the project cost.
4. Customer must submit this workbook and invoices for both the audit and the leak
repairs. A W-9 for payee must also be submitted.
5. Incentives are earned at $0.08 per kWh saved.
6. Incentives will not exceed 100% of the total cost of leak audit, materials to repair, and
external labor.
7. Incentives are capped at $1,000,000 per customer per calendar year.

## Inputs and Calc
Compressed Air Leak Repair Savings | [9 empty] | Comp 1 (VFD, trim)
Compressor Info | Compressor 1 | Compressor 2 | Compressor 3 | Compressor 4 | Compressor 5 | Identified Leak Info |  |  | Legend
Make | [5 empty] | Number of identified leaks | 0 |  | Inputs
Model | [5 empty] | Total identified leak CFM | 0 |  | Calcs
Compressor Type
Size (HP) | [5 empty] | Repaired Leak Info
Rated Capacity (cfm) | [5 empty] | Number of repaired leaks | 0
Control Type | [5 empty] | Total repaired leak CFM (capped at 67% of Total System Capacity) | 0
Sequence Number | 1 | 2 | 3 | 4 | 5
Backup Unit (Y/N) | [5 empty] | System Info
Optional Fields - Leave blank if unknown | [5 empty] | Operating Hours
Full Load Power (kW) | [5 empty] | Staging/Sequencing Type |  | system hours, not facility hours
Zero Flow Power (kW) | [5 empty] | Total Storage Capacity (in gallons; optional) |  | Gal /CFM
Compressor effy (kW/cfm) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Savings Method | IL TRM
Compressor effy source | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Project Info
Identified calcs | [5 empty] | Shifts
Compressor cfm reduction | #N/A | #N/A | #N/A | #N/A | #N/A | Proposal cost
Compressor CFM % savings | [5 empty] | Invoice cost
Compressor kW savings | #N/A | #N/A | #N/A | #N/A | #N/A | Utility Rate ($/kWh) | 0.08
Compressor kWh savings | #N/A | #N/A | #N/A | #N/A | #N/A
System Calcs
Repaired calcs | [5 empty] | Total HP (non back-up) | 0
Compressor cfm reduction | #N/A | #N/A | #N/A | #N/A | #N/A | Total Capacity (cfm) | 0
Compressor CFM % savings | [5 empty] | # compressors | 0
Compressor kW savings | #N/A | #N/A | #N/A | #N/A | #N/A | # compressors with leak svgs | 0
Compressor kWh savings | #N/A | #N/A | #N/A | #N/A | #N/A
Project Summary | Identified | Repaired
Demand Savings (kW) | 0 | 0
Energy Savings (kWh) | 0 | 0
Cost Savings (annual) | 0 | 0
Project Cost | 0 | 0
Payback (yr) | #DIV/0! | #DIV/0!
Benchmarks | Identified | Repaired | Notes
# Leaks | 0 | 0
Leak volume (cfm) | 0 | 0
Repair % (by vol) |  | #DIV/0! | >50% good. Ideally >85%
Leak % (cfm) | #DIV/0! | #DIV/0! | DOE suggests 20-30% for a typical system, large systems are commonly 40-50%, and can be as high as 80%. https://www.airbestpractices.com/system-assessments/leaks/protect-profits-compressed-air-leakage-best-practices
cfm/leak | #DIV/0! | #DIV/0! | AirBestPractices suggests 3cfm/leak for a tight system, 4cfm/leak for a typical system, and 5cfm/leak for a poorly maintained system. https://www.airbestpractices.com/system-assessments/leaks/are-compressed-air-leaks-worth-fixing
Project Cost | 0 | 0
IL TRM Deemed Cost | 0 | 0 | Per IL TRM. If custom calc is used, only use full project cost
TA Cost Ratio | #DIV/0! | #DIV/0! | Good <1, High 1-2, Very High >2
fee($)/leak | #DIV/0! | #DIV/0! | Good <$400/leak, High $400-600/leak, Very High >$600/leak (engineering judgement)
fee($)/cfm | #DIV/0! | #DIV/0! | Good <$60/cfm, High $60-150/cfm, Very High >$150/cfm (engineering judgement)
fee($)/HP | #DIV/0! | #DIV/0! | Good <$11/HP, High $11-20/HP, Very High >$20/HP (engineering judgement)
fee($)/kWh | #DIV/0! | #DIV/0! | Good <$0.05/kWh, High $0.05-$0.17/kWh, Very High >$0.17/kWh (engineering judgement)

## Leak List
[16 empty] | TA CFM | IL TRM CFM | Leaks
| Survey | [5 empty] | 0 | 0 | Repair |  | TA Reported CFM |  | IL TRM v14 CFM |  | Total Leaks | 0 | 0 | 0
Leak # | Group Name | Machine or Post Number | Leak Description | Pressure at Leak (psig) | Decibel Reading (dB) | Measured Leak VolumeA (CFM) | Leak SizeB (CFM) | IL TRM Leak Size (CFM) - Trendline | Leak Repaired (Y/N) | Temporary Connection | Adjusted Identified CFM | Adjusted Repaired CFM | Adjusted Identified CFM | Adjusted Repaired CFM | Repaired Leaks | 0 | 0 | 0
1 | [10 empty] | 0 | 0 |  | 0
2 | [10 empty] | 0 | 0 |  | 0
3 | [10 empty] | 0 | 0 |  | 0
4 | [10 empty] | 0 | 0 |  | 0
5 | [10 empty] | 0 | 0 |  | 0
6 | [10 empty] | 0 | 0 |  | 0
7 | [10 empty] | 0 | 0 |  | 0
8 | [10 empty] | 0 | 0 |  | 0
9 | [10 empty] | 0 | 0 |  | 0
10 | [10 empty] | 0 | 0 |  | 0
11 | [10 empty] | 0 | 0 |  | 0
12 | [10 empty] | 0 | 0 |  | 0
13 | [10 empty] | 0 | 0 |  | 0
14 | [10 empty] | 0 | 0 |  | 0
15 | [10 empty] | 0 | 0 |  | 0
16 | [10 empty] | 0 | 0 |  | 0
17 | [10 empty] | 0 | 0 |  | 0
18 | [10 empty] | 0 | 0 |  | 0
19 | [10 empty] | 0 | 0 |  | 0
20 | [10 empty] | 0 | 0 |  | 0
21 | [10 empty] | 0 | 0 |  | 0
22 | [10 empty] | 0 | 0 |  | 0
23 | [10 empty] | 0 | 0 |  | 0
24 | [10 empty] | 0 | 0 |  | 0
25 | [10 empty] | 0 | 0 |  | 0
26 | [10 empty] | 0 | 0 |  | 0
27 | [10 empty] | 0 | 0 |  | 0
28 | [10 empty] | 0 | 0 |  | 0
29 | [10 empty] | 0 | 0 |  | 0
30 | [10 empty] | 0 | 0 |  | 0
31 | [10 empty] | 0 | 0 |  | 0
32 | [10 empty] | 0 | 0 |  | 0
33 | [10 empty] | 0 | 0 |  | 0
34 | [10 empty] | 0 | 0 |  | 0
35 | [10 empty] | 0 | 0 |  | 0
36 | [10 empty] | 0 | 0 |  | 0
37 | [10 empty] | 0 | 0 |  | 0
38 | [10 empty] | 0 | 0 |  | 0
39 | [10 empty] | 0 | 0 |  | 0
40 | [10 empty] | 0 | 0 |  | 0
41 | [10 empty] | 0 | 0 |  | 0
42 | [10 empty] | 0 | 0 |  | 0
43 | [10 empty] | 0 | 0 |  | 0
44 | [10 empty] | 0 | 0 |  | 0
45 | [10 empty] | 0 | 0 |  | 0
46 | [10 empty] | 0 | 0 |  | 0
47 | [10 empty] | 0 | 0 |  | 0
48 | [10 empty] | 0 | 0 |  | 0
49 | [10 empty] | 0 | 0 |  | 0
50 | [10 empty] | 0 | 0 |  | 0
51 | [10 empty] | 0 | 0 |  | 0
52 | [10 empty] | 0 | 0 |  | 0
53 | [10 empty] | 0 | 0 |  | 0
54 | [10 empty] | 0 | 0 |  | 0
55 | [10 empty] | 0 | 0 |  | 0
56 | [10 empty] | 0 | 0 |  | 0
57 | [10 empty] | 0 | 0 |  | 0
58 | [10 empty] | 0 | 0 |  | 0
59 | [10 empty] | 0 | 0 |  | 0
60 | [10 empty] | 0 | 0 |  | 0
61 | [10 empty] | 0 | 0 |  | 0
62 | [10 empty] | 0 | 0 |  | 0
63 | [10 empty] | 0 | 0 |  | 0
64 | [10 empty] | 0 | 0 |  | 0
65 | [10 empty] | 0 | 0 |  | 0
66 | [10 empty] | 0 | 0 |  | 0
67 | [10 empty] | 0 | 0 |  | 0
68 | [10 empty] | 0 | 0 |  | 0
69 | [10 empty] | 0 | 0 |  | 0
70 | [10 empty] | 0 | 0 |  | 0
71 | [10 empty] | 0 | 0 |  | 0
72 | [10 empty] | 0 | 0 |  | 0
73 | [10 empty] | 0 | 0 |  | 0
74 | [10 empty] | 0 | 0 |  | 0
75 | [10 empty] | 0 | 0 |  | 0
76 | [10 empty] | 0 | 0 |  | 0
77 | [10 empty] | 0 | 0 |  | 0
78 | [10 empty] | 0 | 0 |  | 0
79 | [10 empty] | 0 | 0 |  | 0
80 | [10 empty] | 0 | 0 |  | 0
81 | [10 empty] | 0 | 0 |  | 0
82 | [10 empty] | 0 | 0 |  | 0
83 | [10 empty] | 0 | 0 |  | 0
84 | [10 empty] | 0 | 0 |  | 0
85 | [10 empty] | 0 | 0 |  | 0
86 | [10 empty] | 0 | 0 |  | 0
87 | [10 empty] | 0 | 0 |  | 0
88 | [10 empty] | 0 | 0 |  | 0
89 | [10 empty] | 0 | 0 |  | 0
90 | [10 empty] | 0 | 0 |  | 0
91 | [10 empty] | 0 | 0 |  | 0
92 | [10 empty] | 0 | 0 |  | 0
93 | [10 empty] | 0 | 0 |  | 0
94 | [10 empty] | 0 | 0 |  | 0
95 | [10 empty] | 0 | 0 |  | 0
96 | [10 empty] | 0 | 0 |  | 0
97 | [10 empty] | 0 | 0 |  | 0
98 | [10 empty] | 0 | 0 |  | 0
99 | [10 empty] | 0 | 0 |  | 0
100 | [10 empty] | 0 | 0 |  | 0
101 | [10 empty] | 0 | 0 |  | 0
102 | [10 empty] | 0 | 0 |  | 0
103 | [10 empty] | 0 | 0 |  | 0
104 | [10 empty] | 0 | 0 |  | 0
105 | [10 empty] | 0 | 0 |  | 0
106 | [10 empty] | 0 | 0 |  | 0
107 | [10 empty] | 0 | 0 |  | 0
108 | [10 empty] | 0 | 0 |  | 0
109 | [10 empty] | 0 | 0 |  | 0
110 | [10 empty] | 0 | 0 |  | 0
111 | [10 empty] | 0 | 0 |  | 0
112 | [10 empty] | 0 | 0 |  | 0
113 | [10 empty] | 0 | 0 |  | 0
114 | [10 empty] | 0 | 0 |  | 0
115 | [10 empty] | 0 | 0 |  | 0
116 | [10 empty] | 0 | 0 |  | 0
117 | [10 empty] | 0 | 0 |  | 0
118 | [10 empty] | 0 | 0 |  | 0
119 | [10 empty] | 0 | 0 |  | 0
120 | [10 empty] | 0 | 0 |  | 0
121 | [10 empty] | 0 | 0 |  | 0
122 | [10 empty] | 0 | 0 |  | 0
123 | [10 empty] | 0 | 0 |  | 0
124 | [10 empty] | 0 | 0 |  | 0
125 | [10 empty] | 0 | 0 |  | 0
126 | [10 empty] | 0 | 0 |  | 0
127 | [10 empty] | 0 | 0 |  | 0
128 | [10 empty] | 0 | 0 |  | 0
129 | [10 empty] | 0 | 0 |  | 0
130 | [10 empty] | 0 | 0 |  | 0
131 | [10 empty] | 0 | 0 |  | 0
132 | [10 empty] | 0 | 0 |  | 0
133 | [10 empty] | 0 | 0 |  | 0
134 | [10 empty] | 0 | 0 |  | 0
135 | [10 empty] | 0 | 0 |  | 0
136 | [10 empty] | 0 | 0 |  | 0
137 | [10 empty] | 0 | 0 |  | 0
138 | [10 empty] | 0 | 0 |  | 0
139 | [10 empty] | 0 | 0 |  | 0
140 | [10 empty] | 0 | 0 |  | 0
13 | [10 empty] | 0 | 0 |  | 0
142 | [10 empty] | 0 | 0 |  | 0
143 | [10 empty] | 0 | 0 |  | 0
144 | [10 empty] | 0 | 0 |  | 0
145 | [10 empty] | 0 | 0 |  | 0
146 | [10 empty] | 0 | 0 |  | 0
147 | [10 empty] | 0 | 0 |  | 0
148 | [10 empty] | 0 | 0 |  | 0
149 | [10 empty] | 0 | 0 |  | 0
150 | [10 empty] | 0 | 0 |  | 0
151 | [10 empty] | 0 | 0 |  | 0
152 | [10 empty] | 0 | 0 |  | 0
153 | [10 empty] | 0 | 0 |  | 0
154 | [10 empty] | 0 | 0 |  | 0
155 | [10 empty] | 0 | 0 |  | 0
156 | [10 empty] | 0 | 0 |  | 0
157 | [10 empty] | 0 | 0 |  | 0
158 | [10 empty] | 0 | 0 |  | 0
159 | [10 empty] | 0 | 0 |  | 0
160 | [10 empty] | 0 | 0 |  | 0
161 | [10 empty] | 0 | 0 |  | 0
162 | [10 empty] | 0 | 0 |  | 0
163 | [10 empty] | 0 | 0 |  | 0
164 | [10 empty] | 0 | 0 |  | 0
165 | [10 empty] | 0 | 0 |  | 0
166 | [10 empty] | 0 | 0 |  | 0
167 | [10 empty] | 0 | 0 |  | 0
168 | [10 empty] | 0 | 0 |  | 0
169 | [10 empty] | 0 | 0 |  | 0
170 | [10 empty] | 0 | 0 |  | 0
171 | [10 empty] | 0 | 0 |  | 0
172 | [10 empty] | 0 | 0 |  | 0
173 | [10 empty] | 0 | 0 |  | 0
174 | [10 empty] | 0 | 0 |  | 0
175 | [10 empty] | 0 | 0 |  | 0
176 | [10 empty] | 0 | 0 |  | 0
177 | [10 empty] | 0 | 0 |  | 0
178 | [10 empty] | 0 | 0 |  | 0
179 | [10 empty] | 0 | 0 |  | 0
180 | [10 empty] | 0 | 0 |  | 0
181 | [10 empty] | 0 | 0 |  | 0
182 | [10 empty] | 0 | 0 |  | 0
183 | [10 empty] | 0 | 0 |  | 0
184 | [10 empty] | 0 | 0 |  | 0
185 | [10 empty] | 0 | 0 |  | 0
186 | [10 empty] | 0 | 0 |  | 0
187 | [10 empty] | 0 | 0 |  | 0
188 | [10 empty] | 0 | 0 |  | 0
189 | [10 empty] | 0 | 0 |  | 0
190 | [10 empty] | 0 | 0 |  | 0
191 | [10 empty] | 0 | 0 |  | 0
192 | [10 empty] | 0 | 0 |  | 0
193 | [10 empty] | 0 | 0 |  | 0
194 | [10 empty] | 0 | 0 |  | 0
195 | [10 empty] | 0 | 0 |  | 0
196 | [10 empty] | 0 | 0 |  | 0
197 | [10 empty] | 0 | 0 |  | 0
198 | [10 empty] | 0 | 0 |  | 0
199 | [10 empty] | 0 | 0 |  | 0
200 | [10 empty] | 0 | 0 |  | 0
201 | [10 empty] | 0 | 0 |  | 0
202 | [10 empty] | 0 | 0 |  | 0
203 | [10 empty] | 0 | 0 |  | 0
204 | [10 empty] | 0 | 0 |  | 0
205 | [10 empty] | 0 | 0 |  | 0
206 | [10 empty] | 0 | 0 |  | 0
207 | [10 empty] | 0 | 0 |  | 0
208 | [10 empty] | 0 | 0 |  | 0
209 | [10 empty] | 0 | 0 |  | 0
210 | [10 empty] | 0 | 0 |  | 0
211 | [10 empty] | 0 | 0 |  | 0
212 | [10 empty] | 0 | 0 |  | 0
213 | [10 empty] | 0 | 0 |  | 0
214 | [10 empty] | 0 | 0 |  | 0
215 | [10 empty] | 0 | 0 |  | 0
216 | [10 empty] | 0 | 0 |  | 0
217 | [10 empty] | 0 | 0 |  | 0
218 | [10 empty] | 0 | 0 |  | 0
219 | [10 empty] | 0 | 0 |  | 0
220 | [10 empty] | 0 | 0 |  | 0
221 | [10 empty] | 0 | 0 |  | 0
222 | [10 empty] | 0 | 0 |  | 0
223 | [10 empty] | 0 | 0 |  | 0
224 | [10 empty] | 0 | 0 |  | 0
225 | [10 empty] | 0 | 0 |  | 0
226 | [10 empty] | 0 | 0 |  | 0
227 | [10 empty] | 0 | 0 |  | 0
228 | [10 empty] | 0 | 0 |  | 0
229 | [10 empty] | 0 | 0 |  | 0
230 | [10 empty] | 0 | 0 |  | 0
231 | [10 empty] | 0 | 0 |  | 0
232 | [10 empty] | 0 | 0 |  | 0
233 | [10 empty] | 0 | 0 |  | 0
234 | [10 empty] | 0 | 0 |  | 0
235 | [10 empty] | 0 | 0 |  | 0
236 | [10 empty] | 0 | 0 |  | 0
237 | [10 empty] | 0 | 0 |  | 0
238 | [10 empty] | 0 | 0 |  | 0
239 | [10 empty] | 0 | 0 |  | 0
240 | [10 empty] | 0 | 0 |  | 0
23 | [10 empty] | 0 | 0 |  | 0
242 | [10 empty] | 0 | 0 |  | 0
243 | [10 empty] | 0 | 0 |  | 0
244 | [10 empty] | 0 | 0 |  | 0
245 | [10 empty] | 0 | 0 |  | 0
246 | [10 empty] | 0 | 0 |  | 0
247 | [10 empty] | 0 | 0 |  | 0
248 | [10 empty] | 0 | 0 |  | 0
249 | [10 empty] | 0 | 0 |  | 0
250 | [10 empty] | 0 | 0 |  | 0
251 | [10 empty] | 0 | 0 |  | 0
252 | [10 empty] | 0 | 0 |  | 0
253 | [10 empty] | 0 | 0 |  | 0
254 | [10 empty] | 0 | 0 |  | 0
255 | [10 empty] | 0 | 0 |  | 0
256 | [10 empty] | 0 | 0 |  | 0
257 | [10 empty] | 0 | 0 |  | 0
258 | [10 empty] | 0 | 0 |  | 0
259 | [10 empty] | 0 | 0 |  | 0
260 | [10 empty] | 0 | 0 |  | 0
261 | [10 empty] | 0 | 0 |  | 0
262 | [10 empty] | 0 | 0 |  | 0
263 | [10 empty] | 0 | 0 |  | 0
264 | [10 empty] | 0 | 0 |  | 0
265 | [10 empty] | 0 | 0 |  | 0
266 | [10 empty] | 0 | 0 |  | 0
267 | [10 empty] | 0 | 0 |  | 0
268 | [10 empty] | 0 | 0 |  | 0
269 | [10 empty] | 0 | 0 |  | 0
270 | [10 empty] | 0 | 0 |  | 0
271 | [10 empty] | 0 | 0 |  | 0
272 | [10 empty] | 0 | 0 |  | 0
273 | [10 empty] | 0 | 0 |  | 0
274 | [10 empty] | 0 | 0 |  | 0
275 | [10 empty] | 0 | 0 |  | 0
276 | [10 empty] | 0 | 0 |  | 0
277 | [10 empty] | 0 | 0 |  | 0
278 | [10 empty] | 0 | 0 |  | 0
279 | [10 empty] | 0 | 0 |  | 0
280 | [10 empty] | 0 | 0 |  | 0
281 | [10 empty] | 0 | 0 |  | 0
282 | [10 empty] | 0 | 0 |  | 0
283 | [10 empty] | 0 | 0 |  | 0
284 | [10 empty] | 0 | 0 |  | 0
285 | [10 empty] | 0 | 0 |  | 0
286 | [10 empty] | 0 | 0 |  | 0
287 | [10 empty] | 0 | 0 |  | 0
288 | [10 empty] | 0 | 0 |  | 0
289 | [10 empty] | 0 | 0 |  | 0
290 | [10 empty] | 0 | 0 |  | 0
291 | [10 empty] | 0 | 0 |  | 0
292 | [10 empty] | 0 | 0 |  | 0
293 | [10 empty] | 0 | 0 |  | 0
294 | [10 empty] | 0 | 0 |  | 0
295 | [10 empty] | 0 | 0 |  | 0
296 | [10 empty] | 0 | 0 |  | 0
297 | [10 empty] | 0 | 0 |  | 0
298 | [10 empty] | 0 | 0 |  | 0
299 | [10 empty] | 0 | 0 |  | 0
300 | [10 empty] | 0 | 0 |  | 0
Note on L3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Discount leaks by 50% that are not in use or connected the entire time to account for reduced operating hours.
Note on N3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Discount leaks by 50% that are not in use or connected the entire time to account for reduced operating hours.

## Loading (hidden)
Compressor table - sorted by sequence number
Compressor Info | Compressor 1 | Compressor 2 | Compressor 3 | Compressor 4 | Compressor 5
Make | 0 | 0 | 0 | 0 | 0
Model | 0 | 0 | 0 | 0 | 0
Compressor Type | 0 | 0 | 0 | 0 | 0
Size (HP) | 0 | 0 | 0 | 0 | 0
Rated Capacity (cfm) | 0 | 0 | 0 | 0 | 0
Control Type | 0 | 0 | 0 | 0 | 0
Backup Unit (Y/N) | 0 | 0 | 0 | 0 | 0
Sequence Number | 1 | 2 | 3 | 4 | 5
Leak Info
Total identified leak CFM | 0
Total repaired leak CFM | 0
System Info
Staging/Sequencing Type | 0
Calc Info
# of compressors affected (identification) | 1
# of compressors affected (repaired) | 1
# of compressors in operation | 0
Notes
Identified cfm savings by compressor and system control type | [6 empty] | Simple | Assumes all savings on trim compressor. Selected by default if savings are less than trim compressor capacity
CFM savings by control type | Compressor 1 | Compressor 2 | Compressor 3 | Compressor 4 | Compressor 5 | Total
Simple | 0 | 0 | 0 | 0 | 0 | 0 | Tandem | Assumes savings are split between all operating compressors proportinally to their capacity
Tandem | 0 | 0 | 0 | 0 | 0 | 0
Cascading | 0 | 0 | 0 | 0 | 0 | 0 | Cascading | Assumes cascading pressure setpoints such that sequence 1 is last to load, then 2, then 3, etc. Savings reduce sequence 1 cfm to zero, then start reducing the next in line. Assumes sequence 1 machine to be 80% loaded.
Trim/Base | 0 | 0 | 0 | 0 | 0 | 0
Project identified savings by comp (cfm) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[7 empty] | Trim/Base | Assumes sequence 1 machine is always trim compressor. If savings exceed trim compressor, base machine is reduced from 100% load to 0%, and remainder of savings is realized on trim machine.
Repaired cfm savings by compressor and system control type
CFM savings by control type | Compressor 1 | Compressor 2 | Compressor 3 | Compressor 4 | Compressor 5 | Total
Simple | 0 | 0 | 0 | 0 | 0 | 0
Tandem | 0 | 0 | 0 | 0 | 0 | 0
Cascading | 0 | 0 | 0 | 0 | 0 | 0
Trim/Base | 0 | 0 | 0 | 0 | 0 | 0
Project repaired savings by comp (cfm) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## IL TRM calc (hidden)
[7 empty] | Data from NREL | https://docs.nlr.gov/docs/fy17osti/68577.pdf
Compressor table - sorted by sequence number | [6 empty] | Calculator-standardized Compressor Control Types
Compressor Info | Compressor 1 | Compressor 2 | Compressor 3 | Compressor 4 | Compressor 5 |  | Type | Savings Factor | Source | Shift | Coincidence Factor
Make | 0 | 0 | 0 | 0 | 0 |  | On/Off Control | 1 | NREL | Single shift (8/5) | 0.59
Model | 0 | 0 | 0 | 0 | 0 |  | Reciprocating - Load/unload | 0.74 | NREL | 2-shift (16/5) | 0.95
Compressor Type | 0 | 0 | 0 | 0 | 0 |  | Screw - Load/Unload oil free | 0.73 | NREL | 3-shift (24/5) | 0.95
Size (HP) | 0 | 0 | 0 | 0 | 0 |  | Screw - Load/Unload 1 gal/CFM | 0.43 | NREL | 4-shift (24/7) | 0.95
Rated Capacity (cfm) | 0 | 0 | 0 | 0 | 0 |  | Screw - Load/Unload 3 gal/CFM | 0.53 | NREL | Unknown / Weighted average | 0.89
Full Load Power (kW) | 0 | 0 | 0 | 0 | 0 |  | Screw - Load/Unload 5 gal/CFM | 0.63 | NREL
Zero Flow Power (kW) | 0 | 0 | 0 | 0 | 0 |  | Screw - Load/Unload 10 gal/CFM | 0.73 | NREL
Control Type | 0 | 0 | 0 | 0 | 0 |  | Inlet modulation | 0.31 | IL TRM v14 | Digital Reading | System Air Pressure
Sequence Number | 1 | 2 | 3 | 4 | 5 |  | Variable displacement | 0.69 | IL TRM v14 |  | 100 PSIG | 75 PSIG | 50 PSIG | 25 PSIG | 10 PSIG
[7 empty] | VSD | 0.85 | IL TRM v14 |  | Estimated CFMleaks
Operating Hours | 0 | 0 | 0 | 0 | 0 |  | Centrifugal IGV | 0.3 | IL TRM v14 | 10 dB | 0.5 | 0.3 | 0.2 | 0.1 | 0.05
Compressor kW/cfm (IL TRM table) | [6 empty] | Centrifugal IBV | 0.3 | IL TRM v14 | 20 dB | 0.8 | 0.9 | 0.5 | 0.3 | 0.15
Compressor kW/cfm (Actual) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | Unknown | 0.3 | IL TRM v14 | 30 dB | 1.4 | 1.1 | 0.8 | 0.5 | 0.4
Compressor kW/cfm (Selected) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 40 dB | 1.7 | 1.4 | 1.1 | 0.8 | 0.5
Compressor kW/cfm source | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 50 dB | 2 | 2.8 | 2.2 | 2 | 1.9
Control Factor | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | 60 dB | 3.6 | 3 | 2.8 | 2.8 | 2.3
Savings Factor (kW/cfm) | #N/A | #N/A | #N/A | #N/A | #N/A |  | Type | Caircomp kW/CFM |  | 70 dB | 5.2 | 4.9 | 3.9 | 3.4 | 3
CF (kW/kWh) | #N/A | #N/A | #N/A | #N/A | #N/A |  | Single-acting Reciprocating Air Compressor | 0.23 |  | 80 dB | 7.7 | 6.8 | 5.6 | 5.1 | 3.6
[7 empty] | Double-acting Reciprocating Air Compressor | 0.155 |  | 90 dB | 8.4 | 7.7 | 7.1 | 6.8 | 5.3
Identified Savings | [6 empty] | Lubricant-injected Rotary Screw Compressor | 0.185 |  | 100 dB | 10.6 | 10 | 9.6 | 7.3 | 6
CFM savings | #N/A | #N/A | #N/A | #N/A | #N/A | Calc'd from identified volume | Lubricant-free Rotary Screw Compressor | 0.2
Demand Savings (kW) | #N/A | #N/A | #N/A | #N/A | #N/A |  | Centrifugal Compressor | 0.18 |  | Reading
Energy Savings (kWh) | #N/A | #N/A | #N/A | #N/A | #N/A |  | Average/unknown | 0.19 |  | Pressure (psig) | Leak Orifice Diameter (inches)
[11 empty] | 1/64 | 1/32 | 1/16 | 1/8 | 1/4 | 3/8
Total Demand Svgs (kW) | 0 | [8 empty] | 70 | 0.3 | 1.2 | 4.8 | 19.2 | 76.7 | 173
Total Energy Svgs (kWh) | 0 | [8 empty] | 80 | 0.33 | 1.3 | 5.4 | 21.4 | 85.7 | 193
Deemed Cost | 0 | [8 empty] | 90 | 0.37 | 1.5 | 5.9 | 23.8 | 94.8 | 213
[10 empty] | 100 | 0.41 | 1.6 | 6.5 | 26 | 104 | 234
Repaired Savings | [9 empty] | 125 | 0.49 | 2 | 7.9 | 31.6 | 126 | 284
CFM savings | #N/A | #N/A | #N/A | #N/A | #N/A | Calc'd from repaired volume
Demand Savings (kW) | #N/A | #N/A | #N/A | #N/A | #N/A
Energy Savings (kWh) | #N/A | #N/A | #N/A | #N/A | #N/A
Total Demand Svgs (kW) | 0
Total Energy Svgs (kWh) | 0
Deemed Cost | 0

## IL TRM v14 Table (hidden)
Digital Reading |  | System Air Pressure |  |  |  |  | Interpolation
|  | 100 PSIG | 75 PSIG | 50 PSIG | 25 PSIG | 10 PSIG |  | CFM at the below PSIG
|  | Estimated CFMleaks |  |  |  |  | DB | 100 | 75 | 50 | 25 | 10
| DB | 100 | 75 | 50 | 25 | 10 | 0 | 0 | 0 | 0 | 0 | 0
10 dB | 10 | 0.5 | 0.3 | 0.2 | 0.1 | 0.05 | 1 | 0.05 | 0.03 | 0.02 | 0.01 | 0.005
20 dB | 20 | 0.8 | 0.9 | 0.5 | 0.3 | 0.15 | 2 | 0.1 | 0.06 | 0.04 | 0.02 | 0.01
30 dB | 30 | 1.4 | 1.1 | 0.8 | 0.5 | 0.4 | 3 | 0.15 | 0.09 | 0.06 | 0.03 | 0.015
40 dB | 40 | 1.7 | 1.4 | 1.1 | 0.8 | 0.5 | 4 | 0.2 | 0.12 | 0.08 | 0.04 | 0.02
50 dB | 50 | 2 | 2.8 | 2.2 | 2 | 1.9 | 5 | 0.25 | 0.15 | 0.1 | 0.05 | 0.025
60 dB | 60 | 3.6 | 3 | 2.8 | 2.8 | 2.3 | 6 | 0.3 | 0.18 | 0.12 | 0.06 | 0.03
70 dB | 70 | 5.2 | 4.9 | 3.9 | 3.4 | 3 | 7 | 0.35 | 0.21 | 0.14 | 0.07 | 0.035
80 dB | 80 | 7.7 | 6.8 | 5.6 | 5.1 | 3.6 | 8 | 0.4 | 0.24 | 0.16 | 0.08 | 0.04
90 dB | 90 | 8.4 | 7.7 | 7.1 | 6.8 | 5.3 | 9 | 0.45 | 0.27 | 0.18 | 0.09 | 0.045
100 dB | 100 | 10.6 | 10 | 9.6 | 7.3 | 6 | 10 | 0.5 | 0.3 | 0.2 | 0.1 | 0.05
|  | 100 PSIG | 75 PSIG | 50 PSIG | 25 PSIG | 10 PSIG | 11 | 0.53 | 0.36 | 0.23 | 0.12 | 0.06
x^2 Coeff |  | 0.001242 | 0.001098 | 0.001235 | 0.000803 | 0.000644 | 12 | 0.56 | 0.42 | 0.26 | 0.14 | 0.07
x Coeff |  | -0.022909 | -0.015318 | -0.036561 | -0.002333 | -0.002712 | 13 | 0.59 | 0.48 | 0.29 | 0.16 | 0.08
Intercept |  | 0.66667 | 0.50333 | 0.63667 | -0.053333 | 0 | 14 | 0.62 | 0.54 | 0.32 | 0.18 | 0.09
[7 empty] | 15 | 0.65 | 0.6 | 0.35 | 0.2 | 0.1
Trendline | 10 | 0.56178 | 0.45995 | 0.39456 | 0.003637 | 0.03728 | 16 | 0.68 | 0.66 | 0.38 | 0.22 | 0.11
Trendline | 20 | 0.70529 | 0.63617 | 0.39945 | 0.22121 | 0.20336 | 17 | 0.71 | 0.72 | 0.41 | 0.24 | 0.12
Trendline | 30 | 1.0972 | 1.032 | 0.65134 | 0.59938 | 0.49824 | 18 | 0.74 | 0.78 | 0.44 | 0.26 | 0.13
Trendline | 40 | 1.7375 | 1.6474 | 1.1502 | 1.1381 | 0.92192 | 19 | 0.77 | 0.84 | 0.47 | 0.28 | 0.14
Trendline | 50 | 2.6262 | 2.4824 | 1.8961 | 1.8375 | 1.4744 | 20 | 0.8 | 0.9 | 0.5 | 0.3 | 0.15
Trendline | 60 | 3.7633 | 3.5371 | 2.889 | 2.6975 | 2.1557 | 21 | 0.86 | 0.92 | 0.53 | 0.32 | 0.175
Trendline | 70 | 5.1488 | 4.8113 | 4.1289 | 3.7181 | 2.9658 | 22 | 0.92 | 0.94 | 0.56 | 0.34 | 0.2
Trendline | 80 | 6.7827 | 6.3051 | 5.6158 | 4.8992 | 3.9046 | 23 | 0.98 | 0.96 | 0.59 | 0.36 | 0.225
Trendline | 90 | 8.6651 | 8.0185 | 7.3497 | 6.241 | 4.9723 | 24 | 1.04 | 0.98 | 0.62 | 0.38 | 0.25
Trendline | 100 | 10.7958 | 9.9515 | 9.3306 | 7.7434 | 6.1688 | 25 | 1.1 | 1 | 0.65 | 0.4 | 0.275
[7 empty] | 26 | 1.16 | 1.02 | 0.68 | 0.42 | 0.3
% Difference | 10 | 12.36% | 53.32% | 97.28% | -96.36% | -25.44% | 27 | 1.22 | 1.04 | 0.71 | 0.44 | 0.325
% Difference | 20 | -11.84% | -29.31% | -20.11% | -26.26% | 35.57% | 28 | 1.28 | 1.06 | 0.74 | 0.46 | 0.35
% Difference | 30 | -21.63% | -6.182% | -18.58% | 19.88% | 24.56% | 29 | 1.34 | 1.08 | 0.77 | 0.48 | 0.375
% Difference | 40 | 2.206% | 17.67% | 4.566% | 42.27% | 84.38% | 30 | 1.4 | 1.1 | 0.8 | 0.5 | 0.4
% Difference | 50 | 31.31% | -11.34% | -13.81% | -8.124% | -22.4% | 31 | 1.43 | 1.13 | 0.83 | 0.53 | 0.41
% Difference | 60 | 4.537% | 17.9% | 3.179% | -3.661% | -6.275% | 32 | 1.46 | 1.16 | 0.86 | 0.56 | 0.42
% Difference | 70 | -0.9839% | -1.811% | 5.869% | 9.355% | -1.141% | 33 | 1.49 | 1.19 | 0.89 | 0.59 | 0.43
% Difference | 80 | -11.91% | -7.278% | 0.2819% | -3.937% | 8.462% | 34 | 1.52 | 1.22 | 0.92 | 0.62 | 0.44
% Difference | 90 | 3.155% | 4.137% | 3.517% | -8.221% | -6.183% | 35 | 1.55 | 1.25 | 0.95 | 0.65 | 0.45
% Difference | 100 | 1.847% | -0.4847% | -2.807% | 6.074% | 2.813% | 36 | 1.58 | 1.28 | 0.98 | 0.68 | 0.46
[7 empty] | 37 | 1.61 | 1.31 | 1.01 | 0.71 | 0.47
[7 empty] | 38 | 1.64 | 1.34 | 1.04 | 0.74 | 0.48
[7 empty] | 39 | 1.67 | 1.37 | 1.07 | 0.77 | 0.49
[7 empty] | 40 | 1.7 | 1.4 | 1.1 | 0.8 | 0.5
[7 empty] | 41 | 1.73 | 1.54 | 1.21 | 0.92 | 0.64
[7 empty] | 42 | 1.76 | 1.68 | 1.32 | 1.04 | 0.78
[7 empty] | 43 | 1.79 | 1.82 | 1.43 | 1.16 | 0.92
[7 empty] | 44 | 1.82 | 1.96 | 1.54 | 1.28 | 1.06
[7 empty] | 45 | 1.85 | 2.1 | 1.65 | 1.4 | 1.2
[7 empty] | 46 | 1.88 | 2.24 | 1.76 | 1.52 | 1.34
[7 empty] | 47 | 1.91 | 2.38 | 1.87 | 1.64 | 1.48
[7 empty] | 48 | 1.94 | 2.52 | 1.98 | 1.76 | 1.62
[7 empty] | 49 | 1.97 | 2.66 | 2.09 | 1.88 | 1.76
[7 empty] | 50 | 2 | 2.8 | 2.2 | 2 | 1.9
[7 empty] | 51 | 2.16 | 2.82 | 2.26 | 2.08 | 1.94
[7 empty] | 52 | 2.32 | 2.84 | 2.32 | 2.16 | 1.98
[7 empty] | 53 | 2.48 | 2.86 | 2.38 | 2.24 | 2.02
[7 empty] | 54 | 2.64 | 2.88 | 2.44 | 2.32 | 2.06
[7 empty] | 55 | 2.8 | 2.9 | 2.5 | 2.4 | 2.1
[7 empty] | 56 | 2.96 | 2.92 | 2.56 | 2.48 | 2.14
[7 empty] | 57 | 3.12 | 2.94 | 2.62 | 2.56 | 2.18
[7 empty] | 58 | 3.28 | 2.96 | 2.68 | 2.64 | 2.22
[7 empty] | 59 | 3.44 | 2.98 | 2.74 | 2.72 | 2.26
[7 empty] | 60 | 3.6 | 3 | 2.8 | 2.8 | 2.3
[7 empty] | 61 | 3.76 | 3.19 | 2.91 | 2.86 | 2.37
[7 empty] | 62 | 3.92 | 3.38 | 3.02 | 2.92 | 2.44
[7 empty] | 63 | 4.08 | 3.57 | 3.13 | 2.98 | 2.51
[7 empty] | 64 | 4.24 | 3.76 | 3.24 | 3.04 | 2.58
[7 empty] | 65 | 4.4 | 3.95 | 3.35 | 3.1 | 2.65
[7 empty] | 66 | 4.56 | 4.14 | 3.46 | 3.16 | 2.72
[7 empty] | 67 | 4.72 | 4.33 | 3.57 | 3.22 | 2.79
[7 empty] | 68 | 4.88 | 4.52 | 3.68 | 3.28 | 2.86
[7 empty] | 69 | 5.04 | 4.71 | 3.79 | 3.34 | 2.93
[7 empty] | 70 | 5.2 | 4.9 | 3.9 | 3.4 | 3
[7 empty] | 71 | 5.45 | 5.09 | 4.07 | 3.57 | 3.06
[7 empty] | 72 | 5.7 | 5.28 | 4.24 | 3.74 | 3.12
[7 empty] | 73 | 5.95 | 5.47 | 4.41 | 3.91 | 3.18
[7 empty] | 74 | 6.2 | 5.66 | 4.58 | 4.08 | 3.24
[7 empty] | 75 | 6.45 | 5.85 | 4.75 | 4.25 | 3.3
[7 empty] | 76 | 6.7 | 6.04 | 4.92 | 4.42 | 3.36
[7 empty] | 77 | 6.95 | 6.23 | 5.09 | 4.59 | 3.42
[7 empty] | 78 | 7.2 | 6.42 | 5.26 | 4.76 | 3.48
[7 empty] | 79 | 7.45 | 6.61 | 5.43 | 4.93 | 3.54
[7 empty] | 80 | 7.7 | 6.8 | 5.6 | 5.1 | 3.6
[7 empty] | 81 | 7.77 | 6.89 | 5.75 | 5.27 | 3.77
[7 empty] | 82 | 7.84 | 6.98 | 5.9 | 5.44 | 3.94
[7 empty] | 83 | 7.91 | 7.07 | 6.05 | 5.61 | 4.11
[7 empty] | 84 | 7.98 | 7.16 | 6.2 | 5.78 | 4.28
[7 empty] | 85 | 8.05 | 7.25 | 6.35 | 5.95 | 4.45
[7 empty] | 86 | 8.12 | 7.34 | 6.5 | 6.12 | 4.62
[7 empty] | 87 | 8.19 | 7.43 | 6.65 | 6.29 | 4.79
[7 empty] | 88 | 8.26 | 7.52 | 6.8 | 6.46 | 4.96
[7 empty] | 89 | 8.33 | 7.61 | 6.95 | 6.63 | 5.13
[7 empty] | 90 | 8.4 | 7.7 | 7.1 | 6.8 | 5.3
[7 empty] | 91 | 8.62 | 7.93 | 7.35 | 6.85 | 5.37
[7 empty] | 92 | 8.84 | 8.16 | 7.6 | 6.9 | 5.44
[7 empty] | 93 | 9.06 | 8.39 | 7.85 | 6.95 | 5.51
[7 empty] | 94 | 9.28 | 8.62 | 8.1 | 7 | 5.58
[7 empty] | 95 | 9.5 | 8.85 | 8.35 | 7.05 | 5.65
[7 empty] | 96 | 9.72 | 9.08 | 8.6 | 7.1 | 5.72
[7 empty] | 97 | 9.94 | 9.31 | 8.85 | 7.15 | 5.79
[7 empty] | 98 | 10.16 | 9.54 | 9.1 | 7.2 | 5.86
[7 empty] | 99 | 10.38 | 9.77 | 9.35 | 7.25 | 5.93
[7 empty] | 100 | 10.6 | 10 | 9.6 | 7.3 | 6
Note on I20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Set intercept to 0 to avoid - CFM at 10 db

## Lookups (hidden)
Compressor Types | Compressor Control Types | System Control Types | Savings Methods
Single-acting Reciprocating Air Compressor | On/Off Control | Simple | IL TRM
Double-acting Reciprocating Air Compressor | Reciprocating - Load/unload | Tandem
Lubricant-injected Rotary Screw Compressor | Screw - Load/Unload oil free | Cascading
Lubricant-free Rotary Screw Compressor | Screw - Load/Unload 1 gal/CFM | Trim/Base
Centrifugal Compressor | Screw - Load/Unload 3 gal/CFM
Average/unknown | Screw - Load/Unload 5 gal/CFM
Screw - Load/Unload 10 gal/CFM
Inlet modulation
Variable displacement
VSD
Centrifugal IGV
Centrifugal IBV

## Version History (hidden)
Version # | Date Updated | Lead Engineer | QC Engineer | Changes Made | Future Changes
5 | 2025-09-01 | Ben Reinhart | Brian A'Hearn | Adapted the CA Leak Repair calculated developed for AEP I&M by ES and CLEAResult to be used for AES IN. Removed all references to MI and other calculation methodologies and updated to the IL TRM v13 methodology only. Added a leak list tab. | Future TRM updates or program changes
6 | 2026-03-02 | Ben Reinhart | Melanie Fung | Updated to include changes in v14 of the IL TRM with the main change being an addition of a dB and pressure rating to estimated CFM table. Also, updated the NREL source for control factors to a newer version of the same NREL source. Capped claimed leaks to 67% of system capacity. | Future TRM updates or program changes
7 | 2026-06-01 | Ben Reinhart |  | Added application page and an example completed calculator. | Future TRM updates or program changes