## Instructions
AES Indiana Business Rebates & Incentives Program
Roof Insulation & Cool Roof Calculator
Welcome. This document has been prepared by CLEAResult.
The purpose of this workbook is to determine the savings from roofing projects that involve installation of a cool roofing material and/or improvements to the roof R-Value achieved by replacing existing insulation or installing additional insulation. This workbook uses TMY3 weather data and user-input building data to estimate expected savings from reduced HVAC loads. Common cool roofing materials include (but are not limited to) TPO, PVC, and white EPDM.
Enable Macros!
All required fields must be filled in for savings to be properly displayed.
For technical support on this tool contact custom@aesindianarebates.com.
Input Instructions
Green cells indicate that user input is required.
White cells are calculated values.
Worksheet Summary
Methodology
The Methodology Worksheet provides the heat transfer relationships and radiation methodology considered to produce energy savings values.
Cool Roof Calculator
The Cool Roof Calculator Worksheet requires the inputs described below and provides the associated cooling energy savings, heating impact, and demand savings.
Radiation Calculations
The Radiation Calculations Worksheet pulls the TMY3 data provided in the Cool Roof Calculator Worksheet (latitude, longitude, local standard time meridian, diffuse horizontal irradiance, direct normal irradiance, and dry bulb temperature) and calculates the monthly incoming radiation.
Energy Savings Calculations
The Energy Savings Calculations Worksheet calculates the energy savings based on the inputs in the Cool Roof Calculator Worksheet and the monthly radiation determined in the Radiation Calculations Worksheet.
Operating Hours LookUp
The Operating Hours LookUp Worksheet summarizes operating hours by building type.
Roofing Properties LookUp
The Roofing Properties LookUp Worksheet summarizes emittance and reflectivity for typical roofing types.
Glossary of Inputs
Building Type | Provide the building type from the dropdown list. This information is considered to determine the appropriate annual operating hours. If annual operating hours of the facility is known, select "Operating Hours Known" and input the value for Annual Operating Hours.
Roof Area | Provide the area in square feet that covers the conditioned space of the building.
Conditioning | Indicate whether the building is conditioned with cooling, heating, or both with the dropdown list.
Cooling System Type | Choose from DX/Unitary Cooling/Air Cooled Chiller or Water Cooled Chiller
Cooling Efficiency | For buildings with cooling, provide the efficiency of the cooling system in EER for DX/Unitary Cooling/Air Cooled Chiller or kW/Ton for Water Cooled Chillers
Heating System Type | For buildings with heating, provide the heating system type - electric, gas, or heat pump - from the dropdown list.
Heating System Efficiency | For electric systems the efficiency is taken to be 100%, for heat pumps choose from a list of possible COPs, and for gas fired equipment choose from the efficiency list.
Electricity Rate | For buildings with electric cooling or heating, provide the $/kWh customer electricity price.
Gas Rate | For buildings with gas heating, provide the $/Therm customer gas price.
Incentive Rate | Provide the $/kWh utility incentive rate.
R Value | The R value is a measure of thermal resistance. Provide the R value of the existing roof and the new roof in [hr ft2 °F/ Btu]. The R value should consider the combined ceiling and roof insulation.
Roofing Type | If existing roofing emittance and reflectivity are unknown, select the roofing type from the provided list. Typical emittance and reflectivity values will be considered. If existing roofing emittance and reflectivity are known, select "Roofing Properties Known".
Emittance | Provide an emittance value for the existing roof (unless a Roofing Type was selected) and for the new roof. The emittance describes the roof's ability to emit (radiate) absorbed energy back into the surroundings and is represented as a decimal less than one. ASHRAE Standard 90.1 defines cool roofs as a roof having a minimum thermal emittance of 0.75. If the manufacturer is known, it might be possible to look up values from the Cool Roof Rating Council at http://coolroofs.org/products/results. Leave blank if unknown.
Reflectivity | Provide a reflectivity value for the existing roof (unless a Roofing Type was selcted) and for the new roof. The reflectivity describes the roof's ability to reflect the heat from solar energy and is represented as a decimal less than one. ASHRAE Standard 90.1 defines cool roofs as a roof having a minimum solar reflectivity of 0.55. If the manufacturer is known, it might be possible to look up values from the Cool Roof Rating Council at http://coolroofs.org/products/results. Use the 3-year aged values.
Glossary of Outputs
Cooling Energy Savings [kWh] | The annual energy savings from reduced energy consumption for cooling. | kWh
Cooling Energy Savings [$/year] | The annual monetary savings to the customer from reduced energy consumption for cooling. | $/year
Heating Energy Savings [kWh or Therms] | The annual energy savings (or penalty) from reduced energy consumption for heating. | kWh
Heating Energy Savings [$/year] | The annual monetary savings (or penalty) to the customer from reduced energy consumption for heating. | $/year
Cooling Peak Demand Savings [kW] | The peak demand savings from reduced cooling demand. Peak demand savings is determined for the period of highest radiation. The methodology can be tailored to a utility-specific definition of peak upon request. | kW
Incentive [$] | The total incentive based on total kWh savings and the utility incentive rate.
Please Note: This calculator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this calculator is deemed acceptable for the AES Indiana Custom Incentives program. However, the assumptions used by the applicant to calculate the annual savings will be reviewed by the AES Indiana Custom Incentives program, which is solely responsible for the final determination of the annual energy savings to be used in calculating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities. Incentive amount is calculated based on first year energy savings. The incentives are earned at $0.08 kWh saved. Incentives are limited to a maximum cap of $1,000,000 per project at a service ID and/or building behind a master meter. Total combined custom and prescriptive incentives are capped at $1,000,000 per customer per calendar year.

## Methodology
AES Indiana Business Rebates & Incentives Program
Roof Insulation & Cool Roof Calculator Methodology
A cool roof reflects the sun's heat and emits absorbed radiation back into the atmosphere. This calculator is based on general heat transfer relationships and radiation methodology from Typical Meteorological Year 3 (TMY3) Data. The heat transfer considered is the combined incident solar radiation, radiant energy exchange with the surroundings, and convective heat exchange with the outdoor air. TMY3 data represents the weather during a typical year for a given city and is published by the US DOE's Energy Efficiency and Renewable Energy Office.
Peak cooling is determined for the period of highest radiation. The methodology can be tailored to a utility-specific definition of peak upon request.
Radiation Methodology from TMY3 Data [Radiation Calculations Worksheet]
Methodology from PV Education, Making Use of TMY Data. [http://www.pveducation.org/pvcdrom/properties-of-sunlight/making-use-of-TMY]
TMY3 data can be downloaded from the National Solar Radiation Data Base at http://rredc.nrel.gov/solar/old_data/nsrdb/1991-2005/tmy3/
Cooling and Heating Load Methodology [Energy Savings Calculations Worksheet]
Methodology based on ASHRAE and basic heat transfer relationships. ASHRAE defined the sol-air temperature to be the temperature that would yield the same amount of heat transfer as the combination of incident solar radiation, radiant energy exchange with the surroundings, and convective heat exchange with the outdoor air [1993 ASHRAE Fundamentals, Chapter 26, Nonresidential Air-Conditioning Cooling and Heating Load, page 26.5].

## Roof Calculator
AES Indiana Business Rebates & Incentives Program
Roof Insulation & Cool Roof Calculator
Project Inputs
Customer Name: | Example Calc (School, electric heat)
Project Description: | TPO cool roof replacement and insulation |  | Switchover OAT | 55
Building Type: | Elementary/Secondary Schools |  | Zone Temperature: | 70
Electricity Rate ($/kWh): | 0.08
Building Annual Operating Hours:
Proposed Project Material Cost: | 400000
Proposed Project Labor Cost: | 200000
Total Proposed Cost: | 600000
Roof Area (sqft): | 50000
Conditioning: | Both
Cooling System Type: | DX/Unitary Cooling/Air Cooled Chiller
Cooling Efficiency (SEER): | 12.5
Heating System Type: | Electric Resistance
Heating Equipment Efficiency: | 100%
Natural Gas Rate: | 1 | $/Therm
Existing Roof & Insulation
R Value: | 7 | [hr. ft2 °F/ Btu]
Roofing Type: | Gray EPDM
Proposed Insulation
R Value: | 30 | [hr. ft2 °F/ Btu]
Will a Cool Roof be installed? | Yes
Roof Emittance & Reflectivity Properties
Existing Properties Considered: | 0.86 Emittance, 0.10 Reflectivity
Existing Roof Emittance: |  | (0 to 1)
Existing Roof Reflectivity (3-yr aged): |  | (0 to 1)
Proposed Cool Roof Emittance: | 0.85 | (0 to 1)
Proposed Cool Roof Reflectivity (3-yr aged): | 0.69 | (0 to 1)
Project Savings Summary
Electric Energy Savings (kWh/Yr.) | 61630.417
Cooling Peak Demand Savings | 25.6433
Natural Gas Energy Savings (Therms/Yr.) | 0
Electric Cost Savings ($/Yr.) | 4930.4334
Natural Gas Cost Savings ($/Yr.) | 0
Total Cost Savings ($/Yr.) | 4930.4334
Eligible Custom Incentive | 4930.4334
Incentive is calculated based on: | $0.08 per annual kWh saved
Simple Payback Period with Incentive (Yrs.) | 121.6932
Simple Payback Period without Incentive (Yrs.) | 120.6932
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Leave blank unless the "Operating Hours Known" Building Type was selected. If the "Operating Hours Known" type was selected enter in the annual operating hours of the HVAC system.
Note on C30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Leave blank unless "Roofing Properties Known" is the selected existing roofing type.
Note on C31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Leave blank unless "Roofing Properties Known" is the selected existing roofing type.

## Radiation Calculations (hidden)
Radiation Calculations
Month | Outside Temp Sums [F] |  | Respond Hrs Sum [hrs] |  | Incoming Radiation Sum [Btu/ft^2] |  | Peak Radiation and Current Temp
| Heating | Cooling | Heating | Cooling | Heating | Cooling | Peak Cooling Incoming Radiation [Btuh/ft^2] | Temp During Peak Cooling Radiation [F] | Time of Peak Cooling Incoming Radiation
1 | 17852.52 | 0 | 744 | 0 | -6842.863 | 0 | 0 | 0 | 1/1/1:00
2 | 16000.7 | 1886.38 | 640 | 32 | -4766.9728 | 1886.38 | 99.3971 | 55.94 | 2/24/12:00
3 | 21448.38 | 10913.4 | 573 | 171 | 2728.5886 | 10913.4 | 103.8317 | 59 | 3/13/15:00
4 | 19021.86 | 18881.64 | 423 | 297 | 5935.8464 | 18881.64 | 135.471 | 64.94 | 4/22/15:00
5 | 5736.02 | 42241.3 | 118 | 626 | 1459.5496 | 42241.3 | 151.1275 | 80.06 | 5/30/14:00
6 | 927.18 | 51416.46 | 18 | 702 | 165.9977 | 51416.46 | 154.6562 | 84.02 | 6/29/14:00
7 | 160.98 | 56592.06 | 3 | 741 | 5.3286 | 56592.06 | 181.8067 | 84.02 | 7/20/13:00
8 | 578.26 | 54203.42 | 11 | 733 | 12.13 | 54203.42 | 156.5162 | 84.02 | 8/8/14:00
9 | 5914.36 | 40736.6 | 119 | 601 | 714.9429 | 40736.6 | 97.1052 | 73.04 | 9/18/14:00
10 | 18662.04 | 20633.7 | 414 | 330 | -4095.1883 | 20633.7 | 113.4531 | 60.98 | 10/10/13:00
11 | 23611.68 | 6025.5 | 621 | 99 | -6349.8655 | 6025.5 | 68.1512 | 57.92 | 11/27/13:00
12 | 20644.86 | 507.06 | 735 | 9 | -6002.0272 | 507.06 | 70.1323 | 57.02 | 12/17/13:00
Radiation Calculations |  |  | TMY3 Inputs from http://rredc.nrel.gov/solar/old_data/nsrdb/1991-2005/tmy3/
Month | Day | Hour (Local Time) | Dry-bulb [C]* (TMY3) | Diffuse horizontal irradiance [W/m2]* (TMY3) | Direct normal irradiance [W/m2]* (TMY3) | Dry Bulb [F] | Heating On below 55 F | Cooling on at 55 F | Heating Outside Temp [F] | Cooling Outside Temp [F] | Roof Tilt Angle [0deg] | Diffuse Radiation on Surface [Wh/m2] | Roof Tilt Angle [0deg] | Roof Azimuth Angle [0deg] | Latitude | Day Number [n] | Declination Angle [deg] | Longitude | Local Standard Time Meridian [deg] | Equation of Time [min] | Hour Angle [deg] | Beam Radiation on Surface [Wh/m2] | Total Radiation on Surface [Wh/m2] | Incoming Radiation [Btu/ft2] | Incoming Radiation Heating [Btu/ft2] | Incoming Radiation Cooling [Btu/ft2] | Cooling on at 55 F | Incoming Radiation Cooling [Btu/ft2] | Time (for peak lookup)
1 | 1 | 1 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1 | -22.9862 | 86.148 | -75 | -3.7052 | -4.7783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/1:00
1 | 1 | 2 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.0417 | -22.9828 | 86.148 | -75 | -3.7238 | 10.2171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/2:00
1 | 1 | 3 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.0833 | -22.9793 | 86.148 | -75 | -3.7424 | 25.2124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/3:00
1 | 1 | 4 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.125 | -22.9759 | 86.148 | -75 | -3.761 | 40.2078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/4:00
1 | 1 | 5 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.1667 | -22.9724 | 86.148 | -75 | -3.7796 | 55.2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/5:00
1 | 1 | 6 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.2083 | -22.969 | 86.148 | -75 | -3.7982 | 70.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/6:00
1 | 1 | 7 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.25 | -22.9655 | 86.148 | -75 | -3.8167 | 85.1938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/7:00
1 | 1 | 8 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.2917 | -22.962 | 86.148 | -75 | -3.8353 | 100.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/8:00
1 | 1 | 9 | -2.8 | 34 | 24 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 34 | 0 | 0 | 39.791 | 1.3333 | -22.9585 | 86.148 | -75 | -3.8539 | 115.1845 | -13.2171 | 20.7829 | 6.5878 | 6.5878 | 0 | 0 | 0 | 1/1/9:00
1 | 1 | 10 | -2.2 | 69 | 14 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 69 | 0 | 0 | 39.791 | 1.375 | -22.9549 | 86.148 | -75 | -3.8724 | 130.1799 | -9.8853 | 59.1147 | 18.7383 | 18.7383 | 0 | 0 | 0 | 1/1/10:00
1 | 1 | 11 | -2.2 | 147 | 126 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 147 | 0 | 0 | 39.791 | 1.4167 | -22.9514 | 86.148 | -75 | -3.891 | 145.1753 | -104.6302 | 42.3698 | 13.4305 | 13.4305 | 0 | 0 | 0 | 1/1/11:00
1 | 1 | 12 | -1.7 | 184 | 66 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 184 | 0 | 0 | 39.791 | 1.4583 | -22.9479 | 86.148 | -75 | -3.9095 | 160.1706 | -60.3997 | 123.6003 | 39.1791 | 39.1791 | 0 | 0 | 0 | 1/1/12:00
1 | 1 | 13 | -1.1 | 139 | 36 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 139 | 0 | 0 | 39.791 | 1.5 | -22.9443 | 86.148 | -75 | -3.928 | 175.166 | -34.3644 | 104.6356 | 33.1677 | 33.1677 | 0 | 0 | 0 | 1/1/13:00
1 | 1 | 14 | -1.1 | 190 | 2 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 190 | 0 | 0 | 39.791 | 1.5417 | -22.9407 | 86.148 | -75 | -3.9465 | 190.1614 | -1.8919 | 188.1081 | 59.627 | 59.627 | 0 | 0 | 0 | 1/1/14:00
1 | 1 | 15 | -0.6 | 205 | 11 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 205 | 0 | 0 | 39.791 | 1.5833 | -22.9371 | 86.148 | -75 | -3.9651 | 205.1567 | -9.7892 | 195.2108 | 61.8784 | 61.8784 | 0 | 0 | 0 | 1/1/15:00
1 | 1 | 16 | -0.6 | 113 | 8 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 113 | 0 | 0 | 39.791 | 1.625 | -22.9335 | 86.148 | -75 | -3.9836 | 220.1521 | -6.3221 | 106.6779 | 33.815 | 33.815 | 0 | 0 | 0 | 1/1/16:00
1 | 1 | 17 | -1.1 | 57 | 3 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 57 | 0 | 0 | 39.791 | 1.6667 | -22.9299 | 86.148 | -75 | -4.002 | 235.1475 | -1.9613 | 55.0387 | 17.4463 | 17.4463 | 0 | 0 | 0 | 1/1/17:00
1 | 1 | 18 | -1.1 | 11 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 11 | 0 | 0 | 39.791 | 1.7083 | -22.9263 | 86.148 | -75 | -4.0205 | 250.1429 | 0 | 11 | 3.4868 | 3.4868 | 0 | 0 | 0 | 1/1/18:00
1 | 1 | 19 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.75 | -22.9227 | 86.148 | -75 | -4.039 | 265.1382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/19:00
1 | 1 | 20 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.7917 | -22.919 | 86.148 | -75 | -4.0575 | 280.1336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/20:00
1 | 1 | 21 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.8333 | -22.9154 | 86.148 | -75 | -4.0759 | 295.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/21:00
1 | 1 | 22 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.875 | -22.9117 | 86.148 | -75 | -4.0944 | 310.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/22:00
1 | 1 | 23 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.9167 | -22.908 | 86.148 | -75 | -4.1128 | 325.1198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/23:00
1 | 1 | 24 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 1.9583 | -22.9043 | 86.148 | -75 | -4.1313 | 340.1152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/1/24:00
1 | 2 | 1 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2 | -22.9006 | 86.148 | -75 | -4.1497 | -4.8894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/1:00
1 | 2 | 2 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.0417 | -22.8969 | 86.148 | -75 | -4.1681 | 10.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/2:00
1 | 2 | 3 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.0833 | -22.8931 | 86.148 | -75 | -4.1865 | 25.1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/3:00
1 | 2 | 4 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.125 | -22.8894 | 86.148 | -75 | -4.2049 | 40.0968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/4:00
1 | 2 | 5 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.1667 | -22.8856 | 86.148 | -75 | -4.2233 | 55.0922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/5:00
1 | 2 | 6 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.2083 | -22.8819 | 86.148 | -75 | -4.2417 | 70.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/6:00
1 | 2 | 7 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.25 | -22.8781 | 86.148 | -75 | -4.2601 | 85.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/7:00
1 | 2 | 8 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.2917 | -22.8743 | 86.148 | -75 | -4.2785 | 100.0784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/8:00
1 | 2 | 9 | 0.6 | 25 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 25 | 0 | 0 | 39.791 | 2.3333 | -22.8705 | 86.148 | -75 | -4.2968 | 115.0738 | 0 | 25 | 7.9246 | 7.9246 | 0 | 0 | 0 | 1/2/9:00
1 | 2 | 10 | 1.1 | 54 | 3 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 54 | 0 | 0 | 39.791 | 2.375 | -22.8666 | 86.148 | -75 | -4.3152 | 130.0692 | -2.1133 | 51.8867 | 16.4472 | 16.4472 | 0 | 0 | 0 | 1/2/10:00
1 | 2 | 11 | 1.7 | 92 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 92 | 0 | 0 | 39.791 | 2.4167 | -22.8628 | 86.148 | -75 | -4.3335 | 145.0646 | 0 | 92 | 29.1624 | 29.1624 | 0 | 0 | 0 | 1/2/11:00
1 | 2 | 12 | 2.8 | 131 | 1 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 131 | 0 | 0 | 39.791 | 2.4583 | -22.859 | 86.148 | -75 | -4.3519 | 160.06 | -0.9142 | 130.0858 | 41.2349 | 41.2349 | 0 | 0 | 0 | 1/2/12:00
1 | 2 | 13 | 3.3 | 142 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 142 | 0 | 0 | 39.791 | 2.5 | -22.8551 | 86.148 | -75 | -4.3702 | 175.0555 | 0 | 142 | 45.0115 | 45.0115 | 0 | 0 | 0 | 1/2/13:00
1 | 2 | 14 | 3.9 | 130 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 130 | 0 | 0 | 39.791 | 2.5417 | -22.8512 | 86.148 | -75 | -4.3885 | 190.0509 | 0 | 130 | 41.2077 | 41.2077 | 0 | 0 | 0 | 1/2/14:00
1 | 2 | 15 | 4.4 | 116 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 116 | 0 | 0 | 39.791 | 2.5833 | -22.8474 | 86.148 | -75 | -4.4068 | 205.0463 | 0 | 116 | 36.77 | 36.77 | 0 | 0 | 0 | 1/2/15:00
1 | 2 | 16 | 5 | 136 | 1 | 41 | 1 | 0 | 41 | 0 | 0 | 136 | 0 | 0 | 39.791 | 2.625 | -22.8435 | 86.148 | -75 | -4.4251 | 220.0417 | -0.79057 | 135.2094 | 42.859 | 42.859 | 0 | 0 | 0 | 1/2/16:00
1 | 2 | 17 | 3.9 | 40 | 1 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 40 | 0 | 0 | 39.791 | 2.6667 | -22.8396 | 86.148 | -75 | -4.4434 | 235.0371 | -0.65421 | 39.3458 | 12.4719 | 12.4719 | 0 | 0 | 0 | 1/2/17:00
1 | 2 | 18 | 1.1 | 8 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 8 | 0 | 0 | 39.791 | 2.7083 | -22.8356 | 86.148 | -75 | -4.4617 | 250.0326 | 0 | 8 | 2.5359 | 2.5359 | 0 | 0 | 0 | 1/2/18:00
1 | 2 | 19 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.75 | -22.8317 | 86.148 | -75 | -4.48 | 265.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/19:00
1 | 2 | 20 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.7917 | -22.8278 | 86.148 | -75 | -4.4982 | 280.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/20:00
1 | 2 | 21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.8333 | -22.8238 | 86.148 | -75 | -4.5165 | 295.0189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/21:00
1 | 2 | 22 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.875 | -22.8198 | 86.148 | -75 | -4.5347 | 310.0143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/22:00
1 | 2 | 23 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.9167 | -22.8159 | 86.148 | -75 | -4.553 | 325.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/23:00
1 | 2 | 24 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 2.9583 | -22.8119 | 86.148 | -75 | -4.5712 | 340.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/2/24:00
1 | 3 | 1 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3 | -22.8079 | 86.148 | -75 | -4.5894 | -4.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/1:00
1 | 3 | 2 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.0417 | -22.8038 | 86.148 | -75 | -4.6076 | 9.9961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/2:00
1 | 3 | 3 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.0833 | -22.7998 | 86.148 | -75 | -4.6258 | 24.9915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/3:00
1 | 3 | 4 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.125 | -22.7958 | 86.148 | -75 | -4.644 | 39.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/4:00
1 | 3 | 5 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.1667 | -22.7917 | 86.148 | -75 | -4.6622 | 54.9824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/5:00
1 | 3 | 6 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.2083 | -22.7876 | 86.148 | -75 | -4.6804 | 69.9779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/6:00
1 | 3 | 7 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.25 | -22.7836 | 86.148 | -75 | -4.6985 | 84.9734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/7:00
1 | 3 | 8 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.2917 | -22.7795 | 86.148 | -75 | -4.7167 | 99.9688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/8:00
1 | 3 | 9 | -3.9 | 25 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 25 | 0 | 0 | 39.791 | 3.3333 | -22.7754 | 86.148 | -75 | -4.7348 | 114.9643 | 0 | 25 | 7.9246 | 7.9246 | 0 | 0 | 0 | 1/3/9:00
1 | 3 | 10 | -4.4 | 83 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 83 | 0 | 0 | 39.791 | 3.375 | -22.7713 | 86.148 | -75 | -4.753 | 129.9598 | 0 | 83 | 26.3096 | 26.3096 | 0 | 0 | 0 | 1/3/10:00
1 | 3 | 11 | -3.9 | 145 | 101 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 145 | 0 | 0 | 39.791 | 3.4167 | -22.7671 | 86.148 | -75 | -4.7711 | 144.9552 | -83.6009 | 61.3991 | 19.4625 | 19.4625 | 0 | 0 | 0 | 1/3/11:00
1 | 3 | 12 | -5 | 134 | 460 | 23 | 1 | 0 | 23 | 0 | 0 | 134 | 0 | 0 | 39.791 | 3.4583 | -22.763 | 86.148 | -75 | -4.7892 | 159.9507 | -420.0825 | -286.0825 | -90.6832 | -90.6832 | 0 | 0 | 0 | 1/3/12:00
1 | 3 | 13 | -4.4 | 117 | 479 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 117 | 0 | 0 | 39.791 | 3.5 | -22.7588 | 86.148 | -75 | -4.8073 | 174.9462 | -456.6718 | -339.6718 | -107.67 | -107.67 | 0 | 0 | 0 | 1/3/13:00
1 | 3 | 14 | -4.4 | 151 | 529 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 151 | 0 | 0 | 39.791 | 3.5417 | -22.7547 | 86.148 | -75 | -4.8254 | 189.9416 | -500.1585 | -349.1585 | -110.6771 | -110.6771 | 0 | 0 | 0 | 1/3/14:00
1 | 3 | 15 | -4.4 | 193 | 77 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 193 | 0 | 0 | 39.791 | 3.5833 | -22.7505 | 86.148 | -75 | -4.8435 | 204.9371 | -68.5327 | 124.4673 | 39.4539 | 39.4539 | 0 | 0 | 0 | 1/3/15:00
1 | 3 | 16 | -5.6 | 122 | 71 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 122 | 0 | 0 | 39.791 | 3.625 | -22.7463 | 86.148 | -75 | -4.8616 | 219.9326 | -56.1486 | 65.8514 | 20.8737 | 20.8737 | 0 | 0 | 0 | 1/3/16:00
1 | 3 | 17 | -6.7 | 47 | 22 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 47 | 0 | 0 | 39.791 | 3.6667 | -22.7421 | 86.148 | -75 | -4.8797 | 234.9281 | -14.4012 | 32.5988 | 10.3332 | 10.3332 | 0 | 0 | 0 | 1/3/17:00
1 | 3 | 18 | -7.2 | 14 | 19 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 14 | 0 | 0 | 39.791 | 3.7083 | -22.7379 | 86.148 | -75 | -4.8977 | 249.9236 | -9.322 | 4.678 | 1.4828 | 1.4828 | 0 | 0 | 0 | 1/3/18:00
1 | 3 | 19 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.75 | -22.7337 | 86.148 | -75 | -4.9158 | 264.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/19:00
1 | 3 | 20 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.7917 | -22.7294 | 86.148 | -75 | -4.9338 | 279.9145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/20:00
1 | 3 | 21 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.8333 | -22.7252 | 86.148 | -75 | -4.9519 | 294.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/21:00
1 | 3 | 22 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.875 | -22.7209 | 86.148 | -75 | -4.9699 | 309.9055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/22:00
1 | 3 | 23 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.9167 | -22.7166 | 86.148 | -75 | -4.9879 | 324.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/23:00
1 | 3 | 24 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 3.9583 | -22.7123 | 86.148 | -75 | -5.0059 | 339.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/3/24:00
1 | 4 | 1 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4 | -22.708 | 86.148 | -75 | -5.0239 | -5.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/1:00
1 | 4 | 2 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.0417 | -22.7037 | 86.148 | -75 | -5.0419 | 9.8875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/2:00
1 | 4 | 3 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.0833 | -22.6994 | 86.148 | -75 | -5.0599 | 24.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/3:00
1 | 4 | 4 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.125 | -22.6951 | 86.148 | -75 | -5.0778 | 39.8785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/4:00
1 | 4 | 5 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.1667 | -22.6907 | 86.148 | -75 | -5.0958 | 54.8741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/5:00
1 | 4 | 6 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.2083 | -22.6864 | 86.148 | -75 | -5.1137 | 69.8696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/6:00
1 | 4 | 7 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.25 | -22.682 | 86.148 | -75 | -5.1317 | 84.8651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/7:00
1 | 4 | 8 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.2917 | -22.6776 | 86.148 | -75 | -5.1496 | 99.8606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/8:00
1 | 4 | 9 | -13.9 | 27 | 84 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 27 | 0 | 0 | 39.791 | 4.3333 | -22.6732 | 86.148 | -75 | -5.1675 | 114.8561 | -45.7567 | -18.7567 | -5.9455 | -5.9455 | 0 | 0 | 0 | 1/4/9:00
1 | 4 | 10 | -13.9 | 67 | 291 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 67 | 0 | 0 | 39.791 | 4.375 | -22.6688 | 86.148 | -75 | -5.1854 | 129.8516 | -203.9906 | -136.9906 | -43.4236 | -43.4236 | 0 | 0 | 0 | 1/4/10:00
1 | 4 | 11 | -13.3 | 90 | 420 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 90 | 0 | 0 | 39.791 | 4.4167 | -22.6644 | 86.148 | -75 | -5.2033 | 144.8472 | -347.0626 | -257.0626 | -81.4844 | -81.4844 | 0 | 0 | 0 | 1/4/11:00
1 | 4 | 12 | -12.8 | 177 | 37 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 177 | 0 | 0 | 39.791 | 4.4583 | -22.66 | 86.148 | -75 | -5.2212 | 159.8427 | -33.7515 | 143.2485 | 45.4073 | 45.4073 | 0 | 0 | 0 | 1/4/12:00
1 | 4 | 13 | -12.2 | 173 | 453 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 173 | 0 | 0 | 39.791 | 4.5 | -22.6555 | 86.148 | -75 | -5.2391 | 174.8382 | -431.589 | -258.589 | -81.9682 | -81.9682 | 0 | 0 | 0 | 1/4/13:00
1 | 4 | 14 | -11.1 | 139 | 390 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 139 | 0 | 0 | 39.791 | 4.5417 | -22.651 | 86.148 | -75 | -5.2569 | 189.8338 | -368.6159 | -229.6159 | -72.7842 | -72.7842 | 0 | 0 | 0 | 1/4/14:00
1 | 4 | 15 | -11.7 | 118 | 508 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 118 | 0 | 0 | 39.791 | 4.5833 | -22.6466 | 86.148 | -75 | -5.2748 | 204.8293 | -452.1271 | -334.1271 | -105.9124 | -105.9124 | 0 | 0 | 0 | 1/4/15:00
1 | 4 | 16 | -10.6 | 65 | 670 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 65 | 0 | 0 | 39.791 | 4.625 | -22.6421 | 86.148 | -75 | -5.2926 | 219.8248 | -529.9835 | -464.9835 | -147.3916 | -147.3916 | 0 | 0 | 0 | 1/4/16:00
1 | 4 | 17 | -11.1 | 54 | 298 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 54 | 0 | 0 | 39.791 | 4.6667 | -22.6376 | 86.148 | -75 | -5.3105 | 234.8204 | -195.1674 | -141.1674 | -44.7476 | -44.7476 | 0 | 0 | 0 | 1/4/17:00
1 | 4 | 18 | -12.2 | 10 | 124 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 10 | 0 | 0 | 39.791 | 4.7083 | -22.6331 | 86.148 | -75 | -5.3283 | 249.8159 | -60.8827 | -50.8827 | -16.1289 | -16.1289 | 0 | 0 | 0 | 1/4/18:00
1 | 4 | 19 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.75 | -22.6286 | 86.148 | -75 | -5.3461 | 264.8115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/19:00
1 | 4 | 20 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.7917 | -22.624 | 86.148 | -75 | -5.3639 | 279.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/20:00
1 | 4 | 21 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.8333 | -22.6195 | 86.148 | -75 | -5.3817 | 294.8026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/21:00
1 | 4 | 22 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.875 | -22.615 | 86.148 | -75 | -5.3995 | 309.7981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/22:00
1 | 4 | 23 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.9167 | -22.6104 | 86.148 | -75 | -5.4173 | 324.7937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/23:00
1 | 4 | 24 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 4.9583 | -22.6058 | 86.148 | -75 | -5.435 | 339.7892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/4/24:00
1 | 5 | 1 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5 | -22.6012 | 86.148 | -75 | -5.4528 | -5.2152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/1:00
1 | 5 | 2 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.0417 | -22.5966 | 86.148 | -75 | -5.4705 | 9.7804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/2:00
1 | 5 | 3 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.0833 | -22.592 | 86.148 | -75 | -5.4882 | 24.7759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/3:00
1 | 5 | 4 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.125 | -22.5874 | 86.148 | -75 | -5.506 | 39.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/4:00
1 | 5 | 5 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.1667 | -22.5827 | 86.148 | -75 | -5.5237 | 54.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/5:00
1 | 5 | 6 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.2083 | -22.5781 | 86.148 | -75 | -5.5414 | 69.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/6:00
1 | 5 | 7 | -15.6 | 0 | 0 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.25 | -22.5734 | 86.148 | -75 | -5.5591 | 84.7582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/7:00
1 | 5 | 8 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.2917 | -22.5687 | 86.148 | -75 | -5.5767 | 99.7538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/8:00
1 | 5 | 9 | -12.8 | 39 | 28 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 39 | 0 | 0 | 39.791 | 5.3333 | -22.564 | 86.148 | -75 | -5.5944 | 114.7494 | -15.1937 | 23.8063 | 7.5462 | 7.5462 | 0 | 0 | 0 | 1/5/9:00
1 | 5 | 10 | -11.7 | 85 | 10 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 85 | 0 | 0 | 39.791 | 5.375 | -22.5593 | 86.148 | -75 | -5.6121 | 129.745 | -6.9922 | 78.0078 | 24.7271 | 24.7271 | 0 | 0 | 0 | 1/5/10:00
1 | 5 | 11 | -11.1 | 112 | 10 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 112 | 0 | 0 | 39.791 | 5.4167 | -22.5546 | 86.148 | -75 | -5.6297 | 144.7406 | -8.2491 | 103.7509 | 32.8872 | 32.8872 | 0 | 0 | 0 | 1/5/11:00
1 | 5 | 12 | -10 | 209 | 3 | 14 | 1 | 0 | 14 | 0 | 0 | 209 | 0 | 0 | 39.791 | 5.4583 | -22.5499 | 86.148 | -75 | -5.6473 | 159.7362 | -2.7334 | 206.2666 | 65.3829 | 65.3829 | 0 | 0 | 0 | 1/5/12:00
1 | 5 | 13 | -8.9 | 196 | 130 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 196 | 0 | 0 | 39.791 | 5.5 | -22.5452 | 86.148 | -75 | -5.665 | 174.7318 | -123.7657 | 72.2343 | 22.897 | 22.897 | 0 | 0 | 0 | 1/5/13:00
1 | 5 | 14 | -7.2 | 123 | 665 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 123 | 0 | 0 | 39.791 | 5.5417 | -22.5404 | 86.148 | -75 | -5.6826 | 189.7274 | -628.3012 | -505.3012 | -160.1716 | -160.1716 | 0 | 0 | 0 | 1/5/14:00
1 | 5 | 15 | -6.7 | 46 | 881 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 46 | 0 | 0 | 39.791 | 5.5833 | -22.5357 | 86.148 | -75 | -5.7002 | 204.723 | -784.0378 | -738.0378 | -233.9451 | -233.9451 | 0 | 0 | 0 | 1/5/15:00
1 | 5 | 16 | -6.1 | 37 | 797 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 37 | 0 | 0 | 39.791 | 5.625 | -22.5309 | 86.148 | -75 | -5.7178 | 219.7186 | -630.5509 | -593.5509 | -188.1453 | -188.1453 | 0 | 0 | 0 | 1/5/16:00
1 | 5 | 17 | -6.1 | 26 | 599 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 26 | 0 | 0 | 39.791 | 5.6667 | -22.5261 | 86.148 | -75 | -5.7354 | 234.7142 | -392.4527 | -366.4527 | -116.1591 | -116.1591 | 0 | 0 | 0 | 1/5/17:00
1 | 5 | 18 | -7.2 | 10 | 145 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 10 | 0 | 0 | 39.791 | 5.7083 | -22.5213 | 86.148 | -75 | -5.7529 | 249.7098 | -71.2341 | -61.2341 | -19.4101 | -19.4101 | 0 | 0 | 0 | 1/5/18:00
1 | 5 | 19 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.75 | -22.5165 | 86.148 | -75 | -5.7705 | 264.7054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/19:00
1 | 5 | 20 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.7917 | -22.5117 | 86.148 | -75 | -5.788 | 279.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/20:00
1 | 5 | 21 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.8333 | -22.5069 | 86.148 | -75 | -5.8056 | 294.6966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/21:00
1 | 5 | 22 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.875 | -22.502 | 86.148 | -75 | -5.8231 | 309.6922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/22:00
1 | 5 | 23 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.9167 | -22.4972 | 86.148 | -75 | -5.8406 | 324.6878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/23:00
1 | 5 | 24 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 5.9583 | -22.4923 | 86.148 | -75 | -5.8581 | 339.6835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/5/24:00
1 | 6 | 1 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6 | -22.4874 | 86.148 | -75 | -5.8756 | -5.3209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/1:00
1 | 6 | 2 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.0417 | -22.4825 | 86.148 | -75 | -5.8931 | 9.6747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/2:00
1 | 6 | 3 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.0833 | -22.4776 | 86.148 | -75 | -5.9106 | 24.6704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/3:00
1 | 6 | 4 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.125 | -22.4727 | 86.148 | -75 | -5.928 | 39.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/4:00
1 | 6 | 5 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.1667 | -22.4678 | 86.148 | -75 | -5.9455 | 54.6616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/5:00
1 | 6 | 6 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.2083 | -22.4628 | 86.148 | -75 | -5.9629 | 69.6573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/6:00
1 | 6 | 7 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.25 | -22.4579 | 86.148 | -75 | -5.9803 | 84.6529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/7:00
1 | 6 | 8 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.2917 | -22.4529 | 86.148 | -75 | -5.9978 | 99.6486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/8:00
1 | 6 | 9 | -8.3 | 21 | 97 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 21 | 0 | 0 | 39.791 | 6.3333 | -22.4479 | 86.148 | -75 | -6.0152 | 114.6442 | -52.4285 | -31.4285 | -9.9623 | -9.9623 | 0 | 0 | 0 | 1/6/9:00
1 | 6 | 10 | -5.6 | 62 | 369 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 62 | 0 | 0 | 39.791 | 6.375 | -22.4429 | 86.148 | -75 | -6.0326 | 129.6399 | -257.3387 | -195.3387 | -61.919 | -61.919 | 0 | 0 | 0 | 1/6/10:00
1 | 6 | 11 | -2.8 | 154 | 90 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 154 | 0 | 0 | 39.791 | 6.4167 | -22.4379 | 86.148 | -75 | -6.0499 | 144.6355 | -74.1097 | 79.8903 | 25.3238 | 25.3238 | 0 | 0 | 0 | 1/6/11:00
1 | 6 | 12 | -0.6 | 184 | 78 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 184 | 0 | 0 | 39.791 | 6.4583 | -22.4329 | 86.148 | -75 | -6.0673 | 159.6312 | -70.9838 | 113.0162 | 35.8242 | 35.8242 | 0 | 0 | 0 | 1/6/12:00
1 | 6 | 13 | 1.1 | 175 | 347 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 175 | 0 | 0 | 39.791 | 6.5 | -22.4279 | 86.148 | -75 | -6.0847 | 174.6268 | -330.1052 | -155.1052 | -49.1656 | -49.1656 | 0 | 0 | 0 | 1/6/13:00
1 | 6 | 14 | 2.2 | 200 | 342 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 200 | 0 | 0 | 39.791 | 6.5417 | -22.4229 | 86.148 | -75 | -6.102 | 189.6225 | -322.9893 | -122.9893 | -38.9854 | -38.9854 | 0 | 0 | 0 | 1/6/14:00
1 | 6 | 15 | 3.3 | 171 | 224 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 171 | 0 | 0 | 39.791 | 6.5833 | -22.4178 | 86.148 | -75 | -6.1194 | 204.6182 | -199.3186 | -28.3186 | -8.9765 | -8.9765 | 0 | 0 | 0 | 1/6/15:00
1 | 6 | 16 | 3.3 | 93 | 33 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 93 | 0 | 0 | 39.791 | 6.625 | -22.4127 | 86.148 | -75 | -6.1367 | 219.6138 | -26.1106 | 66.8894 | 21.2028 | 21.2028 | 0 | 0 | 0 | 1/6/16:00
1 | 6 | 17 | 2.8 | 43 | 5 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 43 | 0 | 0 | 39.791 | 6.6667 | -22.4077 | 86.148 | -75 | -6.154 | 234.6095 | -3.2768 | 39.7232 | 12.5916 | 12.5916 | 0 | 0 | 0 | 1/6/17:00
1 | 6 | 18 | 2.2 | 11 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 11 | 0 | 0 | 39.791 | 6.7083 | -22.4026 | 86.148 | -75 | -6.1713 | 249.6052 | 0 | 11 | 3.4868 | 3.4868 | 0 | 0 | 0 | 1/6/18:00
1 | 6 | 19 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.75 | -22.3975 | 86.148 | -75 | -6.1886 | 264.6009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/19:00
1 | 6 | 20 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.7917 | -22.3924 | 86.148 | -75 | -6.2059 | 279.5965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/20:00
1 | 6 | 21 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.8333 | -22.3873 | 86.148 | -75 | -6.2231 | 294.5922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/21:00
1 | 6 | 22 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.875 | -22.3821 | 86.148 | -75 | -6.2404 | 309.5879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/22:00
1 | 6 | 23 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.9167 | -22.377 | 86.148 | -75 | -6.2576 | 324.5836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/23:00
1 | 6 | 24 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 6.9583 | -22.3718 | 86.148 | -75 | -6.2749 | 339.5793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/6/24:00
1 | 7 | 1 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7 | -22.3667 | 86.148 | -75 | -6.2921 | -5.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/1:00
1 | 7 | 2 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.0417 | -22.3615 | 86.148 | -75 | -6.3093 | 9.5707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/2:00
1 | 7 | 3 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.0833 | -22.3563 | 86.148 | -75 | -6.3265 | 24.5664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/3:00
1 | 7 | 4 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.125 | -22.3511 | 86.148 | -75 | -6.3437 | 39.5621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/4:00
1 | 7 | 5 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.1667 | -22.3459 | 86.148 | -75 | -6.3608 | 54.5578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/5:00
1 | 7 | 6 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.2083 | -22.3406 | 86.148 | -75 | -6.378 | 69.5535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/6:00
1 | 7 | 7 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.25 | -22.3354 | 86.148 | -75 | -6.3951 | 84.5492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/7:00
1 | 7 | 8 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.2917 | -22.3301 | 86.148 | -75 | -6.4123 | 99.5449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/8:00
1 | 7 | 9 | 0 | 18 | 3 | 32 | 1 | 0 | 32 | 0 | 0 | 18 | 0 | 0 | 39.791 | 7.3333 | -22.3249 | 86.148 | -75 | -6.4294 | 114.5406 | -1.615 | 16.385 | 5.1938 | 5.1938 | 0 | 0 | 0 | 1/7/9:00
1 | 7 | 10 | 0 | 70 | 6 | 32 | 1 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 39.791 | 7.375 | -22.3196 | 86.148 | -75 | -6.4465 | 129.5364 | -4.1732 | 65.8268 | 20.8659 | 20.8659 | 0 | 0 | 0 | 1/7/10:00
1 | 7 | 11 | 0 | 148 | 6 | 32 | 1 | 0 | 32 | 0 | 0 | 148 | 0 | 0 | 39.791 | 7.4167 | -22.3143 | 86.148 | -75 | -6.4636 | 144.5321 | -4.9316 | 143.0684 | 45.3502 | 45.3502 | 0 | 0 | 0 | 1/7/11:00
1 | 7 | 12 | 0 | 189 | 7 | 32 | 1 | 0 | 32 | 0 | 0 | 189 | 0 | 0 | 39.791 | 7.4583 | -22.309 | 86.148 | -75 | -6.4807 | 159.5278 | -6.3624 | 182.6376 | 57.8929 | 57.8929 | 0 | 0 | 0 | 1/7/12:00
1 | 7 | 13 | 0 | 239 | 1 | 32 | 1 | 0 | 32 | 0 | 0 | 239 | 0 | 0 | 39.791 | 7.5 | -22.3037 | 86.148 | -75 | -6.4978 | 174.5236 | -0.95054 | 238.0495 | 75.4575 | 75.4575 | 0 | 0 | 0 | 1/7/13:00
1 | 7 | 14 | -1.7 | 220 | 2 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 220 | 0 | 0 | 39.791 | 7.5417 | -22.2984 | 86.148 | -75 | -6.5148 | 189.5193 | -1.8879 | 218.1121 | 69.1377 | 69.1377 | 0 | 0 | 0 | 1/7/14:00
1 | 7 | 15 | -3.3 | 174 | 3 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 174 | 0 | 0 | 39.791 | 7.5833 | -22.2931 | 86.148 | -75 | -6.5319 | 204.515 | -2.6689 | 171.3311 | 54.309 | 54.309 | 0 | 0 | 0 | 1/7/15:00
1 | 7 | 16 | -3.9 | 135 | 1 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 135 | 0 | 0 | 39.791 | 7.625 | -22.2877 | 86.148 | -75 | -6.5489 | 219.5108 | -0.79124 | 134.2088 | 42.5418 | 42.5418 | 0 | 0 | 0 | 1/7/16:00
1 | 7 | 17 | -3.9 | 67 | 1 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 67 | 0 | 0 | 39.791 | 7.6667 | -22.2823 | 86.148 | -75 | -6.566 | 234.5065 | -0.65548 | 66.3445 | 21.0301 | 21.0301 | 0 | 0 | 0 | 1/7/17:00
1 | 7 | 18 | -5 | 14 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 14 | 0 | 0 | 39.791 | 7.7083 | -22.277 | 86.148 | -75 | -6.583 | 249.5023 | 0 | 14 | 4.4378 | 4.4378 | 0 | 0 | 0 | 1/7/18:00
1 | 7 | 19 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.75 | -22.2716 | 86.148 | -75 | -6.6 | 264.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/19:00
1 | 7 | 20 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.7917 | -22.2662 | 86.148 | -75 | -6.617 | 279.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/20:00
1 | 7 | 21 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.8333 | -22.2608 | 86.148 | -75 | -6.634 | 294.4895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/21:00
1 | 7 | 22 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.875 | -22.2554 | 86.148 | -75 | -6.6509 | 309.4853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/22:00
1 | 7 | 23 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.9167 | -22.2499 | 86.148 | -75 | -6.6679 | 324.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/23:00
1 | 7 | 24 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 7.9583 | -22.2445 | 86.148 | -75 | -6.6848 | 339.4768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/7/24:00
1 | 8 | 1 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8 | -22.239 | 86.148 | -75 | -6.7018 | -5.5274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/1:00
1 | 8 | 2 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.0417 | -22.2336 | 86.148 | -75 | -6.7187 | 9.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/2:00
1 | 8 | 3 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.0833 | -22.2281 | 86.148 | -75 | -6.7356 | 24.4641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/3:00
1 | 8 | 4 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.125 | -22.2226 | 86.148 | -75 | -6.7525 | 39.4599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/4:00
1 | 8 | 5 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.1667 | -22.2171 | 86.148 | -75 | -6.7693 | 54.4557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/5:00
1 | 8 | 6 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.2083 | -22.2116 | 86.148 | -75 | -6.7862 | 69.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/6:00
1 | 8 | 7 | -19.4 | 0 | 0 | -2.92 | 1 | 0 | -2.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.25 | -22.2061 | 86.148 | -75 | -6.8031 | 84.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/7:00
1 | 8 | 8 | -19.4 | 0 | 0 | -2.92 | 1 | 0 | -2.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.2917 | -22.2005 | 86.148 | -75 | -6.8199 | 99.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/8:00
1 | 8 | 9 | -20 | 20 | 234 | -4 | 1 | 0 | -4 | 0 | 0 | 20 | 0 | 0 | 39.791 | 8.3333 | -22.195 | 86.148 | -75 | -6.8367 | 114.4388 | -125.4483 | -105.4483 | -33.4253 | -33.4253 | 0 | 0 | 0 | 1/8/9:00
1 | 8 | 10 | -19.4 | 42 | 632 | -2.92 | 1 | 0 | -2.92 | 0 | 0 | 42 | 0 | 0 | 39.791 | 8.375 | -22.1894 | 86.148 | -75 | -6.8536 | 129.4346 | -438.3762 | -396.3762 | -125.6443 | -125.6443 | 0 | 0 | 0 | 1/8/10:00
1 | 8 | 11 | -18.9 | 57 | 792 | -2.02 | 1 | 0 | -2.02 | 0 | 0 | 57 | 0 | 0 | 39.791 | 8.4167 | -22.1839 | 86.148 | -75 | -6.8704 | 144.4304 | -649.7511 | -592.7511 | -187.8917 | -187.8917 | 0 | 0 | 0 | 1/8/11:00
1 | 8 | 12 | -17.8 | 67 | 856 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 67 | 0 | 0 | 39.791 | 8.4583 | -22.1783 | 86.148 | -75 | -6.8872 | 159.4262 | -777.0272 | -710.0272 | -225.0662 | -225.0662 | 0 | 0 | 0 | 1/8/12:00
1 | 8 | 13 | -16.7 | 72 | 886 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 72 | 0 | 0 | 39.791 | 8.5 | -22.1727 | 86.148 | -75 | -6.9039 | 174.422 | -841.4559 | -769.4559 | -243.9041 | -243.9041 | 0 | 0 | 0 | 1/8/13:00
1 | 8 | 14 | -15.6 | 71 | 874 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 71 | 0 | 0 | 39.791 | 8.5417 | -22.1671 | 86.148 | -75 | -6.9207 | 189.4178 | -824.5954 | -753.5954 | -238.8766 | -238.8766 | 0 | 0 | 0 | 1/8/14:00
1 | 8 | 15 | -15 | 64 | 841 | 5 | 1 | 0 | 5 | 0 | 0 | 64 | 0 | 0 | 39.791 | 8.5833 | -22.1614 | 86.148 | -75 | -6.9375 | 204.4136 | -747.9899 | -683.9899 | -216.8129 | -216.8129 | 0 | 0 | 0 | 1/8/15:00
1 | 8 | 16 | -14.4 | 52 | 753 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 52 | 0 | 0 | 39.791 | 8.625 | -22.1558 | 86.148 | -75 | -6.9542 | 219.4095 | -595.7711 | -543.7711 | -172.3659 | -172.3659 | 0 | 0 | 0 | 1/8/16:00
1 | 8 | 17 | -14.4 | 36 | 551 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 36 | 0 | 0 | 39.791 | 8.6667 | -22.1502 | 86.148 | -75 | -6.9709 | 234.4053 | -361.1962 | -325.1962 | -103.0815 | -103.0815 | 0 | 0 | 0 | 1/8/17:00
1 | 8 | 18 | -16.1 | 14 | 112 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 14 | 0 | 0 | 39.791 | 8.7083 | -22.1445 | 86.148 | -75 | -6.9876 | 249.4011 | -55.0631 | -41.0631 | -13.0163 | -13.0163 | 0 | 0 | 0 | 1/8/18:00
1 | 8 | 19 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.75 | -22.1389 | 86.148 | -75 | -7.0043 | 264.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/19:00
1 | 8 | 20 | -17.2 | 0 | 0 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.7917 | -22.1332 | 86.148 | -75 | -7.021 | 279.3927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/20:00
1 | 8 | 21 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.8333 | -22.1275 | 86.148 | -75 | -7.0377 | 294.3886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/21:00
1 | 8 | 22 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.875 | -22.1218 | 86.148 | -75 | -7.0544 | 309.3844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/22:00
1 | 8 | 23 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.9167 | -22.1161 | 86.148 | -75 | -7.071 | 324.3802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/23:00
1 | 8 | 24 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 8.9583 | -22.1103 | 86.148 | -75 | -7.0877 | 339.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/8/24:00
1 | 9 | 1 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9 | -22.1046 | 86.148 | -75 | -7.1043 | -5.6281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/1:00
1 | 9 | 2 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.0417 | -22.0989 | 86.148 | -75 | -7.1209 | 9.3678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/2:00
1 | 9 | 3 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.0833 | -22.0931 | 86.148 | -75 | -7.1375 | 24.3636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/3:00
1 | 9 | 4 | -18.9 | 0 | 0 | -2.02 | 1 | 0 | -2.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.125 | -22.0873 | 86.148 | -75 | -7.1541 | 39.3595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/4:00
1 | 9 | 5 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.1667 | -22.0815 | 86.148 | -75 | -7.1707 | 54.3553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/5:00
1 | 9 | 6 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.2083 | -22.0757 | 86.148 | -75 | -7.1872 | 69.3512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/6:00
1 | 9 | 7 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.25 | -22.0699 | 86.148 | -75 | -7.2038 | 84.3471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/7:00
1 | 9 | 8 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.2917 | -22.0641 | 86.148 | -75 | -7.2203 | 99.3429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/8:00
1 | 9 | 9 | -18.3 | 24 | 109 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 24 | 0 | 0 | 39.791 | 9.3333 | -22.0583 | 86.148 | -75 | -7.2368 | 114.3388 | -58.1889 | -34.1889 | -10.8373 | -10.8373 | 0 | 0 | 0 | 1/9/9:00
1 | 9 | 10 | -17.2 | 61 | 462 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 61 | 0 | 0 | 39.791 | 9.375 | -22.0524 | 86.148 | -75 | -7.2533 | 129.3347 | -319.5631 | -258.5631 | -81.96 | -81.96 | 0 | 0 | 0 | 1/9/10:00
1 | 9 | 11 | -16.1 | 95 | 578 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 95 | 0 | 0 | 39.791 | 9.4167 | -22.0466 | 86.148 | -75 | -7.2698 | 144.3305 | -473.274 | -378.274 | -119.9062 | -119.9062 | 0 | 0 | 0 | 1/9/11:00
1 | 9 | 12 | -14.4 | 187 | 523 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 187 | 0 | 0 | 39.791 | 9.4583 | -22.0407 | 86.148 | -75 | -7.2863 | 159.3264 | -474.1161 | -287.1161 | -91.0108 | -91.0108 | 0 | 0 | 0 | 1/9/12:00
1 | 9 | 13 | -12.8 | 172 | 574 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 172 | 0 | 0 | 39.791 | 9.5 | -22.0349 | 86.148 | -75 | -7.3028 | 174.3223 | -544.6507 | -372.6507 | -118.1238 | -118.1238 | 0 | 0 | 0 | 1/9/13:00
1 | 9 | 14 | -11.7 | 180 | 389 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 180 | 0 | 0 | 39.791 | 9.5417 | -22.029 | 86.148 | -75 | -7.3192 | 189.3182 | -366.8008 | -186.8008 | -59.2126 | -59.2126 | 0 | 0 | 0 | 1/9/14:00
1 | 9 | 15 | -11.1 | 118 | 622 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 118 | 0 | 0 | 39.791 | 9.5833 | -22.0231 | 86.148 | -75 | -7.3357 | 204.3141 | -553.0322 | -435.0322 | -137.8976 | -137.8976 | 0 | 0 | 0 | 1/9/15:00
1 | 9 | 16 | -9.4 | 107 | 464 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 107 | 0 | 0 | 39.791 | 9.625 | -22.0171 | 86.148 | -75 | -7.3521 | 219.31 | -367.0639 | -260.0639 | -82.4357 | -82.4357 | 0 | 0 | 0 | 1/9/16:00
1 | 9 | 17 | -10 | 67 | 137 | 14 | 1 | 0 | 14 | 0 | 0 | 67 | 0 | 0 | 39.791 | 9.6667 | -22.0112 | 86.148 | -75 | -7.3685 | 234.3059 | -89.8038 | -22.8038 | -7.2284 | -7.2284 | 0 | 0 | 0 | 1/9/17:00
1 | 9 | 18 | -10 | 13 | 5 | 14 | 1 | 0 | 14 | 0 | 0 | 13 | 0 | 0 | 39.791 | 9.7083 | -22.0053 | 86.148 | -75 | -7.3849 | 249.3018 | -2.458 | 10.542 | 3.3416 | 3.3416 | 0 | 0 | 0 | 1/9/18:00
1 | 9 | 19 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.75 | -21.9993 | 86.148 | -75 | -7.4013 | 264.2977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/19:00
1 | 9 | 20 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.7917 | -21.9934 | 86.148 | -75 | -7.4177 | 279.2936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/20:00
1 | 9 | 21 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.8333 | -21.9874 | 86.148 | -75 | -7.434 | 294.2895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/21:00
1 | 9 | 22 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.875 | -21.9814 | 86.148 | -75 | -7.4504 | 309.2854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/22:00
1 | 9 | 23 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.9167 | -21.9754 | 86.148 | -75 | -7.4667 | 324.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/23:00
1 | 9 | 24 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 9.9583 | -21.9694 | 86.148 | -75 | -7.483 | 339.2772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/9/24:00
1 | 10 | 1 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10 | -21.9634 | 86.148 | -75 | -7.4993 | -5.7268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/1:00
1 | 10 | 2 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.0417 | -21.9574 | 86.148 | -75 | -7.5156 | 9.2691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/2:00
1 | 10 | 3 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.0833 | -21.9513 | 86.148 | -75 | -7.5319 | 24.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/3:00
1 | 10 | 4 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.125 | -21.9453 | 86.148 | -75 | -7.5482 | 39.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/4:00
1 | 10 | 5 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.1667 | -21.9392 | 86.148 | -75 | -7.5644 | 54.2569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/5:00
1 | 10 | 6 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.2083 | -21.9332 | 86.148 | -75 | -7.5806 | 69.2528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/6:00
1 | 10 | 7 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.25 | -21.9271 | 86.148 | -75 | -7.5969 | 84.2488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/7:00
1 | 10 | 8 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.2917 | -21.921 | 86.148 | -75 | -7.6131 | 99.2447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/8:00
1 | 10 | 9 | -10 | 16 | 6 | 14 | 1 | 0 | 14 | 0 | 0 | 16 | 0 | 0 | 39.791 | 10.3333 | -21.9149 | 86.148 | -75 | -7.6293 | 114.2407 | -3.1892 | 12.8108 | 4.0608 | 4.0608 | 0 | 0 | 0 | 1/10/9:00
1 | 10 | 10 | -8.9 | 74 | 3 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 74 | 0 | 0 | 39.791 | 10.375 | -21.9087 | 86.148 | -75 | -7.6455 | 129.2366 | -2.0692 | 71.9308 | 22.8008 | 22.8008 | 0 | 0 | 0 | 1/10/10:00
1 | 10 | 11 | -7.8 | 148 | 3 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 148 | 0 | 0 | 39.791 | 10.4167 | -21.9026 | 86.148 | -75 | -7.6616 | 144.2326 | -2.4516 | 145.5484 | 46.1363 | 46.1363 | 0 | 0 | 0 | 1/10/11:00
1 | 10 | 12 | -6.7 | 178 | 10 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 178 | 0 | 0 | 39.791 | 10.4583 | -21.8965 | 86.148 | -75 | -7.6778 | 159.2286 | -9.0528 | 168.9472 | 53.5533 | 53.5533 | 0 | 0 | 0 | 1/10/12:00
1 | 10 | 13 | -6.1 | 192 | 5 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 192 | 0 | 0 | 39.791 | 10.5 | -21.8903 | 86.148 | -75 | -7.6939 | 174.2245 | -4.7399 | 187.2601 | 59.3582 | 59.3582 | 0 | 0 | 0 | 1/10/13:00
1 | 10 | 14 | -4.4 | 273 | 3 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 273 | 0 | 0 | 39.791 | 10.5417 | -21.8841 | 86.148 | -75 | -7.71 | 189.2205 | -2.827 | 270.173 | 85.6401 | 85.6401 | 0 | 0 | 0 | 1/10/14:00
1 | 10 | 15 | -3.9 | 211 | 5 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 211 | 0 | 0 | 39.791 | 10.5833 | -21.8779 | 86.148 | -75 | -7.7262 | 204.2165 | -4.4439 | 206.5561 | 65.4747 | 65.4747 | 0 | 0 | 0 | 1/10/15:00
1 | 10 | 16 | -3.9 | 145 | 4 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 145 | 0 | 0 | 39.791 | 10.625 | -21.8718 | 86.148 | -75 | -7.7423 | 219.2124 | -3.1636 | 141.8364 | 44.9596 | 44.9596 | 0 | 0 | 0 | 1/10/16:00
1 | 10 | 17 | -3.3 | 68 | 2 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 68 | 0 | 0 | 39.791 | 10.6667 | -21.8656 | 86.148 | -75 | -7.7583 | 234.2084 | -1.3108 | 66.6892 | 21.1393 | 21.1393 | 0 | 0 | 0 | 1/10/17:00
1 | 10 | 18 | -2.2 | 16 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 16 | 0 | 0 | 39.791 | 10.7083 | -21.8593 | 86.148 | -75 | -7.7744 | 249.2044 | 0 | 16 | 5.0717 | 5.0717 | 0 | 0 | 0 | 1/10/18:00
1 | 10 | 19 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.75 | -21.8531 | 86.148 | -75 | -7.7905 | 264.2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/19:00
1 | 10 | 20 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.7917 | -21.8469 | 86.148 | -75 | -7.8065 | 279.1964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/20:00
1 | 10 | 21 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.8333 | -21.8406 | 86.148 | -75 | -7.8225 | 294.1924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/21:00
1 | 10 | 22 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.875 | -21.8344 | 86.148 | -75 | -7.8385 | 309.1884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/22:00
1 | 10 | 23 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.9167 | -21.8281 | 86.148 | -75 | -7.8545 | 324.1844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/23:00
1 | 10 | 24 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 10.9583 | -21.8218 | 86.148 | -75 | -7.8705 | 339.1804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/10/24:00
1 | 11 | 1 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11 | -21.8155 | 86.148 | -75 | -7.8865 | -5.8236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/1:00
1 | 11 | 2 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.0417 | -21.8092 | 86.148 | -75 | -7.9025 | 9.1724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/2:00
1 | 11 | 3 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.0833 | -21.8029 | 86.148 | -75 | -7.9184 | 24.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/3:00
1 | 11 | 4 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.125 | -21.7966 | 86.148 | -75 | -7.9343 | 39.1644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/4:00
1 | 11 | 5 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.1667 | -21.7902 | 86.148 | -75 | -7.9502 | 54.1604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/5:00
1 | 11 | 6 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.2083 | -21.7839 | 86.148 | -75 | -7.9661 | 69.1565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/6:00
1 | 11 | 7 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.25 | -21.7775 | 86.148 | -75 | -7.982 | 84.1525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/7:00
1 | 11 | 8 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.2917 | -21.7711 | 86.148 | -75 | -7.9979 | 99.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/8:00
1 | 11 | 9 | 2.8 | 23 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 23 | 0 | 0 | 39.791 | 11.3333 | -21.7647 | 86.148 | -75 | -8.0138 | 114.1446 | 0 | 23 | 7.2906 | 7.2906 | 0 | 0 | 0 | 1/11/9:00
1 | 11 | 10 | 1.7 | 85 | 22 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 85 | 0 | 0 | 39.791 | 11.375 | -21.7583 | 86.148 | -75 | -8.0296 | 129.1406 | -15.1296 | 69.8704 | 22.1477 | 22.1477 | 0 | 0 | 0 | 1/11/10:00
1 | 11 | 11 | 1.1 | 110 | 16 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 110 | 0 | 0 | 39.791 | 11.4167 | -21.7519 | 86.148 | -75 | -8.0454 | 144.1366 | -13.0487 | 96.9513 | 30.7319 | 30.7319 | 0 | 0 | 0 | 1/11/11:00
1 | 11 | 12 | 1.1 | 228 | 7 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 228 | 0 | 0 | 39.791 | 11.4583 | -21.7455 | 86.148 | -75 | -8.0612 | 159.1327 | -6.328 | 221.672 | 70.2662 | 70.2662 | 0 | 0 | 0 | 1/11/12:00
1 | 11 | 13 | 0 | 148 | 14 | 32 | 1 | 0 | 32 | 0 | 0 | 148 | 0 | 0 | 39.791 | 11.5 | -21.7391 | 86.148 | -75 | -8.077 | 174.1287 | -13.2584 | 134.7416 | 42.7107 | 42.7107 | 0 | 0 | 0 | 1/11/13:00
1 | 11 | 14 | -1.1 | 186 | 9 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 186 | 0 | 0 | 39.791 | 11.5417 | -21.7326 | 86.148 | -75 | -8.0928 | 189.1248 | -8.4754 | 177.5246 | 56.2722 | 56.2722 | 0 | 0 | 0 | 1/11/14:00
1 | 11 | 15 | -2.2 | 168 | 7 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 168 | 0 | 0 | 39.791 | 11.5833 | -21.7262 | 86.148 | -75 | -8.1086 | 204.1209 | -6.2187 | 161.7813 | 51.2819 | 51.2819 | 0 | 0 | 0 | 1/11/15:00
1 | 11 | 16 | -2.8 | 128 | 5 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 128 | 0 | 0 | 39.791 | 11.625 | -21.7197 | 86.148 | -75 | -8.1243 | 219.1169 | -3.9534 | 124.0466 | 39.3206 | 39.3206 | 0 | 0 | 0 | 1/11/16:00
1 | 11 | 17 | -2.2 | 50 | 1 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 50 | 0 | 0 | 39.791 | 11.6667 | -21.7132 | 86.148 | -75 | -8.1401 | 234.113 | -0.65523 | 49.3448 | 15.6414 | 15.6414 | 0 | 0 | 0 | 1/11/17:00
1 | 11 | 18 | -2.8 | 16 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 16 | 0 | 0 | 39.791 | 11.7083 | -21.7067 | 86.148 | -75 | -8.1558 | 249.109 | 0 | 16 | 5.0717 | 5.0717 | 0 | 0 | 0 | 1/11/18:00
1 | 11 | 19 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.75 | -21.7002 | 86.148 | -75 | -8.1715 | 264.1051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/19:00
1 | 11 | 20 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.7917 | -21.6937 | 86.148 | -75 | -8.1872 | 279.1012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/20:00
1 | 11 | 21 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.8333 | -21.6872 | 86.148 | -75 | -8.2029 | 294.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/21:00
1 | 11 | 22 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.875 | -21.6807 | 86.148 | -75 | -8.2186 | 309.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/22:00
1 | 11 | 23 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.9167 | -21.6741 | 86.148 | -75 | -8.2342 | 324.0894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/23:00
1 | 11 | 24 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 11.9583 | -21.6676 | 86.148 | -75 | -8.2499 | 339.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/11/24:00
1 | 12 | 1 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12 | -21.661 | 86.148 | -75 | -8.2655 | -5.9184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/1:00
1 | 12 | 2 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.0417 | -21.6544 | 86.148 | -75 | -8.2811 | 9.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/2:00
1 | 12 | 3 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.0833 | -21.6478 | 86.148 | -75 | -8.2967 | 24.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/3:00
1 | 12 | 4 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.125 | -21.6412 | 86.148 | -75 | -8.3123 | 39.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/4:00
1 | 12 | 5 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.1667 | -21.6346 | 86.148 | -75 | -8.3278 | 54.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/5:00
1 | 12 | 6 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.2083 | -21.628 | 86.148 | -75 | -8.3434 | 69.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/6:00
1 | 12 | 7 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.25 | -21.6213 | 86.148 | -75 | -8.3589 | 84.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/7:00
1 | 12 | 8 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.2917 | -21.6147 | 86.148 | -75 | -8.3744 | 99.0544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/8:00
1 | 12 | 9 | -5 | 21 | 136 | 23 | 1 | 0 | 23 | 0 | 0 | 21 | 0 | 0 | 39.791 | 12.3333 | -21.608 | 86.148 | -75 | -8.3899 | 114.0505 | -71.6477 | -50.6477 | -16.0544 | -16.0544 | 0 | 0 | 0 | 1/12/9:00
1 | 12 | 10 | -3.9 | 52 | 489 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 52 | 0 | 0 | 39.791 | 12.375 | -21.6013 | 86.148 | -75 | -8.4054 | 129.0466 | -335.2876 | -283.2876 | -89.7972 | -89.7972 | 0 | 0 | 0 | 1/12/10:00
1 | 12 | 11 | -2.2 | 75 | 609 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 75 | 0 | 0 | 39.791 | 12.4167 | -21.5947 | 86.148 | -75 | -8.4209 | 144.0428 | -495.639 | -420.639 | -133.3352 | -133.3352 | 0 | 0 | 0 | 1/12/11:00
1 | 12 | 12 | -0.6 | 128 | 549 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 128 | 0 | 0 | 39.791 | 12.4583 | -21.588 | 86.148 | -75 | -8.4364 | 159.0389 | -495.5677 | -367.5677 | -116.5125 | -116.5125 | 0 | 0 | 0 | 1/12/12:00
1 | 12 | 13 | 1.1 | 166 | 530 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 166 | 0 | 0 | 39.791 | 12.5 | -21.5812 | 86.148 | -75 | -8.4518 | 174.0351 | -501.4066 | -335.4066 | -106.318 | -106.318 | 0 | 0 | 0 | 1/12/13:00
1 | 12 | 14 | 2.2 | 167 | 518 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 167 | 0 | 0 | 39.791 | 12.5417 | -21.5745 | 86.148 | -75 | -8.4672 | 189.0312 | -487.4504 | -320.4504 | -101.5772 | -101.5772 | 0 | 0 | 0 | 1/12/14:00
1 | 12 | 15 | 3.3 | 154 | 581 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 154 | 0 | 0 | 39.791 | 12.5833 | -21.5678 | 86.148 | -75 | -8.4826 | 204.0273 | -515.886 | -361.886 | -114.7115 | -114.7115 | 0 | 0 | 0 | 1/12/15:00
1 | 12 | 16 | 3.3 | 139 | 186 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 139 | 0 | 0 | 39.791 | 12.625 | -21.5611 | 86.148 | -75 | -8.498 | 219.0235 | -147.0086 | -8.0086 | -2.5386 | -2.5386 | 0 | 0 | 0 | 1/12/16:00
1 | 12 | 17 | 1.7 | 74 | 60 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 74 | 0 | 0 | 39.791 | 12.6667 | -21.5543 | 86.148 | -75 | -8.5134 | 234.0196 | -39.299 | 34.701 | 10.9996 | 10.9996 | 0 | 0 | 0 | 1/12/17:00
1 | 12 | 18 | 1.1 | 18 | 36 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 18 | 0 | 0 | 39.791 | 12.7083 | -21.5475 | 86.148 | -75 | -8.5288 | 249.0158 | -17.6755 | 0.32448 | 0.10286 | 0.10286 | 0 | 0 | 0 | 1/12/18:00
1 | 12 | 19 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.75 | -21.5408 | 86.148 | -75 | -8.5441 | 264.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/19:00
1 | 12 | 20 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.7917 | -21.534 | 86.148 | -75 | -8.5595 | 279.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/20:00
1 | 12 | 21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.8333 | -21.5272 | 86.148 | -75 | -8.5748 | 294.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/21:00
1 | 12 | 22 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.875 | -21.5204 | 86.148 | -75 | -8.5901 | 309.0005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/22:00
1 | 12 | 23 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.9167 | -21.5136 | 86.148 | -75 | -8.6054 | 323.9967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/23:00
1 | 12 | 24 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 12.9583 | -21.5067 | 86.148 | -75 | -8.6207 | 338.9928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/12/24:00
1 | 13 | 1 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13 | -21.4999 | 86.148 | -75 | -8.6359 | -6.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/1:00
1 | 13 | 2 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.0417 | -21.493 | 86.148 | -75 | -8.6512 | 8.9852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/2:00
1 | 13 | 3 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.0833 | -21.4862 | 86.148 | -75 | -8.6664 | 23.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/3:00
1 | 13 | 4 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.125 | -21.4793 | 86.148 | -75 | -8.6816 | 38.9776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/4:00
1 | 13 | 5 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.1667 | -21.4724 | 86.148 | -75 | -8.6968 | 53.9738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/5:00
1 | 13 | 6 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.2083 | -21.4655 | 86.148 | -75 | -8.712 | 68.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/6:00
1 | 13 | 7 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.25 | -21.4586 | 86.148 | -75 | -8.7272 | 83.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/7:00
1 | 13 | 8 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.2917 | -21.4517 | 86.148 | -75 | -8.7423 | 98.9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/8:00
1 | 13 | 9 | 1.1 | 10 | 2 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 10 | 0 | 0 | 39.791 | 13.3333 | -21.4447 | 86.148 | -75 | -8.7575 | 113.9586 | -1.0488 | 8.9512 | 2.8374 | 2.8374 | 0 | 0 | 0 | 1/13/9:00
1 | 13 | 10 | 1.7 | 50 | 4 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 50 | 0 | 0 | 39.791 | 13.375 | -21.4378 | 86.148 | -75 | -8.7726 | 128.9549 | -2.7343 | 47.2657 | 14.9824 | 14.9824 | 0 | 0 | 0 | 1/13/10:00
1 | 13 | 11 | 2.2 | 92 | 4 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 92 | 0 | 0 | 39.791 | 13.4167 | -21.4308 | 86.148 | -75 | -8.7877 | 143.9511 | -3.2485 | 88.7515 | 28.1327 | 28.1327 | 0 | 0 | 0 | 1/13/11:00
1 | 13 | 12 | 2.8 | 106 | 6 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 106 | 0 | 0 | 39.791 | 13.4583 | -21.4239 | 86.148 | -75 | -8.8028 | 158.9473 | -5.4079 | 100.5921 | 31.8859 | 31.8859 | 0 | 0 | 0 | 1/13/12:00
1 | 13 | 13 | 3.9 | 112 | 7 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 112 | 0 | 0 | 39.791 | 13.5 | -21.4169 | 86.148 | -75 | -8.8179 | 173.9435 | -6.6152 | 105.3848 | 33.4051 | 33.4051 | 0 | 0 | 0 | 1/13/13:00
1 | 13 | 14 | 4.4 | 142 | 8 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 142 | 0 | 0 | 39.791 | 13.5417 | -21.4099 | 86.148 | -75 | -8.8329 | 188.9398 | -7.5223 | 134.4777 | 42.6271 | 42.6271 | 0 | 0 | 0 | 1/13/14:00
1 | 13 | 15 | 6.1 | 193 | 7 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 193 | 0 | 0 | 39.791 | 13.5833 | -21.4029 | 86.148 | -75 | -8.848 | 203.936 | -6.2119 | 186.7881 | 59.2086 | 59.2086 | 0 | 0 | 0 | 1/13/15:00
1 | 13 | 16 | 4.4 | 93 | 3 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 93 | 0 | 0 | 39.791 | 13.625 | -21.3959 | 86.148 | -75 | -8.863 | 218.9323 | -2.37 | 90.63 | 28.7281 | 28.7281 | 0 | 0 | 0 | 1/13/16:00
1 | 13 | 17 | 1.1 | 77 | 2 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 77 | 0 | 0 | 39.791 | 13.6667 | -21.3889 | 86.148 | -75 | -8.878 | 233.9285 | -1.3093 | 75.6907 | 23.9926 | 23.9926 | 0 | 0 | 0 | 1/13/17:00
1 | 13 | 18 | 0 | 21 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 21 | 0 | 0 | 39.791 | 13.7083 | -21.3818 | 86.148 | -75 | -8.893 | 248.9248 | 0 | 21 | 6.6566 | 6.6566 | 0 | 0 | 0 | 1/13/18:00
1 | 13 | 19 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.75 | -21.3748 | 86.148 | -75 | -8.908 | 263.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/19:00
1 | 13 | 20 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.7917 | -21.3677 | 86.148 | -75 | -8.9229 | 278.9173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/20:00
1 | 13 | 21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.8333 | -21.3607 | 86.148 | -75 | -8.9379 | 293.9135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/21:00
1 | 13 | 22 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.875 | -21.3536 | 86.148 | -75 | -8.9528 | 308.9098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/22:00
1 | 13 | 23 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.9167 | -21.3465 | 86.148 | -75 | -8.9677 | 323.9061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/23:00
1 | 13 | 24 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 13.9583 | -21.3394 | 86.148 | -75 | -8.9826 | 338.9023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/13/24:00
1 | 14 | 1 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14 | -21.3323 | 86.148 | -75 | -8.9975 | -6.1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/1:00
1 | 14 | 2 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.0417 | -21.3252 | 86.148 | -75 | -9.0124 | 8.8949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/2:00
1 | 14 | 3 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.0833 | -21.318 | 86.148 | -75 | -9.0272 | 23.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/3:00
1 | 14 | 4 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.125 | -21.3109 | 86.148 | -75 | -9.0421 | 38.8875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/4:00
1 | 14 | 5 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.1667 | -21.3037 | 86.148 | -75 | -9.0569 | 53.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/5:00
1 | 14 | 6 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.2083 | -21.2965 | 86.148 | -75 | -9.0717 | 68.8801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/6:00
1 | 14 | 7 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.25 | -21.2894 | 86.148 | -75 | -9.0865 | 83.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/7:00
1 | 14 | 8 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.2917 | -21.2822 | 86.148 | -75 | -9.1013 | 98.8727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/8:00
1 | 14 | 9 | -6.1 | 26 | 8 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 26 | 0 | 0 | 39.791 | 14.3333 | -21.275 | 86.148 | -75 | -9.116 | 113.869 | -4.1756 | 21.8244 | 6.918 | 6.918 | 0 | 0 | 0 | 1/14/9:00
1 | 14 | 10 | -5.6 | 79 | 177 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 79 | 0 | 0 | 39.791 | 14.375 | -21.2678 | 86.148 | -75 | -9.1308 | 128.8653 | -120.6182 | -41.6182 | -13.1923 | -13.1923 | 0 | 0 | 0 | 1/14/10:00
1 | 14 | 11 | -5 | 88 | 589 | 23 | 1 | 0 | 23 | 0 | 0 | 88 | 0 | 0 | 39.791 | 14.4167 | -21.2605 | 86.148 | -75 | -9.1455 | 143.8616 | -477.3113 | -389.3113 | -123.4049 | -123.4049 | 0 | 0 | 0 | 1/14/11:00
1 | 14 | 12 | -3.9 | 105 | 677 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 105 | 0 | 0 | 39.791 | 14.4583 | -21.2533 | 86.148 | -75 | -9.1602 | 158.8579 | -609.2402 | -504.2402 | -159.8353 | -159.8353 | 0 | 0 | 0 | 1/14/12:00
1 | 14 | 13 | -3.9 | 113 | 706 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 113 | 0 | 0 | 39.791 | 14.5 | -21.2461 | 86.148 | -75 | -9.1749 | 173.8543 | -666.4347 | -553.4347 | -175.4291 | -175.4291 | 0 | 0 | 0 | 1/14/13:00
1 | 14 | 14 | -3.3 | 112 | 713 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 112 | 0 | 0 | 39.791 | 14.5417 | -21.2388 | 86.148 | -75 | -9.1896 | 188.8506 | -669.868 | -557.868 | -176.8344 | -176.8344 | 0 | 0 | 0 | 1/14/14:00
1 | 14 | 15 | -2.2 | 102 | 665 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 102 | 0 | 0 | 39.791 | 14.5833 | -21.2315 | 86.148 | -75 | -9.2042 | 203.8469 | -589.7542 | -487.7542 | -154.6096 | -154.6096 | 0 | 0 | 0 | 1/14/15:00
1 | 14 | 16 | -2.2 | 83 | 558 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 83 | 0 | 0 | 39.791 | 14.625 | -21.2243 | 86.148 | -75 | -9.2189 | 218.8433 | -440.5754 | -357.5754 | -113.3452 | -113.3452 | 0 | 0 | 0 | 1/14/16:00
1 | 14 | 17 | -2.2 | 56 | 342 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 56 | 0 | 0 | 39.791 | 14.6667 | -21.217 | 86.148 | -75 | -9.2335 | 233.8396 | -223.7582 | -167.7582 | -53.1764 | -53.1764 | 0 | 0 | 0 | 1/14/17:00
1 | 14 | 18 | -3.3 | 19 | 35 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 19 | 0 | 0 | 39.791 | 14.7083 | -21.2097 | 86.148 | -75 | -9.2481 | 248.836 | -17.1557 | 1.8443 | 0.58462 | 0.58462 | 0 | 0 | 0 | 1/14/18:00
1 | 14 | 19 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.75 | -21.2023 | 86.148 | -75 | -9.2627 | 263.8323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/19:00
1 | 14 | 20 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.7917 | -21.195 | 86.148 | -75 | -9.2773 | 278.8287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/20:00
1 | 14 | 21 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.8333 | -21.1877 | 86.148 | -75 | -9.2919 | 293.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/21:00
1 | 14 | 22 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.875 | -21.1803 | 86.148 | -75 | -9.3064 | 308.8214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/22:00
1 | 14 | 23 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.9167 | -21.173 | 86.148 | -75 | -9.3209 | 323.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/23:00
1 | 14 | 24 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 14.9583 | -21.1656 | 86.148 | -75 | -9.3355 | 338.8141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/14/24:00
1 | 15 | 1 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15 | -21.1582 | 86.148 | -75 | -9.3499 | -6.1895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/1:00
1 | 15 | 2 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.0417 | -21.1508 | 86.148 | -75 | -9.3644 | 8.8069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/2:00
1 | 15 | 3 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.0833 | -21.1434 | 86.148 | -75 | -9.3789 | 23.8033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/3:00
1 | 15 | 4 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.125 | -21.136 | 86.148 | -75 | -9.3933 | 38.7997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/4:00
1 | 15 | 5 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.1667 | -21.1286 | 86.148 | -75 | -9.4078 | 53.7961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/5:00
1 | 15 | 6 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.2083 | -21.1212 | 86.148 | -75 | -9.4222 | 68.7925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/6:00
1 | 15 | 7 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.25 | -21.1137 | 86.148 | -75 | -9.4366 | 83.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/7:00
1 | 15 | 8 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.2917 | -21.1063 | 86.148 | -75 | -9.451 | 98.7853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/8:00
1 | 15 | 9 | -6.1 | 34 | 29 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 34 | 0 | 0 | 39.791 | 15.3333 | -21.0988 | 86.148 | -75 | -9.4653 | 113.7817 | -15.0644 | 18.9356 | 6.0023 | 6.0023 | 0 | 0 | 0 | 1/15/9:00
1 | 15 | 10 | -4.4 | 97 | 26 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 97 | 0 | 0 | 39.791 | 15.375 | -21.0913 | 86.148 | -75 | -9.4797 | 128.7781 | -17.662 | 79.338 | 25.1488 | 25.1488 | 0 | 0 | 0 | 1/15/10:00
1 | 15 | 11 | -2.8 | 159 | 46 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 159 | 0 | 0 | 39.791 | 15.4167 | -21.0838 | 86.148 | -75 | -9.494 | 143.7745 | -37.1948 | 121.8052 | 38.6101 | 38.6101 | 0 | 0 | 0 | 1/15/11:00
1 | 15 | 12 | -1.1 | 174 | 6 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 174 | 0 | 0 | 39.791 | 15.4583 | -21.0763 | 86.148 | -75 | -9.5083 | 158.7709 | -5.3908 | 168.6092 | 53.4462 | 53.4462 | 0 | 0 | 0 | 1/15/12:00
1 | 15 | 13 | -0.6 | 190 | 180 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 190 | 0 | 0 | 39.791 | 15.5 | -21.0688 | 86.148 | -75 | -9.5226 | 173.7673 | -169.7126 | 20.2874 | 6.4307 | 6.4307 | 0 | 0 | 0 | 1/15/13:00
1 | 15 | 14 | 0.6 | 216 | 53 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 216 | 0 | 0 | 39.791 | 15.5417 | -21.0613 | 86.148 | -75 | -9.5369 | 188.7638 | -49.7496 | 166.2504 | 52.6985 | 52.6985 | 0 | 0 | 0 | 1/15/14:00
1 | 15 | 15 | 1.7 | 154 | 390 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 154 | 0 | 0 | 39.791 | 15.5833 | -21.0538 | 86.148 | -75 | -9.5512 | 203.7602 | -345.6262 | -191.6262 | -60.7422 | -60.7422 | 0 | 0 | 0 | 1/15/15:00
1 | 15 | 16 | 2.2 | 129 | 39 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 129 | 0 | 0 | 39.791 | 15.625 | -21.0462 | 86.148 | -75 | -9.5654 | 218.7566 | -30.7732 | 98.2268 | 31.1362 | 31.1362 | 0 | 0 | 0 | 1/15/16:00
1 | 15 | 17 | 2.8 | 79 | 19 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 79 | 0 | 0 | 39.791 | 15.6667 | -21.0387 | 86.148 | -75 | -9.5797 | 233.7531 | -12.422 | 66.578 | 21.1041 | 21.1041 | 0 | 0 | 0 | 1/15/17:00
1 | 15 | 18 | 2.8 | 15 | 3 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 15 | 0 | 0 | 39.791 | 15.7083 | -21.0311 | 86.148 | -75 | -9.5939 | 248.7495 | -1.4689 | 13.5311 | 4.2891 | 4.2891 | 0 | 0 | 0 | 1/15/18:00
1 | 15 | 19 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.75 | -21.0235 | 86.148 | -75 | -9.6081 | 263.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/19:00
1 | 15 | 20 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.7917 | -21.0159 | 86.148 | -75 | -9.6222 | 278.7424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/20:00
1 | 15 | 21 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.8333 | -21.0083 | 86.148 | -75 | -9.6364 | 293.7389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/21:00
1 | 15 | 22 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.875 | -21.0007 | 86.148 | -75 | -9.6506 | 308.7354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/22:00
1 | 15 | 23 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.9167 | -20.9931 | 86.148 | -75 | -9.6647 | 323.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/23:00
1 | 15 | 24 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 15.9583 | -20.9855 | 86.148 | -75 | -9.6788 | 338.7283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/15/24:00
1 | 16 | 1 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16 | -20.9778 | 86.148 | -75 | -9.6929 | -6.2752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/1:00
1 | 16 | 2 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.0417 | -20.9702 | 86.148 | -75 | -9.707 | 8.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/2:00
1 | 16 | 3 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.0833 | -20.9625 | 86.148 | -75 | -9.721 | 23.7177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/3:00
1 | 16 | 4 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.125 | -20.9548 | 86.148 | -75 | -9.7351 | 38.7142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/4:00
1 | 16 | 5 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.1667 | -20.9472 | 86.148 | -75 | -9.7491 | 53.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/5:00
1 | 16 | 6 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.2083 | -20.9395 | 86.148 | -75 | -9.7631 | 68.7072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/6:00
1 | 16 | 7 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.25 | -20.9318 | 86.148 | -75 | -9.7771 | 83.7037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/7:00
1 | 16 | 8 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.2917 | -20.924 | 86.148 | -75 | -9.7911 | 98.7002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/8:00
1 | 16 | 9 | 0 | 29 | 2 | 32 | 1 | 0 | 32 | 0 | 0 | 29 | 0 | 0 | 39.791 | 16.3333 | -20.9163 | 86.148 | -75 | -9.8051 | 113.6967 | -1.0339 | 27.9661 | 8.8648 | 8.8648 | 0 | 0 | 0 | 1/16/9:00
1 | 16 | 10 | -0.6 | 85 | 2 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 85 | 0 | 0 | 39.791 | 16.375 | -20.9086 | 86.148 | -75 | -9.819 | 128.6932 | -1.3542 | 83.6458 | 26.5142 | 26.5142 | 0 | 0 | 0 | 1/16/10:00
1 | 16 | 11 | -1.1 | 142 | 5 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 142 | 0 | 0 | 39.791 | 16.4167 | -20.9008 | 86.148 | -75 | -9.8329 | 143.6898 | -4.0338 | 137.9662 | 43.7329 | 43.7329 | 0 | 0 | 0 | 1/16/11:00
1 | 16 | 12 | -1.1 | 227 | 6 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 227 | 0 | 0 | 39.791 | 16.4583 | -20.8931 | 86.148 | -75 | -9.8468 | 158.6863 | -5.382 | 221.618 | 70.249 | 70.249 | 0 | 0 | 0 | 1/16/12:00
1 | 16 | 13 | -0.6 | 237 | 1 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 237 | 0 | 0 | 39.791 | 16.5 | -20.8853 | 86.148 | -75 | -9.8607 | 173.6828 | -0.94169 | 236.0583 | 74.8264 | 74.8264 | 0 | 0 | 0 | 1/16/13:00
1 | 16 | 14 | -0.6 | 228 | 1 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 228 | 0 | 0 | 39.791 | 16.5417 | -20.8775 | 86.148 | -75 | -9.8746 | 188.6793 | -0.93779 | 227.0622 | 71.9748 | 71.9748 | 0 | 0 | 0 | 1/16/14:00
1 | 16 | 15 | -1.1 | 213 | 133 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 213 | 0 | 0 | 39.791 | 16.5833 | -20.8697 | 86.148 | -75 | -9.8885 | 203.6759 | -117.7761 | 95.2239 | 30.1843 | 30.1843 | 0 | 0 | 0 | 1/16/15:00
1 | 16 | 16 | -1.7 | 134 | 124 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 134 | 0 | 0 | 39.791 | 16.625 | -20.8619 | 86.148 | -75 | -9.9023 | 218.6724 | -97.772 | 36.228 | 11.4837 | 11.4837 | 0 | 0 | 0 | 1/16/16:00
1 | 16 | 17 | -3.3 | 70 | 286 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 70 | 0 | 0 | 39.791 | 16.6667 | -20.8541 | 86.148 | -75 | -9.9161 | 233.669 | -186.8255 | -116.8255 | -37.0316 | -37.0316 | 0 | 0 | 0 | 1/16/17:00
1 | 16 | 18 | -5.6 | 18 | 159 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 18 | 0 | 0 | 39.791 | 16.7083 | -20.8463 | 86.148 | -75 | -9.9299 | 248.6655 | -77.7502 | -59.7502 | -18.9398 | -18.9398 | 0 | 0 | 0 | 1/16/18:00
1 | 16 | 19 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.75 | -20.8384 | 86.148 | -75 | -9.9437 | 263.6621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/19:00
1 | 16 | 20 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.7917 | -20.8306 | 86.148 | -75 | -9.9575 | 278.6586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/20:00
1 | 16 | 21 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.8333 | -20.8227 | 86.148 | -75 | -9.9712 | 293.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/21:00
1 | 16 | 22 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.875 | -20.8148 | 86.148 | -75 | -9.985 | 308.6518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/22:00
1 | 16 | 23 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.9167 | -20.807 | 86.148 | -75 | -9.9987 | 323.6483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/23:00
1 | 16 | 24 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 16.9583 | -20.7991 | 86.148 | -75 | -10.0124 | 338.6449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/16/24:00
1 | 17 | 1 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17 | -20.7912 | 86.148 | -75 | -10.0261 | -6.3585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/1:00
1 | 17 | 2 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.0417 | -20.7832 | 86.148 | -75 | -10.0398 | 8.6381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/2:00
1 | 17 | 3 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.0833 | -20.7753 | 86.148 | -75 | -10.0534 | 23.6346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/3:00
1 | 17 | 4 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.125 | -20.7674 | 86.148 | -75 | -10.067 | 38.6312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/4:00
1 | 17 | 5 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.1667 | -20.7594 | 86.148 | -75 | -10.0807 | 53.6278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/5:00
1 | 17 | 6 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.2083 | -20.7515 | 86.148 | -75 | -10.0942 | 68.6244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/6:00
1 | 17 | 7 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.25 | -20.7435 | 86.148 | -75 | -10.1078 | 83.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/7:00
1 | 17 | 8 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.2917 | -20.7355 | 86.148 | -75 | -10.1214 | 98.6177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/8:00
1 | 17 | 9 | -10.6 | 18 | 12 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 18 | 0 | 0 | 39.791 | 17.3333 | -20.7276 | 86.148 | -75 | -10.1349 | 113.6143 | -6.1726 | 11.8274 | 3.7491 | 3.7491 | 0 | 0 | 0 | 1/17/9:00
1 | 17 | 10 | -9.4 | 69 | 370 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 69 | 0 | 0 | 39.791 | 17.375 | -20.7196 | 86.148 | -75 | -10.1485 | 128.6109 | -249.715 | -180.715 | -57.2835 | -57.2835 | 0 | 0 | 0 | 1/17/10:00
1 | 17 | 11 | -7.8 | 87 | 604 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 87 | 0 | 0 | 39.791 | 17.4167 | -20.7115 | 86.148 | -75 | -10.162 | 143.6075 | -486.1561 | -399.1561 | -126.5255 | -126.5255 | 0 | 0 | 0 | 1/17/11:00
1 | 17 | 12 | -6.7 | 103 | 698 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 103 | 0 | 0 | 39.791 | 17.4583 | -20.7035 | 86.148 | -75 | -10.1755 | 158.6041 | -625.0484 | -522.0484 | -165.4802 | -165.4802 | 0 | 0 | 0 | 1/17/12:00
1 | 17 | 13 | -6.1 | 111 | 734 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 111 | 0 | 0 | 39.791 | 17.5 | -20.6955 | 86.148 | -75 | -10.1889 | 173.6008 | -690.3241 | -579.3241 | -183.6356 | -183.6356 | 0 | 0 | 0 | 1/17/13:00
1 | 17 | 14 | -6.1 | 108 | 695 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 108 | 0 | 0 | 39.791 | 17.5417 | -20.6874 | 86.148 | -75 | -10.2024 | 188.5974 | -651.1115 | -543.1115 | -172.1569 | -172.1569 | 0 | 0 | 0 | 1/17/14:00
1 | 17 | 15 | -6.1 | 106 | 638 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 106 | 0 | 0 | 39.791 | 17.5833 | -20.6794 | 86.148 | -75 | -10.2158 | 203.594 | -564.4944 | -458.4944 | -145.3347 | -145.3347 | 0 | 0 | 0 | 1/17/15:00
1 | 17 | 16 | -6.7 | 101 | 499 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 101 | 0 | 0 | 39.791 | 17.625 | -20.6713 | 86.148 | -75 | -10.2292 | 218.5907 | -393.1326 | -292.1326 | -92.6009 | -92.6009 | 0 | 0 | 0 | 1/17/16:00
1 | 17 | 17 | -6.7 | 74 | 224 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 74 | 0 | 0 | 39.791 | 17.6667 | -20.6633 | 86.148 | -75 | -10.2426 | 233.5873 | -146.1835 | -72.1835 | -22.8809 | -22.8809 | 0 | 0 | 0 | 1/17/17:00
1 | 17 | 18 | -8.9 | 17 | 31 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 17 | 0 | 0 | 39.791 | 17.7083 | -20.6552 | 86.148 | -75 | -10.256 | 248.584 | -15.1367 | 1.8633 | 0.59062 | 0.59062 | 0 | 0 | 0 | 1/17/18:00
1 | 17 | 19 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.75 | -20.6471 | 86.148 | -75 | -10.2694 | 263.5806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/19:00
1 | 17 | 20 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.7917 | -20.639 | 86.148 | -75 | -10.2828 | 278.5773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/20:00
1 | 17 | 21 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.8333 | -20.6309 | 86.148 | -75 | -10.2961 | 293.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/21:00
1 | 17 | 22 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.875 | -20.6227 | 86.148 | -75 | -10.3094 | 308.5707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/22:00
1 | 17 | 23 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.9167 | -20.6146 | 86.148 | -75 | -10.3227 | 323.5673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/23:00
1 | 17 | 24 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 17.9583 | -20.6064 | 86.148 | -75 | -10.336 | 338.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/17/24:00
1 | 18 | 1 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18 | -20.5983 | 86.148 | -75 | -10.3492 | -6.4393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/1:00
1 | 18 | 2 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.0417 | -20.5901 | 86.148 | -75 | -10.3625 | 8.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/2:00
1 | 18 | 3 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.0833 | -20.5819 | 86.148 | -75 | -10.3757 | 23.5541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/3:00
1 | 18 | 4 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.125 | -20.5737 | 86.148 | -75 | -10.3889 | 38.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/4:00
1 | 18 | 5 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.1667 | -20.5655 | 86.148 | -75 | -10.4021 | 53.5475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/5:00
1 | 18 | 6 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.2083 | -20.5573 | 86.148 | -75 | -10.4153 | 68.5442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/6:00
1 | 18 | 7 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.25 | -20.5491 | 86.148 | -75 | -10.4284 | 83.5409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/7:00
1 | 18 | 8 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.2917 | -20.5409 | 86.148 | -75 | -10.4415 | 98.5376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/8:00
1 | 18 | 9 | -12.2 | 27 | 155 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 27 | 0 | 0 | 39.791 | 18.3333 | -20.5326 | 86.148 | -75 | -10.4547 | 113.5343 | -79.328 | -52.328 | -16.5871 | -16.5871 | 0 | 0 | 0 | 1/18/9:00
1 | 18 | 10 | -10 | 51 | 547 | 14 | 1 | 0 | 14 | 0 | 0 | 51 | 0 | 0 | 39.791 | 18.375 | -20.5244 | 86.148 | -75 | -10.4678 | 128.5311 | -367.943 | -316.943 | -100.4654 | -100.4654 | 0 | 0 | 0 | 1/18/10:00
1 | 18 | 11 | -8.3 | 66 | 718 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 66 | 0 | 0 | 39.791 | 18.4167 | -20.5161 | 86.148 | -75 | -10.4808 | 143.5278 | -576.5533 | -510.5533 | -161.8365 | -161.8365 | 0 | 0 | 0 | 1/18/11:00
1 | 18 | 12 | -7.2 | 81 | 744 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 81 | 0 | 0 | 39.791 | 18.4583 | -20.5078 | 86.148 | -75 | -10.4939 | 158.5245 | -665.0863 | -584.0863 | -185.1451 | -185.1451 | 0 | 0 | 0 | 1/18/12:00
1 | 18 | 13 | -6.1 | 161 | 306 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 161 | 0 | 0 | 39.791 | 18.5 | -20.4995 | 86.148 | -75 | -10.5069 | 173.5213 | -287.4117 | -126.4117 | -40.0703 | -40.0703 | 0 | 0 | 0 | 1/18/13:00
1 | 18 | 14 | -5.6 | 125 | 497 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 125 | 0 | 0 | 39.791 | 18.5417 | -20.4912 | 86.148 | -75 | -10.52 | 188.518 | -465.1238 | -340.1238 | -107.8133 | -107.8133 | 0 | 0 | 0 | 1/18/14:00
1 | 18 | 15 | -4.4 | 82 | 746 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 82 | 0 | 0 | 39.791 | 18.5833 | -20.4829 | 86.148 | -75 | -10.533 | 203.5148 | -659.449 | -577.449 | -183.0412 | -183.0412 | 0 | 0 | 0 | 1/18/15:00
1 | 18 | 16 | -3.9 | 64 | 698 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 64 | 0 | 0 | 39.791 | 18.625 | -20.4746 | 86.148 | -75 | -10.546 | 218.5115 | -549.4155 | -485.4155 | -153.8682 | -153.8682 | 0 | 0 | 0 | 1/18/16:00
1 | 18 | 17 | -3.9 | 52 | 426 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 52 | 0 | 0 | 39.791 | 18.6667 | -20.4663 | 86.148 | -75 | -10.5589 | 233.5083 | -277.7072 | -225.7072 | -71.5452 | -71.5452 | 0 | 0 | 0 | 1/18/17:00
1 | 18 | 18 | -6.1 | 24 | 46 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 24 | 0 | 0 | 39.791 | 18.7083 | -20.4579 | 86.148 | -75 | -10.5719 | 248.505 | -22.4242 | 1.5758 | 0.49951 | 0.49951 | 0 | 0 | 0 | 1/18/18:00
1 | 18 | 19 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.75 | -20.4496 | 86.148 | -75 | -10.5848 | 263.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/19:00
1 | 18 | 20 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.7917 | -20.4412 | 86.148 | -75 | -10.5977 | 278.4986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/20:00
1 | 18 | 21 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.8333 | -20.4328 | 86.148 | -75 | -10.6106 | 293.4953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/21:00
1 | 18 | 22 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.875 | -20.4245 | 86.148 | -75 | -10.6235 | 308.4921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/22:00
1 | 18 | 23 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.9167 | -20.4161 | 86.148 | -75 | -10.6364 | 323.4889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/23:00
1 | 18 | 24 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 18.9583 | -20.4077 | 86.148 | -75 | -10.6492 | 338.4857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/18/24:00
1 | 19 | 1 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19 | -20.3993 | 86.148 | -75 | -10.6621 | -6.5175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/1:00
1 | 19 | 2 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.0417 | -20.3908 | 86.148 | -75 | -10.6749 | 8.4793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/2:00
1 | 19 | 3 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.0833 | -20.3824 | 86.148 | -75 | -10.6876 | 23.4761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/3:00
1 | 19 | 4 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.125 | -20.374 | 86.148 | -75 | -10.7004 | 38.4729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/4:00
1 | 19 | 5 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.1667 | -20.3655 | 86.148 | -75 | -10.7132 | 53.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/5:00
1 | 19 | 6 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.2083 | -20.357 | 86.148 | -75 | -10.7259 | 68.4665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/6:00
1 | 19 | 7 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.25 | -20.3486 | 86.148 | -75 | -10.7386 | 83.4633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/7:00
1 | 19 | 8 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.2917 | -20.3401 | 86.148 | -75 | -10.7513 | 98.4602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/8:00
1 | 19 | 9 | -3.9 | 17 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 17 | 0 | 0 | 39.791 | 19.3333 | -20.3316 | 86.148 | -75 | -10.764 | 113.457 | 0 | 17 | 5.3887 | 5.3887 | 0 | 0 | 0 | 1/19/9:00
1 | 19 | 10 | -3.3 | 59 | 9 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 59 | 0 | 0 | 39.791 | 19.375 | -20.3231 | 86.148 | -75 | -10.7767 | 128.4538 | -6.0334 | 52.9666 | 16.7895 | 16.7895 | 0 | 0 | 0 | 1/19/10:00
1 | 19 | 11 | -3.3 | 85 | 10 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 85 | 0 | 0 | 39.791 | 19.4167 | -20.3145 | 86.148 | -75 | -10.7893 | 143.4507 | -8.0107 | 76.9893 | 24.4043 | 24.4043 | 0 | 0 | 0 | 1/19/11:00
1 | 19 | 12 | -2.2 | 164 | 8 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 164 | 0 | 0 | 39.791 | 19.4583 | -20.306 | 86.148 | -75 | -10.8019 | 158.4475 | -7.1387 | 156.8613 | 49.7223 | 49.7223 | 0 | 0 | 0 | 1/19/12:00
1 | 19 | 13 | -1.1 | 177 | 2 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 177 | 0 | 0 | 39.791 | 19.5 | -20.2975 | 86.148 | -75 | -10.8145 | 173.4444 | -1.8759 | 175.1241 | 55.5113 | 55.5113 | 0 | 0 | 0 | 1/19/13:00
1 | 19 | 14 | -0.6 | 239 | 8 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 239 | 0 | 0 | 39.791 | 19.5417 | -20.2889 | 86.148 | -75 | -10.8271 | 188.4412 | -7.4786 | 231.5214 | 73.3882 | 73.3882 | 0 | 0 | 0 | 1/19/14:00
1 | 19 | 15 | -0.6 | 192 | 4 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 192 | 0 | 0 | 39.791 | 19.5833 | -20.2804 | 86.148 | -75 | -10.8397 | 203.4381 | -3.5324 | 188.4676 | 59.7409 | 59.7409 | 0 | 0 | 0 | 1/19/15:00
1 | 19 | 16 | 0 | 151 | 2 | 32 | 1 | 0 | 32 | 0 | 0 | 151 | 0 | 0 | 39.791 | 19.625 | -20.2718 | 86.148 | -75 | -10.8522 | 218.4349 | -1.5727 | 149.4273 | 47.3658 | 47.3658 | 0 | 0 | 0 | 1/19/16:00
1 | 19 | 17 | 0.6 | 76 | 2 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 76 | 0 | 0 | 39.791 | 19.6667 | -20.2632 | 86.148 | -75 | -10.8647 | 233.4318 | -1.3022 | 74.6978 | 23.6779 | 23.6779 | 0 | 0 | 0 | 1/19/17:00
1 | 19 | 18 | 0 | 22 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 22 | 0 | 0 | 39.791 | 19.7083 | -20.2546 | 86.148 | -75 | -10.8773 | 248.4287 | 0 | 22 | 6.9736 | 6.9736 | 0 | 0 | 0 | 1/19/18:00
1 | 19 | 19 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.75 | -20.246 | 86.148 | -75 | -10.8897 | 263.4256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/19:00
1 | 19 | 20 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.7917 | -20.2374 | 86.148 | -75 | -10.9022 | 278.4224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/20:00
1 | 19 | 21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.8333 | -20.2288 | 86.148 | -75 | -10.9147 | 293.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/21:00
1 | 19 | 22 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.875 | -20.2202 | 86.148 | -75 | -10.9271 | 308.4162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/22:00
1 | 19 | 23 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.9167 | -20.2115 | 86.148 | -75 | -10.9395 | 323.4131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/23:00
1 | 19 | 24 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 19.9583 | -20.2029 | 86.148 | -75 | -10.9519 | 338.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/19/24:00
1 | 20 | 1 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20 | -20.1942 | 86.148 | -75 | -10.9643 | -6.5931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/1:00
1 | 20 | 2 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.0417 | -20.1855 | 86.148 | -75 | -10.9767 | 8.4038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/2:00
1 | 20 | 3 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.0833 | -20.1768 | 86.148 | -75 | -10.989 | 23.4007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/3:00
1 | 20 | 4 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.125 | -20.1681 | 86.148 | -75 | -11.0013 | 38.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/4:00
1 | 20 | 5 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.1667 | -20.1594 | 86.148 | -75 | -11.0136 | 53.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/5:00
1 | 20 | 6 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.2083 | -20.1507 | 86.148 | -75 | -11.0259 | 68.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/6:00
1 | 20 | 7 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.25 | -20.142 | 86.148 | -75 | -11.0382 | 83.3885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/7:00
1 | 20 | 8 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.2917 | -20.1333 | 86.148 | -75 | -11.0504 | 98.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/8:00
1 | 20 | 9 | -7.2 | 28 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 28 | 0 | 0 | 39.791 | 20.3333 | -20.1245 | 86.148 | -75 | -11.0627 | 113.3823 | 0 | 28 | 8.8755 | 8.8755 | 0 | 0 | 0 | 1/20/9:00
1 | 20 | 10 | -8.3 | 93 | 223 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 93 | 0 | 0 | 39.791 | 20.375 | -20.1158 | 86.148 | -75 | -11.0749 | 128.3793 | -148.9785 | -55.9785 | -17.7442 | -17.7442 | 0 | 0 | 0 | 1/20/10:00
1 | 20 | 11 | -8.9 | 94 | 568 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 94 | 0 | 0 | 39.791 | 20.4167 | -20.107 | 86.148 | -75 | -11.0871 | 143.3762 | -453.8936 | -359.8936 | -114.08 | -114.08 | 0 | 0 | 0 | 1/20/11:00
1 | 20 | 12 | -8.3 | 138 | 743 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 138 | 0 | 0 | 39.791 | 20.4583 | -20.0982 | 86.148 | -75 | -11.0992 | 158.3732 | -661.8018 | -523.8018 | -166.036 | -166.036 | 0 | 0 | 0 | 1/20/12:00
1 | 20 | 13 | -8.3 | 222 | 453 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 222 | 0 | 0 | 39.791 | 20.5 | -20.0894 | 86.148 | -75 | -11.1114 | 173.3702 | -424.2959 | -202.2959 | -64.1243 | -64.1243 | 0 | 0 | 0 | 1/20/13:00
1 | 20 | 14 | -7.8 | 277 | 294 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 277 | 0 | 0 | 39.791 | 20.5417 | -20.0806 | 86.148 | -75 | -11.1235 | 188.3671 | -274.516 | 2.484 | 0.78738 | 0.78738 | 0 | 0 | 0 | 1/20/14:00
1 | 20 | 15 | -7.2 | 205 | 23 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 205 | 0 | 0 | 39.791 | 20.5833 | -20.0718 | 86.148 | -75 | -11.1356 | 203.3641 | -20.2901 | 184.7099 | 58.5498 | 58.5498 | 0 | 0 | 0 | 1/20/15:00
1 | 20 | 16 | -7.2 | 112 | 19 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 112 | 0 | 0 | 39.791 | 20.625 | -20.063 | 86.148 | -75 | -11.1477 | 218.3611 | -14.9243 | 97.0757 | 30.7713 | 30.7713 | 0 | 0 | 0 | 1/20/16:00
1 | 20 | 17 | -7.8 | 78 | 12 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 78 | 0 | 0 | 39.791 | 20.6667 | -20.0542 | 86.148 | -75 | -11.1598 | 233.358 | -7.8028 | 70.1972 | 22.2513 | 22.2513 | 0 | 0 | 0 | 1/20/17:00
1 | 20 | 18 | -8.3 | 17 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 17 | 0 | 0 | 39.791 | 20.7083 | -20.0453 | 86.148 | -75 | -11.1719 | 248.355 | 0 | 17 | 5.3887 | 5.3887 | 0 | 0 | 0 | 1/20/18:00
1 | 20 | 19 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.75 | -20.0365 | 86.148 | -75 | -11.1839 | 263.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/19:00
1 | 20 | 20 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.7917 | -20.0276 | 86.148 | -75 | -11.1959 | 278.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/20:00
1 | 20 | 21 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.8333 | -20.0187 | 86.148 | -75 | -11.2079 | 293.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/21:00
1 | 20 | 22 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.875 | -20.0099 | 86.148 | -75 | -11.2199 | 308.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/22:00
1 | 20 | 23 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.9167 | -20.001 | 86.148 | -75 | -11.2319 | 323.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/23:00
1 | 20 | 24 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 20.9583 | -19.9921 | 86.148 | -75 | -11.2438 | 338.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/20/24:00
1 | 21 | 1 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21 | -19.9832 | 86.148 | -75 | -11.2557 | -6.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/1:00
1 | 21 | 2 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.0417 | -19.9742 | 86.148 | -75 | -11.2676 | 8.3311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/2:00
1 | 21 | 3 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.0833 | -19.9653 | 86.148 | -75 | -11.2795 | 23.3281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/3:00
1 | 21 | 4 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.125 | -19.9564 | 86.148 | -75 | -11.2914 | 38.3252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/4:00
1 | 21 | 5 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.1667 | -19.9474 | 86.148 | -75 | -11.3032 | 53.3222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/5:00
1 | 21 | 6 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.2083 | -19.9385 | 86.148 | -75 | -11.3151 | 68.3192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/6:00
1 | 21 | 7 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.25 | -19.9295 | 86.148 | -75 | -11.3269 | 83.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/7:00
1 | 21 | 8 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.2917 | -19.9205 | 86.148 | -75 | -11.3387 | 98.3133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/8:00
1 | 21 | 9 | -4.4 | 26 | 2 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 26 | 0 | 0 | 39.791 | 21.3333 | -19.9115 | 86.148 | -75 | -11.3504 | 113.3104 | -1.0077 | 24.9923 | 7.9221 | 7.9221 | 0 | 0 | 0 | 1/21/9:00
1 | 21 | 10 | -6.1 | 100 | 2 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 100 | 0 | 0 | 39.791 | 21.375 | -19.9025 | 86.148 | -75 | -11.3622 | 128.3075 | -1.3314 | 98.6686 | 31.2762 | 31.2762 | 0 | 0 | 0 | 1/21/10:00
1 | 21 | 11 | -6.1 | 131 | 692 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 131 | 0 | 0 | 39.791 | 21.4167 | -19.8935 | 86.148 | -75 | -11.3739 | 143.3045 | -551.6026 | -420.6026 | -133.3237 | -133.3237 | 0 | 0 | 0 | 1/21/11:00
1 | 21 | 12 | -6.1 | 119 | 737 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 119 | 0 | 0 | 39.791 | 21.4583 | -19.8845 | 86.148 | -75 | -11.3856 | 158.3016 | -655.2297 | -536.2297 | -169.9755 | -169.9755 | 0 | 0 | 0 | 1/21/12:00
1 | 21 | 13 | -5.6 | 135 | 738 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 135 | 0 | 0 | 39.791 | 21.5 | -19.8754 | 86.148 | -75 | -11.3973 | 173.2987 | -690.2209 | -555.2209 | -175.9953 | -175.9953 | 0 | 0 | 0 | 1/21/13:00
1 | 21 | 14 | -5.6 | 233 | 77 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 233 | 0 | 0 | 39.791 | 21.5417 | -19.8664 | 86.148 | -75 | -11.409 | 188.2958 | -71.8087 | 161.1913 | 51.0948 | 51.0948 | 0 | 0 | 0 | 1/21/14:00
1 | 21 | 15 | -5 | 160 | 729 | 23 | 1 | 0 | 23 | 0 | 0 | 160 | 0 | 0 | 39.791 | 21.5833 | -19.8573 | 86.148 | -75 | -11.4206 | 203.2928 | -642.384 | -482.384 | -152.9073 | -152.9073 | 0 | 0 | 0 | 1/21/15:00
1 | 21 | 16 | -5.6 | 205 | 59 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 205 | 0 | 0 | 39.791 | 21.625 | -19.8483 | 86.148 | -75 | -11.4323 | 218.2899 | -46.2892 | 158.7108 | 50.3086 | 50.3086 | 0 | 0 | 0 | 1/21/16:00
1 | 21 | 17 | -6.1 | 93 | 3 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 93 | 0 | 0 | 39.791 | 21.6667 | -19.8392 | 86.148 | -75 | -11.4439 | 233.287 | -1.9478 | 91.0522 | 28.8619 | 28.8619 | 0 | 0 | 0 | 1/21/17:00
1 | 21 | 18 | -6.1 | 18 | 1 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 18 | 0 | 0 | 39.791 | 21.7083 | -19.8301 | 86.148 | -75 | -11.4555 | 248.2841 | -0.48455 | 17.5154 | 5.5521 | 5.5521 | 0 | 0 | 0 | 1/21/18:00
1 | 21 | 19 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.75 | -19.821 | 86.148 | -75 | -11.4671 | 263.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/19:00
1 | 21 | 20 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.7917 | -19.8119 | 86.148 | -75 | -11.4786 | 278.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/20:00
1 | 21 | 21 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.8333 | -19.8028 | 86.148 | -75 | -11.4902 | 293.2755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/21:00
1 | 21 | 22 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.875 | -19.7937 | 86.148 | -75 | -11.5017 | 308.2726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/22:00
1 | 21 | 23 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.9167 | -19.7845 | 86.148 | -75 | -11.5132 | 323.2697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/23:00
1 | 21 | 24 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 21.9583 | -19.7754 | 86.148 | -75 | -11.5246 | 338.2668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/21/24:00
1 | 22 | 1 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22 | -19.7662 | 86.148 | -75 | -11.5361 | -6.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/1:00
1 | 22 | 2 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.0417 | -19.7571 | 86.148 | -75 | -11.5475 | 8.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/2:00
1 | 22 | 3 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.0833 | -19.7479 | 86.148 | -75 | -11.559 | 23.2583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/3:00
1 | 22 | 4 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.125 | -19.7387 | 86.148 | -75 | -11.5704 | 38.2554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/4:00
1 | 22 | 5 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.1667 | -19.7295 | 86.148 | -75 | -11.5817 | 53.2526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/5:00
1 | 22 | 6 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.2083 | -19.7203 | 86.148 | -75 | -11.5931 | 68.2497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/6:00
1 | 22 | 7 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.25 | -19.7111 | 86.148 | -75 | -11.6044 | 83.2469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/7:00
1 | 22 | 8 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.2917 | -19.7019 | 86.148 | -75 | -11.6158 | 98.2441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/8:00
1 | 22 | 9 | -6.7 | 28 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 28 | 0 | 0 | 39.791 | 22.3333 | -19.6926 | 86.148 | -75 | -11.6271 | 113.2412 | 0 | 28 | 8.8755 | 8.8755 | 0 | 0 | 0 | 1/22/9:00
1 | 22 | 10 | -6.7 | 76 | 412 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 76 | 0 | 0 | 39.791 | 22.375 | -19.6834 | 86.148 | -75 | -11.6383 | 128.2384 | -273.3017 | -197.3017 | -62.5412 | -62.5412 | 0 | 0 | 0 | 1/22/10:00
1 | 22 | 11 | -6.7 | 110 | 631 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 110 | 0 | 0 | 39.791 | 22.4167 | -19.6741 | 86.148 | -75 | -11.6496 | 143.2356 | -501.6992 | -391.6992 | -124.1618 | -124.1618 | 0 | 0 | 0 | 1/22/11:00
1 | 22 | 12 | -5.6 | 239 | 404 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 239 | 0 | 0 | 39.791 | 22.4583 | -19.6649 | 86.148 | -75 | -11.6609 | 158.2328 | -358.4877 | -119.4877 | -37.8755 | -37.8755 | 0 | 0 | 0 | 1/22/12:00
1 | 22 | 13 | -5.6 | 275 | 358 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 275 | 0 | 0 | 39.791 | 22.5 | -19.6556 | 86.148 | -75 | -11.6721 | 173.23 | -334.3134 | -59.3134 | -18.8013 | -18.8013 | 0 | 0 | 0 | 1/22/13:00
1 | 22 | 14 | -5 | 226 | 538 | 23 | 1 | 0 | 23 | 0 | 0 | 226 | 0 | 0 | 39.791 | 22.5417 | -19.6463 | 86.148 | -75 | -11.6833 | 188.2272 | -501.0816 | -275.0816 | -87.1961 | -87.1961 | 0 | 0 | 0 | 1/22/14:00
1 | 22 | 15 | -4.4 | 174 | 601 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 174 | 0 | 0 | 39.791 | 22.5833 | -19.637 | 86.148 | -75 | -11.6945 | 203.2244 | -528.9565 | -354.9565 | -112.515 | -112.515 | 0 | 0 | 0 | 1/22/15:00
1 | 22 | 16 | -4.4 | 169 | 207 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 169 | 0 | 0 | 39.791 | 22.625 | -19.6277 | 86.148 | -75 | -11.7056 | 218.2216 | -162.1974 | 6.8026 | 2.1563 | 2.1563 | 0 | 0 | 0 | 1/22/16:00
1 | 22 | 17 | -4.4 | 73 | 245 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 73 | 0 | 0 | 39.791 | 22.6667 | -19.6184 | 86.148 | -75 | -11.7168 | 233.2188 | -158.8211 | -85.8211 | -27.2038 | -27.2038 | 0 | 0 | 0 | 1/22/17:00
1 | 22 | 18 | -6.1 | 23 | 19 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 23 | 0 | 0 | 39.791 | 22.7083 | -19.6091 | 86.148 | -75 | -11.7279 | 248.216 | -9.1845 | 13.8155 | 4.3793 | 4.3793 | 0 | 0 | 0 | 1/22/18:00
1 | 22 | 19 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.75 | -19.5997 | 86.148 | -75 | -11.739 | 263.2133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/19:00
1 | 22 | 20 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.7917 | -19.5904 | 86.148 | -75 | -11.7501 | 278.2105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/20:00
1 | 22 | 21 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.8333 | -19.581 | 86.148 | -75 | -11.7611 | 293.2077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/21:00
1 | 22 | 22 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.875 | -19.5717 | 86.148 | -75 | -11.7722 | 308.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/22:00
1 | 22 | 23 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.9167 | -19.5623 | 86.148 | -75 | -11.7832 | 323.2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/23:00
1 | 22 | 24 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 22.9583 | -19.5529 | 86.148 | -75 | -11.7942 | 338.1994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/22/24:00
1 | 23 | 1 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23 | -19.5435 | 86.148 | -75 | -11.8052 | -6.8033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/1:00
1 | 23 | 2 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.0417 | -19.5341 | 86.148 | -75 | -11.8162 | 8.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/2:00
1 | 23 | 3 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.0833 | -19.5247 | 86.148 | -75 | -11.8271 | 23.1912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/3:00
1 | 23 | 4 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.125 | -19.5153 | 86.148 | -75 | -11.838 | 38.1885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/4:00
1 | 23 | 5 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.1667 | -19.5059 | 86.148 | -75 | -11.8489 | 53.1858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/5:00
1 | 23 | 6 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.2083 | -19.4964 | 86.148 | -75 | -11.8598 | 68.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/6:00
1 | 23 | 7 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.25 | -19.487 | 86.148 | -75 | -11.8707 | 83.1803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/7:00
1 | 23 | 8 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.2917 | -19.4775 | 86.148 | -75 | -11.8815 | 98.1776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/8:00
1 | 23 | 9 | -6.7 | 21 | 327 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 21 | 0 | 0 | 39.791 | 23.3333 | -19.468 | 86.148 | -75 | -11.8924 | 113.1749 | -162.9758 | -141.9758 | -45.0039 | -45.0039 | 0 | 0 | 0 | 1/23/9:00
1 | 23 | 10 | -5.6 | 40 | 669 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 40 | 0 | 0 | 39.791 | 23.375 | -19.4585 | 86.148 | -75 | -11.9032 | 128.1722 | -442.1785 | -402.1785 | -127.4836 | -127.4836 | 0 | 0 | 0 | 1/23/10:00
1 | 23 | 11 | -3.3 | 54 | 818 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 54 | 0 | 0 | 39.791 | 23.4167 | -19.449 | 86.148 | -75 | -11.9139 | 143.1695 | -648.6951 | -594.6951 | -188.508 | -188.508 | 0 | 0 | 0 | 1/23/11:00
1 | 23 | 12 | 0.6 | 63 | 872 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 63 | 0 | 0 | 39.791 | 23.4583 | -19.4395 | 86.148 | -75 | -11.9247 | 158.1668 | -772.246 | -709.246 | -224.8186 | -224.8186 | 0 | 0 | 0 | 1/23/12:00
1 | 23 | 13 | 5.6 | 68 | 901 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 68 | 0 | 0 | 39.791 | 23.5 | -19.43 | 86.148 | -75 | -11.9354 | 173.1641 | -840.0636 | -772.0636 | -244.7307 | -244.7307 | 0 | 0 | 0 | 1/23/13:00
1 | 23 | 14 | 6.7 | 68 | 897 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 68 | 0 | 0 | 39.791 | 23.5417 | -19.4205 | 86.148 | -75 | -11.9462 | 188.1615 | -834.3194 | -766.3194 | -242.9099 | -242.9099 | 0 | 0 | 0 | 1/23/14:00
1 | 23 | 15 | 7.8 | 63 | 871 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 63 | 0 | 0 | 39.791 | 23.5833 | -19.411 | 86.148 | -75 | -11.9569 | 203.1588 | -765.6137 | -702.6137 | -222.7163 | -222.7163 | 0 | 0 | 0 | 1/23/15:00
1 | 23 | 16 | 8.3 | 52 | 797 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 52 | 0 | 0 | 39.791 | 23.625 | -19.4014 | 86.148 | -75 | -11.9676 | 218.1561 | -623.6431 | -571.6431 | -181.2009 | -181.2009 | 0 | 0 | 0 | 1/23/16:00
1 | 23 | 17 | 8.3 | 38 | 649 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 38 | 0 | 0 | 39.791 | 23.6667 | -19.3919 | 86.148 | -75 | -11.9782 | 233.1534 | -419.9898 | -381.9898 | -121.0841 | -121.0841 | 0 | 0 | 0 | 1/23/17:00
1 | 23 | 18 | 6.7 | 19 | 257 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 19 | 0 | 0 | 39.791 | 23.7083 | -19.3823 | 86.148 | -75 | -11.9889 | 248.1508 | -123.913 | -104.913 | -33.2556 | -33.2556 | 0 | 0 | 0 | 1/23/18:00
1 | 23 | 19 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.75 | -19.3727 | 86.148 | -75 | -11.9995 | 263.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/19:00
1 | 23 | 20 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.7917 | -19.3632 | 86.148 | -75 | -12.0101 | 278.1455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/20:00
1 | 23 | 21 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.8333 | -19.3536 | 86.148 | -75 | -12.0207 | 293.1428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/21:00
1 | 23 | 22 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.875 | -19.344 | 86.148 | -75 | -12.0312 | 308.1402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/22:00
1 | 23 | 23 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.9167 | -19.3344 | 86.148 | -75 | -12.0418 | 323.1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/23:00
1 | 23 | 24 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 23.9583 | -19.3247 | 86.148 | -75 | -12.0523 | 338.1349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/23/24:00
1 | 24 | 1 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24 | -19.3151 | 86.148 | -75 | -12.0628 | -6.8677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/1:00
1 | 24 | 2 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.0417 | -19.3055 | 86.148 | -75 | -12.0733 | 8.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/2:00
1 | 24 | 3 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.0833 | -19.2958 | 86.148 | -75 | -12.0837 | 23.1271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/3:00
1 | 24 | 4 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.125 | -19.2862 | 86.148 | -75 | -12.0942 | 38.1245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/4:00
1 | 24 | 5 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.1667 | -19.2765 | 86.148 | -75 | -12.1046 | 53.1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/5:00
1 | 24 | 6 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.2083 | -19.2668 | 86.148 | -75 | -12.115 | 68.1192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/6:00
1 | 24 | 7 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.25 | -19.2571 | 86.148 | -75 | -12.1254 | 83.1167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/7:00
1 | 24 | 8 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.2917 | -19.2474 | 86.148 | -75 | -12.1357 | 98.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/8:00
1 | 24 | 9 | 0 | 23 | 18 | 32 | 1 | 0 | 32 | 0 | 0 | 23 | 0 | 0 | 39.791 | 24.3333 | -19.2377 | 86.148 | -75 | -12.1461 | 113.1115 | -8.9214 | 14.0786 | 4.4627 | 4.4627 | 0 | 0 | 0 | 1/24/9:00
1 | 24 | 10 | 0.6 | 100 | 71 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 100 | 0 | 0 | 39.791 | 24.375 | -19.228 | 86.148 | -75 | -12.1564 | 128.1089 | -46.7554 | 53.2446 | 16.8776 | 16.8776 | 0 | 0 | 0 | 1/24/10:00
1 | 24 | 11 | 0.6 | 172 | 239 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 172 | 0 | 0 | 39.791 | 24.4167 | -19.2183 | 86.148 | -75 | -12.1667 | 143.1063 | -189.0331 | -17.0331 | -5.3992 | -5.3992 | 0 | 0 | 0 | 1/24/11:00
1 | 24 | 12 | 1.7 | 221 | 239 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 221 | 0 | 0 | 39.791 | 24.4583 | -19.2085 | 86.148 | -75 | -12.177 | 158.1038 | -211.2336 | 9.7664 | 3.0958 | 3.0958 | 0 | 0 | 0 | 1/24/12:00
1 | 24 | 13 | 1.7 | 215 | 70 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 215 | 0 | 0 | 39.791 | 24.5 | -19.1988 | 86.148 | -75 | -12.1872 | 173.1012 | -65.1597 | 149.8403 | 47.4967 | 47.4967 | 0 | 0 | 0 | 1/24/13:00
1 | 24 | 14 | 1.7 | 219 | 70 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 219 | 0 | 0 | 39.791 | 24.5417 | -19.189 | 86.148 | -75 | -12.1975 | 188.0986 | -65.0167 | 153.9833 | 48.81 | 48.81 | 0 | 0 | 0 | 1/24/14:00
1 | 24 | 15 | 2.8 | 186 | 145 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 186 | 0 | 0 | 39.791 | 24.5833 | -19.1793 | 86.148 | -75 | -12.2077 | 203.0961 | -127.2837 | 58.7163 | 18.612 | 18.612 | 0 | 0 | 0 | 1/24/15:00
1 | 24 | 16 | 3.3 | 174 | 220 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 174 | 0 | 0 | 39.791 | 24.625 | -19.1695 | 86.148 | -75 | -12.2179 | 218.0935 | -171.8948 | 2.1052 | 0.66731 | 0.66731 | 0 | 0 | 0 | 1/24/16:00
1 | 24 | 17 | 1.7 | 91 | 210 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 91 | 0 | 0 | 39.791 | 24.6667 | -19.1597 | 86.148 | -75 | -12.2281 | 233.091 | -135.6463 | -44.6463 | -14.1521 | -14.1521 | 0 | 0 | 0 | 1/24/17:00
1 | 24 | 18 | 0 | 28 | 39 | 32 | 1 | 0 | 32 | 0 | 0 | 28 | 0 | 0 | 39.791 | 24.7083 | -19.1499 | 86.148 | -75 | -12.2382 | 248.0884 | -18.7519 | 9.2481 | 2.9315 | 2.9315 | 0 | 0 | 0 | 1/24/18:00
1 | 24 | 19 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.75 | -19.1401 | 86.148 | -75 | -12.2484 | 263.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/19:00
1 | 24 | 20 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.7917 | -19.1303 | 86.148 | -75 | -12.2585 | 278.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/20:00
1 | 24 | 21 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.8333 | -19.1205 | 86.148 | -75 | -12.2686 | 293.0809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/21:00
1 | 24 | 22 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.875 | -19.1106 | 86.148 | -75 | -12.2786 | 308.0783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/22:00
1 | 24 | 23 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.9167 | -19.1008 | 86.148 | -75 | -12.2887 | 323.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/23:00
1 | 24 | 24 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 24.9583 | -19.0909 | 86.148 | -75 | -12.2987 | 338.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/24/24:00
1 | 25 | 1 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25 | -19.0811 | 86.148 | -75 | -12.3087 | -6.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/1:00
1 | 25 | 2 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.0417 | -19.0712 | 86.148 | -75 | -12.3187 | 8.0683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/2:00
1 | 25 | 3 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.0833 | -19.0613 | 86.148 | -75 | -12.3287 | 23.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/3:00
1 | 25 | 4 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.125 | -19.0514 | 86.148 | -75 | -12.3386 | 38.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/4:00
1 | 25 | 5 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.1667 | -19.0415 | 86.148 | -75 | -12.3486 | 53.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/5:00
1 | 25 | 6 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.2083 | -19.0316 | 86.148 | -75 | -12.3585 | 68.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/6:00
1 | 25 | 7 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.25 | -19.0217 | 86.148 | -75 | -12.3684 | 83.0559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/7:00
1 | 25 | 8 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.2917 | -19.0117 | 86.148 | -75 | -12.3782 | 98.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/8:00
1 | 25 | 9 | -0.6 | 15 | 3 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 15 | 0 | 0 | 39.791 | 25.3333 | -19.0018 | 86.148 | -75 | -12.3881 | 113.051 | -1.4785 | 13.5215 | 4.2861 | 4.2861 | 0 | 0 | 0 | 1/25/9:00
1 | 25 | 10 | 0 | 50 | 12 | 32 | 1 | 0 | 32 | 0 | 0 | 50 | 0 | 0 | 39.791 | 25.375 | -18.9919 | 86.148 | -75 | -12.3979 | 128.0485 | -7.8729 | 42.1271 | 13.3536 | 13.3536 | 0 | 0 | 0 | 1/25/10:00
1 | 25 | 11 | 0.6 | 71 | 2 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 71 | 0 | 0 | 39.791 | 25.4167 | -18.9819 | 86.148 | -75 | -12.4077 | 143.0461 | -1.5776 | 69.4224 | 22.0057 | 22.0057 | 0 | 0 | 0 | 1/25/11:00
1 | 25 | 12 | 1.1 | 96 | 6 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 96 | 0 | 0 | 39.791 | 25.4583 | -18.9719 | 86.148 | -75 | -12.4175 | 158.0436 | -5.292 | 90.708 | 28.7528 | 28.7528 | 0 | 0 | 0 | 1/25/12:00
1 | 25 | 13 | 1.7 | 169 | 6 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 169 | 0 | 0 | 39.791 | 25.5 | -18.962 | 86.148 | -75 | -12.4273 | 173.0412 | -5.5758 | 163.4242 | 51.8026 | 51.8026 | 0 | 0 | 0 | 1/25/13:00
1 | 25 | 14 | 2.8 | 130 | 4 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 130 | 0 | 0 | 39.791 | 25.5417 | -18.952 | 86.148 | -75 | -12.437 | 188.0388 | -3.7098 | 126.2902 | 40.0318 | 40.0318 | 0 | 0 | 0 | 1/25/14:00
1 | 25 | 15 | 5 | 113 | 2 | 41 | 1 | 0 | 41 | 0 | 0 | 113 | 0 | 0 | 39.791 | 25.5833 | -18.942 | 86.148 | -75 | -12.4467 | 203.0363 | -1.7531 | 111.2469 | 35.2633 | 35.2633 | 0 | 0 | 0 | 1/25/15:00
1 | 25 | 16 | 6.7 | 87 | 1 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 87 | 0 | 0 | 39.791 | 25.625 | -18.932 | 86.148 | -75 | -12.4564 | 218.0339 | -0.78012 | 86.2199 | 27.3302 | 27.3302 | 0 | 0 | 0 | 1/25/16:00
1 | 25 | 17 | 7.8 | 54 | 2 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 54 | 0 | 0 | 39.791 | 25.6667 | -18.9219 | 86.148 | -75 | -12.4661 | 233.0315 | -1.2893 | 52.7107 | 16.7084 | 16.7084 | 0 | 0 | 0 | 1/25/17:00
1 | 25 | 18 | 8.3 | 14 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 14 | 0 | 0 | 39.791 | 25.7083 | -18.9119 | 86.148 | -75 | -12.4758 | 248.0291 | 0 | 14 | 4.4378 | 4.4378 | 0 | 0 | 0 | 1/25/18:00
1 | 25 | 19 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.75 | -18.9019 | 86.148 | -75 | -12.4854 | 263.0267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/19:00
1 | 25 | 20 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.7917 | -18.8918 | 86.148 | -75 | -12.495 | 278.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/20:00
1 | 25 | 21 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.8333 | -18.8818 | 86.148 | -75 | -12.5046 | 293.0218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/21:00
1 | 25 | 22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.875 | -18.8717 | 86.148 | -75 | -12.5142 | 308.0195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/22:00
1 | 25 | 23 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.9167 | -18.8616 | 86.148 | -75 | -12.5237 | 323.0171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/23:00
1 | 25 | 24 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 25.9583 | -18.8516 | 86.148 | -75 | -12.5333 | 338.0147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/25/24:00
1 | 26 | 1 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26 | -18.8415 | 86.148 | -75 | -12.5428 | -6.9877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/1:00
1 | 26 | 2 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.0417 | -18.8314 | 86.148 | -75 | -12.5523 | 8.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/2:00
1 | 26 | 3 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.0833 | -18.8213 | 86.148 | -75 | -12.5617 | 23.0076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/3:00
1 | 26 | 4 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.125 | -18.8111 | 86.148 | -75 | -12.5712 | 38.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/4:00
1 | 26 | 5 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.1667 | -18.801 | 86.148 | -75 | -12.5806 | 53.0028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/5:00
1 | 26 | 6 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.2083 | -18.7909 | 86.148 | -75 | -12.59 | 68.0005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/6:00
1 | 26 | 7 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.25 | -18.7807 | 86.148 | -75 | -12.5994 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/7:00
1 | 26 | 8 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.2917 | -18.7706 | 86.148 | -75 | -12.6088 | 97.9958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/8:00
1 | 26 | 9 | -1.1 | 33 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 33 | 0 | 0 | 39.791 | 26.3333 | -18.7604 | 86.148 | -75 | -12.6181 | 112.9935 | 0 | 33 | 10.4604 | 10.4604 | 0 | 0 | 0 | 1/26/9:00
1 | 26 | 10 | -1.1 | 111 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 111 | 0 | 0 | 39.791 | 26.375 | -18.7502 | 86.148 | -75 | -12.6275 | 127.9911 | 0 | 111 | 35.1851 | 35.1851 | 0 | 0 | 0 | 1/26/10:00
1 | 26 | 11 | -1.1 | 200 | 1 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 200 | 0 | 0 | 39.791 | 26.4167 | -18.74 | 86.148 | -75 | -12.6368 | 142.9888 | -0.78665 | 199.2133 | 63.1472 | 63.1472 | 0 | 0 | 0 | 1/26/11:00
1 | 26 | 12 | -1.1 | 254 | 1 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 254 | 0 | 0 | 39.791 | 26.4583 | -18.7298 | 86.148 | -75 | -12.646 | 157.9865 | -0.88015 | 253.1199 | 80.2346 | 80.2346 | 0 | 0 | 0 | 1/26/12:00
1 | 26 | 13 | -1.1 | 257 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 257 | 0 | 0 | 39.791 | 26.5 | -18.7196 | 86.148 | -75 | -12.6553 | 172.9842 | 0 | 257 | 81.4645 | 81.4645 | 0 | 0 | 0 | 1/26/13:00
1 | 26 | 14 | -1.1 | 244 | 1 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 244 | 0 | 0 | 39.791 | 26.5417 | -18.7094 | 86.148 | -75 | -12.6646 | 187.9819 | -0.92602 | 243.074 | 77.0502 | 77.0502 | 0 | 0 | 0 | 1/26/14:00
1 | 26 | 15 | -1.7 | 228 | 1 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 228 | 0 | 0 | 39.791 | 26.5833 | -18.6992 | 86.148 | -75 | -12.6738 | 202.9796 | -0.87525 | 227.1248 | 71.9946 | 71.9946 | 0 | 0 | 0 | 1/26/15:00
1 | 26 | 16 | -1.7 | 180 | 1 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 180 | 0 | 0 | 39.791 | 26.625 | -18.689 | 86.148 | -75 | -12.683 | 217.9773 | -0.77882 | 179.2212 | 56.81 | 56.81 | 0 | 0 | 0 | 1/26/16:00
1 | 26 | 17 | -2.2 | 111 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 111 | 0 | 0 | 39.791 | 26.6667 | -18.6787 | 86.148 | -75 | -12.6921 | 232.975 | 0 | 111 | 35.1851 | 35.1851 | 0 | 0 | 0 | 1/26/17:00
1 | 26 | 18 | -3.3 | 31 | 11 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 31 | 0 | 0 | 39.791 | 26.7083 | -18.6685 | 86.148 | -75 | -12.7013 | 247.9727 | -5.2566 | 25.7434 | 8.1602 | 8.1602 | 0 | 0 | 0 | 1/26/18:00
1 | 26 | 19 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.75 | -18.6582 | 86.148 | -75 | -12.7104 | 262.9704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/19:00
1 | 26 | 20 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.7917 | -18.6479 | 86.148 | -75 | -12.7196 | 277.9681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/20:00
1 | 26 | 21 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.8333 | -18.6377 | 86.148 | -75 | -12.7286 | 292.9658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/21:00
1 | 26 | 22 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.875 | -18.6274 | 86.148 | -75 | -12.7377 | 307.9636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/22:00
1 | 26 | 23 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.9167 | -18.6171 | 86.148 | -75 | -12.7468 | 322.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/23:00
1 | 26 | 24 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 26.9583 | -18.6068 | 86.148 | -75 | -12.7558 | 337.9591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/26/24:00
1 | 27 | 1 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27 | -18.5964 | 86.148 | -75 | -12.7648 | -7.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/1:00
1 | 27 | 2 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.0417 | -18.5861 | 86.148 | -75 | -12.7738 | 7.9546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/2:00
1 | 27 | 3 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.0833 | -18.5758 | 86.148 | -75 | -12.7828 | 22.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/3:00
1 | 27 | 4 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.125 | -18.5654 | 86.148 | -75 | -12.7917 | 37.9501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/4:00
1 | 27 | 5 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.1667 | -18.5551 | 86.148 | -75 | -12.8006 | 52.9478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/5:00
1 | 27 | 6 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.2083 | -18.5447 | 86.148 | -75 | -12.8095 | 67.9456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/6:00
1 | 27 | 7 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.25 | -18.5344 | 86.148 | -75 | -12.8184 | 82.9434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/7:00
1 | 27 | 8 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.2917 | -18.524 | 86.148 | -75 | -12.8273 | 97.9412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/8:00
1 | 27 | 9 | -11.1 | 27 | 96 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 27 | 0 | 0 | 39.791 | 27.3333 | -18.5136 | 86.148 | -75 | -12.8361 | 112.939 | -46.7707 | -19.7707 | -6.267 | -6.267 | 0 | 0 | 0 | 1/27/9:00
1 | 27 | 10 | -10 | 69 | 422 | 14 | 1 | 0 | 14 | 0 | 0 | 69 | 0 | 0 | 39.791 | 27.375 | -18.5032 | 86.148 | -75 | -12.8449 | 127.9368 | -274.7562 | -205.7562 | -65.2211 | -65.2211 | 0 | 0 | 0 | 1/27/10:00
1 | 27 | 11 | -8.3 | 113 | 539 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 113 | 0 | 0 | 39.791 | 27.4167 | -18.4928 | 86.148 | -75 | -12.8537 | 142.9346 | -422.8269 | -309.8269 | -98.2097 | -98.2097 | 0 | 0 | 0 | 1/27/11:00
1 | 27 | 12 | -7.2 | 111 | 704 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 111 | 0 | 0 | 39.791 | 27.4583 | -18.4823 | 86.148 | -75 | -12.8625 | 157.9324 | -618.2872 | -507.2872 | -160.8012 | -160.8012 | 0 | 0 | 0 | 1/27/12:00
1 | 27 | 13 | -6.7 | 129 | 693 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 129 | 0 | 0 | 39.791 | 27.5 | -18.4719 | 86.148 | -75 | -12.8713 | 172.9302 | -641.7382 | -512.7382 | -162.529 | -162.529 | 0 | 0 | 0 | 1/27/13:00
1 | 27 | 14 | -6.1 | 134 | 672 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 134 | 0 | 0 | 39.791 | 27.5417 | -18.4615 | 86.148 | -75 | -12.88 | 187.928 | -621.2894 | -487.2894 | -154.4622 | -154.4622 | 0 | 0 | 0 | 1/27/14:00
1 | 27 | 15 | -5.6 | 141 | 498 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 141 | 0 | 0 | 39.791 | 27.5833 | -18.451 | 86.148 | -75 | -12.8887 | 202.9258 | -435.1838 | -294.1838 | -93.2511 | -93.2511 | 0 | 0 | 0 | 1/27/15:00
1 | 27 | 16 | -5.6 | 125 | 466 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 125 | 0 | 0 | 39.791 | 27.625 | -18.4406 | 86.148 | -75 | -12.8974 | 217.9237 | -362.2887 | -237.2887 | -75.2164 | -75.2164 | 0 | 0 | 0 | 1/27/16:00
1 | 27 | 17 | -6.1 | 98 | 196 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 98 | 0 | 0 | 39.791 | 27.6667 | -18.4301 | 86.148 | -75 | -12.9061 | 232.9215 | -125.7998 | -27.7998 | -8.8121 | -8.8121 | 0 | 0 | 0 | 1/27/17:00
1 | 27 | 18 | -7.2 | 26 | 31 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 26 | 0 | 0 | 39.791 | 27.7083 | -18.4196 | 86.148 | -75 | -12.9147 | 247.9193 | -14.7643 | 11.2357 | 3.5615 | 3.5615 | 0 | 0 | 0 | 1/27/18:00
1 | 27 | 19 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.75 | -18.4092 | 86.148 | -75 | -12.9233 | 262.9172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/19:00
1 | 27 | 20 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.7917 | -18.3987 | 86.148 | -75 | -12.9319 | 277.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/20:00
1 | 27 | 21 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.8333 | -18.3882 | 86.148 | -75 | -12.9405 | 292.9129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/21:00
1 | 27 | 22 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.875 | -18.3777 | 86.148 | -75 | -12.9491 | 307.9107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/22:00
1 | 27 | 23 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.9167 | -18.3671 | 86.148 | -75 | -12.9576 | 322.9086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/23:00
1 | 27 | 24 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 27.9583 | -18.3566 | 86.148 | -75 | -12.9661 | 337.9065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/27/24:00
1 | 28 | 1 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28 | -18.3461 | 86.148 | -75 | -12.9746 | -7.0957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/1:00
1 | 28 | 2 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.0417 | -18.3355 | 86.148 | -75 | -12.9831 | 7.9022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/2:00
1 | 28 | 3 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.0833 | -18.325 | 86.148 | -75 | -12.9916 | 22.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/3:00
1 | 28 | 4 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.125 | -18.3144 | 86.148 | -75 | -13 | 37.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/4:00
1 | 28 | 5 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.1667 | -18.3038 | 86.148 | -75 | -13.0084 | 52.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/5:00
1 | 28 | 6 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.2083 | -18.2932 | 86.148 | -75 | -13.0168 | 67.8938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/6:00
1 | 28 | 7 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.25 | -18.2826 | 86.148 | -75 | -13.0252 | 82.8917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/7:00
1 | 28 | 8 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.2917 | -18.272 | 86.148 | -75 | -13.0335 | 97.8896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/8:00
1 | 28 | 9 | -8.3 | 34 | 16 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 34 | 0 | 0 | 39.791 | 28.3333 | -18.2614 | 86.148 | -75 | -13.0418 | 112.8875 | -7.7494 | 26.2506 | 8.321 | 8.321 | 0 | 0 | 0 | 1/28/9:00
1 | 28 | 10 | -6.1 | 108 | 194 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 108 | 0 | 0 | 39.791 | 28.375 | -18.2508 | 86.148 | -75 | -13.0501 | 127.8855 | -125.818 | -17.818 | -5.648 | -5.648 | 0 | 0 | 0 | 1/28/10:00
1 | 28 | 11 | -3.9 | 172 | 99 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 172 | 0 | 0 | 39.791 | 28.4167 | -18.2402 | 86.148 | -75 | -13.0584 | 142.8834 | -77.4424 | 94.5576 | 29.9731 | 29.9731 | 0 | 0 | 0 | 1/28/11:00
1 | 28 | 12 | -1.1 | 232 | 197 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 232 | 0 | 0 | 39.791 | 28.4583 | -18.2295 | 86.148 | -75 | -13.0667 | 157.8813 | -172.6338 | 59.3662 | 18.8181 | 18.8181 | 0 | 0 | 0 | 1/28/12:00
1 | 28 | 13 | 0 | 221 | 292 | 32 | 1 | 0 | 32 | 0 | 0 | 221 | 0 | 0 | 39.791 | 28.5 | -18.2189 | 86.148 | -75 | -13.0749 | 172.8793 | -269.9033 | -48.9033 | -15.5015 | -15.5015 | 0 | 0 | 0 | 1/28/13:00
1 | 28 | 14 | 1.7 | 262 | 160 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 262 | 0 | 0 | 39.791 | 28.5417 | -18.2082 | 86.148 | -75 | -13.0831 | 187.8772 | -147.68 | 114.32 | 36.2375 | 36.2375 | 0 | 0 | 0 | 1/28/14:00
1 | 28 | 15 | 2.2 | 163 | 119 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 163 | 0 | 0 | 39.791 | 28.5833 | -18.1976 | 86.148 | -75 | -13.0913 | 202.8752 | -103.8169 | 59.1831 | 18.76 | 18.76 | 0 | 0 | 0 | 1/28/15:00
1 | 28 | 16 | 2.8 | 190 | 237 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 190 | 0 | 0 | 39.791 | 28.625 | -18.1869 | 86.148 | -75 | -13.0995 | 217.8731 | -183.9102 | 6.0898 | 1.9304 | 1.9304 | 0 | 0 | 0 | 1/28/16:00
1 | 28 | 17 | 2.2 | 102 | 202 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 102 | 0 | 0 | 39.791 | 28.6667 | -18.1762 | 86.148 | -75 | -13.1077 | 232.8711 | -129.3406 | -27.3406 | -8.6665 | -8.6665 | 0 | 0 | 0 | 1/28/17:00
1 | 28 | 18 | 1.7 | 24 | 136 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 24 | 0 | 0 | 39.791 | 28.7083 | -18.1655 | 86.148 | -75 | -13.1158 | 247.869 | -64.5411 | -40.5411 | -12.8508 | -12.8508 | 0 | 0 | 0 | 1/28/18:00
1 | 28 | 19 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.75 | -18.1548 | 86.148 | -75 | -13.1239 | 262.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/19:00
1 | 28 | 20 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.7917 | -18.1441 | 86.148 | -75 | -13.132 | 277.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/20:00
1 | 28 | 21 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.8333 | -18.1334 | 86.148 | -75 | -13.1401 | 292.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/21:00
1 | 28 | 22 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.875 | -18.1227 | 86.148 | -75 | -13.1481 | 307.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/22:00
1 | 28 | 23 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.9167 | -18.1119 | 86.148 | -75 | -13.1561 | 322.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/23:00
1 | 28 | 24 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 28.9583 | -18.1012 | 86.148 | -75 | -13.1641 | 337.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/28/24:00
1 | 29 | 1 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29 | -18.0904 | 86.148 | -75 | -13.1721 | -7.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/1:00
1 | 29 | 2 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.0417 | -18.0797 | 86.148 | -75 | -13.1801 | 7.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/2:00
1 | 29 | 3 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.0833 | -18.0689 | 86.148 | -75 | -13.188 | 22.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/3:00
1 | 29 | 4 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.125 | -18.0581 | 86.148 | -75 | -13.1959 | 37.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/4:00
1 | 29 | 5 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.1667 | -18.0473 | 86.148 | -75 | -13.2038 | 52.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/5:00
1 | 29 | 6 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.2083 | -18.0365 | 86.148 | -75 | -13.2117 | 67.8451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/6:00
1 | 29 | 7 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.25 | -18.0257 | 86.148 | -75 | -13.2196 | 82.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/7:00
1 | 29 | 8 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.2917 | -18.0149 | 86.148 | -75 | -13.2274 | 97.8412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/8:00
1 | 29 | 9 | -2.2 | 37 | 11 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 37 | 0 | 0 | 39.791 | 29.3333 | -18.0041 | 86.148 | -75 | -13.2352 | 112.8392 | -5.296 | 31.704 | 10.0496 | 10.0496 | 0 | 0 | 0 | 1/29/9:00
1 | 29 | 10 | -2.2 | 106 | 217 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 106 | 0 | 0 | 39.791 | 29.375 | -17.9932 | 86.148 | -75 | -13.243 | 127.8373 | -140.179 | -34.179 | -10.8342 | -10.8342 | 0 | 0 | 0 | 1/29/10:00
1 | 29 | 11 | -1.1 | 171 | 234 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 171 | 0 | 0 | 39.791 | 29.4167 | -17.9824 | 86.148 | -75 | -13.2507 | 142.8353 | -182.5191 | -11.5191 | -3.6514 | -3.6514 | 0 | 0 | 0 | 1/29/11:00
1 | 29 | 12 | -0.6 | 126 | 652 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 126 | 0 | 0 | 39.791 | 29.4583 | -17.9715 | 86.148 | -75 | -13.2585 | 157.8334 | -570.0694 | -444.0694 | -140.7622 | -140.7622 | 0 | 0 | 0 | 1/29/12:00
1 | 29 | 13 | -0.6 | 213 | 303 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 213 | 0 | 0 | 39.791 | 29.5 | -17.9607 | 86.148 | -75 | -13.2662 | 172.8315 | -279.5404 | -66.5404 | -21.0921 | -21.0921 | 0 | 0 | 0 | 1/29/13:00
1 | 29 | 14 | 0 | 193 | 277 | 32 | 1 | 0 | 32 | 0 | 0 | 193 | 0 | 0 | 39.791 | 29.5417 | -17.9498 | 86.148 | -75 | -13.2739 | 187.8295 | -255.2289 | -62.2289 | -19.7255 | -19.7255 | 0 | 0 | 0 | 1/29/14:00
1 | 29 | 15 | -1.1 | 155 | 326 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 155 | 0 | 0 | 39.791 | 29.5833 | -17.9389 | 86.148 | -75 | -13.2816 | 202.8276 | -283.9105 | -128.9105 | -40.8624 | -40.8624 | 0 | 0 | 0 | 1/29/15:00
1 | 29 | 16 | -1.7 | 119 | 511 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 119 | 0 | 0 | 39.791 | 29.625 | -17.928 | 86.148 | -75 | -13.2892 | 217.8257 | -395.751 | -276.751 | -87.7252 | -87.7252 | 0 | 0 | 0 | 1/29/16:00
1 | 29 | 17 | -1.1 | 79 | 394 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 79 | 0 | 0 | 39.791 | 29.6667 | -17.9171 | 86.148 | -75 | -13.2969 | 232.8238 | -251.6396 | -172.6396 | -54.7237 | -54.7237 | 0 | 0 | 0 | 1/29/17:00
1 | 29 | 18 | -1.7 | 27 | 51 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 27 | 0 | 0 | 39.791 | 29.7083 | -17.9062 | 86.148 | -75 | -13.3045 | 247.8219 | -24.1116 | 2.8884 | 0.91558 | 0.91558 | 0 | 0 | 0 | 1/29/18:00
1 | 29 | 19 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.75 | -17.8953 | 86.148 | -75 | -13.3121 | 262.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/19:00
1 | 29 | 20 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.7917 | -17.8844 | 86.148 | -75 | -13.3196 | 277.8181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/20:00
1 | 29 | 21 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.8333 | -17.8734 | 86.148 | -75 | -13.3272 | 292.8162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/21:00
1 | 29 | 22 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.875 | -17.8625 | 86.148 | -75 | -13.3347 | 307.8143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/22:00
1 | 29 | 23 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.9167 | -17.8516 | 86.148 | -75 | -13.3422 | 322.8124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/23:00
1 | 29 | 24 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 29.9583 | -17.8406 | 86.148 | -75 | -13.3497 | 337.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/29/24:00
1 | 30 | 1 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30 | -17.8296 | 86.148 | -75 | -13.3571 | -7.1913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/1:00
1 | 30 | 2 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.0417 | -17.8186 | 86.148 | -75 | -13.3646 | 7.8069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/2:00
1 | 30 | 3 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.0833 | -17.8077 | 86.148 | -75 | -13.372 | 22.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/3:00
1 | 30 | 4 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.125 | -17.7967 | 86.148 | -75 | -13.3794 | 37.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/4:00
1 | 30 | 5 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.1667 | -17.7857 | 86.148 | -75 | -13.3868 | 52.8013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/5:00
1 | 30 | 6 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.2083 | -17.7746 | 86.148 | -75 | -13.3941 | 67.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/6:00
1 | 30 | 7 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.25 | -17.7636 | 86.148 | -75 | -13.4014 | 82.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/7:00
1 | 30 | 8 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.2917 | -17.7526 | 86.148 | -75 | -13.4087 | 97.7958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/8:00
1 | 30 | 9 | 1.1 | 28 | 2 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 28 | 0 | 0 | 39.791 | 30.3333 | -17.7416 | 86.148 | -75 | -13.416 | 112.794 | -0.9571 | 27.0429 | 8.5721 | 8.5721 | 0 | 0 | 0 | 1/30/9:00
1 | 30 | 10 | 1.1 | 90 | 9 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 90 | 0 | 0 | 39.791 | 30.375 | -17.7305 | 86.148 | -75 | -13.4233 | 127.7922 | -5.7906 | 84.2094 | 26.6929 | 26.6929 | 0 | 0 | 0 | 1/30/10:00
1 | 30 | 11 | 0.6 | 147 | 6 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 147 | 0 | 0 | 39.791 | 30.4167 | -17.7195 | 86.148 | -75 | -13.4305 | 142.7904 | -4.6663 | 142.3337 | 45.1173 | 45.1173 | 0 | 0 | 0 | 1/30/11:00
1 | 30 | 12 | 0.6 | 197 | 3 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 197 | 0 | 0 | 39.791 | 30.4583 | -17.7084 | 86.148 | -75 | -13.4378 | 157.7886 | -2.617 | 194.383 | 61.616 | 61.616 | 0 | 0 | 0 | 1/30/12:00
1 | 30 | 13 | -0.6 | 198 | 2 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 198 | 0 | 0 | 39.791 | 30.5 | -17.6973 | 86.148 | -75 | -13.4449 | 172.7868 | -1.8416 | 196.1584 | 62.1788 | 62.1788 | 0 | 0 | 0 | 1/30/13:00
1 | 30 | 14 | -1.1 | 230 | 4 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 230 | 0 | 0 | 39.791 | 30.5417 | -17.6862 | 86.148 | -75 | -13.4521 | 187.785 | -3.679 | 226.321 | 71.7398 | 71.7398 | 0 | 0 | 0 | 1/30/14:00
1 | 30 | 15 | -1.1 | 198 | 4 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 198 | 0 | 0 | 39.791 | 30.5833 | -17.6751 | 86.148 | -75 | -13.4593 | 202.7832 | -3.4772 | 194.5228 | 61.6603 | 61.6603 | 0 | 0 | 0 | 1/30/15:00
1 | 30 | 16 | -1.7 | 180 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 180 | 0 | 0 | 39.791 | 30.625 | -17.664 | 86.148 | -75 | -13.4664 | 217.7814 | 0 | 180 | 57.0569 | 57.0569 | 0 | 0 | 0 | 1/30/16:00
1 | 30 | 17 | -2.2 | 108 | 1 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 108 | 0 | 0 | 39.791 | 30.6667 | -17.6529 | 86.148 | -75 | -13.4735 | 232.7796 | -0.63697 | 107.363 | 34.0322 | 34.0322 | 0 | 0 | 0 | 1/30/17:00
1 | 30 | 18 | -2.8 | 35 | 1 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 35 | 0 | 0 | 39.791 | 30.7083 | -17.6418 | 86.148 | -75 | -13.4806 | 247.7779 | -0.47089 | 34.5291 | 10.9451 | 10.9451 | 0 | 0 | 0 | 1/30/18:00
1 | 30 | 19 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.75 | -17.6307 | 86.148 | -75 | -13.4877 | 262.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/19:00
1 | 30 | 20 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.7917 | -17.6196 | 86.148 | -75 | -13.4947 | 277.7743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/20:00
1 | 30 | 21 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.8333 | -17.6084 | 86.148 | -75 | -13.5017 | 292.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/21:00
1 | 30 | 22 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.875 | -17.5973 | 86.148 | -75 | -13.5087 | 307.7708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/22:00
1 | 30 | 23 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.9167 | -17.5861 | 86.148 | -75 | -13.5157 | 322.7691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/23:00
1 | 30 | 24 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 30.9583 | -17.5749 | 86.148 | -75 | -13.5227 | 337.7673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/30/24:00
1 | 31 | 1 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31 | -17.5637 | 86.148 | -75 | -13.5296 | -7.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/1:00
1 | 31 | 2 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.0417 | -17.5526 | 86.148 | -75 | -13.5365 | 7.7639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/2:00
1 | 31 | 3 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.0833 | -17.5414 | 86.148 | -75 | -13.5434 | 22.7622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/3:00
1 | 31 | 4 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.125 | -17.5302 | 86.148 | -75 | -13.5503 | 37.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/4:00
1 | 31 | 5 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.1667 | -17.519 | 86.148 | -75 | -13.5571 | 52.7587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/5:00
1 | 31 | 6 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.2083 | -17.5077 | 86.148 | -75 | -13.5639 | 67.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/6:00
1 | 31 | 7 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.25 | -17.4965 | 86.148 | -75 | -13.5707 | 82.7553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/7:00
1 | 31 | 8 | -3.9 | 1 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 1 | 0 | 0 | 39.791 | 31.2917 | -17.4853 | 86.148 | -75 | -13.5775 | 97.7536 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 1/31/8:00
1 | 31 | 9 | -3.9 | 33 | 116 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 33 | 0 | 0 | 39.791 | 31.3333 | -17.474 | 86.148 | -75 | -13.5843 | 112.7519 | -55.1725 | -22.1725 | -7.0283 | -7.0283 | 0 | 0 | 0 | 1/31/9:00
1 | 31 | 10 | -3.3 | 88 | 346 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 88 | 0 | 0 | 39.791 | 31.375 | -17.4628 | 86.148 | -75 | -13.591 | 127.7503 | -221.7139 | -133.7139 | -42.385 | -42.385 | 0 | 0 | 0 | 1/31/10:00
1 | 31 | 11 | -1.7 | 155 | 400 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 155 | 0 | 0 | 39.791 | 31.4167 | -17.4515 | 86.148 | -75 | -13.5977 | 142.7486 | -310.1612 | -155.1612 | -49.1834 | -49.1834 | 0 | 0 | 0 | 1/31/11:00
1 | 31 | 12 | -1.7 | 224 | 33 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 224 | 0 | 0 | 39.791 | 31.4583 | -17.4402 | 86.148 | -75 | -13.6044 | 157.7469 | -28.7191 | 195.2809 | 61.9006 | 61.9006 | 0 | 0 | 0 | 1/31/12:00
1 | 31 | 13 | -1.7 | 230 | 141 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 230 | 0 | 0 | 39.791 | 31.5 | -17.4289 | 86.148 | -75 | -13.6111 | 172.7452 | -129.569 | 100.431 | 31.8349 | 31.8349 | 0 | 0 | 0 | 1/31/13:00
1 | 31 | 14 | -1.1 | 274 | 147 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 274 | 0 | 0 | 39.791 | 31.5417 | -17.4176 | 86.148 | -75 | -13.6177 | 187.7436 | -134.9515 | 139.0485 | 44.0759 | 44.0759 | 0 | 0 | 0 | 1/31/14:00
1 | 31 | 15 | -1.1 | 165 | 20 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 165 | 0 | 0 | 39.791 | 31.5833 | -17.4064 | 86.148 | -75 | -13.6243 | 202.7419 | -17.3529 | 147.6471 | 46.8015 | 46.8015 | 0 | 0 | 0 | 1/31/15:00
1 | 31 | 16 | -1.7 | 198 | 12 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 198 | 0 | 0 | 39.791 | 31.625 | -17.395 | 86.148 | -75 | -13.6309 | 217.7403 | -9.2541 | 188.7459 | 59.8292 | 59.8292 | 0 | 0 | 0 | 1/31/16:00
1 | 31 | 17 | -1.7 | 68 | 3 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 68 | 0 | 0 | 39.791 | 31.6667 | -17.3837 | 86.148 | -75 | -13.6375 | 232.7386 | -1.9055 | 66.0945 | 20.9508 | 20.9508 | 0 | 0 | 0 | 1/31/17:00
1 | 31 | 18 | -2.2 | 29 | 4 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 29 | 0 | 0 | 39.791 | 31.7083 | -17.3724 | 86.148 | -75 | -13.6441 | 247.737 | -1.8757 | 27.1243 | 8.5979 | 8.5979 | 0 | 0 | 0 | 1/31/18:00
1 | 31 | 19 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.75 | -17.3611 | 86.148 | -75 | -13.6506 | 262.7353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/19:00
1 | 31 | 20 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.7917 | -17.3497 | 86.148 | -75 | -13.6571 | 277.7337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/20:00
1 | 31 | 21 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.8333 | -17.3384 | 86.148 | -75 | -13.6636 | 292.7321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/21:00
1 | 31 | 22 | -3.8 | 0 | 0 | 25.16 | 1 | 0 | 25.16 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.875 | -17.327 | 86.148 | -75 | -13.6701 | 307.7305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/22:00
1 | 31 | 23 | -5.4 | 0 | 0 | 22.28 | 1 | 0 | 22.28 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.9167 | -17.3157 | 86.148 | -75 | -13.6765 | 322.7289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/23:00
1 | 31 | 24 | -7.1 | 0 | 0 | 19.22 | 1 | 0 | 19.22 | 0 | 0 | 0 | 0 | 0 | 39.791 | 31.9583 | -17.3043 | 86.148 | -75 | -13.6829 | 337.7273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1/31/24:00
2 | 1 | 1899-12-31 | -8.8 | 0 | 0 | 16.16 | 1 | 0 | 16.16 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32 | -17.2929 | 86.148 | -75 | -13.6893 | -7.2743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/1:00
2 | 1 | 1900-01-01 | -10.5 | 0 | 0 | 13.1 | 1 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.0417 | -17.2815 | 86.148 | -75 | -13.6957 | 7.7241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/2:00
2 | 1 | 1900-01-02 | -12.1 | 0 | 0 | 10.22 | 1 | 0 | 10.22 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.0833 | -17.2701 | 86.148 | -75 | -13.7021 | 22.7225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/3:00
2 | 1 | 1900-01-03 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.125 | -17.2587 | 86.148 | -75 | -13.7084 | 37.7209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/4:00
2 | 1 | 1900-01-04 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.1667 | -17.2473 | 86.148 | -75 | -13.7147 | 52.7193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/5:00
2 | 1 | 1900-01-05 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.2083 | -17.2359 | 86.148 | -75 | -13.721 | 67.7177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/6:00
2 | 1 | 1900-01-06 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.25 | -17.2244 | 86.148 | -75 | -13.7273 | 82.7162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/7:00
2 | 1 | 1900-01-07 | -14.4 | 1 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 1 | 0 | 0 | 39.791 | 32.2917 | -17.213 | 86.148 | -75 | -13.7335 | 97.7146 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 2/1/8:00
2 | 1 | 1900-01-08 | -14.4 | 43 | 1 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 43 | 0 | 0 | 39.791 | 32.3333 | -17.2015 | 86.148 | -75 | -13.7398 | 112.7131 | -0.47268 | 42.5273 | 13.4804 | 13.4804 | 0 | 0 | 0 | 2/1/9:00
2 | 1 | 1900-01-09 | -13.9 | 126 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 126 | 0 | 0 | 39.791 | 32.375 | -17.1901 | 86.148 | -75 | -13.746 | 127.7115 | 0 | 126 | 39.9398 | 39.9398 | 0 | 0 | 0 | 2/1/10:00
2 | 1 | 1900-01-10 | -13.3 | 214 | 1 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 214 | 0 | 0 | 39.791 | 32.4167 | -17.1786 | 86.148 | -75 | -13.7522 | 142.71 | -0.77306 | 213.2269 | 67.5892 | 67.5892 | 0 | 0 | 0 | 2/1/11:00
2 | 1 | 1900-01-11 | -12.2 | 275 | 1 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 275 | 0 | 0 | 39.791 | 32.4583 | -17.1671 | 86.148 | -75 | -13.7583 | 157.7084 | -0.86818 | 274.1318 | 86.895 | 86.895 | 0 | 0 | 0 | 2/1/12:00
2 | 1 | 1900-01-12 | -12.2 | 297 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 297 | 0 | 0 | 39.791 | 32.5 | -17.1556 | 86.148 | -75 | -13.7644 | 172.7069 | 0 | 297 | 94.1438 | 94.1438 | 0 | 0 | 0 | 2/1/13:00
2 | 1 | 1900-01-13 | -12.2 | 290 | 1 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 290 | 0 | 0 | 39.791 | 32.5417 | -17.1441 | 86.148 | -75 | -13.7706 | 187.7054 | -0.91627 | 289.0837 | 91.6345 | 91.6345 | 0 | 0 | 0 | 2/1/14:00
2 | 1 | 1900-01-14 | -12.2 | 266 | 2 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 266 | 0 | 0 | 39.791 | 32.5833 | -17.1326 | 86.148 | -75 | -13.7766 | 202.7038 | -1.7318 | 264.2682 | 83.7684 | 83.7684 | 0 | 0 | 0 | 2/1/15:00
2 | 1 | 1900-01-15 | -11.7 | 205 | 54 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 205 | 0 | 0 | 39.791 | 32.625 | -17.1211 | 86.148 | -75 | -13.7827 | 217.7023 | -41.5482 | 163.4518 | 51.8114 | 51.8114 | 0 | 0 | 0 | 2/1/16:00
2 | 1 | 1900-01-16 | -11.1 | 85 | 29 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 85 | 0 | 0 | 39.791 | 32.6667 | -17.1096 | 86.148 | -75 | -13.7888 | 232.7008 | -18.3657 | 66.6343 | 21.1219 | 21.1219 | 0 | 0 | 0 | 2/1/17:00
2 | 1 | 1900-01-17 | -10.6 | 40 | 46 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 40 | 0 | 0 | 39.791 | 32.7083 | -17.0981 | 86.148 | -75 | -13.7948 | 247.6993 | -21.4752 | 18.5248 | 5.872 | 5.872 | 0 | 0 | 0 | 2/1/18:00
2 | 1 | 1900-01-18 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.75 | -17.0866 | 86.148 | -75 | -13.8008 | 262.6978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/19:00
2 | 1 | 1900-01-19 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.7917 | -17.075 | 86.148 | -75 | -13.8068 | 277.6963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/20:00
2 | 1 | 1900-01-20 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.8333 | -17.0635 | 86.148 | -75 | -13.8127 | 292.6948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/21:00
2 | 1 | 1900-01-21 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.875 | -17.0519 | 86.148 | -75 | -13.8187 | 307.6933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/22:00
2 | 1 | 1900-01-22 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.9167 | -17.0403 | 86.148 | -75 | -13.8246 | 322.6919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/23:00
2 | 1 | 1900-01-23 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 32.9583 | -17.0288 | 86.148 | -75 | -13.8305 | 337.6904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/1/24:00
2 | 2 | 1899-12-31 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33 | -17.0172 | 86.148 | -75 | -13.8363 | -7.3111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/1:00
2 | 2 | 1900-01-01 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.0417 | -17.0056 | 86.148 | -75 | -13.8422 | 7.6875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/2:00
2 | 2 | 1900-01-02 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.0833 | -16.994 | 86.148 | -75 | -13.848 | 22.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/3:00
2 | 2 | 1900-01-03 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.125 | -16.9824 | 86.148 | -75 | -13.8538 | 37.6845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/4:00
2 | 2 | 1900-01-04 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.1667 | -16.9707 | 86.148 | -75 | -13.8596 | 52.6831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/5:00
2 | 2 | 1900-01-05 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.2083 | -16.9591 | 86.148 | -75 | -13.8653 | 67.6817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/6:00
2 | 2 | 1900-01-06 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.25 | -16.9475 | 86.148 | -75 | -13.8711 | 82.6802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/7:00
2 | 2 | 1900-01-07 | -12.8 | 1 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 1 | 0 | 0 | 39.791 | 33.2917 | -16.9358 | 86.148 | -75 | -13.8768 | 97.6788 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 2/2/8:00
2 | 2 | 1900-01-08 | -12.8 | 48 | 6 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 48 | 0 | 0 | 39.791 | 33.3333 | -16.9242 | 86.148 | -75 | -13.8825 | 112.6774 | -2.8183 | 45.1817 | 14.3218 | 14.3218 | 0 | 0 | 0 | 2/2/9:00
2 | 2 | 1900-01-09 | -12.2 | 123 | 6 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 123 | 0 | 0 | 39.791 | 33.375 | -16.9125 | 86.148 | -75 | -13.8882 | 127.676 | -3.813 | 119.187 | 37.7802 | 37.7802 | 0 | 0 | 0 | 2/2/10:00
2 | 2 | 1900-01-10 | -11.1 | 212 | 2 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 212 | 0 | 0 | 39.791 | 33.4167 | -16.9009 | 86.148 | -75 | -13.8938 | 142.6746 | -1.5414 | 210.4586 | 66.7117 | 66.7117 | 0 | 0 | 0 | 2/2/11:00
2 | 2 | 1900-01-11 | -11.1 | 265 | 11 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 265 | 0 | 0 | 39.791 | 33.4583 | -16.8892 | 86.148 | -75 | -13.8994 | 157.6731 | -9.5266 | 255.4734 | 80.9806 | 80.9806 | 0 | 0 | 0 | 2/2/12:00
2 | 2 | 1900-01-12 | -9.4 | 314 | 85 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 314 | 0 | 0 | 39.791 | 33.5 | -16.8775 | 86.148 | -75 | -13.905 | 172.6717 | -77.7824 | 236.2176 | 74.8768 | 74.8768 | 0 | 0 | 0 | 2/2/13:00
2 | 2 | 1900-01-13 | -8.9 | 326 | 296 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 326 | 0 | 0 | 39.791 | 33.5417 | -16.8658 | 86.148 | -75 | -13.9106 | 187.6704 | -270.6727 | 55.3273 | 17.5378 | 17.5378 | 0 | 0 | 0 | 2/2/14:00
2 | 2 | 1900-01-14 | -8.9 | 261 | 148 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 261 | 0 | 0 | 39.791 | 33.5833 | -16.8541 | 86.148 | -75 | -13.9162 | 202.669 | -127.8904 | 133.1096 | 42.1934 | 42.1934 | 0 | 0 | 0 | 2/2/15:00
2 | 2 | 1900-01-15 | -8.9 | 152 | 322 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 152 | 0 | 0 | 39.791 | 33.625 | -16.8424 | 86.148 | -75 | -13.9217 | 217.6676 | -247.1576 | -95.1576 | -30.1633 | -30.1633 | 0 | 0 | 0 | 2/2/16:00
2 | 2 | 1900-01-16 | -8.9 | 79 | 641 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 79 | 0 | 0 | 39.791 | 33.6667 | -16.8307 | 86.148 | -75 | -13.9272 | 232.6662 | -404.6867 | -325.6867 | -103.237 | -103.237 | 0 | 0 | 0 | 2/2/17:00
2 | 2 | 1900-01-17 | -11.1 | 39 | 198 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 39 | 0 | 0 | 39.791 | 33.7083 | -16.819 | 86.148 | -75 | -13.9327 | 247.6648 | -92.0093 | -53.0093 | -16.803 | -16.803 | 0 | 0 | 0 | 2/2/18:00
2 | 2 | 1900-01-18 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.75 | -16.8072 | 86.148 | -75 | -13.9382 | 262.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/19:00
2 | 2 | 1900-01-19 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.7917 | -16.7955 | 86.148 | -75 | -13.9436 | 277.6621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/20:00
2 | 2 | 1900-01-20 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.8333 | -16.7837 | 86.148 | -75 | -13.949 | 292.6607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/21:00
2 | 2 | 1900-01-21 | -16.1 | 0 | 0 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.875 | -16.772 | 86.148 | -75 | -13.9544 | 307.6594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/22:00
2 | 2 | 1900-01-22 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.9167 | -16.7602 | 86.148 | -75 | -13.9598 | 322.6581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/23:00
2 | 2 | 1900-01-23 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 33.9583 | -16.7484 | 86.148 | -75 | -13.9652 | 337.6567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/2/24:00
2 | 3 | 1899-12-31 | -18.9 | 0 | 0 | -2.02 | 1 | 0 | -2.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34 | -16.7367 | 86.148 | -75 | -13.9705 | -7.3446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/1:00
2 | 3 | 1900-01-01 | -21.1 | 0 | 0 | -5.98 | 1 | 0 | -5.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.0417 | -16.7249 | 86.148 | -75 | -13.9758 | 7.6541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/2:00
2 | 3 | 1900-01-02 | -21.7 | 0 | 0 | -7.06 | 1 | 0 | -7.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.0833 | -16.7131 | 86.148 | -75 | -13.9811 | 22.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/3:00
2 | 3 | 1900-01-03 | -21.1 | 0 | 0 | -5.98 | 1 | 0 | -5.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.125 | -16.7013 | 86.148 | -75 | -13.9863 | 37.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/4:00
2 | 3 | 1900-01-04 | -21.7 | 0 | 0 | -7.06 | 1 | 0 | -7.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.1667 | -16.6894 | 86.148 | -75 | -13.9916 | 52.6501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/5:00
2 | 3 | 1900-01-05 | -23.3 | 0 | 0 | -9.94 | 1 | 0 | -9.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.2083 | -16.6776 | 86.148 | -75 | -13.9968 | 67.6488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/6:00
2 | 3 | 1900-01-06 | -20.6 | 0 | 0 | -5.08 | 1 | 0 | -5.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.25 | -16.6658 | 86.148 | -75 | -14.002 | 82.6475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/7:00
2 | 3 | 1900-01-07 | -22.8 | 1 | 1 | -9.04 | 1 | 0 | -9.04 | 0 | 0 | 1 | 0 | 0 | 39.791 | 34.2917 | -16.6539 | 86.148 | -75 | -14.0072 | 97.6462 | -0.28136 | 0.71864 | 0.2278 | 0.2278 | 0 | 0 | 0 | 2/3/8:00
2 | 3 | 1900-01-08 | -22.2 | 36 | 159 | -7.96 | 1 | 0 | -7.96 | 0 | 0 | 36 | 0 | 0 | 39.791 | 34.3333 | -16.6421 | 86.148 | -75 | -14.0123 | 112.6449 | -74.2114 | -38.2114 | -12.1123 | -12.1123 | 0 | 0 | 0 | 2/3/9:00
2 | 3 | 1900-01-09 | -16.7 | 131 | 286 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 131 | 0 | 0 | 39.791 | 34.375 | -16.6302 | 86.148 | -75 | -14.0175 | 127.6436 | -180.9868 | -49.9868 | -15.8449 | -15.8449 | 0 | 0 | 0 | 2/3/10:00
2 | 3 | 1900-01-10 | -12.8 | 89 | 695 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 89 | 0 | 0 | 39.791 | 34.4167 | -16.6184 | 86.148 | -75 | -14.0226 | 142.6424 | -533.9571 | -444.9571 | -141.0436 | -141.0436 | 0 | 0 | 0 | 2/3/11:00
2 | 3 | 1900-01-11 | -10.6 | 106 | 806 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 106 | 0 | 0 | 39.791 | 34.4583 | -16.6065 | 86.148 | -75 | -14.0277 | 157.6411 | -696.2902 | -590.2902 | -187.1117 | -187.1117 | 0 | 0 | 0 | 2/3/12:00
2 | 3 | 1900-01-12 | -8.9 | 114 | 843 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 114 | 0 | 0 | 39.791 | 34.5 | -16.5946 | 86.148 | -75 | -14.0327 | 172.6398 | -769.7373 | -655.7373 | -207.8573 | -207.8573 | 0 | 0 | 0 | 2/3/13:00
2 | 3 | 1900-01-13 | -7.8 | 113 | 836 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 113 | 0 | 0 | 39.791 | 34.5417 | -16.5827 | 86.148 | -75 | -14.0378 | 187.6386 | -762.8866 | -649.8866 | -206.0027 | -206.0027 | 0 | 0 | 0 | 2/3/14:00
2 | 3 | 1900-01-14 | -7.8 | 105 | 807 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 105 | 0 | 0 | 39.791 | 34.5833 | -16.5708 | 86.148 | -75 | -14.0428 | 202.6373 | -695.8429 | -590.8429 | -187.2869 | -187.2869 | 0 | 0 | 0 | 2/3/15:00
2 | 3 | 1900-01-15 | -7.8 | 94 | 726 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 94 | 0 | 0 | 39.791 | 34.625 | -16.5589 | 86.148 | -75 | -14.0478 | 217.6361 | -555.8617 | -461.8617 | -146.4021 | -146.4021 | 0 | 0 | 0 | 2/3/16:00
2 | 3 | 1900-01-16 | -7.8 | 65 | 577 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 65 | 0 | 0 | 39.791 | 34.6667 | -16.547 | 86.148 | -75 | -14.0527 | 232.6348 | -363.0974 | -298.0974 | -94.4917 | -94.4917 | 0 | 0 | 0 | 2/3/17:00
2 | 3 | 1900-01-17 | -9.4 | 35 | 151 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 35 | 0 | 0 | 39.791 | 34.7083 | -16.5351 | 86.148 | -75 | -14.0577 | 247.6336 | -69.8289 | -34.8289 | -11.0402 | -11.0402 | 0 | 0 | 0 | 2/3/18:00
2 | 3 | 1900-01-18 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.75 | -16.5232 | 86.148 | -75 | -14.0626 | 262.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/19:00
2 | 3 | 1900-01-19 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.7917 | -16.5112 | 86.148 | -75 | -14.0675 | 277.6311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/20:00
2 | 3 | 1900-01-20 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.8333 | -16.4993 | 86.148 | -75 | -14.0724 | 292.6299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/21:00
2 | 3 | 1900-01-21 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.875 | -16.4874 | 86.148 | -75 | -14.0773 | 307.6287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/22:00
2 | 3 | 1900-01-22 | -15.6 | 0 | 0 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.9167 | -16.4754 | 86.148 | -75 | -14.0821 | 322.6275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/23:00
2 | 3 | 1900-01-23 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 34.9583 | -16.4634 | 86.148 | -75 | -14.0869 | 337.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/3/24:00
2 | 4 | 1899-12-31 | -17.2 | 0 | 0 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35 | -16.4514 | 86.148 | -75 | -14.0917 | -7.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/1:00
2 | 4 | 1900-01-01 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.0417 | -16.4395 | 86.148 | -75 | -14.0965 | 7.6239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/2:00
2 | 4 | 1900-01-02 | -19.4 | 0 | 0 | -2.92 | 1 | 0 | -2.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.0833 | -16.4275 | 86.148 | -75 | -14.1012 | 22.6227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/3:00
2 | 4 | 1900-01-03 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.125 | -16.4155 | 86.148 | -75 | -14.106 | 37.6215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/4:00
2 | 4 | 1900-01-04 | -17.2 | 0 | 0 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.1667 | -16.4035 | 86.148 | -75 | -14.1107 | 52.6203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/5:00
2 | 4 | 1900-01-05 | -17.2 | 0 | 0 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.2083 | -16.3915 | 86.148 | -75 | -14.1154 | 67.6192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/6:00
2 | 4 | 1900-01-06 | -20 | 0 | 0 | -4 | 1 | 0 | -4 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.25 | -16.3794 | 86.148 | -75 | -14.12 | 82.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/7:00
2 | 4 | 1900-01-07 | -18.3 | 1 | 4 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 1 | 0 | 0 | 39.791 | 35.2917 | -16.3674 | 86.148 | -75 | -14.1246 | 97.6168 | -1.1123 | -0.11226 | -0.035586 | -0.035586 | 0 | 0 | 0 | 2/4/8:00
2 | 4 | 1900-01-08 | -15.6 | 35 | 179 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 35 | 0 | 0 | 39.791 | 35.3333 | -16.3554 | 86.148 | -75 | -14.1293 | 112.6157 | -83.0096 | -48.0096 | -15.2182 | -15.2182 | 0 | 0 | 0 | 2/4/9:00
2 | 4 | 1900-01-09 | -12.2 | 60 | 645 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 60 | 0 | 0 | 39.791 | 35.375 | -16.3433 | 86.148 | -75 | -14.1339 | 127.6145 | -406.4261 | -346.4261 | -109.811 | -109.811 | 0 | 0 | 0 | 2/4/10:00
2 | 4 | 1900-01-10 | -9.4 | 81 | 776 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 81 | 0 | 0 | 39.791 | 35.4167 | -16.3313 | 86.148 | -75 | -14.1384 | 142.6134 | -594.2995 | -513.2995 | -162.707 | -162.707 | 0 | 0 | 0 | 2/4/11:00
2 | 4 | 1900-01-11 | -7.2 | 194 | 618 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 194 | 0 | 0 | 39.791 | 35.4583 | -16.3192 | 86.148 | -75 | -14.143 | 157.6123 | -532.5148 | -338.5148 | -107.3033 | -107.3033 | 0 | 0 | 0 | 2/4/12:00
2 | 4 | 1900-01-12 | -6.7 | 102 | 873 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 102 | 0 | 0 | 39.791 | 35.5 | -16.3071 | 86.148 | -75 | -14.1475 | 172.6111 | -795.3452 | -693.3452 | -219.7783 | -219.7783 | 0 | 0 | 0 | 2/4/13:00
2 | 4 | 1900-01-13 | -5.6 | 122 | 804 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 122 | 0 | 0 | 39.791 | 35.5417 | -16.295 | 86.148 | -75 | -14.152 | 187.61 | -732.1164 | -610.1164 | -193.3962 | -193.3962 | 0 | 0 | 0 | 2/4/14:00
2 | 4 | 1900-01-14 | -5 | 130 | 751 | 23 | 1 | 0 | 23 | 0 | 0 | 130 | 0 | 0 | 39.791 | 35.5833 | -16.283 | 86.148 | -75 | -14.1565 | 202.6089 | -646.1024 | -516.1024 | -163.5955 | -163.5955 | 0 | 0 | 0 | 2/4/15:00
2 | 4 | 1900-01-15 | -4.4 | 175 | 495 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 175 | 0 | 0 | 39.791 | 35.625 | -16.2709 | 86.148 | -75 | -14.1609 | 217.6078 | -378.0067 | -203.0067 | -64.3496 | -64.3496 | 0 | 0 | 0 | 2/4/16:00
2 | 4 | 1900-01-16 | -4.4 | 122 | 106 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 122 | 0 | 0 | 39.791 | 35.6667 | -16.2588 | 86.148 | -75 | -14.1654 | 232.6067 | -66.4775 | 55.5225 | 17.5996 | 17.5996 | 0 | 0 | 0 | 2/4/17:00
2 | 4 | 1900-01-17 | -5.6 | 41 | 12 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 41 | 0 | 0 | 39.791 | 35.7083 | -16.2467 | 86.148 | -75 | -14.1698 | 247.6056 | -5.5212 | 35.4788 | 11.2462 | 11.2462 | 0 | 0 | 0 | 2/4/18:00
2 | 4 | 1900-01-18 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.75 | -16.2345 | 86.148 | -75 | -14.1742 | 262.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/19:00
2 | 4 | 1900-01-19 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.7917 | -16.2224 | 86.148 | -75 | -14.1785 | 277.6034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/20:00
2 | 4 | 1900-01-20 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.8333 | -16.2103 | 86.148 | -75 | -14.1829 | 292.6023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/21:00
2 | 4 | 1900-01-21 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.875 | -16.1981 | 86.148 | -75 | -14.1872 | 307.6012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/22:00
2 | 4 | 1900-01-22 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.9167 | -16.186 | 86.148 | -75 | -14.1915 | 322.6001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/23:00
2 | 4 | 1900-01-23 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 35.9583 | -16.1738 | 86.148 | -75 | -14.1958 | 337.5991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/4/24:00
2 | 5 | 1899-12-31 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36 | -16.1617 | 86.148 | -75 | -14.2 | -7.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/1:00
2 | 5 | 1900-01-01 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.0417 | -16.1495 | 86.148 | -75 | -14.2042 | 7.5969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/2:00
2 | 5 | 1900-01-02 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.0833 | -16.1373 | 86.148 | -75 | -14.2085 | 22.5959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/3:00
2 | 5 | 1900-01-03 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.125 | -16.1251 | 86.148 | -75 | -14.2126 | 37.5948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/4:00
2 | 5 | 1900-01-04 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.1667 | -16.1129 | 86.148 | -75 | -14.2168 | 52.5938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/5:00
2 | 5 | 1900-01-05 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.2083 | -16.1007 | 86.148 | -75 | -14.2209 | 67.5928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/6:00
2 | 5 | 1900-01-06 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.25 | -16.0885 | 86.148 | -75 | -14.2251 | 82.5917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/7:00
2 | 5 | 1900-01-07 | -5.6 | 1 | 1 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 1 | 0 | 0 | 39.791 | 36.2917 | -16.0763 | 86.148 | -75 | -14.2292 | 97.5907 | -0.27475 | 0.72525 | 0.22989 | 0.22989 | 0 | 0 | 0 | 2/5/8:00
2 | 5 | 1900-01-08 | -5.6 | 39 | 5 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 39 | 0 | 0 | 39.791 | 36.3333 | -16.0641 | 86.148 | -75 | -14.2332 | 112.5897 | -2.3036 | 36.6964 | 11.6321 | 11.6321 | 0 | 0 | 0 | 2/5/9:00
2 | 5 | 1900-01-09 | -4.4 | 119 | 4 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 119 | 0 | 0 | 39.791 | 36.375 | -16.0518 | 86.148 | -75 | -14.2373 | 127.5887 | -2.5096 | 116.4904 | 36.9254 | 36.9254 | 0 | 0 | 0 | 2/5/10:00
2 | 5 | 1900-01-10 | -3.9 | 211 | 1 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 211 | 0 | 0 | 39.791 | 36.4167 | -16.0396 | 86.148 | -75 | -14.2413 | 142.5877 | -0.76339 | 210.2366 | 66.6413 | 66.6413 | 0 | 0 | 0 | 2/5/11:00
2 | 5 | 1900-01-11 | -2.8 | 256 | 4 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 256 | 0 | 0 | 39.791 | 36.4583 | -16.0273 | 86.148 | -75 | -14.2453 | 157.5867 | -3.4377 | 252.5623 | 80.0578 | 80.0578 | 0 | 0 | 0 | 2/5/12:00
2 | 5 | 1900-01-12 | -2.8 | 302 | 2 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 302 | 0 | 0 | 39.791 | 36.5 | -16.0151 | 86.148 | -75 | -14.2493 | 172.5857 | -1.8179 | 300.1821 | 95.1525 | 95.1525 | 0 | 0 | 0 | 2/5/13:00
2 | 5 | 1900-01-13 | -2.2 | 350 | 4 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 350 | 0 | 0 | 39.791 | 36.5417 | -16.0028 | 86.148 | -75 | -14.2533 | 187.5847 | -3.6343 | 346.3657 | 109.7919 | 109.7919 | 0 | 0 | 0 | 2/5/14:00
2 | 5 | 1900-01-14 | -1.7 | 314 | 4 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 314 | 0 | 0 | 39.791 | 36.5833 | -15.9905 | 86.148 | -75 | -14.2572 | 202.5837 | -3.4333 | 310.5667 | 98.4442 | 98.4442 | 0 | 0 | 0 | 2/5/15:00
2 | 5 | 1900-01-15 | -1.7 | 248 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 248 | 0 | 0 | 39.791 | 36.625 | -15.9783 | 86.148 | -75 | -14.2611 | 217.5827 | 0 | 248 | 78.6117 | 78.6117 | 0 | 0 | 0 | 2/5/16:00
2 | 5 | 1900-01-16 | -1.7 | 150 | 1 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 150 | 0 | 0 | 39.791 | 36.6667 | -15.966 | 86.148 | -75 | -14.265 | 232.5817 | -0.62492 | 149.3751 | 47.3493 | 47.3493 | 0 | 0 | 0 | 2/5/17:00
2 | 5 | 1900-01-17 | -1.7 | 46 | 1 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 46 | 0 | 0 | 39.791 | 36.7083 | -15.9537 | 86.148 | -75 | -14.2689 | 247.5808 | -0.45767 | 45.5423 | 14.4361 | 14.4361 | 0 | 0 | 0 | 2/5/18:00
2 | 5 | 1900-01-18 | -1.7 | 2 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 2 | 0 | 0 | 39.791 | 36.75 | -15.9414 | 86.148 | -75 | -14.2727 | 262.5798 | 0 | 2 | 0.63397 | 0.63397 | 0 | 0 | 0 | 2/5/19:00
2 | 5 | 1900-01-19 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.7917 | -15.9291 | 86.148 | -75 | -14.2765 | 277.5789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/20:00
2 | 5 | 1900-01-20 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.8333 | -15.9167 | 86.148 | -75 | -14.2803 | 292.5779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/21:00
2 | 5 | 1900-01-21 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.875 | -15.9044 | 86.148 | -75 | -14.2841 | 307.577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/22:00
2 | 5 | 1900-01-22 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.9167 | -15.8921 | 86.148 | -75 | -14.2879 | 322.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/23:00
2 | 5 | 1900-01-23 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 36.9583 | -15.8797 | 86.148 | -75 | -14.2916 | 337.5751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/5/24:00
2 | 6 | 1899-12-31 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37 | -15.8674 | 86.148 | -75 | -14.2953 | -7.4258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/1:00
2 | 6 | 1900-01-01 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.0417 | -15.855 | 86.148 | -75 | -14.299 | 7.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/2:00
2 | 6 | 1900-01-02 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.0833 | -15.8427 | 86.148 | -75 | -14.3027 | 22.5723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/3:00
2 | 6 | 1900-01-03 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.125 | -15.8303 | 86.148 | -75 | -14.3063 | 37.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/4:00
2 | 6 | 1900-01-04 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.1667 | -15.8179 | 86.148 | -75 | -14.31 | 52.5705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/5:00
2 | 6 | 1900-01-05 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.2083 | -15.8055 | 86.148 | -75 | -14.3136 | 67.5696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/6:00
2 | 6 | 1900-01-06 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.25 | -15.7931 | 86.148 | -75 | -14.3171 | 82.5687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/7:00
2 | 6 | 1900-01-07 | -7.2 | 3 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 3 | 0 | 0 | 39.791 | 37.2917 | -15.7807 | 86.148 | -75 | -14.3207 | 97.5678 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 2/6/8:00
2 | 6 | 1900-01-08 | -7.8 | 50 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 50 | 0 | 0 | 39.791 | 37.3333 | -15.7683 | 86.148 | -75 | -14.3242 | 112.5669 | 0 | 50 | 15.8491 | 15.8491 | 0 | 0 | 0 | 2/6/9:00
2 | 6 | 1900-01-09 | -8.3 | 146 | 100 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 146 | 0 | 0 | 39.791 | 37.375 | -15.7559 | 86.148 | -75 | -14.3277 | 127.5661 | -62.4646 | 83.5354 | 26.4793 | 26.4793 | 0 | 0 | 0 | 2/6/10:00
2 | 6 | 1900-01-10 | -7.8 | 216 | 401 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 216 | 0 | 0 | 39.791 | 37.4167 | -15.7435 | 86.148 | -75 | -14.3312 | 142.5652 | -305.1178 | -89.1178 | -28.2488 | -28.2488 | 0 | 0 | 0 | 2/6/11:00
2 | 6 | 1900-01-11 | -7.2 | 268 | 250 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 268 | 0 | 0 | 39.791 | 37.4583 | -15.731 | 86.148 | -75 | -14.3347 | 157.5643 | -214.2844 | 53.7156 | 17.0269 | 17.0269 | 0 | 0 | 0 | 2/6/12:00
2 | 6 | 1900-01-12 | -6.7 | 261 | 378 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 261 | 0 | 0 | 39.791 | 37.5 | -15.7186 | 86.148 | -75 | -14.3381 | 172.5635 | -342.774 | -81.774 | -25.9209 | -25.9209 | 0 | 0 | 0 | 2/6/13:00
2 | 6 | 1900-01-13 | -6.1 | 185 | 663 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 185 | 0 | 0 | 39.791 | 37.5417 | -15.7061 | 86.148 | -75 | -14.3415 | 187.5626 | -601.0148 | -416.0148 | -131.8694 | -131.8694 | 0 | 0 | 0 | 2/6/14:00
2 | 6 | 1900-01-14 | -6.1 | 98 | 786 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 98 | 0 | 0 | 39.791 | 37.5833 | -15.6937 | 86.148 | -75 | -14.3449 | 202.5618 | -673.0034 | -575.0034 | -182.266 | -182.266 | 0 | 0 | 0 | 2/6/15:00
2 | 6 | 1900-01-15 | -6.1 | 82 | 763 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 82 | 0 | 0 | 39.791 | 37.625 | -15.6812 | 86.148 | -75 | -14.3483 | 217.5609 | -579.4307 | -497.4307 | -157.6769 | -157.6769 | 0 | 0 | 0 | 2/6/16:00
2 | 6 | 1900-01-16 | -6.1 | 64 | 623 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 64 | 0 | 0 | 39.791 | 37.6667 | -15.6688 | 86.148 | -75 | -14.3517 | 232.5601 | -387.8858 | -323.8858 | -102.6661 | -102.6661 | 0 | 0 | 0 | 2/6/17:00
2 | 6 | 1900-01-17 | -7.2 | 26 | 426 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 26 | 0 | 0 | 39.791 | 37.7083 | -15.6563 | 86.148 | -75 | -14.355 | 247.5593 | -193.8905 | -167.8905 | -53.2184 | -53.2184 | 0 | 0 | 0 | 2/6/18:00
2 | 6 | 1900-01-18 | -10 | 2 | 13 | 14 | 1 | 0 | 14 | 0 | 0 | 2 | 0 | 0 | 39.791 | 37.75 | -15.6438 | 86.148 | -75 | -14.3583 | 262.5584 | -3.4893 | -1.4893 | -0.47208 | -0.47208 | 0 | 0 | 0 | 2/6/19:00
2 | 6 | 1900-01-19 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.7917 | -15.6313 | 86.148 | -75 | -14.3616 | 277.5576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/20:00
2 | 6 | 1900-01-20 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.8333 | -15.6188 | 86.148 | -75 | -14.3648 | 292.5568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/21:00
2 | 6 | 1900-01-21 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.875 | -15.6063 | 86.148 | -75 | -14.3681 | 307.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/22:00
2 | 6 | 1900-01-22 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.9167 | -15.5938 | 86.148 | -75 | -14.3713 | 322.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/23:00
2 | 6 | 1900-01-23 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 37.9583 | -15.5812 | 86.148 | -75 | -14.3745 | 337.5544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/6/24:00
2 | 7 | 1899-12-31 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38 | -15.5687 | 86.148 | -75 | -14.3777 | -7.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/1:00
2 | 7 | 1900-01-01 | -16.1 | 0 | 0 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.0417 | -15.5562 | 86.148 | -75 | -14.3808 | 7.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/2:00
2 | 7 | 1900-01-02 | -15.6 | 0 | 0 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.0833 | -15.5436 | 86.148 | -75 | -14.3839 | 22.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/3:00
2 | 7 | 1900-01-03 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.125 | -15.5311 | 86.148 | -75 | -14.387 | 37.5512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/4:00
2 | 7 | 1900-01-04 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.1667 | -15.5185 | 86.148 | -75 | -14.3901 | 52.5505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/5:00
2 | 7 | 1900-01-05 | -16.1 | 0 | 0 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.2083 | -15.506 | 86.148 | -75 | -14.3932 | 67.5497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/6:00
2 | 7 | 1900-01-06 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.25 | -15.4934 | 86.148 | -75 | -14.3962 | 82.5489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/7:00
2 | 7 | 1900-01-07 | -16.7 | 2 | 2 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 2 | 0 | 0 | 39.791 | 38.2917 | -15.4808 | 86.148 | -75 | -14.3992 | 97.5482 | -0.53619 | 1.4638 | 0.464 | 0.464 | 0 | 0 | 0 | 2/7/8:00
2 | 7 | 1900-01-08 | -17.2 | 40 | 235 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 40 | 0 | 0 | 39.791 | 38.3333 | -15.4682 | 86.148 | -75 | -14.4022 | 112.5474 | -106.843 | -66.843 | -21.1881 | -21.1881 | 0 | 0 | 0 | 2/7/9:00
2 | 7 | 1900-01-09 | -15.6 | 75 | 564 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 75 | 0 | 0 | 39.791 | 38.375 | -15.4556 | 86.148 | -75 | -14.4052 | 127.5467 | -350.7389 | -275.7389 | -87.4044 | -87.4044 | 0 | 0 | 0 | 2/7/10:00
2 | 7 | 1900-01-10 | -14.4 | 101 | 719 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 101 | 0 | 0 | 39.791 | 38.4167 | -15.443 | 86.148 | -75 | -14.4081 | 142.546 | -545.267 | -444.267 | -140.8249 | -140.8249 | 0 | 0 | 0 | 2/7/11:00
2 | 7 | 1900-01-11 | -13.3 | 119 | 786 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 119 | 0 | 0 | 39.791 | 38.4583 | -15.4304 | 86.148 | -75 | -14.411 | 157.5452 | -671.8803 | -552.8803 | -175.2534 | -175.2534 | 0 | 0 | 0 | 2/7/12:00
2 | 7 | 1900-01-12 | -12.2 | 128 | 822 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 128 | 0 | 0 | 39.791 | 38.5 | -15.4178 | 86.148 | -75 | -14.4139 | 172.5445 | -743.593 | -615.593 | -195.1322 | -195.1322 | 0 | 0 | 0 | 2/7/13:00
2 | 7 | 1900-01-13 | -10.6 | 210 | 614 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 210 | 0 | 0 | 39.791 | 38.5417 | -15.4051 | 86.148 | -75 | -14.4168 | 187.5438 | -555.2856 | -345.2856 | -109.4495 | -109.4495 | 0 | 0 | 0 | 2/7/14:00
2 | 7 | 1900-01-14 | -10 | 186 | 638 | 14 | 1 | 0 | 14 | 0 | 0 | 186 | 0 | 0 | 39.791 | 38.5833 | -15.3925 | 86.148 | -75 | -14.4197 | 202.5431 | -544.9091 | -358.9091 | -113.7679 | -113.7679 | 0 | 0 | 0 | 2/7/15:00
2 | 7 | 1900-01-15 | -9.4 | 112 | 637 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 112 | 0 | 0 | 39.791 | 38.625 | -15.3799 | 86.148 | -75 | -14.4225 | 217.5424 | -482.3185 | -370.3185 | -117.3845 | -117.3845 | 0 | 0 | 0 | 2/7/16:00
2 | 7 | 1900-01-16 | -9.4 | 74 | 536 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 74 | 0 | 0 | 39.791 | 38.6667 | -15.3672 | 86.148 | -75 | -14.4253 | 232.5417 | -332.4331 | -258.4331 | -81.9188 | -81.9188 | 0 | 0 | 0 | 2/7/17:00
2 | 7 | 1900-01-17 | -11.7 | 48 | 171 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 48 | 0 | 0 | 39.791 | 38.7083 | -15.3546 | 86.148 | -75 | -14.4281 | 247.541 | -77.3819 | -29.3819 | -9.3136 | -9.3136 | 0 | 0 | 0 | 2/7/18:00
2 | 7 | 1900-01-18 | -13.3 | 1 | 1 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 1 | 0 | 0 | 39.791 | 38.75 | -15.3419 | 86.148 | -75 | -14.4309 | 262.5403 | -0.26553 | 0.73447 | 0.23281 | 0.23281 | 0 | 0 | 0 | 2/7/19:00
2 | 7 | 1900-01-19 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.7917 | -15.3292 | 86.148 | -75 | -14.4336 | 277.5396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/20:00
2 | 7 | 1900-01-20 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.8333 | -15.3165 | 86.148 | -75 | -14.4363 | 292.5389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/21:00
2 | 7 | 1900-01-21 | -15.6 | 0 | 0 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.875 | -15.3039 | 86.148 | -75 | -14.439 | 307.5382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/22:00
2 | 7 | 1900-01-22 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.9167 | -15.2912 | 86.148 | -75 | -14.4417 | 322.5376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/23:00
2 | 7 | 1900-01-23 | -15.6 | 0 | 0 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 38.9583 | -15.2785 | 86.148 | -75 | -14.4443 | 337.5369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/7/24:00
2 | 8 | 1899-12-31 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39 | -15.2658 | 86.148 | -75 | -14.447 | -7.4637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/1:00
2 | 8 | 1900-01-01 | -17.2 | 0 | 0 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.0417 | -15.253 | 86.148 | -75 | -14.4496 | 7.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/2:00
2 | 8 | 1900-01-02 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.0833 | -15.2403 | 86.148 | -75 | -14.4522 | 22.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/3:00
2 | 8 | 1900-01-03 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.125 | -15.2276 | 86.148 | -75 | -14.4547 | 37.5343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/4:00
2 | 8 | 1900-01-04 | -19.4 | 0 | 0 | -2.92 | 1 | 0 | -2.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.1667 | -15.2149 | 86.148 | -75 | -14.4573 | 52.5337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/5:00
2 | 8 | 1900-01-05 | -21.1 | 0 | 0 | -5.98 | 1 | 0 | -5.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.2083 | -15.2021 | 86.148 | -75 | -14.4598 | 67.5331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/6:00
2 | 8 | 1900-01-06 | -20.6 | 0 | 0 | -5.08 | 1 | 0 | -5.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.25 | -15.1894 | 86.148 | -75 | -14.4623 | 82.5324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/7:00
2 | 8 | 1900-01-07 | -21.1 | 3 | 12 | -5.98 | 1 | 0 | -5.98 | 0 | 0 | 3 | 0 | 0 | 39.791 | 39.2917 | -15.1766 | 86.148 | -75 | -14.4647 | 97.5318 | -3.177 | -0.17701 | -0.056108 | -0.056108 | 0 | 0 | 0 | 2/8/8:00
2 | 8 | 1900-01-08 | -20.6 | 34 | 371 | -5.08 | 1 | 0 | -5.08 | 0 | 0 | 34 | 0 | 0 | 39.791 | 39.3333 | -15.1638 | 86.148 | -75 | -14.4672 | 112.5312 | -167.5403 | -133.5403 | -42.3299 | -42.3299 | 0 | 0 | 0 | 2/8/9:00
2 | 8 | 1900-01-09 | -18.3 | 62 | 666 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 62 | 0 | 0 | 39.791 | 39.375 | -15.1511 | 86.148 | -75 | -14.4696 | 127.5306 | -412.3126 | -350.3126 | -111.043 | -111.043 | 0 | 0 | 0 | 2/8/10:00
2 | 8 | 1900-01-10 | -15 | 78 | 808 | 5 | 1 | 0 | 5 | 0 | 0 | 78 | 0 | 0 | 39.791 | 39.4167 | -15.1383 | 86.148 | -75 | -14.472 | 142.53 | -610.6986 | -532.6986 | -168.8562 | -168.8562 | 0 | 0 | 0 | 2/8/11:00
2 | 8 | 1900-01-11 | -11.1 | 92 | 876 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 92 | 0 | 0 | 39.791 | 39.4583 | -15.1255 | 86.148 | -75 | -14.4744 | 157.5294 | -746.7389 | -654.7389 | -207.5408 | -207.5408 | 0 | 0 | 0 | 2/8/12:00
2 | 8 | 1900-01-12 | -8.9 | 98 | 897 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 98 | 0 | 0 | 39.791 | 39.5 | -15.1127 | 86.148 | -75 | -14.4768 | 172.5288 | -809.4247 | -711.4247 | -225.5092 | -225.5092 | 0 | 0 | 0 | 2/8/13:00
2 | 8 | 1900-01-13 | -6.1 | 98 | 898 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 98 | 0 | 0 | 39.791 | 39.5417 | -15.0999 | 86.148 | -75 | -14.4791 | 187.5282 | -810.1564 | -712.1564 | -225.7411 | -225.7411 | 0 | 0 | 0 | 2/8/14:00
2 | 8 | 1900-01-14 | -5.6 | 100 | 826 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 100 | 0 | 0 | 39.791 | 39.5833 | -15.0871 | 86.148 | -75 | -14.4814 | 202.5276 | -703.6437 | -603.6437 | -191.3445 | -191.3445 | 0 | 0 | 0 | 2/8/15:00
2 | 8 | 1900-01-15 | -6.1 | 100 | 692 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 100 | 0 | 0 | 39.791 | 39.625 | -15.0743 | 86.148 | -75 | -14.4837 | 217.5271 | -522.358 | -422.358 | -133.8801 | -133.8801 | 0 | 0 | 0 | 2/8/16:00
2 | 8 | 1900-01-16 | -6.7 | 61 | 661 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 61 | 0 | 0 | 39.791 | 39.6667 | -15.0615 | 86.148 | -75 | -14.486 | 232.5265 | -408.3167 | -347.3167 | -110.0933 | -110.0933 | 0 | 0 | 0 | 2/8/17:00
2 | 8 | 1900-01-17 | -9.4 | 45 | 220 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 45 | 0 | 0 | 39.791 | 39.7083 | -15.0486 | 86.148 | -75 | -14.4882 | 247.5259 | -98.9602 | -53.9602 | -17.1044 | -17.1044 | 0 | 0 | 0 | 2/8/18:00
2 | 8 | 1900-01-18 | -10 | 2 | 4 | 14 | 1 | 0 | 14 | 0 | 0 | 2 | 0 | 0 | 39.791 | 39.75 | -15.0358 | 86.148 | -75 | -14.4904 | 262.5254 | -1.0502 | 0.94975 | 0.30105 | 0.30105 | 0 | 0 | 0 | 2/8/19:00
2 | 8 | 1900-01-19 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.7917 | -15.0229 | 86.148 | -75 | -14.4926 | 277.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/20:00
2 | 8 | 1900-01-20 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.8333 | -15.0101 | 86.148 | -75 | -14.4948 | 292.5243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/21:00
2 | 8 | 1900-01-21 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.875 | -14.9972 | 86.148 | -75 | -14.497 | 307.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/22:00
2 | 8 | 1900-01-22 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.9167 | -14.9844 | 86.148 | -75 | -14.4991 | 322.5232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/23:00
2 | 8 | 1900-01-23 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 39.9583 | -14.9715 | 86.148 | -75 | -14.5012 | 337.5227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/8/24:00
2 | 9 | 1899-12-31 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40 | -14.9586 | 86.148 | -75 | -14.5033 | -7.4778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/1:00
2 | 9 | 1900-01-01 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.0417 | -14.9457 | 86.148 | -75 | -14.5054 | 7.5217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/2:00
2 | 9 | 1900-01-02 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.0833 | -14.9328 | 86.148 | -75 | -14.5074 | 22.5211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/3:00
2 | 9 | 1900-01-03 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.125 | -14.9199 | 86.148 | -75 | -14.5094 | 37.5206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/4:00
2 | 9 | 1900-01-04 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.1667 | -14.907 | 86.148 | -75 | -14.5114 | 52.5201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/5:00
2 | 9 | 1900-01-05 | -15.6 | 0 | 0 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.2083 | -14.8941 | 86.148 | -75 | -14.5134 | 67.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/6:00
2 | 9 | 1900-01-06 | -16.1 | 0 | 0 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.25 | -14.8812 | 86.148 | -75 | -14.5154 | 82.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/7:00
2 | 9 | 1900-01-07 | -14.4 | 3 | 4 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 3 | 0 | 0 | 39.791 | 40.2917 | -14.8683 | 86.148 | -75 | -14.5173 | 97.5187 | -1.0456 | 1.9544 | 0.61952 | 0.61952 | 0 | 0 | 0 | 2/9/8:00
2 | 9 | 1900-01-08 | -13.3 | 51 | 21 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 51 | 0 | 0 | 39.791 | 40.3333 | -14.8553 | 86.148 | -75 | -14.5192 | 112.5182 | -9.4189 | 41.5811 | 13.1805 | 13.1805 | 0 | 0 | 0 | 2/9/9:00
2 | 9 | 1900-01-09 | -11.1 | 149 | 95 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 149 | 0 | 0 | 39.791 | 40.375 | -14.8424 | 86.148 | -75 | -14.5211 | 127.5177 | -58.5464 | 90.4536 | 28.6722 | 28.6722 | 0 | 0 | 0 | 2/9/10:00
2 | 9 | 1900-01-10 | -8.9 | 245 | 338 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 245 | 0 | 0 | 39.791 | 40.4167 | -14.8294 | 86.148 | -75 | -14.523 | 142.5173 | -254.5924 | -9.5924 | -3.0406 | -3.0406 | 0 | 0 | 0 | 2/9/11:00
2 | 9 | 1900-01-11 | -7.2 | 353 | 132 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 353 | 0 | 0 | 39.791 | 40.4583 | -14.8165 | 86.148 | -75 | -14.5248 | 157.5168 | -112.2045 | 240.7955 | 76.328 | 76.328 | 0 | 0 | 0 | 2/9/12:00
2 | 9 | 1900-01-12 | -6.7 | 284 | 200 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 284 | 0 | 0 | 39.791 | 40.5 | -14.8035 | 86.148 | -75 | -14.5266 | 172.5163 | -180.0144 | 103.9856 | 32.9616 | 32.9616 | 0 | 0 | 0 | 2/9/13:00
2 | 9 | 1900-01-13 | -5 | 355 | 115 | 23 | 1 | 0 | 23 | 0 | 0 | 355 | 0 | 0 | 39.791 | 40.5417 | -14.7905 | 86.148 | -75 | -14.5284 | 187.5159 | -103.491 | 251.509 | 79.724 | 79.724 | 0 | 0 | 0 | 2/9/14:00
2 | 9 | 1900-01-14 | -4.4 | 250 | 276 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 250 | 0 | 0 | 39.791 | 40.5833 | -14.7775 | 86.148 | -75 | -14.5302 | 202.5155 | -234.4832 | 15.5168 | 4.9186 | 4.9186 | 0 | 0 | 0 | 2/9/15:00
2 | 9 | 1900-01-15 | -4.4 | 205 | 5 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 205 | 0 | 0 | 39.791 | 40.625 | -14.7646 | 86.148 | -75 | -14.5319 | 217.515 | -3.7623 | 201.2377 | 63.7888 | 63.7888 | 0 | 0 | 0 | 2/9/16:00
2 | 9 | 1900-01-16 | -4.4 | 105 | 2 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 105 | 0 | 0 | 39.791 | 40.6667 | -14.7516 | 86.148 | -75 | -14.5337 | 232.5146 | -1.2303 | 103.7697 | 32.8932 | 32.8932 | 0 | 0 | 0 | 2/9/17:00
2 | 9 | 1900-01-17 | -4.4 | 39 | 6 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 39 | 0 | 0 | 39.791 | 40.7083 | -14.7386 | 86.148 | -75 | -14.5354 | 247.5142 | -2.6821 | 36.3179 | 11.5121 | 11.5121 | 0 | 0 | 0 | 2/9/18:00
2 | 9 | 1900-01-18 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.75 | -14.7256 | 86.148 | -75 | -14.5371 | 262.5137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/19:00
2 | 9 | 1900-01-19 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.7917 | -14.7125 | 86.148 | -75 | -14.5387 | 277.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/20:00
2 | 9 | 1900-01-20 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.8333 | -14.6995 | 86.148 | -75 | -14.5404 | 292.5129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/21:00
2 | 9 | 1900-01-21 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.875 | -14.6865 | 86.148 | -75 | -14.542 | 307.5125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/22:00
2 | 9 | 1900-01-22 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.9167 | -14.6735 | 86.148 | -75 | -14.5436 | 322.5121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/23:00
2 | 9 | 1900-01-23 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 40.9583 | -14.6604 | 86.148 | -75 | -14.5451 | 337.5117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/9/24:00
2 | 10 | 1899-12-31 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41 | -14.6474 | 86.148 | -75 | -14.5467 | -7.4887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/1:00
2 | 10 | 1900-01-01 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.0417 | -14.6343 | 86.148 | -75 | -14.5482 | 7.5109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/2:00
2 | 10 | 1900-01-02 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.0833 | -14.6213 | 86.148 | -75 | -14.5497 | 22.5106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/3:00
2 | 10 | 1900-01-03 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.125 | -14.6082 | 86.148 | -75 | -14.5512 | 37.5102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/4:00
2 | 10 | 1900-01-04 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.1667 | -14.5951 | 86.148 | -75 | -14.5527 | 52.5098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/5:00
2 | 10 | 1900-01-05 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.2083 | -14.582 | 86.148 | -75 | -14.5541 | 67.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/6:00
2 | 10 | 1900-01-06 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.25 | -14.5689 | 86.148 | -75 | -14.5555 | 82.5091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/7:00
2 | 10 | 1900-01-07 | -5 | 3 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 3 | 0 | 0 | 39.791 | 41.2917 | -14.5558 | 86.148 | -75 | -14.5569 | 97.5088 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 2/10/8:00
2 | 10 | 1900-01-08 | -4.4 | 49 | 4 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 49 | 0 | 0 | 39.791 | 41.3333 | -14.5427 | 86.148 | -75 | -14.5583 | 112.5084 | -1.7817 | 47.2183 | 14.9674 | 14.9674 | 0 | 0 | 0 | 2/10/9:00
2 | 10 | 1900-01-09 | -3.9 | 139 | 2 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 139 | 0 | 0 | 39.791 | 41.375 | -14.5296 | 86.148 | -75 | -14.5596 | 127.5081 | -1.2269 | 137.7731 | 43.6717 | 43.6717 | 0 | 0 | 0 | 2/10/10:00
2 | 10 | 1900-01-10 | -3.3 | 206 | 4 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 206 | 0 | 0 | 39.791 | 41.4167 | -14.5165 | 86.148 | -75 | -14.5609 | 142.5078 | -3.0025 | 202.9975 | 64.3467 | 64.3467 | 0 | 0 | 0 | 2/10/11:00
2 | 10 | 1900-01-11 | -2.8 | 284 | 3 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 284 | 0 | 0 | 39.791 | 41.4583 | -14.5034 | 86.148 | -75 | -14.5622 | 157.5074 | -2.5428 | 281.4572 | 89.217 | 89.217 | 0 | 0 | 0 | 2/10/12:00
2 | 10 | 1900-01-12 | -2.2 | 332 | 2 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 332 | 0 | 0 | 39.791 | 41.5 | -14.4903 | 86.148 | -75 | -14.5635 | 172.5071 | -1.7954 | 330.2046 | 104.6691 | 104.6691 | 0 | 0 | 0 | 2/10/13:00
2 | 10 | 1900-01-13 | -1.1 | 351 | 1 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 351 | 0 | 0 | 39.791 | 41.5417 | -14.4771 | 86.148 | -75 | -14.5648 | 187.5068 | -0.8976 | 350.1024 | 110.9763 | 110.9763 | 0 | 0 | 0 | 2/10/14:00
2 | 10 | 1900-01-14 | -0.6 | 306 | 1 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 306 | 0 | 0 | 39.791 | 41.5833 | -14.464 | 86.148 | -75 | -14.566 | 202.5065 | -0.84721 | 305.1528 | 96.7281 | 96.7281 | 0 | 0 | 0 | 2/10/15:00
2 | 10 | 1900-01-15 | 0.6 | 153 | 1 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 153 | 0 | 0 | 39.791 | 41.625 | -14.4508 | 86.148 | -75 | -14.5672 | 217.5062 | -0.74997 | 152.25 | 48.2606 | 48.2606 | 0 | 0 | 0 | 2/10/16:00
2 | 10 | 1900-01-16 | 0.6 | 103 | 1 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 103 | 0 | 0 | 39.791 | 41.6667 | -14.4377 | 86.148 | -75 | -14.5684 | 232.5059 | -0.6125 | 102.3875 | 32.4551 | 32.4551 | 0 | 0 | 0 | 2/10/17:00
2 | 10 | 1900-01-17 | 0.6 | 32 | 1 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 32 | 0 | 0 | 39.791 | 41.7083 | -14.4245 | 86.148 | -75 | -14.5696 | 247.5056 | -0.44414 | 31.5559 | 10.0027 | 10.0027 | 0 | 0 | 0 | 2/10/18:00
2 | 10 | 1900-01-18 | 1.1 | 3 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 3 | 0 | 0 | 39.791 | 41.75 | -14.4113 | 86.148 | -75 | -14.5707 | 262.5053 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 2/10/19:00
2 | 10 | 1900-01-19 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.7917 | -14.3981 | 86.148 | -75 | -14.5719 | 277.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/20:00
2 | 10 | 1900-01-20 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.8333 | -14.385 | 86.148 | -75 | -14.573 | 292.5048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/21:00
2 | 10 | 1900-01-21 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.875 | -14.3718 | 86.148 | -75 | -14.574 | 307.5045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/22:00
2 | 10 | 1900-01-22 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.9167 | -14.3586 | 86.148 | -75 | -14.5751 | 322.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/23:00
2 | 10 | 1900-01-23 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 41.9583 | -14.3454 | 86.148 | -75 | -14.5761 | 337.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/10/24:00
2 | 11 | 1899-12-31 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42 | -14.3321 | 86.148 | -75 | -14.5771 | -7.4963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/1:00
2 | 11 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.0417 | -14.3189 | 86.148 | -75 | -14.5781 | 7.5035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/2:00
2 | 11 | 1900-01-02 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.0833 | -14.3057 | 86.148 | -75 | -14.5791 | 22.5032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/3:00
2 | 11 | 1900-01-03 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.125 | -14.2925 | 86.148 | -75 | -14.58 | 37.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/4:00
2 | 11 | 1900-01-04 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.1667 | -14.2792 | 86.148 | -75 | -14.581 | 52.5028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/5:00
2 | 11 | 1900-01-05 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.2083 | -14.266 | 86.148 | -75 | -14.5819 | 67.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/6:00
2 | 11 | 1900-01-06 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.25 | -14.2527 | 86.148 | -75 | -14.5827 | 82.5023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/7:00
2 | 11 | 1900-01-07 | 2.2 | 3 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 3 | 0 | 0 | 39.791 | 42.2917 | -14.2395 | 86.148 | -75 | -14.5836 | 97.5021 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 2/11/8:00
2 | 11 | 1900-01-08 | 2.2 | 42 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 42 | 0 | 0 | 39.791 | 42.3333 | -14.2262 | 86.148 | -75 | -14.5844 | 112.5019 | 0 | 42 | 13.3133 | 13.3133 | 0 | 0 | 0 | 2/11/9:00
2 | 11 | 1900-01-09 | 2.2 | 108 | 1 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 108 | 0 | 0 | 39.791 | 42.375 | -14.2129 | 86.148 | -75 | -14.5852 | 127.5017 | -0.6106 | 107.3894 | 34.0406 | 34.0406 | 0 | 0 | 0 | 2/11/10:00
2 | 11 | 1900-01-10 | 2.2 | 146 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 146 | 0 | 0 | 39.791 | 42.4167 | -14.1996 | 86.148 | -75 | -14.586 | 142.5015 | 0 | 146 | 46.2795 | 46.2795 | 0 | 0 | 0 | 2/11/11:00
2 | 11 | 1900-01-11 | 2.8 | 211 | 1 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 211 | 0 | 0 | 39.791 | 42.4583 | -14.1864 | 86.148 | -75 | -14.5868 | 157.5013 | -0.8451 | 210.1549 | 66.6154 | 66.6154 | 0 | 0 | 0 | 2/11/12:00
2 | 11 | 1900-01-12 | 2.8 | 217 | 1 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 217 | 0 | 0 | 39.791 | 42.5 | -14.1731 | 86.148 | -75 | -14.5875 | 172.5011 | -0.89533 | 216.1047 | 68.5014 | 68.5014 | 0 | 0 | 0 | 2/11/13:00
2 | 11 | 1900-01-13 | 2.8 | 233 | 2 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 233 | 0 | 0 | 39.791 | 42.5417 | -14.1598 | 86.148 | -75 | -14.5883 | 187.5009 | -1.7904 | 231.2096 | 73.2894 | 73.2894 | 0 | 0 | 0 | 2/11/14:00
2 | 11 | 1900-01-14 | 2.8 | 205 | 1 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 205 | 0 | 0 | 39.791 | 42.5833 | -14.1465 | 86.148 | -75 | -14.589 | 202.5008 | -0.84478 | 204.1552 | 64.7136 | 64.7136 | 0 | 0 | 0 | 2/11/15:00
2 | 11 | 1900-01-15 | 2.8 | 164 | 1 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 164 | 0 | 0 | 39.791 | 42.625 | -14.1331 | 86.148 | -75 | -14.5896 | 217.5006 | -0.74741 | 163.2526 | 51.7482 | 51.7482 | 0 | 0 | 0 | 2/11/16:00
2 | 11 | 1900-01-16 | 2.2 | 104 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 104 | 0 | 0 | 39.791 | 42.6667 | -14.1198 | 86.148 | -75 | -14.5903 | 232.5004 | 0 | 104 | 32.9662 | 32.9662 | 0 | 0 | 0 | 2/11/17:00
2 | 11 | 1900-01-17 | 2.2 | 36 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 36 | 0 | 0 | 39.791 | 42.7083 | -14.1065 | 86.148 | -75 | -14.5909 | 247.5003 | 0 | 36 | 11.4114 | 11.4114 | 0 | 0 | 0 | 2/11/18:00
2 | 11 | 1900-01-18 | 1.1 | 5 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 5 | 0 | 0 | 39.791 | 42.75 | -14.0932 | 86.148 | -75 | -14.5915 | 262.5001 | 0 | 5 | 1.5849 | 1.5849 | 0 | 0 | 0 | 2/11/19:00
2 | 11 | 1900-01-19 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.7917 | -14.0798 | 86.148 | -75 | -14.5921 | 277.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/20:00
2 | 11 | 1900-01-20 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.8333 | -14.0665 | 86.148 | -75 | -14.5927 | 292.4998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/21:00
2 | 11 | 1900-01-21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.875 | -14.0531 | 86.148 | -75 | -14.5932 | 307.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/22:00
2 | 11 | 1900-01-22 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.9167 | -14.0398 | 86.148 | -75 | -14.5938 | 322.4996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/23:00
2 | 11 | 1900-01-23 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 42.9583 | -14.0264 | 86.148 | -75 | -14.5943 | 337.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/11/24:00
2 | 12 | 1899-12-31 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43 | -14.013 | 86.148 | -75 | -14.5947 | -7.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/1:00
2 | 12 | 1900-01-01 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.0417 | -13.9996 | 86.148 | -75 | -14.5952 | 7.4992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/2:00
2 | 12 | 1900-01-02 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.0833 | -13.9863 | 86.148 | -75 | -14.5956 | 22.4991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/3:00
2 | 12 | 1900-01-03 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.125 | -13.9729 | 86.148 | -75 | -14.596 | 37.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/4:00
2 | 12 | 1900-01-04 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.1667 | -13.9595 | 86.148 | -75 | -14.5964 | 52.4989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/5:00
2 | 12 | 1900-01-05 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.2083 | -13.9461 | 86.148 | -75 | -14.5968 | 67.4988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/6:00
2 | 12 | 1900-01-06 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.25 | -13.9327 | 86.148 | -75 | -14.5971 | 82.4987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/7:00
2 | 12 | 1900-01-07 | -3.3 | 5 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 5 | 0 | 0 | 39.791 | 43.2917 | -13.9192 | 86.148 | -75 | -14.5974 | 97.4986 | 0 | 5 | 1.5849 | 1.5849 | 0 | 0 | 0 | 2/12/8:00
2 | 12 | 1900-01-08 | -3.9 | 64 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 64 | 0 | 0 | 39.791 | 43.3333 | -13.9058 | 86.148 | -75 | -14.5977 | 112.4986 | 0 | 64 | 20.2869 | 20.2869 | 0 | 0 | 0 | 2/12/9:00
2 | 12 | 1900-01-09 | -3.9 | 169 | 1 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 169 | 0 | 0 | 39.791 | 43.375 | -13.8924 | 86.148 | -75 | -14.598 | 127.4985 | -0.60772 | 168.3923 | 53.3774 | 53.3774 | 0 | 0 | 0 | 2/12/10:00
2 | 12 | 1900-01-10 | -3.9 | 272 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 272 | 0 | 0 | 39.791 | 43.4167 | -13.8789 | 86.148 | -75 | -14.5983 | 142.4984 | 0 | 272 | 86.2192 | 86.2192 | 0 | 0 | 0 | 2/12/11:00
2 | 12 | 1900-01-11 | -4.4 | 325 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 325 | 0 | 0 | 39.791 | 43.4583 | -13.8655 | 86.148 | -75 | -14.5985 | 157.4984 | 0 | 325 | 103.0193 | 103.0193 | 0 | 0 | 0 | 2/12/12:00
2 | 12 | 1900-01-12 | -4.4 | 382 | 1 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 382 | 0 | 0 | 39.791 | 43.5 | -13.852 | 86.148 | -75 | -14.5987 | 172.4983 | -0.89288 | 381.1071 | 120.8043 | 120.8043 | 0 | 0 | 0 | 2/12/13:00
2 | 12 | 1900-01-13 | -5 | 345 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 345 | 0 | 0 | 39.791 | 43.5417 | -13.8386 | 86.148 | -75 | -14.5989 | 187.4983 | 0 | 345 | 109.359 | 109.359 | 0 | 0 | 0 | 2/12/14:00
2 | 12 | 1900-01-14 | -5 | 312 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 312 | 0 | 0 | 39.791 | 43.5833 | -13.8251 | 86.148 | -75 | -14.5991 | 202.4982 | 0 | 312 | 98.8986 | 98.8986 | 0 | 0 | 0 | 2/12/15:00
2 | 12 | 1900-01-15 | -5 | 259 | 1 | 23 | 1 | 0 | 23 | 0 | 0 | 259 | 0 | 0 | 39.791 | 43.625 | -13.8117 | 86.148 | -75 | -14.5992 | 217.4982 | -0.74477 | 258.2552 | 81.8624 | 81.8624 | 0 | 0 | 0 | 2/12/16:00
2 | 12 | 1900-01-16 | -5.6 | 176 | 1 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 176 | 0 | 0 | 39.791 | 43.6667 | -13.7982 | 86.148 | -75 | -14.5993 | 232.4982 | -0.60692 | 175.3931 | 55.5965 | 55.5965 | 0 | 0 | 0 | 2/12/17:00
2 | 12 | 1900-01-17 | -6.1 | 63 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 63 | 0 | 0 | 39.791 | 43.7083 | -13.7847 | 86.148 | -75 | -14.5994 | 247.4981 | 0 | 63 | 19.9699 | 19.9699 | 0 | 0 | 0 | 2/12/18:00
2 | 12 | 1900-01-18 | -6.1 | 6 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 6 | 0 | 0 | 39.791 | 43.75 | -13.7712 | 86.148 | -75 | -14.5995 | 262.4981 | 0 | 6 | 1.9019 | 1.9019 | 0 | 0 | 0 | 2/12/19:00
2 | 12 | 1900-01-19 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.7917 | -13.7577 | 86.148 | -75 | -14.5996 | 277.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/20:00
2 | 12 | 1900-01-20 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.8333 | -13.7442 | 86.148 | -75 | -14.5996 | 292.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/21:00
2 | 12 | 1900-01-21 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.875 | -13.7307 | 86.148 | -75 | -14.5996 | 307.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/22:00
2 | 12 | 1900-01-22 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.9167 | -13.7172 | 86.148 | -75 | -14.5996 | 322.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/23:00
2 | 12 | 1900-01-23 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 43.9583 | -13.7037 | 86.148 | -75 | -14.5996 | 337.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/12/24:00
2 | 13 | 1899-12-31 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44 | -13.6901 | 86.148 | -75 | -14.5995 | -7.5019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/1:00
2 | 13 | 1900-01-01 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.0417 | -13.6766 | 86.148 | -75 | -14.5994 | 7.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/2:00
2 | 13 | 1900-01-02 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.0833 | -13.663 | 86.148 | -75 | -14.5993 | 22.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/3:00
2 | 13 | 1900-01-03 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.125 | -13.6495 | 86.148 | -75 | -14.5992 | 37.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/4:00
2 | 13 | 1900-01-04 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.1667 | -13.6359 | 86.148 | -75 | -14.5991 | 52.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/5:00
2 | 13 | 1900-01-05 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.2083 | -13.6224 | 86.148 | -75 | -14.5989 | 67.4983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/6:00
2 | 13 | 1900-01-06 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.25 | -13.6088 | 86.148 | -75 | -14.5987 | 82.4983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/7:00
2 | 13 | 1900-01-07 | -9.4 | 8 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 8 | 0 | 0 | 39.791 | 44.2917 | -13.5952 | 86.148 | -75 | -14.5985 | 97.4984 | 0 | 8 | 2.5359 | 2.5359 | 0 | 0 | 0 | 2/13/8:00
2 | 13 | 1900-01-08 | -9.4 | 67 | 1 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 67 | 0 | 0 | 39.791 | 44.3333 | -13.5817 | 86.148 | -75 | -14.5983 | 112.4984 | -0.4361 | 66.5639 | 21.0996 | 21.0996 | 0 | 0 | 0 | 2/13/9:00
2 | 13 | 1900-01-09 | -9.4 | 170 | 1 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 170 | 0 | 0 | 39.791 | 44.375 | -13.5681 | 86.148 | -75 | -14.598 | 127.4985 | -0.60483 | 169.3952 | 53.6953 | 53.6953 | 0 | 0 | 0 | 2/13/10:00
2 | 13 | 1900-01-10 | -9.4 | 287 | 1 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 287 | 0 | 0 | 39.791 | 44.4167 | -13.5545 | 86.148 | -75 | -14.5978 | 142.4986 | -0.7426 | 286.2574 | 90.7386 | 90.7386 | 0 | 0 | 0 | 2/13/11:00
2 | 13 | 1900-01-11 | -8.3 | 242 | 406 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 242 | 0 | 0 | 39.791 | 44.4583 | -13.5409 | 86.148 | -75 | -14.5975 | 157.4986 | -341.0405 | -99.0405 | -31.3941 | -31.3941 | 0 | 0 | 0 | 2/13/12:00
2 | 13 | 1900-01-12 | -7.2 | 265 | 665 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 265 | 0 | 0 | 39.791 | 44.5 | -13.5273 | 86.148 | -75 | -14.5971 | 172.4987 | -592.0983 | -327.0983 | -103.6844 | -103.6844 | 0 | 0 | 0 | 2/13/13:00
2 | 13 | 1900-01-13 | -6.7 | 166 | 810 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 166 | 0 | 0 | 39.791 | 44.5417 | -13.5137 | 86.148 | -75 | -14.5968 | 187.4988 | -721.1204 | -555.1204 | -175.9635 | -175.9635 | 0 | 0 | 0 | 2/13/14:00
2 | 13 | 1900-01-14 | -6.1 | 194 | 813 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 194 | 0 | 0 | 39.791 | 44.5833 | -13.5001 | 86.148 | -75 | -14.5964 | 202.4989 | -682.6666 | -488.6666 | -154.8988 | -154.8988 | 0 | 0 | 0 | 2/13/15:00
2 | 13 | 1900-01-15 | -5.6 | 234 | 125 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 234 | 0 | 0 | 39.791 | 44.625 | -13.4864 | 86.148 | -75 | -14.5961 | 217.499 | -92.7567 | 141.2433 | 44.7717 | 44.7717 | 0 | 0 | 0 | 2/13/16:00
2 | 13 | 1900-01-16 | -5.6 | 169 | 145 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 169 | 0 | 0 | 39.791 | 44.6667 | -13.4728 | 86.148 | -75 | -14.5957 | 232.4991 | -87.5809 | 81.4191 | 25.8084 | 25.8084 | 0 | 0 | 0 | 2/13/17:00
2 | 13 | 1900-01-17 | -4.4 | 60 | 46 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 60 | 0 | 0 | 39.791 | 44.7083 | -13.4592 | 86.148 | -75 | -14.5952 | 247.4992 | -20.0073 | 39.9927 | 12.677 | 12.677 | 0 | 0 | 0 | 2/13/18:00
2 | 13 | 1900-01-18 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.75 | -13.4455 | 86.148 | -75 | -14.5948 | 262.4993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/19:00
2 | 13 | 1900-01-19 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.7917 | -13.4319 | 86.148 | -75 | -14.5943 | 277.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/20:00
2 | 13 | 1900-01-20 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.8333 | -13.4182 | 86.148 | -75 | -14.5938 | 292.4995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/21:00
2 | 13 | 1900-01-21 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.875 | -13.4046 | 86.148 | -75 | -14.5933 | 307.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/22:00
2 | 13 | 1900-01-22 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.9167 | -13.3909 | 86.148 | -75 | -14.5927 | 322.4998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/23:00
2 | 13 | 1900-01-23 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 44.9583 | -13.3772 | 86.148 | -75 | -14.5922 | 337.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/13/24:00
2 | 14 | 1899-12-31 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45 | -13.3635 | 86.148 | -75 | -14.5916 | -7.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/1:00
2 | 14 | 1900-01-01 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.0417 | -13.3498 | 86.148 | -75 | -14.591 | 7.5003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/2:00
2 | 14 | 1900-01-02 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.0833 | -13.3362 | 86.148 | -75 | -14.5904 | 22.5004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/3:00
2 | 14 | 1900-01-03 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.125 | -13.3225 | 86.148 | -75 | -14.5897 | 37.5006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/4:00
2 | 14 | 1900-01-04 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.1667 | -13.3087 | 86.148 | -75 | -14.5891 | 52.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/5:00
2 | 14 | 1900-01-05 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.2083 | -13.295 | 86.148 | -75 | -14.5884 | 67.5009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/6:00
2 | 14 | 1900-01-06 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.25 | -13.2813 | 86.148 | -75 | -14.5876 | 82.5011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/7:00
2 | 14 | 1900-01-07 | -7.8 | 3 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 3 | 0 | 0 | 39.791 | 45.2917 | -13.2676 | 86.148 | -75 | -14.5869 | 97.5013 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 2/14/8:00
2 | 14 | 1900-01-08 | -7.8 | 62 | 161 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 62 | 0 | 0 | 39.791 | 45.3333 | -13.2539 | 86.148 | -75 | -14.5862 | 112.5015 | -69.7067 | -7.7067 | -2.4429 | -2.4429 | 0 | 0 | 0 | 2/14/9:00
2 | 14 | 1900-01-09 | -7.8 | 199 | 101 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 199 | 0 | 0 | 39.791 | 45.375 | -13.2401 | 86.148 | -75 | -14.5854 | 127.5017 | -60.7944 | 138.2056 | 43.8088 | 43.8088 | 0 | 0 | 0 | 2/14/10:00
2 | 14 | 1900-01-10 | -7.8 | 185 | 7 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 185 | 0 | 0 | 39.791 | 45.4167 | -13.2264 | 86.148 | -75 | -14.5846 | 142.5019 | -5.1791 | 179.8209 | 57.0001 | 57.0001 | 0 | 0 | 0 | 2/14/11:00
2 | 14 | 1900-01-11 | -7.2 | 250 | 3 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 250 | 0 | 0 | 39.791 | 45.4583 | -13.2126 | 86.148 | -75 | -14.5837 | 157.5021 | -2.5122 | 247.4878 | 78.4493 | 78.4493 | 0 | 0 | 0 | 2/14/12:00
2 | 14 | 1900-01-12 | -7.2 | 394 | 265 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 394 | 0 | 0 | 39.791 | 45.5 | -13.1989 | 86.148 | -75 | -14.5829 | 172.5023 | -235.2722 | 158.7278 | 50.3139 | 50.3139 | 0 | 0 | 0 | 2/14/13:00
2 | 14 | 1900-01-13 | -7.2 | 263 | 69 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 263 | 0 | 0 | 39.791 | 45.5417 | -13.1851 | 86.148 | -75 | -14.582 | 187.5025 | -61.2516 | 201.7484 | 63.9507 | 63.9507 | 0 | 0 | 0 | 2/14/14:00
2 | 14 | 1900-01-14 | -6.7 | 273 | 1 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 273 | 0 | 0 | 39.791 | 45.5833 | -13.1714 | 86.148 | -75 | -14.5811 | 202.5027 | -0.83704 | 272.163 | 86.2709 | 86.2709 | 0 | 0 | 0 | 2/14/15:00
2 | 14 | 1900-01-15 | -7.2 | 245 | 233 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 245 | 0 | 0 | 39.791 | 45.625 | -13.1576 | 86.148 | -75 | -14.5802 | 217.5029 | -172.2462 | 72.7538 | 23.0617 | 23.0617 | 0 | 0 | 0 | 2/14/16:00
2 | 14 | 1900-01-16 | -7.2 | 165 | 43 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 165 | 0 | 0 | 39.791 | 45.6667 | -13.1438 | 86.148 | -75 | -14.5793 | 232.5032 | -25.8433 | 139.1567 | 44.1103 | 44.1103 | 0 | 0 | 0 | 2/14/17:00
2 | 14 | 1900-01-17 | -7.8 | 50 | 11 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 50 | 0 | 0 | 39.791 | 45.7083 | -13.13 | 86.148 | -75 | -14.5783 | 247.5034 | -4.7487 | 45.2513 | 14.3439 | 14.3439 | 0 | 0 | 0 | 2/14/18:00
2 | 14 | 1900-01-18 | -8.3 | 7 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 7 | 0 | 0 | 39.791 | 45.75 | -13.1162 | 86.148 | -75 | -14.5774 | 262.5037 | 0 | 7 | 2.2189 | 2.2189 | 0 | 0 | 0 | 2/14/19:00
2 | 14 | 1900-01-19 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.7917 | -13.1024 | 86.148 | -75 | -14.5764 | 277.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/20:00
2 | 14 | 1900-01-20 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.8333 | -13.0886 | 86.148 | -75 | -14.5754 | 292.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/21:00
2 | 14 | 1900-01-21 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.875 | -13.0748 | 86.148 | -75 | -14.5743 | 307.5044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/22:00
2 | 14 | 1900-01-22 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.9167 | -13.061 | 86.148 | -75 | -14.5733 | 322.5047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/23:00
2 | 14 | 1900-01-23 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 45.9583 | -13.0472 | 86.148 | -75 | -14.5722 | 337.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/14/24:00
2 | 15 | 1899-12-31 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46 | -13.0334 | 86.148 | -75 | -14.5711 | -7.4948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/1:00
2 | 15 | 1900-01-01 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.0417 | -13.0195 | 86.148 | -75 | -14.5699 | 7.5055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/2:00
2 | 15 | 1900-01-02 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.0833 | -13.0057 | 86.148 | -75 | -14.5688 | 22.5058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/3:00
2 | 15 | 1900-01-03 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.125 | -12.9918 | 86.148 | -75 | -14.5676 | 37.5061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/4:00
2 | 15 | 1900-01-04 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.1667 | -12.978 | 86.148 | -75 | -14.5664 | 52.5064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/5:00
2 | 15 | 1900-01-05 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.2083 | -12.9641 | 86.148 | -75 | -14.5652 | 67.5067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/6:00
2 | 15 | 1900-01-06 | -16.1 | 0 | 0 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.25 | -12.9503 | 86.148 | -75 | -14.564 | 82.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/7:00
2 | 15 | 1900-01-07 | -16.7 | 7 | 8 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 7 | 0 | 0 | 39.791 | 46.2917 | -12.9364 | 86.148 | -75 | -14.5627 | 97.5073 | -1.9289 | 5.0711 | 1.6074 | 1.6074 | 0 | 0 | 0 | 2/15/8:00
2 | 15 | 1900-01-08 | -16.1 | 56 | 252 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 56 | 0 | 0 | 39.791 | 46.3333 | -12.9225 | 86.148 | -75 | -14.5614 | 112.5076 | -108.3135 | -52.3135 | -16.5825 | -16.5825 | 0 | 0 | 0 | 2/15/9:00
2 | 15 | 1900-01-09 | -13.9 | 85 | 608 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 85 | 0 | 0 | 39.791 | 46.375 | -12.9086 | 86.148 | -75 | -14.5601 | 127.508 | -364.1891 | -279.1891 | -88.4981 | -88.4981 | 0 | 0 | 0 | 2/15/10:00
2 | 15 | 1900-01-10 | -12.2 | 113 | 740 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 113 | 0 | 0 | 39.791 | 46.4167 | -12.8947 | 86.148 | -75 | -14.5588 | 142.5083 | -545.4639 | -432.4639 | -137.0835 | -137.0835 | 0 | 0 | 0 | 2/15/11:00
2 | 15 | 1900-01-11 | -11.1 | 133 | 811 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 133 | 0 | 0 | 39.791 | 46.4583 | -12.8808 | 86.148 | -75 | -14.5575 | 157.5086 | -676.9763 | -543.9763 | -172.431 | -172.431 | 0 | 0 | 0 | 2/15/12:00
2 | 15 | 1900-01-12 | -10 | 142 | 833 | 14 | 1 | 0 | 14 | 0 | 0 | 142 | 0 | 0 | 39.791 | 46.5 | -12.8669 | 86.148 | -75 | -14.5561 | 172.509 | -737.3835 | -595.3835 | -188.7262 | -188.7262 | 0 | 0 | 0 | 2/15/13:00
2 | 15 | 1900-01-13 | -8.9 | 141 | 827 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 141 | 0 | 0 | 39.791 | 46.5417 | -12.853 | 86.148 | -75 | -14.5547 | 187.5093 | -731.9552 | -590.9552 | -187.3225 | -187.3225 | 0 | 0 | 0 | 2/15/14:00
2 | 15 | 1900-01-14 | -7.8 | 132 | 806 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 132 | 0 | 0 | 39.791 | 46.5833 | -12.8391 | 86.148 | -75 | -14.5533 | 202.5097 | -672.4553 | -540.4553 | -171.3149 | -171.3149 | 0 | 0 | 0 | 2/15/15:00
2 | 15 | 1900-01-15 | -7.2 | 113 | 737 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 113 | 0 | 0 | 39.791 | 46.625 | -12.8252 | 86.148 | -75 | -14.5519 | 217.51 | -542.7083 | -429.7083 | -136.21 | -136.21 | 0 | 0 | 0 | 2/15/16:00
2 | 15 | 1900-01-16 | -7.2 | 84 | 601 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 84 | 0 | 0 | 39.791 | 46.6667 | -12.8113 | 86.148 | -75 | -14.5504 | 232.5104 | -359.3509 | -275.3509 | -87.2814 | -87.2814 | 0 | 0 | 0 | 2/15/17:00
2 | 15 | 1900-01-17 | -7.8 | 48 | 300 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 48 | 0 | 0 | 39.791 | 46.7083 | -12.7974 | 86.148 | -75 | -14.5489 | 247.5108 | -128.512 | -80.512 | -25.5209 | -25.5209 | 0 | 0 | 0 | 2/15/18:00
2 | 15 | 1900-01-18 | -11.1 | 8 | 8 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 8 | 0 | 0 | 39.791 | 46.75 | -12.7834 | 86.148 | -75 | -14.5474 | 262.5111 | -1.9142 | 6.0858 | 1.9291 | 1.9291 | 0 | 0 | 0 | 2/15/19:00
2 | 15 | 1900-01-19 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.7917 | -12.7695 | 86.148 | -75 | -14.5459 | 277.5115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/20:00
2 | 15 | 1900-01-20 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.8333 | -12.7555 | 86.148 | -75 | -14.5444 | 292.5119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/21:00
2 | 15 | 1900-01-21 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.875 | -12.7416 | 86.148 | -75 | -14.5428 | 307.5123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/22:00
2 | 15 | 1900-01-22 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.9167 | -12.7276 | 86.148 | -75 | -14.5412 | 322.5127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/23:00
2 | 15 | 1900-01-23 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 46.9583 | -12.7137 | 86.148 | -75 | -14.5396 | 337.5131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/15/24:00
2 | 16 | 1899-12-31 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47 | -12.6997 | 86.148 | -75 | -14.538 | -7.4865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/1:00
2 | 16 | 1900-01-01 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.0417 | -12.6857 | 86.148 | -75 | -14.5364 | 7.5139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/2:00
2 | 16 | 1900-01-02 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.0833 | -12.6717 | 86.148 | -75 | -14.5347 | 22.5143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/3:00
2 | 16 | 1900-01-03 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.125 | -12.6577 | 86.148 | -75 | -14.533 | 37.5147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/4:00
2 | 16 | 1900-01-04 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.1667 | -12.6437 | 86.148 | -75 | -14.5313 | 52.5152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/5:00
2 | 16 | 1900-01-05 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.2083 | -12.6297 | 86.148 | -75 | -14.5296 | 67.5156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/6:00
2 | 16 | 1900-01-06 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.25 | -12.6157 | 86.148 | -75 | -14.5278 | 82.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/7:00
2 | 16 | 1900-01-07 | -6.7 | 6 | 1 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 6 | 0 | 0 | 39.791 | 47.2917 | -12.6017 | 86.148 | -75 | -14.526 | 97.5165 | -0.23772 | 5.7623 | 1.8265 | 1.8265 | 0 | 0 | 0 | 2/16/8:00
2 | 16 | 1900-01-08 | -6.7 | 70 | 83 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 70 | 0 | 0 | 39.791 | 47.3333 | -12.5877 | 86.148 | -75 | -14.5242 | 112.5169 | -35.4128 | 34.5872 | 10.9635 | 10.9635 | 0 | 0 | 0 | 2/16/9:00
2 | 16 | 1900-01-09 | -5 | 80 | 2 | 23 | 1 | 0 | 23 | 0 | 0 | 80 | 0 | 0 | 39.791 | 47.375 | -12.5737 | 86.148 | -75 | -14.5224 | 127.5174 | -1.1921 | 78.8079 | 24.9807 | 24.9807 | 0 | 0 | 0 | 2/16/10:00
2 | 16 | 1900-01-10 | -2.8 | 143 | 565 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 143 | 0 | 0 | 39.791 | 47.4167 | -12.5597 | 86.148 | -75 | -14.5206 | 142.5179 | -414.8931 | -271.8931 | -86.1854 | -86.1854 | 0 | 0 | 0 | 2/16/11:00
2 | 16 | 1900-01-11 | -0.6 | 178 | 660 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 178 | 0 | 0 | 39.791 | 47.4583 | -12.5456 | 86.148 | -75 | -14.5187 | 157.5183 | -549.1547 | -371.1547 | -117.6496 | -117.6496 | 0 | 0 | 0 | 2/16/12:00
2 | 16 | 1900-01-12 | 1.1 | 201 | 684 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 201 | 0 | 0 | 39.791 | 47.5 | -12.5316 | 86.148 | -75 | -14.5168 | 172.5188 | -603.6689 | -402.6689 | -127.639 | -127.639 | 0 | 0 | 0 | 2/16/13:00
2 | 16 | 1900-01-13 | 1.7 | 190 | 683 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 190 | 0 | 0 | 39.791 | 47.5417 | -12.5175 | 86.148 | -75 | -14.5149 | 187.5193 | -602.665 | -412.665 | -130.8076 | -130.8076 | 0 | 0 | 0 | 2/16/14:00
2 | 16 | 1900-01-14 | 1.7 | 187 | 651 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 187 | 0 | 0 | 39.791 | 47.5833 | -12.5035 | 86.148 | -75 | -14.513 | 202.5198 | -541.3166 | -354.3166 | -112.3122 | -112.3122 | 0 | 0 | 0 | 2/16/15:00
2 | 16 | 1900-01-15 | 2.2 | 159 | 573 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 159 | 0 | 0 | 39.791 | 47.625 | -12.4894 | 86.148 | -75 | -14.5111 | 217.5202 | -420.2478 | -261.2478 | -82.811 | -82.811 | 0 | 0 | 0 | 2/16/16:00
2 | 16 | 1900-01-16 | 2.2 | 155 | 24 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 155 | 0 | 0 | 39.791 | 47.6667 | -12.4754 | 86.148 | -75 | -14.5091 | 232.5207 | -14.2741 | 140.7259 | 44.6077 | 44.6077 | 0 | 0 | 0 | 2/16/17:00
2 | 16 | 1900-01-17 | 1.7 | 58 | 1 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 58 | 0 | 0 | 39.791 | 47.7083 | -12.4613 | 86.148 | -75 | -14.5071 | 247.5212 | -0.42496 | 57.575 | 18.2503 | 18.2503 | 0 | 0 | 0 | 2/16/18:00
2 | 16 | 1900-01-18 | 1.7 | 5 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 5 | 0 | 0 | 39.791 | 47.75 | -12.4472 | 86.148 | -75 | -14.5051 | 262.5217 | 0 | 5 | 1.5849 | 1.5849 | 0 | 0 | 0 | 2/16/19:00
2 | 16 | 1900-01-19 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.7917 | -12.4331 | 86.148 | -75 | -14.5031 | 277.5222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/20:00
2 | 16 | 1900-01-20 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.8333 | -12.419 | 86.148 | -75 | -14.501 | 292.5228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/21:00
2 | 16 | 1900-01-21 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.875 | -12.405 | 86.148 | -75 | -14.4989 | 307.5233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/22:00
2 | 16 | 1900-01-22 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.9167 | -12.3909 | 86.148 | -75 | -14.4968 | 322.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/23:00
2 | 16 | 1900-01-23 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 47.9583 | -12.3767 | 86.148 | -75 | -14.4947 | 337.5243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/16/24:00
2 | 17 | 1899-12-31 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48 | -12.3626 | 86.148 | -75 | -14.4926 | -7.4751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/1:00
2 | 17 | 1900-01-01 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.0417 | -12.3485 | 86.148 | -75 | -14.4904 | 7.5254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/2:00
2 | 17 | 1900-01-02 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.0833 | -12.3344 | 86.148 | -75 | -14.4882 | 22.5259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/3:00
2 | 17 | 1900-01-03 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.125 | -12.3203 | 86.148 | -75 | -14.486 | 37.5265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/4:00
2 | 17 | 1900-01-04 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.1667 | -12.3061 | 86.148 | -75 | -14.4838 | 52.5271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/5:00
2 | 17 | 1900-01-05 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.2083 | -12.292 | 86.148 | -75 | -14.4816 | 67.5276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/6:00
2 | 17 | 1900-01-06 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.25 | -12.2779 | 86.148 | -75 | -14.4793 | 82.5282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/7:00
2 | 17 | 1900-01-07 | -6.7 | 8 | 2 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 8 | 0 | 0 | 39.791 | 48.2917 | -12.2637 | 86.148 | -75 | -14.477 | 97.5287 | -0.46864 | 7.5314 | 2.3873 | 2.3873 | 0 | 0 | 0 | 2/17/8:00
2 | 17 | 1900-01-08 | -3.3 | 57 | 200 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 57 | 0 | 0 | 39.791 | 48.3333 | -12.2496 | 86.148 | -75 | -14.4747 | 112.5293 | -84.699 | -27.699 | -8.7801 | -8.7801 | 0 | 0 | 0 | 2/17/9:00
2 | 17 | 1900-01-09 | -0.6 | 103 | 475 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 103 | 0 | 0 | 39.791 | 48.375 | -12.2354 | 86.148 | -75 | -14.4724 | 127.5299 | -281.7131 | -178.7131 | -56.6489 | -56.6489 | 0 | 0 | 0 | 2/17/10:00
2 | 17 | 1900-01-10 | 0.6 | 139 | 618 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 139 | 0 | 0 | 39.791 | 48.4167 | -12.2212 | 86.148 | -75 | -14.47 | 142.5305 | -452.0704 | -313.0704 | -99.2379 | -99.2379 | 0 | 0 | 0 | 2/17/11:00
2 | 17 | 1900-01-11 | 1.7 | 170 | 687 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 170 | 0 | 0 | 39.791 | 48.4583 | -12.2071 | 86.148 | -75 | -14.4676 | 157.5311 | -569.7442 | -399.7442 | -126.7119 | -126.7119 | 0 | 0 | 0 | 2/17/12:00
2 | 17 | 1900-01-12 | 2.8 | 183 | 720 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 183 | 0 | 0 | 39.791 | 48.5 | -12.1929 | 86.148 | -75 | -14.4652 | 172.5317 | -633.4902 | -450.4902 | -142.7975 | -142.7975 | 0 | 0 | 0 | 2/17/13:00
2 | 17 | 1900-01-13 | 3.3 | 297 | 552 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 297 | 0 | 0 | 39.791 | 48.5417 | -12.1787 | 86.148 | -75 | -14.4628 | 187.5323 | -485.5519 | -188.5519 | -59.7677 | -59.7677 | 0 | 0 | 0 | 2/17/14:00
2 | 17 | 1900-01-14 | 3.3 | 169 | 681 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 169 | 0 | 0 | 39.791 | 48.5833 | -12.1645 | 86.148 | -75 | -14.4604 | 202.5329 | -564.309 | -395.309 | -125.3061 | -125.3061 | 0 | 0 | 0 | 2/17/15:00
2 | 17 | 1900-01-15 | 3.9 | 144 | 603 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 144 | 0 | 0 | 39.791 | 48.625 | -12.1503 | 86.148 | -75 | -14.4579 | 217.5335 | -440.419 | -296.419 | -93.9596 | -93.9596 | 0 | 0 | 0 | 2/17/16:00
2 | 17 | 1900-01-16 | 3.3 | 102 | 473 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 102 | 0 | 0 | 39.791 | 48.6667 | -12.1361 | 86.148 | -75 | -14.4555 | 232.5341 | -279.7801 | -177.7801 | -56.3532 | -56.3532 | 0 | 0 | 0 | 2/17/17:00
2 | 17 | 1900-01-17 | 2.8 | 56 | 190 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 56 | 0 | 0 | 39.791 | 48.7083 | -12.1219 | 86.148 | -75 | -14.453 | 247.5348 | -80.078 | -24.078 | -7.6323 | -7.6323 | 0 | 0 | 0 | 2/17/18:00
2 | 17 | 1900-01-18 | 1.1 | 7 | 2 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 7 | 0 | 0 | 39.791 | 48.75 | -12.1077 | 86.148 | -75 | -14.4504 | 262.5354 | -0.46368 | 6.5363 | 2.0719 | 2.0719 | 0 | 0 | 0 | 2/17/19:00
2 | 17 | 1900-01-19 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.7917 | -12.0935 | 86.148 | -75 | -14.4479 | 277.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/20:00
2 | 17 | 1900-01-20 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.8333 | -12.0793 | 86.148 | -75 | -14.4453 | 292.5367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/21:00
2 | 17 | 1900-01-21 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.875 | -12.065 | 86.148 | -75 | -14.4428 | 307.5373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/22:00
2 | 17 | 1900-01-22 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.9167 | -12.0508 | 86.148 | -75 | -14.4401 | 322.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/23:00
2 | 17 | 1900-01-23 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 48.9583 | -12.0366 | 86.148 | -75 | -14.4375 | 337.5386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/17/24:00
2 | 18 | 1899-12-31 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49 | -12.0223 | 86.148 | -75 | -14.4349 | -7.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/1:00
2 | 18 | 1900-01-01 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.0417 | -12.0081 | 86.148 | -75 | -14.4322 | 7.5399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/2:00
2 | 18 | 1900-01-02 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.0833 | -11.9938 | 86.148 | -75 | -14.4295 | 22.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/3:00
2 | 18 | 1900-01-03 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.125 | -11.9795 | 86.148 | -75 | -14.4268 | 37.5413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/4:00
2 | 18 | 1900-01-04 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.1667 | -11.9653 | 86.148 | -75 | -14.4241 | 52.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/5:00
2 | 18 | 1900-01-05 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.2083 | -11.951 | 86.148 | -75 | -14.4213 | 67.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/6:00
2 | 18 | 1900-01-06 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.25 | -11.9367 | 86.148 | -75 | -14.4186 | 82.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/7:00
2 | 18 | 1900-01-07 | -1.7 | 14 | 34 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 14 | 0 | 0 | 39.791 | 49.2917 | -11.9224 | 86.148 | -75 | -14.4158 | 97.5441 | -7.8512 | 6.1488 | 1.9491 | 1.9491 | 0 | 0 | 0 | 2/18/8:00
2 | 18 | 1900-01-08 | -1.1 | 81 | 85 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 81 | 0 | 0 | 39.791 | 49.3333 | -11.9082 | 86.148 | -75 | -14.4129 | 112.5448 | -35.7272 | 45.2728 | 14.3507 | 14.3507 | 0 | 0 | 0 | 2/18/9:00
2 | 18 | 1900-01-09 | 0.6 | 166 | 108 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 166 | 0 | 0 | 39.791 | 49.375 | -11.8939 | 86.148 | -75 | -14.4101 | 127.5455 | -63.7302 | 102.2698 | 32.4177 | 32.4177 | 0 | 0 | 0 | 2/18/10:00
2 | 18 | 1900-01-10 | 1.7 | 172 | 459 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 172 | 0 | 0 | 39.791 | 49.4167 | -11.8796 | 86.148 | -75 | -14.4073 | 142.5462 | -334.4539 | -162.4539 | -51.495 | -51.495 | 0 | 0 | 0 | 2/18/11:00
2 | 18 | 1900-01-11 | 3.9 | 97 | 826 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 97 | 0 | 0 | 39.791 | 49.4583 | -11.8653 | 86.148 | -75 | -14.4044 | 157.5469 | -682.7308 | -585.7308 | -185.6664 | -185.6664 | 0 | 0 | 0 | 2/18/12:00
2 | 18 | 1900-01-12 | 4.4 | 310 | 11 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 310 | 0 | 0 | 39.791 | 49.5 | -11.8509 | 86.148 | -75 | -14.4015 | 172.5476 | -9.6479 | 300.3521 | 95.2064 | 95.2064 | 0 | 0 | 0 | 2/18/13:00
2 | 18 | 1900-01-13 | 5 | 360 | 5 | 41 | 1 | 0 | 41 | 0 | 0 | 360 | 0 | 0 | 39.791 | 49.5417 | -11.8366 | 86.148 | -75 | -14.3986 | 187.5484 | -4.384 | 355.616 | 112.7241 | 112.7241 | 0 | 0 | 0 | 2/18/14:00
2 | 18 | 1900-01-14 | 5 | 227 | 2 | 41 | 1 | 0 | 41 | 0 | 0 | 227 | 0 | 0 | 39.791 | 49.5833 | -11.8223 | 86.148 | -75 | -14.3956 | 202.5491 | -1.6514 | 225.3486 | 71.4316 | 71.4316 | 0 | 0 | 0 | 2/18/15:00
2 | 18 | 1900-01-15 | 5 | 238 | 3 | 41 | 1 | 0 | 41 | 0 | 0 | 238 | 0 | 0 | 39.791 | 49.625 | -11.808 | 86.148 | -75 | -14.3927 | 217.5498 | -2.1818 | 235.8182 | 74.7503 | 74.7503 | 0 | 0 | 0 | 2/18/16:00
2 | 18 | 1900-01-16 | 4.4 | 144 | 5 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 144 | 0 | 0 | 39.791 | 49.6667 | -11.7936 | 86.148 | -75 | -14.3897 | 232.5506 | -2.9408 | 141.0592 | 44.7133 | 44.7133 | 0 | 0 | 0 | 2/18/17:00
2 | 18 | 1900-01-17 | 3.3 | 61 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 61 | 0 | 0 | 39.791 | 49.7083 | -11.7793 | 86.148 | -75 | -14.3867 | 247.5513 | 0 | 61 | 19.3359 | 19.3359 | 0 | 0 | 0 | 2/18/18:00
2 | 18 | 1900-01-18 | 2.8 | 10 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 10 | 0 | 0 | 39.791 | 49.75 | -11.765 | 86.148 | -75 | -14.3837 | 262.5521 | 0 | 10 | 3.1698 | 3.1698 | 0 | 0 | 0 | 2/18/19:00
2 | 18 | 1900-01-19 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.7917 | -11.7506 | 86.148 | -75 | -14.3806 | 277.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/20:00
2 | 18 | 1900-01-20 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.8333 | -11.7363 | 86.148 | -75 | -14.3775 | 292.5536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/21:00
2 | 18 | 1900-01-21 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.875 | -11.7219 | 86.148 | -75 | -14.3745 | 307.5544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/22:00
2 | 18 | 1900-01-22 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.9167 | -11.7075 | 86.148 | -75 | -14.3714 | 322.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/23:00
2 | 18 | 1900-01-23 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 49.9583 | -11.6932 | 86.148 | -75 | -14.3682 | 337.5559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/18/24:00
2 | 19 | 1899-12-31 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50 | -11.6788 | 86.148 | -75 | -14.3651 | -7.4433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/1:00
2 | 19 | 1900-01-01 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.0417 | -11.6644 | 86.148 | -75 | -14.3619 | 7.5575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/2:00
2 | 19 | 1900-01-02 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.0833 | -11.65 | 86.148 | -75 | -14.3587 | 22.5583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/3:00
2 | 19 | 1900-01-03 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.125 | -11.6356 | 86.148 | -75 | -14.3555 | 37.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/4:00
2 | 19 | 1900-01-04 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.1667 | -11.6212 | 86.148 | -75 | -14.3523 | 52.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/5:00
2 | 19 | 1900-01-05 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.2083 | -11.6068 | 86.148 | -75 | -14.349 | 67.5607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/6:00
2 | 19 | 1900-01-06 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.25 | -11.5924 | 86.148 | -75 | -14.3458 | 82.5616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/7:00
2 | 19 | 1900-01-07 | -7.2 | 14 | 20 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 14 | 0 | 0 | 39.791 | 50.2917 | -11.578 | 86.148 | -75 | -14.3425 | 97.5624 | -4.5503 | 9.4497 | 2.9954 | 2.9954 | 0 | 0 | 0 | 2/19/8:00
2 | 19 | 1900-01-08 | -5.6 | 71 | 268 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 71 | 0 | 0 | 39.791 | 50.3333 | -11.5636 | 86.148 | -75 | -14.3392 | 112.5632 | -111.7924 | -40.7924 | -12.9305 | -12.9305 | 0 | 0 | 0 | 2/19/9:00
2 | 19 | 1900-01-09 | -3.3 | 145 | 451 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 145 | 0 | 0 | 39.791 | 50.375 | -11.5492 | 86.148 | -75 | -14.3358 | 127.564 | -264.7779 | -119.7779 | -37.9675 | -37.9675 | 0 | 0 | 0 | 2/19/10:00
2 | 19 | 1900-01-10 | -2.2 | 182 | 579 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 182 | 0 | 0 | 39.791 | 50.4167 | -11.5348 | 86.148 | -75 | -14.3325 | 142.5649 | -420.227 | -238.227 | -75.5138 | -75.5138 | 0 | 0 | 0 | 2/19/11:00
2 | 19 | 1900-01-11 | -1.1 | 123 | 783 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 123 | 0 | 0 | 39.791 | 50.4583 | -11.5203 | 86.148 | -75 | -14.3291 | 157.5657 | -644.9872 | -521.9872 | -165.4608 | -165.4608 | 0 | 0 | 0 | 2/19/12:00
2 | 19 | 1900-01-12 | -1.1 | 233 | 552 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 233 | 0 | 0 | 39.791 | 50.5 | -11.5059 | 86.148 | -75 | -14.3257 | 172.5666 | -482.5985 | -249.5985 | -79.1184 | -79.1184 | 0 | 0 | 0 | 2/19/13:00
2 | 19 | 1900-01-13 | 0 | 265 | 617 | 32 | 1 | 0 | 32 | 0 | 0 | 265 | 0 | 0 | 39.791 | 50.5417 | -11.4914 | 86.148 | -75 | -14.3223 | 187.5674 | -539.2104 | -274.2104 | -86.9199 | -86.9199 | 0 | 0 | 0 | 2/19/14:00
2 | 19 | 1900-01-14 | 0 | 297 | 1 | 32 | 1 | 0 | 32 | 0 | 0 | 297 | 0 | 0 | 39.791 | 50.5833 | -11.477 | 86.148 | -75 | -14.3188 | 202.5683 | -0.8227 | 296.1773 | 93.883 | 93.883 | 0 | 0 | 0 | 2/19/15:00
2 | 19 | 1900-01-15 | 0.6 | 230 | 3 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 230 | 0 | 0 | 39.791 | 50.625 | -11.4625 | 86.148 | -75 | -14.3154 | 217.5692 | -2.1722 | 227.8278 | 72.2174 | 72.2174 | 0 | 0 | 0 | 2/19/16:00
2 | 19 | 1900-01-16 | 0.6 | 170 | 4 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 170 | 0 | 0 | 39.791 | 50.6667 | -11.4481 | 86.148 | -75 | -14.3119 | 232.57 | -2.339 | 167.661 | 53.1456 | 53.1456 | 0 | 0 | 0 | 2/19/17:00
2 | 19 | 1900-01-17 | 0.6 | 36 | 27 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 36 | 0 | 0 | 39.791 | 50.7083 | -11.4336 | 86.148 | -75 | -14.3084 | 247.5709 | -11.1839 | 24.8161 | 7.8663 | 7.8663 | 0 | 0 | 0 | 2/19/18:00
2 | 19 | 1900-01-18 | -0.6 | 5 | 1 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 5 | 0 | 0 | 39.791 | 50.75 | -11.4191 | 86.148 | -75 | -14.3049 | 262.5718 | -0.22408 | 4.7759 | 1.5139 | 1.5139 | 0 | 0 | 0 | 2/19/19:00
2 | 19 | 1900-01-19 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.7917 | -11.4047 | 86.148 | -75 | -14.3013 | 277.5727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/20:00
2 | 19 | 1900-01-20 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.8333 | -11.3902 | 86.148 | -75 | -14.2978 | 292.5736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/21:00
2 | 19 | 1900-01-21 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.875 | -11.3757 | 86.148 | -75 | -14.2942 | 307.5744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/22:00
2 | 19 | 1900-01-22 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.9167 | -11.3612 | 86.148 | -75 | -14.2906 | 322.5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/23:00
2 | 19 | 1900-01-23 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 50.9583 | -11.3467 | 86.148 | -75 | -14.287 | 337.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/19/24:00
2 | 20 | 1899-12-31 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51 | -11.3322 | 86.148 | -75 | -14.2833 | -7.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/1:00
2 | 20 | 1900-01-01 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.0417 | -11.3177 | 86.148 | -75 | -14.2797 | 7.5781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/2:00
2 | 20 | 1900-01-02 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.0833 | -11.3032 | 86.148 | -75 | -14.276 | 22.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/3:00
2 | 20 | 1900-01-03 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.125 | -11.2887 | 86.148 | -75 | -14.2723 | 37.5799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/4:00
2 | 20 | 1900-01-04 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.1667 | -11.2741 | 86.148 | -75 | -14.2686 | 52.5809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/5:00
2 | 20 | 1900-01-05 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.2083 | -11.2596 | 86.148 | -75 | -14.2648 | 67.5818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/6:00
2 | 20 | 1900-01-06 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.25 | -11.2451 | 86.148 | -75 | -14.2611 | 82.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/7:00
2 | 20 | 1900-01-07 | -2.8 | 7 | 3 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 7 | 0 | 0 | 39.791 | 51.2917 | -11.2306 | 86.148 | -75 | -14.2573 | 97.5837 | -0.67232 | 6.3277 | 2.0058 | 2.0058 | 0 | 0 | 0 | 2/20/8:00
2 | 20 | 1900-01-08 | -1.1 | 59 | 212 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 59 | 0 | 0 | 39.791 | 51.3333 | -11.216 | 86.148 | -75 | -14.2535 | 112.5846 | -87.756 | -28.756 | -9.1151 | -9.1151 | 0 | 0 | 0 | 2/20/9:00
2 | 20 | 1900-01-09 | 1.1 | 102 | 512 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 102 | 0 | 0 | 39.791 | 51.375 | -11.2015 | 86.148 | -75 | -14.2497 | 127.5856 | -299.043 | -197.043 | -62.4592 | -62.4592 | 0 | 0 | 0 | 2/20/10:00
2 | 20 | 1900-01-10 | 2.8 | 149 | 633 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 149 | 0 | 0 | 39.791 | 51.4167 | -11.1869 | 86.148 | -75 | -14.2458 | 142.5865 | -457.5794 | -308.5794 | -97.8143 | -97.8143 | 0 | 0 | 0 | 2/20/11:00
2 | 20 | 1900-01-11 | 4.4 | 218 | 624 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 218 | 0 | 0 | 39.791 | 51.4583 | -11.1723 | 86.148 | -75 | -14.2419 | 157.5875 | -512.2326 | -294.2326 | -93.2666 | -93.2666 | 0 | 0 | 0 | 2/20/12:00
2 | 20 | 1900-01-12 | 5.6 | 183 | 662 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 183 | 0 | 0 | 39.791 | 51.5 | -11.1578 | 86.148 | -75 | -14.2381 | 172.5885 | -576.8715 | -393.8715 | -124.8504 | -124.8504 | 0 | 0 | 0 | 2/20/13:00
2 | 20 | 1900-01-13 | 6.7 | 176 | 737 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 176 | 0 | 0 | 39.791 | 51.5417 | -11.1432 | 86.148 | -75 | -14.2341 | 187.5895 | -641.9117 | -465.9117 | -147.6859 | -147.6859 | 0 | 0 | 0 | 2/20/14:00
2 | 20 | 1900-01-14 | 6.7 | 158 | 705 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 158 | 0 | 0 | 39.791 | 51.5833 | -11.1286 | 86.148 | -75 | -14.2302 | 202.5904 | -577.8288 | -419.8288 | -133.0784 | -133.0784 | 0 | 0 | 0 | 2/20/15:00
2 | 20 | 1900-01-15 | 7.2 | 141 | 631 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 141 | 0 | 0 | 39.791 | 51.625 | -11.1141 | 86.148 | -75 | -14.2263 | 217.5914 | -454.8249 | -313.8249 | -99.477 | -99.477 | 0 | 0 | 0 | 2/20/16:00
2 | 20 | 1900-01-16 | 7.2 | 105 | 490 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 105 | 0 | 0 | 39.791 | 51.6667 | -11.0995 | 86.148 | -75 | -14.2223 | 232.5924 | -284.8142 | -179.8142 | -56.998 | -56.998 | 0 | 0 | 0 | 2/20/17:00
2 | 20 | 1900-01-17 | 6.7 | 68 | 181 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 68 | 0 | 0 | 39.791 | 51.7083 | -11.0849 | 86.148 | -75 | -14.2183 | 247.5934 | -74.2954 | -6.2954 | -1.9955 | -1.9955 | 0 | 0 | 0 | 2/20/18:00
2 | 20 | 1900-01-18 | 3.9 | 10 | 4 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 10 | 0 | 0 | 39.791 | 51.75 | -11.0703 | 86.148 | -75 | -14.2143 | 262.5944 | -0.88033 | 9.1197 | 2.8908 | 2.8908 | 0 | 0 | 0 | 2/20/19:00
2 | 20 | 1900-01-19 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.7917 | -11.0557 | 86.148 | -75 | -14.2103 | 277.5954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/20:00
2 | 20 | 1900-01-20 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.8333 | -11.0411 | 86.148 | -75 | -14.2062 | 292.5964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/21:00
2 | 20 | 1900-01-21 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.875 | -11.0265 | 86.148 | -75 | -14.2022 | 307.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/22:00
2 | 20 | 1900-01-22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.9167 | -11.0119 | 86.148 | -75 | -14.1981 | 322.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/23:00
2 | 20 | 1900-01-23 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 51.9583 | -10.9973 | 86.148 | -75 | -14.194 | 337.5995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/20/24:00
2 | 21 | 1899-12-31 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52 | -10.9826 | 86.148 | -75 | -14.1898 | -7.3995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/1:00
2 | 21 | 1900-01-01 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.0417 | -10.968 | 86.148 | -75 | -14.1857 | 7.6016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/2:00
2 | 21 | 1900-01-02 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.0833 | -10.9534 | 86.148 | -75 | -14.1815 | 22.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/3:00
2 | 21 | 1900-01-03 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.125 | -10.9387 | 86.148 | -75 | -14.1773 | 37.6037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/4:00
2 | 21 | 1900-01-04 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.1667 | -10.9241 | 86.148 | -75 | -14.1731 | 52.6047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/5:00
2 | 21 | 1900-01-05 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.2083 | -10.9094 | 86.148 | -75 | -14.1689 | 67.6058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/6:00
2 | 21 | 1900-01-06 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.25 | -10.8948 | 86.148 | -75 | -14.1646 | 82.6068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/7:00
2 | 21 | 1900-01-07 | 1.7 | 11 | 1 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 11 | 0 | 0 | 39.791 | 52.2917 | -10.8801 | 86.148 | -75 | -14.1604 | 97.6079 | -0.2207 | 10.7793 | 3.4168 | 3.4168 | 0 | 0 | 0 | 2/21/8:00
2 | 21 | 1900-01-08 | 2.2 | 59 | 7 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 59 | 0 | 0 | 39.791 | 52.3333 | -10.8655 | 86.148 | -75 | -14.1561 | 112.609 | -2.8752 | 56.1248 | 17.7906 | 17.7906 | 0 | 0 | 0 | 2/21/9:00
2 | 21 | 1900-01-09 | 3.3 | 179 | 9 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 179 | 0 | 0 | 39.791 | 52.375 | -10.8508 | 86.148 | -75 | -14.1518 | 127.6101 | -5.2292 | 173.7708 | 55.0823 | 55.0823 | 0 | 0 | 0 | 2/21/10:00
2 | 21 | 1900-01-10 | 5.6 | 230 | 10 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 230 | 0 | 0 | 39.791 | 52.4167 | -10.8361 | 86.148 | -75 | -14.1475 | 142.6111 | -7.1994 | 222.8006 | 70.6239 | 70.6239 | 0 | 0 | 0 | 2/21/11:00
2 | 21 | 1900-01-11 | 7.8 | 252 | 7 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 252 | 0 | 0 | 39.791 | 52.4583 | -10.8214 | 86.148 | -75 | -14.1431 | 157.6122 | -5.7259 | 246.2741 | 78.0646 | 78.0646 | 0 | 0 | 0 | 2/21/12:00
2 | 21 | 1900-01-12 | 8.9 | 291 | 7 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 291 | 0 | 0 | 39.791 | 52.5 | -10.8068 | 86.148 | -75 | -14.1387 | 172.6133 | -6.0794 | 284.9206 | 90.3148 | 90.3148 | 0 | 0 | 0 | 2/21/13:00
2 | 21 | 1900-01-13 | 9.4 | 177 | 6 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 177 | 0 | 0 | 39.791 | 52.5417 | -10.7921 | 86.148 | -75 | -14.1343 | 187.6144 | -5.2078 | 171.7922 | 54.4551 | 54.4551 | 0 | 0 | 0 | 2/21/14:00
2 | 21 | 1900-01-14 | 8.9 | 165 | 5 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 165 | 0 | 0 | 39.791 | 52.5833 | -10.7774 | 86.148 | -75 | -14.1299 | 202.6155 | -4.0823 | 160.9177 | 51.0081 | 51.0081 | 0 | 0 | 0 | 2/21/15:00
2 | 21 | 1900-01-15 | 8.9 | 133 | 2 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 133 | 0 | 0 | 39.791 | 52.625 | -10.7627 | 86.148 | -75 | -14.1255 | 217.6166 | -1.4349 | 131.5651 | 41.7038 | 41.7038 | 0 | 0 | 0 | 2/21/16:00
2 | 21 | 1900-01-16 | 8.3 | 171 | 1 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 171 | 0 | 0 | 39.791 | 52.6667 | -10.748 | 86.148 | -75 | -14.1211 | 232.6177 | -0.57768 | 170.4223 | 54.0209 | 54.0209 | 0 | 0 | 0 | 2/21/17:00
2 | 21 | 1900-01-17 | 8.9 | 41 | 1 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 41 | 0 | 0 | 39.791 | 52.7083 | -10.7333 | 86.148 | -75 | -14.1166 | 247.6189 | -0.40665 | 40.5934 | 12.8674 | 12.8674 | 0 | 0 | 0 | 2/21/18:00
2 | 21 | 1900-01-18 | 8.9 | 12 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 12 | 0 | 0 | 39.791 | 52.75 | -10.7186 | 86.148 | -75 | -14.1121 | 262.62 | 0 | 12 | 3.8038 | 3.8038 | 0 | 0 | 0 | 2/21/19:00
2 | 21 | 1900-01-19 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.7917 | -10.7038 | 86.148 | -75 | -14.1076 | 277.6211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/20:00
2 | 21 | 1900-01-20 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.8333 | -10.6891 | 86.148 | -75 | -14.1031 | 292.6222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/21:00
2 | 21 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.875 | -10.6744 | 86.148 | -75 | -14.0985 | 307.6234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/22:00
2 | 21 | 1900-01-22 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.9167 | -10.6597 | 86.148 | -75 | -14.094 | 322.6245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/23:00
2 | 21 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 52.9583 | -10.6449 | 86.148 | -75 | -14.0894 | 337.6257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/21/24:00
2 | 22 | 1899-12-31 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53 | -10.6302 | 86.148 | -75 | -14.0848 | -7.3732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/1:00
2 | 22 | 1900-01-01 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.0417 | -10.6154 | 86.148 | -75 | -14.0801 | 7.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/2:00
2 | 22 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.0833 | -10.6007 | 86.148 | -75 | -14.0755 | 22.6291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/3:00
2 | 22 | 1900-01-03 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.125 | -10.5859 | 86.148 | -75 | -14.0708 | 37.6303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/4:00
2 | 22 | 1900-01-04 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.1667 | -10.5712 | 86.148 | -75 | -14.0661 | 52.6315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/5:00
2 | 22 | 1900-01-05 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.2083 | -10.5564 | 86.148 | -75 | -14.0614 | 67.6326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/6:00
2 | 22 | 1900-01-06 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.25 | -10.5416 | 86.148 | -75 | -14.0567 | 82.6338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/7:00
2 | 22 | 1900-01-07 | 7.8 | 7 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 7 | 0 | 0 | 39.791 | 53.2917 | -10.5269 | 86.148 | -75 | -14.052 | 97.635 | 0 | 7 | 2.2189 | 2.2189 | 0 | 0 | 0 | 2/22/8:00
2 | 22 | 1900-01-08 | 8.3 | 43 | 1 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 43 | 0 | 0 | 39.791 | 53.3333 | -10.5121 | 86.148 | -75 | -14.0472 | 112.6362 | -0.40753 | 42.5925 | 13.5011 | 13.5011 | 0 | 0 | 0 | 2/22/9:00
2 | 22 | 1900-01-09 | 8.9 | 84 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 84 | 0 | 0 | 39.791 | 53.375 | -10.4973 | 86.148 | -75 | -14.0424 | 127.6374 | 0 | 84 | 26.6265 | 26.6265 | 0 | 0 | 0 | 2/22/10:00
2 | 22 | 1900-01-10 | 8.9 | 135 | 1 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 135 | 0 | 0 | 39.791 | 53.4167 | -10.4825 | 86.148 | -75 | -14.0376 | 142.6386 | -0.71697 | 134.283 | 42.5654 | 42.5654 | 0 | 0 | 0 | 2/22/11:00
2 | 22 | 1900-01-11 | 9.4 | 160 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 160 | 0 | 0 | 39.791 | 53.4583 | -10.4677 | 86.148 | -75 | -14.0328 | 157.6398 | -0.81506 | 159.1849 | 50.4588 | 50.4588 | 0 | 0 | 0 | 2/22/12:00
2 | 22 | 1900-01-12 | 9.4 | 190 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 190 | 0 | 0 | 39.791 | 53.5 | -10.4529 | 86.148 | -75 | -14.0279 | 172.641 | -0.86552 | 189.1345 | 59.9523 | 59.9523 | 0 | 0 | 0 | 2/22/13:00
2 | 22 | 1900-01-13 | 10 | 190 | 1 | 50 | 1 | 0 | 50 | 0 | 0 | 190 | 0 | 0 | 39.791 | 53.5417 | -10.4381 | 86.148 | -75 | -14.0231 | 187.6422 | -0.86491 | 189.1351 | 59.9525 | 59.9525 | 0 | 0 | 0 | 2/22/14:00
2 | 22 | 1900-01-14 | 10 | 298 | 1 | 50 | 1 | 0 | 50 | 0 | 0 | 298 | 0 | 0 | 39.791 | 53.5833 | -10.4233 | 86.148 | -75 | -14.0182 | 202.6435 | -0.81324 | 297.1868 | 94.203 | 94.203 | 0 | 0 | 0 | 2/22/15:00
2 | 22 | 1900-01-15 | 10 | 145 | 1 | 50 | 1 | 0 | 50 | 0 | 0 | 145 | 0 | 0 | 39.791 | 53.625 | -10.4085 | 86.148 | -75 | -14.0133 | 217.6447 | -0.71403 | 144.286 | 45.7361 | 45.7361 | 0 | 0 | 0 | 2/22/16:00
2 | 22 | 1900-01-16 | 9.4 | 86 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 86 | 0 | 0 | 39.791 | 53.6667 | -10.3937 | 86.148 | -75 | -14.0084 | 232.6459 | 0 | 86 | 27.2605 | 27.2605 | 0 | 0 | 0 | 2/22/17:00
2 | 22 | 1900-01-17 | 10 | 35 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 35 | 0 | 0 | 39.791 | 53.7083 | -10.3789 | 86.148 | -75 | -14.0034 | 247.6471 | 0 | 35 | 11.0944 | 11.0944 | 0 | 0 | 0 | 2/22/18:00
2 | 22 | 1900-01-18 | 10 | 10 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 39.791 | 53.75 | -10.364 | 86.148 | -75 | -13.9985 | 262.6484 | 0 | 10 | 3.1698 | 3.1698 | 0 | 0 | 0 | 2/22/19:00
2 | 22 | 1900-01-19 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.7917 | -10.3492 | 86.148 | -75 | -13.9935 | 277.6496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/20:00
2 | 22 | 1900-01-20 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.8333 | -10.3344 | 86.148 | -75 | -13.9885 | 292.6509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/21:00
2 | 22 | 1900-01-21 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.875 | -10.3195 | 86.148 | -75 | -13.9835 | 307.6521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/22:00
2 | 22 | 1900-01-22 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.9167 | -10.3047 | 86.148 | -75 | -13.9784 | 322.6534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/23:00
2 | 22 | 1900-01-23 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 53.9583 | -10.2898 | 86.148 | -75 | -13.9734 | 337.6547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/22/24:00
2 | 23 | 1899-12-31 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 54 | -10.275 | 86.148 | -75 | -13.9683 | -7.3441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/23/1:00
2 | 23 | 1900-01-01 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 54.0417 | -10.2601 | 86.148 | -75 | -13.9632 | 7.6572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/23/2:00
2 | 23 | 1900-01-02 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 54.0833 | -10.2452 | 86.148 | -75 | -13.9581 | 22.6585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/23/3:00
2 | 23 | 1900-01-03 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 54.125 | -10.2304 | 86.148 | -75 | -13.9529 | 37.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/23/4:00
2 | 23 | 1900-01-04 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 54.1667 | -10.2155 | 86.148 | -75 | -13.9478 | 52.6611 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 2/23/5:00
2 | 23 | 1900-01-05 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 54.2083 | -10.2006 | 86.148 | -75 | -13.9426 | 67.6623 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 2/23/6:00
2 | 23 | 1900-01-06 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 54.25 | -10.1857 | 86.148 | -75 | -13.9374 | 82.6636 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 2/23/7:00
2 | 23 | 1900-01-07 | 12.8 | 9 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 9 | 0 | 0 | 39.791 | 54.2917 | -10.1708 | 86.148 | -75 | -13.9322 | 97.6649 | 0 | 9 | 2.8528 | 0 | 2.8528 | 55.04 | 2.8528 | 2/23/8:00
2 | 23 | 1900-01-08 | 12.8 | 68 | 1 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 68 | 0 | 0 | 39.791 | 54.3333 | -10.156 | 86.148 | -75 | -13.927 | 112.6663 | -0.40431 | 67.5957 | 21.4267 | 0 | 21.4267 | 55.04 | 21.4267 | 2/23/9:00
2 | 23 | 1900-01-09 | 13.3 | 160 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 160 | 0 | 0 | 39.791 | 54.375 | -10.1411 | 86.148 | -75 | -13.9217 | 127.6676 | 0 | 160 | 50.7172 | 0 | 50.7172 | 55.94 | 50.7172 | 2/23/10:00
2 | 23 | 1900-01-10 | 15 | 227 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 227 | 0 | 0 | 39.791 | 54.4167 | -10.1262 | 86.148 | -75 | -13.9165 | 142.6689 | 0 | 227 | 71.955 | 0 | 71.955 | 59 | 71.955 | 2/23/11:00
2 | 23 | 1900-01-11 | 16.1 | 289 | 1 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 289 | 0 | 0 | 39.791 | 54.4583 | -10.1113 | 86.148 | -75 | -13.9112 | 157.6702 | -0.81208 | 288.1879 | 91.3505 | 0 | 91.3505 | 60.98 | 91.3505 | 2/23/12:00
2 | 23 | 1900-01-12 | 18.3 | 302 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 302 | 0 | 0 | 39.791 | 54.5 | -10.0963 | 86.148 | -75 | -13.9059 | 172.6715 | -0.8625 | 301.1375 | 95.4553 | 0 | 95.4553 | 64.94 | 95.4553 | 2/23/13:00
2 | 23 | 1900-01-13 | 19.4 | 305 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 305 | 0 | 0 | 39.791 | 54.5417 | -10.0814 | 86.148 | -75 | -13.9005 | 187.6729 | 0 | 305 | 96.6797 | 0 | 96.6797 | 66.92 | 96.6797 | 2/23/14:00
2 | 23 | 1900-01-14 | 20.6 | 265 | 2 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 265 | 0 | 0 | 39.791 | 54.5833 | -10.0665 | 86.148 | -75 | -13.8952 | 202.6742 | -1.6199 | 263.3801 | 83.4869 | 0 | 83.4869 | 69.08 | 83.4869 | 2/23/15:00
2 | 23 | 1900-01-15 | 20.6 | 184 | 57 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 184 | 0 | 0 | 39.791 | 54.625 | -10.0516 | 86.148 | -75 | -13.8898 | 217.6755 | -40.5002 | 143.4998 | 45.4869 | 0 | 45.4869 | 69.08 | 45.4869 | 2/23/16:00
2 | 23 | 1900-01-16 | 19.4 | 88 | 32 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 88 | 0 | 0 | 39.791 | 54.6667 | -10.0367 | 86.148 | -75 | -13.8844 | 232.6769 | -18.2491 | 69.7509 | 22.1098 | 0 | 22.1098 | 66.92 | 22.1098 | 2/23/17:00
2 | 23 | 1900-01-17 | 18.3 | 31 | 5 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 31 | 0 | 0 | 39.791 | 54.7083 | -10.0217 | 86.148 | -75 | -13.879 | 247.6782 | -1.9938 | 29.0062 | 9.1945 | 0 | 9.1945 | 64.94 | 9.1945 | 2/23/18:00
2 | 23 | 1900-01-18 | 17.2 | 8 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 8 | 0 | 0 | 39.791 | 54.75 | -10.0068 | 86.148 | -75 | -13.8736 | 262.6796 | 0 | 8 | 2.5359 | 0 | 2.5359 | 62.96 | 2.5359 | 2/23/19:00
2 | 23 | 1900-01-19 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 54.7917 | -9.9918 | 86.148 | -75 | -13.8682 | 277.681 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 2/23/20:00
2 | 23 | 1900-01-20 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 54.8333 | -9.9769 | 86.148 | -75 | -13.8627 | 292.6823 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 2/23/21:00
2 | 23 | 1900-01-21 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 54.875 | -9.9619 | 86.148 | -75 | -13.8572 | 307.6837 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 2/23/22:00
2 | 23 | 1900-01-22 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 54.9167 | -9.947 | 86.148 | -75 | -13.8517 | 322.6851 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 2/23/23:00
2 | 23 | 1900-01-23 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 54.9583 | -9.932 | 86.148 | -75 | -13.8462 | 337.6864 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 2/23/24:00
2 | 24 | 1899-12-31 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 55 | -9.9171 | 86.148 | -75 | -13.8407 | -7.3122 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 2/24/1:00
2 | 24 | 1900-01-01 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 55.0417 | -9.9021 | 86.148 | -75 | -13.8351 | 7.6892 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 2/24/2:00
2 | 24 | 1900-01-02 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 55.0833 | -9.8871 | 86.148 | -75 | -13.8295 | 22.6906 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 2/24/3:00
2 | 24 | 1900-01-03 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 55.125 | -9.8721 | 86.148 | -75 | -13.8239 | 37.692 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 2/24/4:00
2 | 24 | 1900-01-04 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 55.1667 | -9.8572 | 86.148 | -75 | -13.8183 | 52.6934 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 2/24/5:00
2 | 24 | 1900-01-05 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 55.2083 | -9.8422 | 86.148 | -75 | -13.8127 | 67.6948 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 2/24/6:00
2 | 24 | 1900-01-06 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 55.25 | -9.8272 | 86.148 | -75 | -13.807 | 82.6962 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 2/24/7:00
2 | 24 | 1900-01-07 | 13.3 | 7 | 2 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 7 | 0 | 0 | 39.791 | 55.2917 | -9.8122 | 86.148 | -75 | -13.8014 | 97.6977 | -0.42096 | 6.579 | 2.0854 | 0 | 2.0854 | 55.94 | 2.0854 | 2/24/8:00
2 | 24 | 1900-01-08 | 13.3 | 36 | 1 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 36 | 0 | 0 | 39.791 | 55.3333 | -9.7972 | 86.148 | -75 | -13.7957 | 112.6991 | -0.40109 | 35.5989 | 11.2842 | 0 | 11.2842 | 55.94 | 11.2842 | 2/24/9:00
2 | 24 | 1900-01-09 | 13.3 | 90 | 4 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 90 | 0 | 0 | 39.791 | 55.375 | -9.7822 | 86.148 | -75 | -13.79 | 127.7005 | -2.2872 | 87.7128 | 27.8034 | 0 | 27.8034 | 55.94 | 27.8034 | 2/24/10:00
2 | 24 | 1900-01-10 | 13.3 | 210 | 2 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 210 | 0 | 0 | 39.791 | 55.4167 | -9.7672 | 86.148 | -75 | -13.7842 | 142.7019 | -1.4219 | 208.5781 | 66.1156 | 0 | 66.1156 | 55.94 | 66.1156 | 2/24/11:00
2 | 24 | 1900-01-11 | 13.3 | 316 | 3 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 316 | 0 | 0 | 39.791 | 55.4583 | -9.7522 | 86.148 | -75 | -13.7785 | 157.7034 | -2.4272 | 313.5728 | 99.3971 | 0 | 99.3971 | 55.94 | 99.3971 | 2/24/12:00
2 | 24 | 1900-01-12 | 8.9 | 296 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 296 | 0 | 0 | 39.791 | 55.5 | -9.7371 | 86.148 | -75 | -13.7727 | 172.7048 | 0 | 296 | 93.8268 | 93.8268 | 0 | 0 | 0 | 2/24/13:00
2 | 24 | 1900-01-13 | 6.7 | 325 | 1 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 325 | 0 | 0 | 39.791 | 55.5417 | -9.7221 | 86.148 | -75 | -13.7669 | 187.7063 | -0.85858 | 324.1414 | 102.7472 | 102.7472 | 0 | 0 | 0 | 2/24/14:00
2 | 24 | 1900-01-14 | 6.1 | 321 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 321 | 0 | 0 | 39.791 | 55.5833 | -9.7071 | 86.148 | -75 | -13.7611 | 202.7077 | 0 | 321 | 101.7514 | 101.7514 | 0 | 0 | 0 | 2/24/15:00
2 | 24 | 1900-01-15 | 5 | 266 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 266 | 0 | 0 | 39.791 | 55.625 | -9.6921 | 86.148 | -75 | -13.7553 | 217.7092 | 0 | 266 | 84.3174 | 84.3174 | 0 | 0 | 0 | 2/24/16:00
2 | 24 | 1900-01-16 | 4.4 | 180 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 180 | 0 | 0 | 39.791 | 55.6667 | -9.677 | 86.148 | -75 | -13.7495 | 232.7106 | -0.56647 | 179.4335 | 56.8773 | 56.8773 | 0 | 0 | 0 | 2/24/17:00
2 | 24 | 1900-01-17 | 3.9 | 74 | 1 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 74 | 0 | 0 | 39.791 | 55.7083 | -9.662 | 86.148 | -75 | -13.7436 | 247.7121 | -0.3947 | 73.6053 | 23.3316 | 23.3316 | 0 | 0 | 0 | 2/24/18:00
2 | 24 | 1900-01-18 | 3.3 | 14 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 14 | 0 | 0 | 39.791 | 55.75 | -9.6469 | 86.148 | -75 | -13.7377 | 262.7136 | 0 | 14 | 4.4378 | 4.4378 | 0 | 0 | 0 | 2/24/19:00
2 | 24 | 1900-01-19 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 55.7917 | -9.6319 | 86.148 | -75 | -13.7318 | 277.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/24/20:00
2 | 24 | 1900-01-20 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 55.8333 | -9.6168 | 86.148 | -75 | -13.7259 | 292.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/24/21:00
2 | 24 | 1900-01-21 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 55.875 | -9.6018 | 86.148 | -75 | -13.72 | 307.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/24/22:00
2 | 24 | 1900-01-22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 55.9167 | -9.5867 | 86.148 | -75 | -13.714 | 322.7195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/24/23:00
2 | 24 | 1900-01-23 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 55.9583 | -9.5717 | 86.148 | -75 | -13.7081 | 337.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/24/24:00
2 | 25 | 1899-12-31 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56 | -9.5566 | 86.148 | -75 | -13.7021 | -7.2775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/1:00
2 | 25 | 1900-01-01 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.0417 | -9.5415 | 86.148 | -75 | -13.6961 | 7.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/2:00
2 | 25 | 1900-01-02 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.0833 | -9.5264 | 86.148 | -75 | -13.69 | 22.7255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/3:00
2 | 25 | 1900-01-03 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.125 | -9.5114 | 86.148 | -75 | -13.684 | 37.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/4:00
2 | 25 | 1900-01-04 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.1667 | -9.4963 | 86.148 | -75 | -13.6779 | 52.7285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/5:00
2 | 25 | 1900-01-05 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.2083 | -9.4812 | 86.148 | -75 | -13.6719 | 67.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/6:00
2 | 25 | 1900-01-06 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.25 | -9.4661 | 86.148 | -75 | -13.6658 | 82.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/7:00
2 | 25 | 1900-01-07 | 2.8 | 15 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 15 | 0 | 0 | 39.791 | 56.2917 | -9.451 | 86.148 | -75 | -13.6596 | 97.7331 | 0 | 15 | 4.7547 | 4.7547 | 0 | 0 | 0 | 2/25/8:00
2 | 25 | 1900-01-08 | 3.3 | 73 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 73 | 0 | 0 | 39.791 | 56.3333 | -9.4359 | 86.148 | -75 | -13.6535 | 112.7346 | 0 | 73 | 23.1397 | 23.1397 | 0 | 0 | 0 | 2/25/9:00
2 | 25 | 1900-01-09 | 3.3 | 168 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 168 | 0 | 0 | 39.791 | 56.375 | -9.4208 | 86.148 | -75 | -13.6473 | 127.7362 | 0 | 168 | 53.2531 | 53.2531 | 0 | 0 | 0 | 2/25/10:00
2 | 25 | 1900-01-10 | 3.3 | 231 | 1 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 231 | 0 | 0 | 39.791 | 56.4167 | -9.4057 | 86.148 | -75 | -13.6412 | 142.7377 | -0.7079 | 230.2921 | 72.9986 | 72.9986 | 0 | 0 | 0 | 2/25/11:00
2 | 25 | 1900-01-11 | 3.9 | 287 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 287 | 0 | 0 | 39.791 | 56.4583 | -9.3905 | 86.148 | -75 | -13.635 | 157.7393 | 0 | 287 | 90.974 | 90.974 | 0 | 0 | 0 | 2/25/12:00
2 | 25 | 1900-01-12 | 4.4 | 321 | 2 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 321 | 0 | 0 | 39.791 | 56.5 | -9.3754 | 86.148 | -75 | -13.6288 | 172.7408 | -1.7126 | 319.2874 | 101.2085 | 101.2085 | 0 | 0 | 0 | 2/25/13:00
2 | 25 | 1900-01-13 | 5 | 324 | 1 | 41 | 1 | 0 | 41 | 0 | 0 | 324 | 0 | 0 | 39.791 | 56.5417 | -9.3603 | 86.148 | -75 | -13.6225 | 187.7424 | -0.85533 | 323.1447 | 102.4312 | 102.4312 | 0 | 0 | 0 | 2/25/14:00
2 | 25 | 1900-01-14 | 5 | 304 | 1 | 41 | 1 | 0 | 41 | 0 | 0 | 304 | 0 | 0 | 39.791 | 56.5833 | -9.3452 | 86.148 | -75 | -13.6163 | 202.7439 | -0.80315 | 303.1968 | 96.1081 | 96.1081 | 0 | 0 | 0 | 2/25/15:00
2 | 25 | 1900-01-15 | 5 | 251 | 1 | 41 | 1 | 0 | 41 | 0 | 0 | 251 | 0 | 0 | 39.791 | 56.625 | -9.33 | 86.148 | -75 | -13.61 | 217.7455 | -0.70331 | 250.2967 | 79.3397 | 79.3397 | 0 | 0 | 0 | 2/25/16:00
2 | 25 | 1900-01-16 | 5 | 149 | 1 | 41 | 1 | 0 | 41 | 0 | 0 | 149 | 0 | 0 | 39.791 | 56.6667 | -9.3149 | 86.148 | -75 | -13.6037 | 232.7471 | -0.56259 | 148.4374 | 47.0521 | 47.0521 | 0 | 0 | 0 | 2/25/17:00
2 | 25 | 1900-01-17 | 5 | 66 | 1 | 41 | 1 | 0 | 41 | 0 | 0 | 66 | 0 | 0 | 39.791 | 56.7083 | -9.2997 | 86.148 | -75 | -13.5974 | 247.7486 | -0.39056 | 65.6094 | 20.797 | 20.797 | 0 | 0 | 0 | 2/25/18:00
2 | 25 | 1900-01-18 | 3.9 | 12 | 3 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 12 | 0 | 0 | 39.791 | 56.75 | -9.2846 | 86.148 | -75 | -13.5911 | 262.7502 | -0.59685 | 11.4031 | 3.6146 | 3.6146 | 0 | 0 | 0 | 2/25/19:00
2 | 25 | 1900-01-19 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.7917 | -9.2695 | 86.148 | -75 | -13.5848 | 277.7518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/20:00
2 | 25 | 1900-01-20 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.8333 | -9.2543 | 86.148 | -75 | -13.5784 | 292.7534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/21:00
2 | 25 | 1900-01-21 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.875 | -9.2391 | 86.148 | -75 | -13.572 | 307.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/22:00
2 | 25 | 1900-01-22 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.9167 | -9.224 | 86.148 | -75 | -13.5656 | 322.7566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/23:00
2 | 25 | 1900-01-23 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 56.9583 | -9.2088 | 86.148 | -75 | -13.5592 | 337.7582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/25/24:00
2 | 26 | 1899-12-31 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57 | -9.1936 | 86.148 | -75 | -13.5528 | -7.2402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/1:00
2 | 26 | 1900-01-01 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.0417 | -9.1785 | 86.148 | -75 | -13.5463 | 7.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/2:00
2 | 26 | 1900-01-02 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.0833 | -9.1633 | 86.148 | -75 | -13.5399 | 22.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/3:00
2 | 26 | 1900-01-03 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.125 | -9.1481 | 86.148 | -75 | -13.5334 | 37.7647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/4:00
2 | 26 | 1900-01-04 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.1667 | -9.1329 | 86.148 | -75 | -13.5269 | 52.7663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/5:00
2 | 26 | 1900-01-05 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.2083 | -9.1177 | 86.148 | -75 | -13.5204 | 67.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/6:00
2 | 26 | 1900-01-06 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.25 | -9.1025 | 86.148 | -75 | -13.5138 | 82.7695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/7:00
2 | 26 | 1900-01-07 | 4.4 | 9 | 2 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 9 | 0 | 0 | 39.791 | 57.2917 | -9.0873 | 86.148 | -75 | -13.5073 | 97.7712 | -0.40735 | 8.5927 | 2.7237 | 2.7237 | 0 | 0 | 0 | 2/26/8:00
2 | 26 | 1900-01-08 | 4.4 | 92 | 40 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 92 | 0 | 0 | 39.791 | 57.3333 | -9.0721 | 86.148 | -75 | -13.5007 | 112.7728 | -15.7846 | 76.2154 | 24.1589 | 24.1589 | 0 | 0 | 0 | 2/26/9:00
2 | 26 | 1900-01-09 | 5.6 | 148 | 442 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 148 | 0 | 0 | 39.791 | 57.375 | -9.0569 | 86.148 | -75 | -13.4941 | 127.7745 | -249.9747 | -101.9747 | -32.3242 | -32.3242 | 0 | 0 | 0 | 2/26/10:00
2 | 26 | 1900-01-10 | 6.1 | 92 | 768 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 92 | 0 | 0 | 39.791 | 57.4167 | -9.0417 | 86.148 | -75 | -13.4875 | 142.7761 | -541.3025 | -449.3025 | -142.4211 | -142.4211 | 0 | 0 | 0 | 2/26/11:00
2 | 26 | 1900-01-11 | 7.8 | 88 | 860 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 88 | 0 | 0 | 39.791 | 57.4583 | -9.0265 | 86.148 | -75 | -13.4809 | 157.7778 | -690.5036 | -602.5036 | -190.9831 | -190.9831 | 0 | 0 | 0 | 2/26/12:00
2 | 26 | 1900-01-12 | 8.9 | 86 | 916 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 86 | 0 | 0 | 39.791 | 57.5 | -9.0113 | 86.148 | -75 | -13.4742 | 172.7794 | -781.4604 | -695.4604 | -220.4488 | -220.4488 | 0 | 0 | 0 | 2/26/13:00
2 | 26 | 1900-01-13 | 10.6 | 89 | 851 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 89 | 0 | 0 | 39.791 | 57.5417 | -8.996 | 86.148 | -75 | -13.4675 | 187.7811 | -725.0666 | -636.0666 | -201.622 | -201.622 | 0 | 0 | 0 | 2/26/14:00
2 | 26 | 1900-01-14 | 11.1 | 80 | 819 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 80 | 0 | 0 | 39.791 | 57.5833 | -8.9808 | 86.148 | -75 | -13.4609 | 202.7828 | -654.9167 | -574.9167 | -182.2386 | -182.2386 | 0 | 0 | 0 | 2/26/15:00
2 | 26 | 1900-01-15 | 12.2 | 80 | 819 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 80 | 0 | 0 | 39.791 | 57.625 | -8.9656 | 86.148 | -75 | -13.4542 | 217.7845 | -572.962 | -492.962 | -156.2603 | -156.2603 | 0 | 0 | 0 | 2/26/16:00
2 | 26 | 1900-01-16 | 11.7 | 55 | 746 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 55 | 0 | 0 | 39.791 | 57.6667 | -8.9503 | 86.148 | -75 | -13.4474 | 232.7861 | -416.7322 | -361.7322 | -114.6628 | -114.6628 | 0 | 0 | 0 | 2/26/17:00
2 | 26 | 1900-01-17 | 10.6 | 64 | 342 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 64 | 0 | 0 | 39.791 | 57.7083 | -8.9351 | 86.148 | -75 | -13.4407 | 247.7878 | -132.1329 | -68.1329 | -21.5969 | -21.5969 | 0 | 0 | 0 | 2/26/18:00
2 | 26 | 1900-01-18 | 8.3 | 12 | 42 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 12 | 0 | 0 | 39.791 | 57.75 | -8.9199 | 86.148 | -75 | -13.4339 | 262.7895 | -8.1694 | 3.8306 | 1.2142 | 1.2142 | 0 | 0 | 0 | 2/26/19:00
2 | 26 | 1900-01-19 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.7917 | -8.9046 | 86.148 | -75 | -13.4272 | 277.7912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/20:00
2 | 26 | 1900-01-20 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.8333 | -8.8894 | 86.148 | -75 | -13.4204 | 292.7929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/21:00
2 | 26 | 1900-01-21 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.875 | -8.8741 | 86.148 | -75 | -13.4136 | 307.7946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/22:00
2 | 26 | 1900-01-22 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.9167 | -8.8588 | 86.148 | -75 | -13.4067 | 322.7963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/23:00
2 | 26 | 1900-01-23 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 57.9583 | -8.8436 | 86.148 | -75 | -13.3999 | 337.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/26/24:00
2 | 27 | 1899-12-31 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58 | -8.8283 | 86.148 | -75 | -13.393 | -7.2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/1:00
2 | 27 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.0417 | -8.813 | 86.148 | -75 | -13.3862 | 7.8015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/2:00
2 | 27 | 1900-01-02 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.0833 | -8.7978 | 86.148 | -75 | -13.3793 | 22.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/3:00
2 | 27 | 1900-01-03 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.125 | -8.7825 | 86.148 | -75 | -13.3723 | 37.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/4:00
2 | 27 | 1900-01-04 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.1667 | -8.7672 | 86.148 | -75 | -13.3654 | 52.8066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/5:00
2 | 27 | 1900-01-05 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.2083 | -8.7519 | 86.148 | -75 | -13.3585 | 67.8084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/6:00
2 | 27 | 1900-01-06 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.25 | -8.7366 | 86.148 | -75 | -13.3515 | 82.8101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/7:00
2 | 27 | 1900-01-07 | -1.7 | 4 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 4 | 0 | 0 | 39.791 | 58.2917 | -8.7213 | 86.148 | -75 | -13.3445 | 97.8119 | 0 | 4 | 1.2679 | 1.2679 | 0 | 0 | 0 | 2/27/8:00
2 | 27 | 1900-01-08 | -1.7 | 64 | 19 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 64 | 0 | 0 | 39.791 | 58.3333 | -8.706 | 86.148 | -75 | -13.3375 | 112.8136 | -7.436 | 56.564 | 17.9298 | 17.9298 | 0 | 0 | 0 | 2/27/9:00
2 | 27 | 1900-01-09 | -1.7 | 156 | 7 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 156 | 0 | 0 | 39.791 | 58.375 | -8.6907 | 86.148 | -75 | -13.3305 | 127.8154 | -3.9368 | 152.0632 | 48.2014 | 48.2014 | 0 | 0 | 0 | 2/27/10:00
2 | 27 | 1900-01-10 | -1.7 | 222 | 3 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 222 | 0 | 0 | 39.791 | 58.4167 | -8.6754 | 86.148 | -75 | -13.3234 | 142.8171 | -2.1051 | 219.8949 | 69.7028 | 69.7028 | 0 | 0 | 0 | 2/27/11:00
2 | 27 | 1900-01-11 | -1.7 | 266 | 3 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 266 | 0 | 0 | 39.791 | 58.4583 | -8.6601 | 86.148 | -75 | -13.3164 | 157.8189 | -2.3993 | 263.6007 | 83.5568 | 83.5568 | 0 | 0 | 0 | 2/27/12:00
2 | 27 | 1900-01-12 | -1.1 | 255 | 5 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 255 | 0 | 0 | 39.791 | 58.5 | -8.6448 | 86.148 | -75 | -13.3093 | 172.8207 | -4.2495 | 250.7505 | 79.4835 | 79.4835 | 0 | 0 | 0 | 2/27/13:00
2 | 27 | 1900-01-13 | -1.1 | 270 | 6 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 270 | 0 | 0 | 39.791 | 58.5417 | -8.6295 | 86.148 | -75 | -13.3022 | 187.8224 | -5.0919 | 264.9081 | 83.9713 | 83.9713 | 0 | 0 | 0 | 2/27/14:00
2 | 27 | 1900-01-14 | -1.1 | 257 | 5 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 257 | 0 | 0 | 39.791 | 58.5833 | -8.6142 | 86.148 | -75 | -13.2951 | 202.8242 | -3.9804 | 253.0196 | 80.2028 | 80.2028 | 0 | 0 | 0 | 2/27/15:00
2 | 27 | 1900-01-15 | -1.1 | 219 | 1 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 219 | 0 | 0 | 39.791 | 58.625 | -8.5988 | 86.148 | -75 | -13.288 | 217.826 | -0.69579 | 218.3042 | 69.1986 | 69.1986 | 0 | 0 | 0 | 2/27/16:00
2 | 27 | 1900-01-16 | -1.1 | 153 | 1 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 153 | 0 | 0 | 39.791 | 58.6667 | -8.5835 | 86.148 | -75 | -13.2808 | 232.8278 | -0.55459 | 152.4454 | 48.3225 | 48.3225 | 0 | 0 | 0 | 2/27/17:00
2 | 27 | 1900-01-17 | -1.1 | 71 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 71 | 0 | 0 | 39.791 | 58.7083 | -8.5682 | 86.148 | -75 | -13.2737 | 247.8296 | 0 | 71 | 22.5058 | 22.5058 | 0 | 0 | 0 | 2/27/18:00
2 | 27 | 1900-01-18 | -1.1 | 17 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 17 | 0 | 0 | 39.791 | 58.75 | -8.5528 | 86.148 | -75 | -13.2665 | 262.8314 | 0 | 17 | 5.3887 | 5.3887 | 0 | 0 | 0 | 2/27/19:00
2 | 27 | 1900-01-19 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.7917 | -8.5375 | 86.148 | -75 | -13.2593 | 277.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/20:00
2 | 27 | 1900-01-20 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.8333 | -8.5221 | 86.148 | -75 | -13.2521 | 292.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/21:00
2 | 27 | 1900-01-21 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.875 | -8.5068 | 86.148 | -75 | -13.2449 | 307.8368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/22:00
2 | 27 | 1900-01-22 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.9167 | -8.4914 | 86.148 | -75 | -13.2376 | 322.8386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/23:00
2 | 27 | 1900-01-23 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 58.9583 | -8.4761 | 86.148 | -75 | -13.2303 | 337.8404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/27/24:00
2 | 28 | 1899-12-31 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59 | -8.4607 | 86.148 | -75 | -13.2231 | -7.1578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/1:00
2 | 28 | 1900-01-01 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.0417 | -8.4454 | 86.148 | -75 | -13.2158 | 7.8441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/2:00
2 | 28 | 1900-01-02 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.0833 | -8.43 | 86.148 | -75 | -13.2084 | 22.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/3:00
2 | 28 | 1900-01-03 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.125 | -8.4146 | 86.148 | -75 | -13.2011 | 37.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/4:00
2 | 28 | 1900-01-04 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.1667 | -8.3992 | 86.148 | -75 | -13.1938 | 52.8496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/5:00
2 | 28 | 1900-01-05 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.2083 | -8.3839 | 86.148 | -75 | -13.1864 | 67.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/6:00
2 | 28 | 1900-01-06 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.25 | -8.3685 | 86.148 | -75 | -13.179 | 82.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/7:00
2 | 28 | 1900-01-07 | -5.6 | 17 | 87 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 17 | 0 | 0 | 39.791 | 59.2917 | -8.3531 | 86.148 | -75 | -13.1716 | 97.8551 | -17.1279 | -0.12794 | -0.040555 | -0.040555 | 0 | 0 | 0 | 2/28/8:00
2 | 28 | 1900-01-08 | -3.9 | 45 | 505 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 45 | 0 | 0 | 39.791 | 59.3333 | -8.3377 | 86.148 | -75 | -13.1642 | 112.857 | -195.9972 | -150.9972 | -47.8635 | -47.8635 | 0 | 0 | 0 | 2/28/9:00
2 | 28 | 1900-01-09 | -2.2 | 67 | 721 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 67 | 0 | 0 | 39.791 | 59.375 | -8.3223 | 86.148 | -75 | -13.1567 | 127.8588 | -403.2107 | -336.2107 | -106.5729 | -106.5729 | 0 | 0 | 0 | 2/28/10:00
2 | 28 | 1900-01-10 | -0.6 | 85 | 826 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 85 | 0 | 0 | 39.791 | 59.4167 | -8.3069 | 86.148 | -75 | -13.1493 | 142.8607 | -577.0179 | -492.0179 | -155.9611 | -155.9611 | 0 | 0 | 0 | 2/28/11:00
2 | 28 | 1900-01-11 | 1.7 | 96 | 871 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 96 | 0 | 0 | 39.791 | 59.4583 | -8.2915 | 86.148 | -75 | -13.1418 | 157.8625 | -693.833 | -597.833 | -189.5026 | -189.5026 | 0 | 0 | 0 | 2/28/12:00
2 | 28 | 1900-01-12 | 3.9 | 102 | 890 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 102 | 0 | 0 | 39.791 | 59.5 | -8.2761 | 86.148 | -75 | -13.1343 | 172.8644 | -753.4875 | -651.4875 | -206.5101 | -206.5101 | 0 | 0 | 0 | 2/28/13:00
2 | 28 | 1900-01-13 | 6.1 | 102 | 898 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 102 | 0 | 0 | 39.791 | 59.5417 | -8.2607 | 86.148 | -75 | -13.1268 | 187.8663 | -758.9971 | -656.9971 | -208.2566 | -208.2566 | 0 | 0 | 0 | 2/28/14:00
2 | 28 | 1900-01-14 | 7.8 | 96 | 872 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 96 | 0 | 0 | 39.791 | 59.5833 | -8.2453 | 86.148 | -75 | -13.1193 | 202.8682 | -691.0193 | -595.0193 | -188.6107 | -188.6107 | 0 | 0 | 0 | 2/28/15:00
2 | 28 | 1900-01-15 | 9.4 | 84 | 823 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 84 | 0 | 0 | 39.791 | 59.625 | -8.2299 | 86.148 | -75 | -13.1118 | 217.8701 | -569.459 | -485.459 | -153.882 | -153.882 | 0 | 0 | 0 | 2/28/16:00
2 | 28 | 1900-01-16 | 9.4 | 66 | 724 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 66 | 0 | 0 | 39.791 | 59.6667 | -8.2144 | 86.148 | -75 | -13.1042 | 232.8719 | -398.5458 | -332.5458 | -105.4112 | -105.4112 | 0 | 0 | 0 | 2/28/17:00
2 | 28 | 1900-01-17 | 7.8 | 44 | 497 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 44 | 0 | 0 | 39.791 | 59.7083 | -8.199 | 86.148 | -75 | -13.0966 | 247.8738 | -187.7277 | -143.7277 | -45.5592 | -45.5592 | 0 | 0 | 0 | 2/28/18:00
2 | 28 | 1900-01-18 | 3.9 | 15 | 69 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 15 | 0 | 0 | 39.791 | 59.75 | -8.1836 | 86.148 | -75 | -13.089 | 262.8757 | -12.7944 | 2.2056 | 0.69915 | 0.69915 | 0 | 0 | 0 | 2/28/19:00
2 | 28 | 1900-01-19 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.7917 | -8.1682 | 86.148 | -75 | -13.0814 | 277.8776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/20:00
2 | 28 | 1900-01-20 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.8333 | -8.1527 | 86.148 | -75 | -13.0738 | 292.8795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/21:00
2 | 28 | 1900-01-21 | 1.5 | 0 | 0 | 34.7 | 1 | 0 | 34.7 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.875 | -8.1373 | 86.148 | -75 | -13.0662 | 307.8815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/22:00
2 | 28 | 1900-01-22 | -0.2 | 0 | 0 | 31.64 | 1 | 0 | 31.64 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.9167 | -8.1218 | 86.148 | -75 | -13.0585 | 322.8834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/23:00
2 | 28 | 1900-01-23 | -2 | 0 | 0 | 28.4 | 1 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 39.791 | 59.9583 | -8.1064 | 86.148 | -75 | -13.0508 | 337.8853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2/28/24:00
3 | 1 | 1899-12-31 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60 | -8.091 | 86.148 | -75 | -13.0431 | -7.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/1:00
3 | 1 | 1900-01-01 | -5.7 | 0 | 0 | 21.74 | 1 | 0 | 21.74 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.0417 | -8.0755 | 86.148 | -75 | -13.0354 | 7.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/2:00
3 | 1 | 1900-01-02 | -7.5 | 0 | 0 | 18.5 | 1 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.0833 | -8.06 | 86.148 | -75 | -13.0277 | 22.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/3:00
3 | 1 | 1900-01-03 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.125 | -8.0446 | 86.148 | -75 | -13.02 | 37.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/4:00
3 | 1 | 1900-01-04 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.1667 | -8.0291 | 86.148 | -75 | -13.0122 | 52.8949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/5:00
3 | 1 | 1900-01-05 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.2083 | -8.0137 | 86.148 | -75 | -13.0044 | 67.8969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/6:00
3 | 1 | 1900-01-06 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.25 | -7.9982 | 86.148 | -75 | -12.9966 | 82.8988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/7:00
3 | 1 | 1900-01-07 | -9.4 | 28 | 33 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 28 | 0 | 0 | 39.791 | 60.2917 | -7.9827 | 86.148 | -75 | -12.9888 | 97.9008 | -6.3847 | 21.6153 | 6.8517 | 6.8517 | 0 | 0 | 0 | 3/1/8:00
3 | 1 | 1900-01-08 | -7.2 | 98 | 4 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 98 | 0 | 0 | 39.791 | 60.3333 | -7.9672 | 86.148 | -75 | -12.981 | 112.9027 | -1.5394 | 96.4606 | 30.5763 | 30.5763 | 0 | 0 | 0 | 3/1/9:00
3 | 1 | 1900-01-09 | -5.6 | 151 | 3 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 151 | 0 | 0 | 39.791 | 60.375 | -7.9518 | 86.148 | -75 | -12.9732 | 127.9047 | -1.6682 | 149.3318 | 47.3356 | 47.3356 | 0 | 0 | 0 | 3/1/10:00
3 | 1 | 1900-01-10 | -3.3 | 184 | 4 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 184 | 0 | 0 | 39.791 | 60.4167 | -7.9363 | 86.148 | -75 | -12.9653 | 142.9067 | -2.7816 | 181.2184 | 57.4431 | 57.4431 | 0 | 0 | 0 | 3/1/11:00
3 | 1 | 1900-01-11 | -2.8 | 257 | 10 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 257 | 0 | 0 | 39.791 | 60.4583 | -7.9208 | 86.148 | -75 | -12.9574 | 157.9086 | -7.9337 | 249.0663 | 78.9497 | 78.9497 | 0 | 0 | 0 | 3/1/12:00
3 | 1 | 1900-01-12 | -1.7 | 292 | 4 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 292 | 0 | 0 | 39.791 | 60.5 | -7.9053 | 86.148 | -75 | -12.9495 | 172.9106 | -3.3731 | 288.6269 | 91.4897 | 91.4897 | 0 | 0 | 0 | 3/1/13:00
3 | 1 | 1900-01-13 | 0 | 212 | 605 | 32 | 1 | 0 | 32 | 0 | 0 | 212 | 0 | 0 | 39.791 | 60.5417 | -7.8898 | 86.148 | -75 | -12.9416 | 187.9126 | -509.2371 | -297.2371 | -94.219 | -94.219 | 0 | 0 | 0 | 3/1/14:00
3 | 1 | 1900-01-14 | 1.1 | 273 | 214 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 273 | 0 | 0 | 39.791 | 60.5833 | -7.8743 | 86.148 | -75 | -12.9337 | 202.9146 | -168.7932 | 104.2068 | 33.0317 | 33.0317 | 0 | 0 | 0 | 3/1/15:00
3 | 1 | 1900-01-15 | 1.7 | 165 | 413 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 165 | 0 | 0 | 39.791 | 60.625 | -7.8588 | 86.148 | -75 | -12.9258 | 217.9166 | -284.1428 | -119.1428 | -37.7662 | -37.7662 | 0 | 0 | 0 | 3/1/16:00
3 | 1 | 1900-01-16 | 2.2 | 122 | 377 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 122 | 0 | 0 | 39.791 | 60.6667 | -7.8433 | 86.148 | -75 | -12.9178 | 232.9185 | -205.9545 | -83.9545 | -26.6121 | -26.6121 | 0 | 0 | 0 | 3/1/17:00
3 | 1 | 1900-01-17 | 1.1 | 79 | 143 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 79 | 0 | 0 | 39.791 | 60.7083 | -7.8278 | 86.148 | -75 | -12.9098 | 247.9205 | -53.3822 | 25.6178 | 8.1204 | 8.1204 | 0 | 0 | 0 | 3/1/18:00
3 | 1 | 1900-01-18 | 0 | 15 | 93 | 32 | 1 | 0 | 32 | 0 | 0 | 15 | 0 | 0 | 39.791 | 60.75 | -7.8123 | 86.148 | -75 | -12.9018 | 262.9225 | -16.8132 | -1.8132 | -0.57475 | -0.57475 | 0 | 0 | 0 | 3/1/19:00
3 | 1 | 1900-01-19 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.7917 | -7.7967 | 86.148 | -75 | -12.8938 | 277.9245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/20:00
3 | 1 | 1900-01-20 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.8333 | -7.7812 | 86.148 | -75 | -12.8858 | 292.9265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/21:00
3 | 1 | 1900-01-21 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.875 | -7.7657 | 86.148 | -75 | -12.8778 | 307.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/22:00
3 | 1 | 1900-01-22 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.9167 | -7.7502 | 86.148 | -75 | -12.8697 | 322.9306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/23:00
3 | 1 | 1900-01-23 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 60.9583 | -7.7346 | 86.148 | -75 | -12.8616 | 337.9326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/1/24:00
3 | 2 | 1899-12-31 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61 | -7.7191 | 86.148 | -75 | -12.8536 | -7.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/1:00
3 | 2 | 1900-01-01 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.0417 | -7.7036 | 86.148 | -75 | -12.8454 | 7.9366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/2:00
3 | 2 | 1900-01-02 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.0833 | -7.688 | 86.148 | -75 | -12.8373 | 22.9387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/3:00
3 | 2 | 1900-01-03 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.125 | -7.6725 | 86.148 | -75 | -12.8292 | 37.9407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/4:00
3 | 2 | 1900-01-04 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.1667 | -7.6569 | 86.148 | -75 | -12.821 | 52.9427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/5:00
3 | 2 | 1900-01-05 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.2083 | -7.6414 | 86.148 | -75 | -12.8129 | 67.9448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/6:00
3 | 2 | 1900-01-06 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.25 | -7.6258 | 86.148 | -75 | -12.8047 | 82.9468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/7:00
3 | 2 | 1900-01-07 | -1.7 | 26 | 31 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 26 | 0 | 0 | 39.791 | 61.2917 | -7.6103 | 86.148 | -75 | -12.7965 | 97.9489 | -5.8925 | 20.1075 | 6.3737 | 6.3737 | 0 | 0 | 0 | 3/2/8:00
3 | 2 | 1900-01-08 | 0 | 63 | 6 | 32 | 1 | 0 | 32 | 0 | 0 | 63 | 0 | 0 | 39.791 | 61.3333 | -7.5947 | 86.148 | -75 | -12.7883 | 112.9509 | -2.2895 | 60.7105 | 19.2442 | 19.2442 | 0 | 0 | 0 | 3/2/9:00
3 | 2 | 1900-01-09 | 1.1 | 173 | 3 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 173 | 0 | 0 | 39.791 | 61.375 | -7.5792 | 86.148 | -75 | -12.78 | 127.953 | -1.6586 | 171.3414 | 54.3122 | 54.3122 | 0 | 0 | 0 | 3/2/10:00
3 | 2 | 1900-01-10 | 2.2 | 191 | 13 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 191 | 0 | 0 | 39.791 | 61.4167 | -7.5636 | 86.148 | -75 | -12.7718 | 142.9551 | -8.9986 | 182.0014 | 57.6913 | 57.6913 | 0 | 0 | 0 | 3/2/11:00
3 | 2 | 1900-01-11 | 3.9 | 258 | 11 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 258 | 0 | 0 | 39.791 | 61.4583 | -7.548 | 86.148 | -75 | -12.7635 | 157.9571 | -8.6912 | 249.3088 | 79.0265 | 79.0265 | 0 | 0 | 0 | 3/2/12:00
3 | 2 | 1900-01-12 | 5.6 | 192 | 567 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 192 | 0 | 0 | 39.791 | 61.5 | -7.5324 | 86.148 | -75 | -12.7552 | 172.9592 | -476.2255 | -284.2255 | -90.0945 | -90.0945 | 0 | 0 | 0 | 3/2/13:00
3 | 2 | 1900-01-13 | 7.8 | 253 | 272 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 253 | 0 | 0 | 39.791 | 61.5417 | -7.5169 | 86.148 | -75 | -12.7469 | 187.9613 | -227.9798 | 25.0202 | 7.931 | 7.931 | 0 | 0 | 0 | 3/2/14:00
3 | 2 | 1900-01-14 | 7.8 | 194 | 26 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 194 | 0 | 0 | 39.791 | 61.5833 | -7.5013 | 86.148 | -75 | -12.7386 | 202.9633 | -20.4097 | 173.5903 | 55.0251 | 55.0251 | 0 | 0 | 0 | 3/2/15:00
3 | 2 | 1900-01-15 | 6.1 | 202 | 10 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 202 | 0 | 0 | 39.791 | 61.625 | -7.4857 | 86.148 | -75 | -12.7303 | 217.9654 | -6.8399 | 195.1601 | 61.8623 | 61.8623 | 0 | 0 | 0 | 3/2/16:00
3 | 2 | 1900-01-16 | 4.4 | 87 | 3 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 87 | 0 | 0 | 39.791 | 61.6667 | -7.4701 | 86.148 | -75 | -12.7219 | 232.9675 | -1.6261 | 85.3739 | 27.062 | 27.062 | 0 | 0 | 0 | 3/2/17:00
3 | 2 | 1900-01-17 | 3.3 | 58 | 2 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 58 | 0 | 0 | 39.791 | 61.7083 | -7.4545 | 86.148 | -75 | -12.7136 | 247.9696 | -0.73763 | 57.2624 | 18.1512 | 18.1512 | 0 | 0 | 0 | 3/2/18:00
3 | 2 | 1900-01-18 | 2.8 | 12 | 1 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 12 | 0 | 0 | 39.791 | 61.75 | -7.4389 | 86.148 | -75 | -12.7052 | 262.9717 | -0.17609 | 11.8239 | 3.748 | 3.748 | 0 | 0 | 0 | 3/2/19:00
3 | 2 | 1900-01-19 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.7917 | -7.4233 | 86.148 | -75 | -12.6968 | 277.9738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/20:00
3 | 2 | 1900-01-20 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.8333 | -7.4077 | 86.148 | -75 | -12.6884 | 292.9759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/21:00
3 | 2 | 1900-01-21 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.875 | -7.3921 | 86.148 | -75 | -12.68 | 307.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/22:00
3 | 2 | 1900-01-22 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.9167 | -7.3765 | 86.148 | -75 | -12.6715 | 322.9801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/23:00
3 | 2 | 1900-01-23 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 61.9583 | -7.3609 | 86.148 | -75 | -12.6631 | 337.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/2/24:00
3 | 3 | 1899-12-31 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62 | -7.3453 | 86.148 | -75 | -12.6546 | -7.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/1:00
3 | 3 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.0417 | -7.3297 | 86.148 | -75 | -12.6461 | 7.9865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/2:00
3 | 3 | 1900-01-02 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.0833 | -7.3141 | 86.148 | -75 | -12.6376 | 22.9886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/3:00
3 | 3 | 1900-01-03 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.125 | -7.2984 | 86.148 | -75 | -12.6291 | 37.9907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/4:00
3 | 3 | 1900-01-04 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.1667 | -7.2828 | 86.148 | -75 | -12.6205 | 52.9929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/5:00
3 | 3 | 1900-01-05 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.2083 | -7.2672 | 86.148 | -75 | -12.612 | 67.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/6:00
3 | 3 | 1900-01-06 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.25 | -7.2516 | 86.148 | -75 | -12.6034 | 82.9971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/7:00
3 | 3 | 1900-01-07 | 1.1 | 14 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 14 | 0 | 0 | 39.791 | 62.2917 | -7.2359 | 86.148 | -75 | -12.5948 | 97.9993 | 0 | 14 | 4.4378 | 4.4378 | 0 | 0 | 0 | 3/3/8:00
3 | 3 | 1900-01-08 | 1.1 | 83 | 2 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 83 | 0 | 0 | 39.791 | 62.3333 | -7.2203 | 86.148 | -75 | -12.5862 | 113.0014 | -0.75661 | 82.2434 | 26.0697 | 26.0697 | 0 | 0 | 0 | 3/3/9:00
3 | 3 | 1900-01-09 | 1.1 | 190 | 1 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 190 | 0 | 0 | 39.791 | 62.375 | -7.2046 | 86.148 | -75 | -12.5776 | 128.0036 | -0.54963 | 189.4504 | 60.0525 | 60.0525 | 0 | 0 | 0 | 3/3/10:00
3 | 3 | 1900-01-10 | 1.7 | 251 | 2 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 251 | 0 | 0 | 39.791 | 62.4167 | -7.189 | 86.148 | -75 | -12.569 | 143.0058 | -1.3779 | 249.6221 | 79.1258 | 79.1258 | 0 | 0 | 0 | 3/3/11:00
3 | 3 | 1900-01-11 | 2.2 | 297 | 1 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 297 | 0 | 0 | 39.791 | 62.4583 | -7.1733 | 86.148 | -75 | -12.5603 | 158.0079 | -0.78681 | 296.2132 | 93.8944 | 93.8944 | 0 | 0 | 0 | 3/3/12:00
3 | 3 | 1900-01-12 | 3.3 | 334 | 2 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 334 | 0 | 0 | 39.791 | 62.5 | -7.1577 | 86.148 | -75 | -12.5517 | 173.0101 | -1.6729 | 332.3271 | 105.3419 | 105.3419 | 0 | 0 | 0 | 3/3/13:00
3 | 3 | 1900-01-13 | 2.8 | 356 | 2 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 356 | 0 | 0 | 39.791 | 62.5417 | -7.142 | 86.148 | -75 | -12.543 | 188.0123 | -1.6691 | 354.3309 | 112.3167 | 112.3167 | 0 | 0 | 0 | 3/3/14:00
3 | 3 | 1900-01-14 | 2.2 | 328 | 1 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 328 | 0 | 0 | 39.791 | 62.5833 | -7.1264 | 86.148 | -75 | -12.5343 | 203.0144 | -0.78116 | 327.2188 | 103.7227 | 103.7227 | 0 | 0 | 0 | 3/3/15:00
3 | 3 | 1900-01-15 | 2.8 | 252 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 252 | 0 | 0 | 39.791 | 62.625 | -7.1107 | 86.148 | -75 | -12.5256 | 218.0166 | 0 | 252 | 79.8796 | 79.8796 | 0 | 0 | 0 | 3/3/16:00
3 | 3 | 1900-01-16 | 2.2 | 174 | 1 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 174 | 0 | 0 | 39.791 | 62.6667 | -7.095 | 86.148 | -75 | -12.5169 | 233.0188 | -0.53773 | 173.4623 | 54.9845 | 54.9845 | 0 | 0 | 0 | 3/3/17:00
3 | 3 | 1900-01-17 | 2.2 | 81 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 81 | 0 | 0 | 39.791 | 62.7083 | -7.0794 | 86.148 | -75 | -12.5081 | 248.021 | 0 | 81 | 25.6756 | 25.6756 | 0 | 0 | 0 | 3/3/18:00
3 | 3 | 1900-01-18 | 1.7 | 19 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 19 | 0 | 0 | 39.791 | 62.75 | -7.0637 | 86.148 | -75 | -12.4994 | 263.0232 | 0 | 19 | 6.0227 | 6.0227 | 0 | 0 | 0 | 3/3/19:00
3 | 3 | 1900-01-19 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.7917 | -7.048 | 86.148 | -75 | -12.4906 | 278.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/20:00
3 | 3 | 1900-01-20 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.8333 | -7.0324 | 86.148 | -75 | -12.4818 | 293.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/21:00
3 | 3 | 1900-01-21 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.875 | -7.0167 | 86.148 | -75 | -12.473 | 308.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/22:00
3 | 3 | 1900-01-22 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.9167 | -7.001 | 86.148 | -75 | -12.4642 | 323.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/23:00
3 | 3 | 1900-01-23 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 62.9583 | -6.9853 | 86.148 | -75 | -12.4554 | 338.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/3/24:00
3 | 4 | 1899-12-31 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63 | -6.9696 | 86.148 | -75 | -12.4465 | -6.9636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/1:00
3 | 4 | 1900-01-01 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.0417 | -6.9539 | 86.148 | -75 | -12.4377 | 8.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/2:00
3 | 4 | 1900-01-02 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.0833 | -6.9382 | 86.148 | -75 | -12.4288 | 23.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/3:00
3 | 4 | 1900-01-03 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.125 | -6.9225 | 86.148 | -75 | -12.4199 | 38.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/4:00
3 | 4 | 1900-01-04 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.1667 | -6.9068 | 86.148 | -75 | -12.411 | 53.0453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/5:00
3 | 4 | 1900-01-05 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.2083 | -6.8911 | 86.148 | -75 | -12.4021 | 68.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/6:00
3 | 4 | 1900-01-06 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.25 | -6.8754 | 86.148 | -75 | -12.3931 | 83.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/7:00
3 | 4 | 1900-01-07 | 0.6 | 25 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 25 | 0 | 0 | 39.791 | 63.2917 | -6.8597 | 86.148 | -75 | -12.3842 | 98.052 | 0 | 25 | 7.9246 | 7.9246 | 0 | 0 | 0 | 3/4/8:00
3 | 4 | 1900-01-08 | 0.6 | 104 | 1 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 104 | 0 | 0 | 39.791 | 63.3333 | -6.844 | 86.148 | -75 | -12.3752 | 113.0542 | -0.37502 | 103.625 | 32.8473 | 32.8473 | 0 | 0 | 0 | 3/4/9:00
3 | 4 | 1900-01-09 | 0.6 | 195 | 1 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 195 | 0 | 0 | 39.791 | 63.375 | -6.8283 | 86.148 | -75 | -12.3662 | 128.0564 | -0.54639 | 194.4536 | 61.6384 | 61.6384 | 0 | 0 | 0 | 3/4/10:00
3 | 4 | 1900-01-10 | 1.7 | 279 | 2 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 279 | 0 | 0 | 39.791 | 63.4167 | -6.8126 | 86.148 | -75 | -12.3572 | 143.0587 | -1.3714 | 277.6286 | 88.0034 | 88.0034 | 0 | 0 | 0 | 3/4/11:00
3 | 4 | 1900-01-11 | 1.1 | 320 | 1 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 320 | 0 | 0 | 39.791 | 63.4583 | -6.7968 | 86.148 | -75 | -12.3482 | 158.0609 | -0.78347 | 319.2165 | 101.1861 | 101.1861 | 0 | 0 | 0 | 3/4/12:00
3 | 4 | 1900-01-12 | 1.7 | 326 | 1 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 326 | 0 | 0 | 39.791 | 63.5 | -6.7811 | 86.148 | -75 | -12.3392 | 173.0632 | -0.83299 | 325.167 | 103.0723 | 103.0723 | 0 | 0 | 0 | 3/4/13:00
3 | 4 | 1900-01-13 | 2.8 | 348 | 1 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 348 | 0 | 0 | 39.791 | 63.5417 | -6.7654 | 86.148 | -75 | -12.3301 | 188.0655 | -0.83088 | 347.1691 | 110.0465 | 110.0465 | 0 | 0 | 0 | 3/4/14:00
3 | 4 | 1900-01-14 | 3.3 | 294 | 1 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 294 | 0 | 0 | 39.791 | 63.5833 | -6.7496 | 86.148 | -75 | -12.3211 | 203.0677 | -0.77726 | 293.2227 | 92.9465 | 92.9465 | 0 | 0 | 0 | 3/4/15:00
3 | 4 | 1900-01-15 | 3.9 | 212 | 87 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 212 | 0 | 0 | 39.791 | 63.625 | -6.7339 | 86.148 | -75 | -12.312 | 218.07 | -58.7935 | 153.2065 | 48.5638 | 48.5638 | 0 | 0 | 0 | 3/4/16:00
3 | 4 | 1900-01-16 | 3.9 | 143 | 327 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 143 | 0 | 0 | 39.791 | 63.6667 | -6.7182 | 86.148 | -75 | -12.3029 | 233.0723 | -174.4056 | -31.4056 | -9.955 | -9.955 | 0 | 0 | 0 | 3/4/17:00
3 | 4 | 1900-01-17 | 3.3 | 56 | 470 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 56 | 0 | 0 | 39.791 | 63.7083 | -6.7024 | 86.148 | -75 | -12.2938 | 248.0745 | -169.0348 | -113.0348 | -35.8301 | -35.8301 | 0 | 0 | 0 | 3/4/18:00
3 | 4 | 1900-01-18 | 2.2 | 20 | 41 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 20 | 0 | 0 | 39.791 | 63.75 | -6.6867 | 86.148 | -75 | -12.2847 | 263.0768 | -6.8269 | 13.1731 | 4.1756 | 4.1756 | 0 | 0 | 0 | 3/4/19:00
3 | 4 | 1900-01-19 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.7917 | -6.6709 | 86.148 | -75 | -12.2756 | 278.0791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/20:00
3 | 4 | 1900-01-20 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.8333 | -6.6552 | 86.148 | -75 | -12.2664 | 293.0814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/21:00
3 | 4 | 1900-01-21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.875 | -6.6394 | 86.148 | -75 | -12.2573 | 308.0837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/22:00
3 | 4 | 1900-01-22 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.9167 | -6.6237 | 86.148 | -75 | -12.2481 | 323.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/23:00
3 | 4 | 1900-01-23 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 63.9583 | -6.6079 | 86.148 | -75 | -12.2389 | 338.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/4/24:00
3 | 5 | 1899-12-31 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64 | -6.5922 | 86.148 | -75 | -12.2297 | -6.9094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/1:00
3 | 5 | 1900-01-01 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.0417 | -6.5764 | 86.148 | -75 | -12.2205 | 8.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/2:00
3 | 5 | 1900-01-02 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.0833 | -6.5606 | 86.148 | -75 | -12.2112 | 23.0952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/3:00
3 | 5 | 1900-01-03 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.125 | -6.5449 | 86.148 | -75 | -12.202 | 38.0975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/4:00
3 | 5 | 1900-01-04 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.1667 | -6.5291 | 86.148 | -75 | -12.1927 | 53.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/5:00
3 | 5 | 1900-01-05 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.2083 | -6.5133 | 86.148 | -75 | -12.1834 | 68.1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/6:00
3 | 5 | 1900-01-06 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.25 | -6.4975 | 86.148 | -75 | -12.1741 | 83.1045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/7:00
3 | 5 | 1900-01-07 | -2.2 | 24 | 40 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 24 | 0 | 0 | 39.791 | 64.2917 | -6.4817 | 86.148 | -75 | -12.1648 | 98.1068 | -7.1964 | 16.8036 | 5.3264 | 5.3264 | 0 | 0 | 0 | 3/5/8:00
3 | 5 | 1900-01-08 | 0 | 74 | 371 | 32 | 1 | 0 | 32 | 0 | 0 | 74 | 0 | 0 | 39.791 | 64.3333 | -6.466 | 86.148 | -75 | -12.1555 | 113.1091 | -137.9121 | -63.9121 | -20.259 | -20.259 | 0 | 0 | 0 | 3/5/9:00
3 | 5 | 1900-01-09 | 1.1 | 142 | 352 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 142 | 0 | 0 | 39.791 | 64.375 | -6.4502 | 86.148 | -75 | -12.1462 | 128.1115 | -191.1836 | -49.1836 | -15.5904 | -15.5904 | 0 | 0 | 0 | 3/5/10:00
3 | 5 | 1900-01-10 | 2.8 | 188 | 627 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 188 | 0 | 0 | 39.791 | 64.4167 | -6.4344 | 86.148 | -75 | -12.1368 | 143.1138 | -427.8807 | -239.8807 | -76.038 | -76.038 | 0 | 0 | 0 | 3/5/11:00
3 | 5 | 1900-01-11 | 5 | 223 | 530 | 41 | 1 | 0 | 41 | 0 | 0 | 223 | 0 | 0 | 39.791 | 64.4583 | -6.4186 | 86.148 | -75 | -12.1274 | 158.1161 | -413.4483 | -190.4483 | -60.3688 | -60.3688 | 0 | 0 | 0 | 3/5/12:00
3 | 5 | 1900-01-12 | 6.7 | 220 | 656 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 220 | 0 | 0 | 39.791 | 64.5 | -6.4028 | 86.148 | -75 | -12.1181 | 173.1185 | -544.126 | -324.126 | -102.7423 | -102.7423 | 0 | 0 | 0 | 3/5/13:00
3 | 5 | 1900-01-13 | 8.3 | 170 | 705 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 170 | 0 | 0 | 39.791 | 64.5417 | -6.387 | 86.148 | -75 | -12.1087 | 188.1208 | -583.1423 | -413.1423 | -130.9589 | -130.9589 | 0 | 0 | 0 | 3/5/14:00
3 | 5 | 1900-01-14 | 7.8 | 312 | 159 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 312 | 0 | 0 | 39.791 | 64.5833 | -6.3712 | 86.148 | -75 | -12.0993 | 203.1232 | -122.9561 | 189.0439 | 59.9236 | 59.9236 | 0 | 0 | 0 | 3/5/15:00
3 | 5 | 1900-01-15 | 8.3 | 266 | 168 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 266 | 0 | 0 | 39.791 | 64.625 | -6.3554 | 86.148 | -75 | -12.0898 | 218.1255 | -112.8264 | 153.1736 | 48.5533 | 48.5533 | 0 | 0 | 0 | 3/5/16:00
3 | 5 | 1900-01-16 | 8.9 | 151 | 60 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 151 | 0 | 0 | 39.791 | 64.6667 | -6.3396 | 86.148 | -75 | -12.0804 | 233.1279 | -31.7342 | 119.2658 | 37.8052 | 37.8052 | 0 | 0 | 0 | 3/5/17:00
3 | 5 | 1900-01-17 | 7.8 | 62 | 9 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 62 | 0 | 0 | 39.791 | 64.7083 | -6.3238 | 86.148 | -75 | -12.0709 | 248.1303 | -3.1948 | 58.8052 | 18.6402 | 18.6402 | 0 | 0 | 0 | 3/5/18:00
3 | 5 | 1900-01-18 | 7.8 | 19 | 1 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 19 | 0 | 0 | 39.791 | 64.75 | -6.308 | 86.148 | -75 | -12.0615 | 263.1326 | -0.16164 | 18.8384 | 5.9714 | 5.9714 | 0 | 0 | 0 | 3/5/19:00
3 | 5 | 1900-01-19 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.7917 | -6.2921 | 86.148 | -75 | -12.052 | 278.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/20:00
3 | 5 | 1900-01-20 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.8333 | -6.2763 | 86.148 | -75 | -12.0425 | 293.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/21:00
3 | 5 | 1900-01-21 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.875 | -6.2605 | 86.148 | -75 | -12.033 | 308.1398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/22:00
3 | 5 | 1900-01-22 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.9167 | -6.2447 | 86.148 | -75 | -12.0235 | 323.1421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/23:00
3 | 5 | 1900-01-23 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 64.9583 | -6.2289 | 86.148 | -75 | -12.0139 | 338.1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/5/24:00
3 | 6 | 1899-12-31 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65 | -6.213 | 86.148 | -75 | -12.0044 | -6.8531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/1:00
3 | 6 | 1900-01-01 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.0417 | -6.1972 | 86.148 | -75 | -11.9948 | 8.1493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/2:00
3 | 6 | 1900-01-02 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.0833 | -6.1814 | 86.148 | -75 | -11.9852 | 23.1517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/3:00
3 | 6 | 1900-01-03 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.125 | -6.1655 | 86.148 | -75 | -11.9756 | 38.1541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/4:00
3 | 6 | 1900-01-04 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.1667 | -6.1497 | 86.148 | -75 | -11.966 | 53.1565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/5:00
3 | 6 | 1900-01-05 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.2083 | -6.1338 | 86.148 | -75 | -11.9564 | 68.1589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/6:00
3 | 6 | 1900-01-06 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.25 | -6.118 | 86.148 | -75 | -11.9467 | 83.1613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/7:00
3 | 6 | 1900-01-07 | -0.6 | 16 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 16 | 0 | 0 | 39.791 | 65.2917 | -6.1021 | 86.148 | -75 | -11.9371 | 98.1637 | 0 | 16 | 5.0717 | 5.0717 | 0 | 0 | 0 | 3/6/8:00
3 | 6 | 1900-01-08 | -1.1 | 84 | 8 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 84 | 0 | 0 | 39.791 | 65.3333 | -6.0863 | 86.148 | -75 | -11.9274 | 113.1661 | -2.9475 | 81.0525 | 25.6922 | 25.6922 | 0 | 0 | 0 | 3/6/9:00
3 | 6 | 1900-01-09 | -1.1 | 181 | 3 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 181 | 0 | 0 | 39.791 | 65.375 | -6.0704 | 86.148 | -75 | -11.9178 | 128.1686 | -1.6196 | 179.3804 | 56.8605 | 56.8605 | 0 | 0 | 0 | 3/6/10:00
3 | 6 | 1900-01-10 | -1.1 | 218 | 4 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 218 | 0 | 0 | 39.791 | 65.4167 | -6.0546 | 86.148 | -75 | -11.9081 | 143.171 | -2.7164 | 215.2836 | 68.2411 | 68.2411 | 0 | 0 | 0 | 3/6/11:00
3 | 6 | 1900-01-11 | -1.1 | 279 | 6 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 279 | 0 | 0 | 39.791 | 65.4583 | -6.0387 | 86.148 | -75 | -11.8983 | 158.1734 | -4.66 | 274.34 | 86.961 | 86.961 | 0 | 0 | 0 | 3/6/12:00
3 | 6 | 1900-01-12 | -1.1 | 325 | 4 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 325 | 0 | 0 | 39.791 | 65.5 | -6.0229 | 86.148 | -75 | -11.8886 | 173.1758 | -3.3035 | 321.6965 | 101.9722 | 101.9722 | 0 | 0 | 0 | 3/6/13:00
3 | 6 | 1900-01-13 | 0.6 | 305 | 3 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 305 | 0 | 0 | 39.791 | 65.5417 | -6.007 | 86.148 | -75 | -11.8789 | 188.1783 | -2.4701 | 302.5299 | 95.8967 | 95.8967 | 0 | 0 | 0 | 3/6/14:00
3 | 6 | 1900-01-14 | 1.7 | 279 | 38 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 279 | 0 | 0 | 39.791 | 65.5833 | -5.9911 | 86.148 | -75 | -11.8691 | 203.1807 | -29.2331 | 249.7669 | 79.1718 | 79.1718 | 0 | 0 | 0 | 3/6/15:00
3 | 6 | 1900-01-15 | 2.2 | 199 | 178 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 199 | 0 | 0 | 39.791 | 65.625 | -5.9753 | 86.148 | -75 | -11.8594 | 218.1832 | -118.783 | 80.217 | 25.4274 | 25.4274 | 0 | 0 | 0 | 3/6/16:00
3 | 6 | 1900-01-16 | 2.8 | 126 | 59 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 126 | 0 | 0 | 39.791 | 65.6667 | -5.9594 | 86.148 | -75 | -11.8496 | 233.1856 | -30.9392 | 95.0608 | 30.1326 | 30.1326 | 0 | 0 | 0 | 3/6/17:00
3 | 6 | 1900-01-17 | 2.2 | 80 | 2 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 80 | 0 | 0 | 39.791 | 65.7083 | -5.9435 | 86.148 | -75 | -11.8398 | 248.188 | -0.70047 | 79.2995 | 25.1366 | 25.1366 | 0 | 0 | 0 | 3/6/18:00
3 | 6 | 1900-01-18 | 2.2 | 15 | 1 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 15 | 0 | 0 | 39.791 | 65.75 | -5.9276 | 86.148 | -75 | -11.83 | 263.1905 | -0.15671 | 14.8433 | 4.7051 | 4.7051 | 0 | 0 | 0 | 3/6/19:00
3 | 6 | 1900-01-19 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.7917 | -5.9118 | 86.148 | -75 | -11.8202 | 278.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/20:00
3 | 6 | 1900-01-20 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.8333 | -5.8959 | 86.148 | -75 | -11.8104 | 293.1954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/21:00
3 | 6 | 1900-01-21 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.875 | -5.88 | 86.148 | -75 | -11.8005 | 308.1979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/22:00
3 | 6 | 1900-01-22 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.9167 | -5.8641 | 86.148 | -75 | -11.7907 | 323.2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/23:00
3 | 6 | 1900-01-23 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 65.9583 | -5.8482 | 86.148 | -75 | -11.7808 | 338.2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/6/24:00
3 | 7 | 1899-12-31 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66 | -5.8323 | 86.148 | -75 | -11.7709 | -6.7947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/1:00
3 | 7 | 1900-01-01 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.0417 | -5.8164 | 86.148 | -75 | -11.761 | 8.2078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/2:00
3 | 7 | 1900-01-02 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.0833 | -5.8005 | 86.148 | -75 | -11.7511 | 23.2102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/3:00
3 | 7 | 1900-01-03 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.125 | -5.7846 | 86.148 | -75 | -11.7412 | 38.2127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/4:00
3 | 7 | 1900-01-04 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.1667 | -5.7687 | 86.148 | -75 | -11.7312 | 53.2152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/5:00
3 | 7 | 1900-01-05 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.2083 | -5.7528 | 86.148 | -75 | -11.7213 | 68.2177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/6:00
3 | 7 | 1900-01-06 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.25 | -5.7369 | 86.148 | -75 | -11.7113 | 83.2202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/7:00
3 | 7 | 1900-01-07 | -8.3 | 27 | 11 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 27 | 0 | 0 | 39.791 | 66.2917 | -5.721 | 86.148 | -75 | -11.7013 | 98.2227 | -1.9046 | 25.0954 | 7.9548 | 7.9548 | 0 | 0 | 0 | 3/7/8:00
3 | 7 | 1900-01-08 | -7.8 | 104 | 288 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 104 | 0 | 0 | 39.791 | 66.3333 | -5.7051 | 86.148 | -75 | -11.6913 | 113.2252 | -105.1569 | -1.1569 | -0.36671 | -0.36671 | 0 | 0 | 0 | 3/7/9:00
3 | 7 | 1900-01-09 | -7.8 | 172 | 489 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 172 | 0 | 0 | 39.791 | 66.375 | -5.6892 | 86.148 | -75 | -11.6813 | 128.2277 | -262.3817 | -90.3817 | -28.6494 | -28.6494 | 0 | 0 | 0 | 3/7/10:00
3 | 7 | 1900-01-10 | -7.2 | 252 | 101 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 252 | 0 | 0 | 39.791 | 66.4167 | -5.6733 | 86.148 | -75 | -11.6713 | 143.2302 | -68.2521 | 183.7479 | 58.2449 | 58.2449 | 0 | 0 | 0 | 3/7/11:00
3 | 7 | 1900-01-11 | -6.7 | 297 | 428 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 297 | 0 | 0 | 39.791 | 66.4583 | -5.6573 | 86.148 | -75 | -11.6613 | 158.2327 | -330.9338 | -33.9338 | -10.7564 | -10.7564 | 0 | 0 | 0 | 3/7/12:00
3 | 7 | 1900-01-12 | -6.1 | 307 | 217 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 307 | 0 | 0 | 39.791 | 66.5 | -5.6414 | 86.148 | -75 | -11.6512 | 173.2352 | -178.4285 | 128.5715 | 40.7549 | 40.7549 | 0 | 0 | 0 | 3/7/13:00
3 | 7 | 1900-01-13 | -6.1 | 371 | 311 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 371 | 0 | 0 | 39.791 | 66.5417 | -5.6255 | 86.148 | -75 | -11.6412 | 188.2377 | -254.8735 | 116.1265 | 36.8101 | 36.8101 | 0 | 0 | 0 | 3/7/14:00
3 | 7 | 1900-01-14 | -6.7 | 297 | 309 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 297 | 0 | 0 | 39.791 | 66.5833 | -5.6096 | 86.148 | -75 | -11.6311 | 203.2402 | -236.4509 | 60.5491 | 19.193 | 19.193 | 0 | 0 | 0 | 3/7/15:00
3 | 7 | 1900-01-15 | -6.1 | 230 | 217 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 230 | 0 | 0 | 39.791 | 66.625 | -5.5936 | 86.148 | -75 | -11.621 | 218.2428 | -143.8694 | 86.1306 | 27.3019 | 27.3019 | 0 | 0 | 0 | 3/7/16:00
3 | 7 | 1900-01-16 | -6.7 | 167 | 83 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 167 | 0 | 0 | 39.791 | 66.6667 | -5.5777 | 86.148 | -75 | -11.6109 | 233.2453 | -43.1451 | 123.8549 | 39.2598 | 39.2598 | 0 | 0 | 0 | 3/7/17:00
3 | 7 | 1900-01-17 | -6.7 | 104 | 143 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 104 | 0 | 0 | 39.791 | 66.7083 | -5.5618 | 86.148 | -75 | -11.6008 | 248.2478 | -49.3985 | 54.6015 | 17.3077 | 17.3077 | 0 | 0 | 0 | 3/7/18:00
3 | 7 | 1900-01-18 | -8.3 | 21 | 70 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 21 | 0 | 0 | 39.791 | 66.75 | -5.5458 | 86.148 | -75 | -11.5907 | 263.2503 | -10.6215 | 10.3785 | 3.2898 | 3.2898 | 0 | 0 | 0 | 3/7/19:00
3 | 7 | 1900-01-19 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.7917 | -5.5299 | 86.148 | -75 | -11.5805 | 278.2529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/20:00
3 | 7 | 1900-01-20 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.8333 | -5.5139 | 86.148 | -75 | -11.5704 | 293.2554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/21:00
3 | 7 | 1900-01-21 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.875 | -5.498 | 86.148 | -75 | -11.5602 | 308.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/22:00
3 | 7 | 1900-01-22 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.9167 | -5.482 | 86.148 | -75 | -11.55 | 323.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/23:00
3 | 7 | 1900-01-23 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 66.9583 | -5.4661 | 86.148 | -75 | -11.5398 | 338.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/7/24:00
3 | 8 | 1899-12-31 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67 | -5.4501 | 86.148 | -75 | -11.5296 | -6.7344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/1:00
3 | 8 | 1900-01-01 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.0417 | -5.4342 | 86.148 | -75 | -11.5194 | 8.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/2:00
3 | 8 | 1900-01-02 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.0833 | -5.4182 | 86.148 | -75 | -11.5092 | 23.2707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/3:00
3 | 8 | 1900-01-03 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.125 | -5.4023 | 86.148 | -75 | -11.4989 | 38.2733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/4:00
3 | 8 | 1900-01-04 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.1667 | -5.3863 | 86.148 | -75 | -11.4887 | 53.2758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/5:00
3 | 8 | 1900-01-05 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.2083 | -5.3703 | 86.148 | -75 | -11.4784 | 68.2784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/6:00
3 | 8 | 1900-01-06 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.25 | -5.3544 | 86.148 | -75 | -11.4681 | 83.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/7:00
3 | 8 | 1900-01-07 | -10 | 22 | 190 | 14 | 1 | 0 | 14 | 0 | 0 | 22 | 0 | 0 | 39.791 | 67.2917 | -5.3384 | 86.148 | -75 | -11.4578 | 98.2835 | -32.2555 | -10.2555 | -3.2508 | -3.2508 | 0 | 0 | 0 | 3/8/8:00
3 | 8 | 1900-01-08 | -8.3 | 62 | 366 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 62 | 0 | 0 | 39.791 | 67.3333 | -5.3224 | 86.148 | -75 | -11.4475 | 113.2861 | -132.4246 | -70.4246 | -22.3234 | -22.3234 | 0 | 0 | 0 | 3/8/9:00
3 | 8 | 1900-01-09 | -6.7 | 165 | 395 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 165 | 0 | 0 | 39.791 | 67.375 | -5.3065 | 86.148 | -75 | -11.4372 | 128.2887 | -210.6365 | -45.6365 | -14.466 | -14.466 | 0 | 0 | 0 | 3/8/10:00
3 | 8 | 1900-01-10 | -4.4 | 136 | 666 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 136 | 0 | 0 | 39.791 | 67.4167 | -5.2905 | 86.148 | -75 | -11.4269 | 143.2913 | -447.8104 | -311.8104 | -98.8384 | -98.8384 | 0 | 0 | 0 | 3/8/11:00
3 | 8 | 1900-01-11 | -2.8 | 218 | 669 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 218 | 0 | 0 | 39.791 | 67.4583 | -5.2745 | 86.148 | -75 | -11.4165 | 158.2939 | -514.936 | -296.936 | -94.1235 | -94.1235 | 0 | 0 | 0 | 3/8/12:00
3 | 8 | 1900-01-12 | -1.1 | 243 | 58 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 243 | 0 | 0 | 39.791 | 67.5 | -5.2585 | 86.148 | -75 | -11.4061 | 173.2965 | -47.4773 | 195.5227 | 61.9773 | 61.9773 | 0 | 0 | 0 | 3/8/13:00
3 | 8 | 1900-01-13 | 0 | 258 | 480 | 32 | 1 | 0 | 32 | 0 | 0 | 258 | 0 | 0 | 39.791 | 67.5417 | -5.2425 | 86.148 | -75 | -11.3958 | 188.2991 | -391.5044 | -133.5044 | -42.3186 | -42.3186 | 0 | 0 | 0 | 3/8/14:00
3 | 8 | 1900-01-14 | 0.6 | 285 | 96 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 285 | 0 | 0 | 39.791 | 67.5833 | -5.2266 | 86.148 | -75 | -11.3854 | 203.3017 | -73.0633 | 211.9367 | 67.1802 | 67.1802 | 0 | 0 | 0 | 3/8/15:00
3 | 8 | 1900-01-15 | 1.7 | 203 | 282 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 203 | 0 | 0 | 39.791 | 67.625 | -5.2106 | 86.148 | -75 | -11.375 | 218.3043 | -185.7263 | 17.2737 | 5.4754 | 5.4754 | 0 | 0 | 0 | 3/8/16:00
3 | 8 | 1900-01-16 | 1.7 | 140 | 543 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 140 | 0 | 0 | 39.791 | 67.6667 | -5.1946 | 86.148 | -75 | -11.3646 | 233.3069 | -279.7481 | -139.7481 | -44.2977 | -44.2977 | 0 | 0 | 0 | 3/8/17:00
3 | 8 | 1900-01-17 | 1.7 | 79 | 2 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 79 | 0 | 0 | 39.791 | 67.7083 | -5.1786 | 86.148 | -75 | -11.3542 | 248.3095 | -0.68119 | 78.3188 | 24.8257 | 24.8257 | 0 | 0 | 0 | 3/8/18:00
3 | 8 | 1900-01-18 | 1.7 | 13 | 9 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 13 | 0 | 0 | 39.791 | 67.75 | -5.1626 | 86.148 | -75 | -11.3437 | 263.3121 | -1.3204 | 11.6796 | 3.7022 | 3.7022 | 0 | 0 | 0 | 3/8/19:00
3 | 8 | 1900-01-19 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.7917 | -5.1466 | 86.148 | -75 | -11.3333 | 278.3147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/20:00
3 | 8 | 1900-01-20 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.8333 | -5.1306 | 86.148 | -75 | -11.3228 | 293.3173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/21:00
3 | 8 | 1900-01-21 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.875 | -5.1146 | 86.148 | -75 | -11.3123 | 308.3199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/22:00
3 | 8 | 1900-01-22 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.9167 | -5.0986 | 86.148 | -75 | -11.3019 | 323.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/23:00
3 | 8 | 1900-01-23 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 67.9583 | -5.0826 | 86.148 | -75 | -11.2914 | 338.3252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/8/24:00
3 | 9 | 1899-12-31 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 68 | -5.0666 | 86.148 | -75 | -11.2808 | -6.6722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/9/1:00
3 | 9 | 1900-01-01 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 68.0417 | -5.0506 | 86.148 | -75 | -11.2703 | 8.3304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/9/2:00
3 | 9 | 1900-01-02 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 68.0833 | -5.0346 | 86.148 | -75 | -11.2598 | 23.3331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/9/3:00
3 | 9 | 1900-01-03 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 68.125 | -5.0185 | 86.148 | -75 | -11.2492 | 38.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/9/4:00
3 | 9 | 1900-01-04 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 68.1667 | -5.0025 | 86.148 | -75 | -11.2387 | 53.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/9/5:00
3 | 9 | 1900-01-05 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 68.2083 | -4.9865 | 86.148 | -75 | -11.2281 | 68.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/9/6:00
3 | 9 | 1900-01-06 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 68.25 | -4.9705 | 86.148 | -75 | -11.2175 | 83.3436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/9/7:00
3 | 9 | 1900-01-07 | 10 | 29 | 61 | 50 | 1 | 0 | 50 | 0 | 0 | 29 | 0 | 0 | 39.791 | 68.2917 | -4.9545 | 86.148 | -75 | -11.2069 | 98.3463 | -10.1498 | 18.8502 | 5.9752 | 5.9752 | 0 | 0 | 0 | 3/9/8:00
3 | 9 | 1900-01-08 | 13.3 | 96 | 317 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 96 | 0 | 0 | 39.791 | 68.3333 | -4.9384 | 86.148 | -75 | -11.1963 | 113.3489 | -113.6434 | -17.6434 | -5.5926 | 0 | -5.5926 | 55.94 | -5.5926 | 3/9/9:00
3 | 9 | 1900-01-09 | 14.4 | 146 | 473 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 146 | 0 | 0 | 39.791 | 68.375 | -4.9224 | 86.148 | -75 | -11.1857 | 128.3516 | -250.6559 | -104.6559 | -33.1741 | 0 | -33.1741 | 57.92 | -33.1741 | 3/9/10:00
3 | 9 | 1900-01-10 | 16.1 | 153 | 650 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 153 | 0 | 0 | 39.791 | 68.4167 | -4.9064 | 86.148 | -75 | -11.1751 | 143.3542 | -434.8396 | -281.8396 | -89.3382 | 0 | -89.3382 | 60.98 | -89.3382 | 3/9/11:00
3 | 9 | 1900-01-11 | 17.8 | 123 | 783 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 123 | 0 | 0 | 39.791 | 68.4583 | -4.8904 | 86.148 | -75 | -11.1644 | 158.3569 | -599.9119 | -476.9119 | -151.1727 | 0 | -151.1727 | 64.04 | -151.1727 | 3/9/12:00
3 | 9 | 1900-01-12 | 18.9 | 228 | 657 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 228 | 0 | 0 | 39.791 | 68.5 | -4.8743 | 86.148 | -75 | -11.1538 | 173.3596 | -535.3559 | -307.3559 | -97.4264 | 0 | -97.4264 | 66.02 | -97.4264 | 3/9/13:00
3 | 9 | 1900-01-13 | 20 | 231 | 641 | 68 | 0 | 1 | 0 | 68 | 0 | 231 | 0 | 0 | 39.791 | 68.5417 | -4.8583 | 86.148 | -75 | -11.1431 | 188.3622 | -520.2903 | -289.2903 | -91.7 | 0 | -91.7 | 68 | -91.7 | 3/9/14:00
3 | 9 | 1900-01-14 | 20.6 | 250 | 663 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 250 | 0 | 0 | 39.791 | 68.5833 | -4.8422 | 86.148 | -75 | -11.1324 | 203.3649 | -501.8117 | -251.8117 | -79.8199 | 0 | -79.8199 | 69.08 | -79.8199 | 3/9/15:00
3 | 9 | 1900-01-15 | 20.6 | 265 | 251 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 265 | 0 | 0 | 39.791 | 68.625 | -4.8262 | 86.148 | -75 | -11.1217 | 218.3676 | -164.1932 | 100.8068 | 31.954 | 0 | 31.954 | 69.08 | 31.954 | 3/9/16:00
3 | 9 | 1900-01-16 | 19.4 | 169 | 212 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 169 | 0 | 0 | 39.791 | 68.6667 | -4.8102 | 86.148 | -75 | -11.111 | 233.3702 | -108.2263 | 60.7737 | 19.2642 | 0 | 19.2642 | 66.92 | 19.2642 | 3/9/17:00
3 | 9 | 1900-01-17 | 19.4 | 88 | 354 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 88 | 0 | 0 | 39.791 | 68.7083 | -4.7941 | 86.148 | -75 | -11.1003 | 248.3729 | -118.8361 | -30.8361 | -9.7745 | 0 | -9.7745 | 66.92 | -9.7745 | 3/9/18:00
3 | 9 | 1900-01-18 | 17.8 | 27 | 40 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 27 | 0 | 0 | 39.791 | 68.75 | -4.7781 | 86.148 | -75 | -11.0896 | 263.3756 | -5.6657 | 21.3343 | 6.7626 | 0 | 6.7626 | 64.04 | 6.7626 | 3/9/19:00
3 | 9 | 1900-01-19 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 68.7917 | -4.762 | 86.148 | -75 | -11.0788 | 278.3783 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 3/9/20:00
3 | 9 | 1900-01-20 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 68.8333 | -4.746 | 86.148 | -75 | -11.0681 | 293.381 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 3/9/21:00
3 | 9 | 1900-01-21 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 68.875 | -4.7299 | 86.148 | -75 | -11.0573 | 308.3837 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 3/9/22:00
3 | 9 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 68.9167 | -4.7139 | 86.148 | -75 | -11.0465 | 323.3864 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 3/9/23:00
3 | 9 | 1900-01-23 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 68.9583 | -4.6978 | 86.148 | -75 | -11.0357 | 338.3891 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 3/9/24:00
3 | 10 | 1899-12-31 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 69 | -4.6818 | 86.148 | -75 | -11.0249 | -6.6082 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 3/10/1:00
3 | 10 | 1900-01-01 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 69.0417 | -4.6657 | 86.148 | -75 | -11.0141 | 8.3945 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 3/10/2:00
3 | 10 | 1900-01-02 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 69.0833 | -4.6496 | 86.148 | -75 | -11.0033 | 23.3972 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 3/10/3:00
3 | 10 | 1900-01-03 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 69.125 | -4.6336 | 86.148 | -75 | -10.9925 | 38.3999 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 3/10/4:00
3 | 10 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 69.1667 | -4.6175 | 86.148 | -75 | -10.9816 | 53.4026 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 3/10/5:00
3 | 10 | 1900-01-05 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 69.2083 | -4.6014 | 86.148 | -75 | -10.9708 | 68.4053 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 3/10/6:00
3 | 10 | 1900-01-06 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 69.25 | -4.5854 | 86.148 | -75 | -10.9599 | 83.408 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 3/10/7:00
3 | 10 | 1900-01-07 | 16.1 | 16 | 1 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 16 | 0 | 0 | 39.791 | 69.2917 | -4.5693 | 86.148 | -75 | -10.949 | 98.4107 | -0.16302 | 15.837 | 5.02 | 0 | 5.02 | 60.98 | 5.02 | 3/10/8:00
3 | 10 | 1900-01-08 | 17.2 | 83 | 1 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 83 | 0 | 0 | 39.791 | 69.3333 | -4.5532 | 86.148 | -75 | -10.9381 | 113.4135 | -0.35517 | 82.6448 | 26.197 | 0 | 26.197 | 62.96 | 26.197 | 3/10/9:00
3 | 10 | 1900-01-09 | 17.8 | 217 | 8 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 217 | 0 | 0 | 39.791 | 69.375 | -4.5371 | 86.148 | -75 | -10.9272 | 128.4162 | -4.2126 | 212.7874 | 67.4499 | 0 | 67.4499 | 64.04 | 67.4499 | 3/10/10:00
3 | 10 | 1900-01-10 | 16.1 | 141 | 10 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 141 | 0 | 0 | 39.791 | 69.4167 | -4.521 | 86.148 | -75 | -10.9163 | 143.4189 | -6.6555 | 134.3445 | 42.5849 | 0 | 42.5849 | 60.98 | 42.5849 | 3/10/11:00
3 | 10 | 1900-01-11 | 12.8 | 158 | 1 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 158 | 0 | 0 | 39.791 | 69.4583 | -4.505 | 86.148 | -75 | -10.9054 | 158.4217 | -0.76259 | 157.2374 | 49.8415 | 0 | 49.8415 | 55.04 | 49.8415 | 3/10/12:00
3 | 10 | 1900-01-12 | 15 | 350 | 259 | 59 | 0 | 1 | 0 | 59 | 0 | 350 | 0 | 0 | 39.791 | 69.5 | -4.4889 | 86.148 | -75 | -10.8944 | 173.4244 | -210.069 | 139.931 | 44.3557 | 0 | 44.3557 | 59 | 44.3557 | 3/10/13:00
3 | 10 | 1900-01-13 | 16.7 | 359 | 210 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 359 | 0 | 0 | 39.791 | 69.5417 | -4.4728 | 86.148 | -75 | -10.8835 | 188.4271 | -169.6134 | 189.3866 | 60.0322 | 0 | 60.0322 | 62.06 | 60.0322 | 3/10/14:00
3 | 10 | 1900-01-14 | 15 | 164 | 6 | 59 | 0 | 1 | 0 | 59 | 0 | 164 | 0 | 0 | 39.791 | 69.5833 | -4.4567 | 86.148 | -75 | -10.8725 | 203.4299 | -4.5158 | 159.4842 | 50.5537 | 0 | 50.5537 | 59 | 50.5537 | 3/10/15:00
3 | 10 | 1900-01-15 | 13.9 | 225 | 174 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 225 | 0 | 0 | 39.791 | 69.625 | -4.4406 | 86.148 | -75 | -10.8615 | 218.4326 | -113.0392 | 111.9608 | 35.4896 | 0 | 35.4896 | 57.02 | 35.4896 | 3/10/16:00
3 | 10 | 1900-01-16 | 14.4 | 117 | 518 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 117 | 0 | 0 | 39.791 | 69.6667 | -4.4245 | 86.148 | -75 | -10.8505 | 233.4354 | -261.9823 | -144.9823 | -45.9568 | 0 | -45.9568 | 57.92 | -45.9568 | 3/10/17:00
3 | 10 | 1900-01-17 | 14.4 | 93 | 60 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 93 | 0 | 0 | 39.791 | 69.7083 | -4.4084 | 86.148 | -75 | -10.8395 | 248.4381 | -19.8446 | 73.1554 | 23.189 | 0 | 23.189 | 57.92 | 23.189 | 3/10/18:00
3 | 10 | 1900-01-18 | 9.4 | 8 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 8 | 0 | 0 | 39.791 | 69.75 | -4.3923 | 86.148 | -75 | -10.8285 | 263.4409 | -0.13653 | 7.8635 | 2.4926 | 2.4926 | 0 | 0 | 0 | 3/10/19:00
3 | 10 | 1900-01-19 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 69.7917 | -4.3763 | 86.148 | -75 | -10.8175 | 278.4436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/10/20:00
3 | 10 | 1900-01-20 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 69.8333 | -4.3602 | 86.148 | -75 | -10.8065 | 293.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/10/21:00
3 | 10 | 1900-01-21 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 69.875 | -4.3441 | 86.148 | -75 | -10.7954 | 308.4491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/10/22:00
3 | 10 | 1900-01-22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 69.9167 | -4.3279 | 86.148 | -75 | -10.7844 | 323.4519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/10/23:00
3 | 10 | 1900-01-23 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 69.9583 | -4.3118 | 86.148 | -75 | -10.7733 | 338.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/10/24:00
3 | 11 | 1899-12-31 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70 | -4.2957 | 86.148 | -75 | -10.7622 | -6.5426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/1:00
3 | 11 | 1900-01-01 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.0417 | -4.2796 | 86.148 | -75 | -10.7512 | 8.4602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/2:00
3 | 11 | 1900-01-02 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.0833 | -4.2635 | 86.148 | -75 | -10.7401 | 23.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/3:00
3 | 11 | 1900-01-03 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.125 | -4.2474 | 86.148 | -75 | -10.729 | 38.4658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/4:00
3 | 11 | 1900-01-04 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.1667 | -4.2313 | 86.148 | -75 | -10.7178 | 53.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/5:00
3 | 11 | 1900-01-05 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.2083 | -4.2152 | 86.148 | -75 | -10.7067 | 68.4713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/6:00
3 | 11 | 1900-01-06 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.25 | -4.1991 | 86.148 | -75 | -10.6956 | 83.4741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/7:00
3 | 11 | 1900-01-07 | 1.7 | 33 | 8 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 33 | 0 | 0 | 39.791 | 70.2917 | -4.1829 | 86.148 | -75 | -10.6844 | 98.4769 | -1.2772 | 31.7228 | 10.0556 | 10.0556 | 0 | 0 | 0 | 3/11/8:00
3 | 11 | 1900-01-08 | 2.2 | 112 | 4 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 112 | 0 | 0 | 39.791 | 70.3333 | -4.1668 | 86.148 | -75 | -10.6732 | 113.4797 | -1.4073 | 110.5927 | 35.0559 | 35.0559 | 0 | 0 | 0 | 3/11/9:00
3 | 11 | 1900-01-09 | 2.8 | 175 | 6 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 175 | 0 | 0 | 39.791 | 70.375 | -4.1507 | 86.148 | -75 | -10.6621 | 128.4825 | -3.1393 | 171.8607 | 54.4768 | 54.4768 | 0 | 0 | 0 | 3/11/10:00
3 | 11 | 1900-01-10 | 2.8 | 247 | 10 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 247 | 0 | 0 | 39.791 | 70.4167 | -4.1346 | 86.148 | -75 | -10.6509 | 143.4853 | -6.6209 | 240.3791 | 76.196 | 76.196 | 0 | 0 | 0 | 3/11/11:00
3 | 11 | 1900-01-11 | 3.3 | 305 | 5 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 305 | 0 | 0 | 39.791 | 70.4583 | -4.1185 | 86.148 | -75 | -10.6397 | 158.4881 | -3.7949 | 301.2051 | 95.4768 | 95.4768 | 0 | 0 | 0 | 3/11/12:00
3 | 11 | 1900-01-12 | 5.6 | 282 | 119 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 282 | 0 | 0 | 39.791 | 70.5 | -4.1023 | 86.148 | -75 | -10.6285 | 173.4909 | -96.0637 | 185.9363 | 58.9385 | 58.9385 | 0 | 0 | 0 | 3/11/13:00
3 | 11 | 1900-01-13 | 6.7 | 201 | 675 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 201 | 0 | 0 | 39.791 | 70.5417 | -4.0862 | 86.148 | -75 | -10.6172 | 188.4937 | -542.4492 | -341.4492 | -108.2334 | -108.2334 | 0 | 0 | 0 | 3/11/14:00
3 | 11 | 1900-01-14 | 8.3 | 182 | 704 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 182 | 0 | 0 | 39.791 | 70.5833 | -4.0701 | 86.148 | -75 | -10.606 | 203.4965 | -526.8172 | -344.8172 | -109.301 | -109.301 | 0 | 0 | 0 | 3/11/15:00
3 | 11 | 1900-01-15 | 8.3 | 202 | 356 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 202 | 0 | 0 | 39.791 | 70.625 | -4.0539 | 86.148 | -75 | -10.5948 | 218.4993 | -229.6517 | -27.6517 | -8.7651 | -8.7651 | 0 | 0 | 0 | 3/11/16:00
3 | 11 | 1900-01-16 | 8.3 | 144 | 409 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 144 | 0 | 0 | 39.791 | 70.6667 | -4.0378 | 86.148 | -75 | -10.5835 | 233.5021 | -204.8925 | -60.8925 | -19.3018 | -19.3018 | 0 | 0 | 0 | 3/11/17:00
3 | 11 | 1900-01-17 | 7.8 | 59 | 507 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 59 | 0 | 0 | 39.791 | 70.7083 | -4.0217 | 86.148 | -75 | -10.5723 | 248.5049 | -165.152 | -106.152 | -33.6483 | -33.6483 | 0 | 0 | 0 | 3/11/18:00
3 | 11 | 1900-01-18 | 6.1 | 21 | 162 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 21 | 0 | 0 | 39.791 | 70.75 | -4.0055 | 86.148 | -75 | -10.561 | 263.5078 | -21.2824 | -0.2824 | -0.089516 | -0.089516 | 0 | 0 | 0 | 3/11/19:00
3 | 11 | 1900-01-19 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.7917 | -3.9894 | 86.148 | -75 | -10.5497 | 278.5106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/20:00
3 | 11 | 1900-01-20 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.8333 | -3.9732 | 86.148 | -75 | -10.5384 | 293.5134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/21:00
3 | 11 | 1900-01-21 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.875 | -3.9571 | 86.148 | -75 | -10.5271 | 308.5162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/22:00
3 | 11 | 1900-01-22 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.9167 | -3.9409 | 86.148 | -75 | -10.5158 | 323.5191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/23:00
3 | 11 | 1900-01-23 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 70.9583 | -3.9248 | 86.148 | -75 | -10.5045 | 338.5219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/11/24:00
3 | 12 | 1899-12-31 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71 | -3.9086 | 86.148 | -75 | -10.4931 | -6.4753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/1:00
3 | 12 | 1900-01-01 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.0417 | -3.8925 | 86.148 | -75 | -10.4818 | 8.5276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/2:00
3 | 12 | 1900-01-02 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.0833 | -3.8763 | 86.148 | -75 | -10.4704 | 23.5304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/3:00
3 | 12 | 1900-01-03 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.125 | -3.8602 | 86.148 | -75 | -10.459 | 38.5332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/4:00
3 | 12 | 1900-01-04 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.1667 | -3.844 | 86.148 | -75 | -10.4477 | 53.5361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/5:00
3 | 12 | 1900-01-05 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.2083 | -3.8279 | 86.148 | -75 | -10.4363 | 68.5389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/6:00
3 | 12 | 1900-01-06 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.25 | -3.8117 | 86.148 | -75 | -10.4249 | 83.5418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/7:00
3 | 12 | 1900-01-07 | 3.9 | 12 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 12 | 0 | 0 | 39.791 | 71.2917 | -3.7956 | 86.148 | -75 | -10.4135 | 98.5446 | 0 | 12 | 3.8038 | 3.8038 | 0 | 0 | 0 | 3/12/8:00
3 | 12 | 1900-01-08 | 4.4 | 63 | 6 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 63 | 0 | 0 | 39.791 | 71.3333 | -3.7794 | 86.148 | -75 | -10.402 | 113.5475 | -2.091 | 60.909 | 19.3071 | 19.3071 | 0 | 0 | 0 | 3/12/9:00
3 | 12 | 1900-01-09 | 4.4 | 212 | 6 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 212 | 0 | 0 | 39.791 | 71.375 | -3.7632 | 86.148 | -75 | -10.3906 | 128.5503 | -3.119 | 208.881 | 66.2116 | 66.2116 | 0 | 0 | 0 | 3/12/10:00
3 | 12 | 1900-01-10 | 4.4 | 145 | 7 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 145 | 0 | 0 | 39.791 | 71.4167 | -3.7471 | 86.148 | -75 | -10.3792 | 143.5532 | -4.6102 | 140.3898 | 44.5011 | 44.5011 | 0 | 0 | 0 | 3/12/11:00
3 | 12 | 1900-01-11 | 4.4 | 282 | 4 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 282 | 0 | 0 | 39.791 | 71.4583 | -3.7309 | 86.148 | -75 | -10.3677 | 158.5561 | -3.0213 | 278.9787 | 88.4314 | 88.4314 | 0 | 0 | 0 | 3/12/12:00
3 | 12 | 1900-01-12 | 5.6 | 357 | 2 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 357 | 0 | 0 | 39.791 | 71.5 | -3.7147 | 86.148 | -75 | -10.3563 | 173.5589 | -1.6068 | 355.3932 | 112.6534 | 112.6534 | 0 | 0 | 0 | 3/12/13:00
3 | 12 | 1900-01-13 | 6.7 | 393 | 1 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 393 | 0 | 0 | 39.791 | 71.5417 | -3.6986 | 86.148 | -75 | -10.3448 | 188.5618 | -0.79952 | 392.2005 | 124.3207 | 124.3207 | 0 | 0 | 0 | 3/12/14:00
3 | 12 | 1900-01-14 | 7.8 | 282 | 2 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 282 | 0 | 0 | 39.791 | 71.5833 | -3.6824 | 86.148 | -75 | -10.3333 | 203.5647 | -1.4879 | 280.5121 | 88.9174 | 88.9174 | 0 | 0 | 0 | 3/12/15:00
3 | 12 | 1900-01-15 | 8.3 | 247 | 1 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 247 | 0 | 0 | 39.791 | 71.625 | -3.6662 | 86.148 | -75 | -10.3218 | 218.5675 | -0.64047 | 246.3595 | 78.0917 | 78.0917 | 0 | 0 | 0 | 3/12/16:00
3 | 12 | 1900-01-16 | 8.9 | 198 | 1 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 198 | 0 | 0 | 39.791 | 71.6667 | -3.65 | 86.148 | -75 | -10.3103 | 233.5704 | -0.49611 | 197.5039 | 62.6053 | 62.6053 | 0 | 0 | 0 | 3/12/17:00
3 | 12 | 1900-01-17 | 8.3 | 62 | 1 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 62 | 0 | 0 | 39.791 | 71.7083 | -3.6339 | 86.148 | -75 | -10.2988 | 248.5733 | -0.3207 | 61.6793 | 19.5513 | 19.5513 | 0 | 0 | 0 | 3/12/18:00
3 | 12 | 1900-01-18 | 8.3 | 17 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 17 | 0 | 0 | 39.791 | 71.75 | -3.6177 | 86.148 | -75 | -10.2873 | 263.5762 | 0 | 17 | 5.3887 | 5.3887 | 0 | 0 | 0 | 3/12/19:00
3 | 12 | 1900-01-19 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.7917 | -3.6015 | 86.148 | -75 | -10.2757 | 278.5791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/20:00
3 | 12 | 1900-01-20 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.8333 | -3.5853 | 86.148 | -75 | -10.2642 | 293.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/21:00
3 | 12 | 1900-01-21 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.875 | -3.5691 | 86.148 | -75 | -10.2526 | 308.5848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/22:00
3 | 12 | 1900-01-22 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.9167 | -3.553 | 86.148 | -75 | -10.2411 | 323.5877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/23:00
3 | 12 | 1900-01-23 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 71.9583 | -3.5368 | 86.148 | -75 | -10.2295 | 338.5906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/12/24:00
3 | 13 | 1899-12-31 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72 | -3.5206 | 86.148 | -75 | -10.2179 | -6.4065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/1:00
3 | 13 | 1900-01-01 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72.0417 | -3.5044 | 86.148 | -75 | -10.2063 | 8.5964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/2:00
3 | 13 | 1900-01-02 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72.0833 | -3.4882 | 86.148 | -75 | -10.1947 | 23.5993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/3:00
3 | 13 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72.125 | -3.472 | 86.148 | -75 | -10.1831 | 38.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/4:00
3 | 13 | 1900-01-04 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72.1667 | -3.4558 | 86.148 | -75 | -10.1715 | 53.6051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/5:00
3 | 13 | 1900-01-05 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72.2083 | -3.4396 | 86.148 | -75 | -10.1599 | 68.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/6:00
3 | 13 | 1900-01-06 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72.25 | -3.4234 | 86.148 | -75 | -10.1482 | 83.6109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/7:00
3 | 13 | 1900-01-07 | 11.7 | 25 | 16 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 25 | 0 | 0 | 39.791 | 72.2917 | -3.4072 | 86.148 | -75 | -10.1366 | 98.6139 | -2.4467 | 22.5533 | 7.149 | 7.149 | 0 | 0 | 0 | 3/13/8:00
3 | 13 | 1900-01-08 | 12.2 | 88 | 6 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 88 | 0 | 0 | 39.791 | 72.3333 | -3.391 | 86.148 | -75 | -10.1249 | 113.6168 | -2.0709 | 85.9291 | 27.238 | 27.238 | 0 | 0 | 0 | 3/13/9:00
3 | 13 | 1900-01-09 | 13.3 | 152 | 12 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 152 | 0 | 0 | 39.791 | 72.375 | -3.3748 | 86.148 | -75 | -10.1132 | 128.6197 | -6.1971 | 145.8029 | 46.217 | 0 | 46.217 | 55.94 | 46.217 | 3/13/10:00
3 | 13 | 1900-01-10 | 13.9 | 237 | 7 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 237 | 0 | 0 | 39.791 | 72.4167 | -3.3586 | 86.148 | -75 | -10.1015 | 143.6226 | -4.5856 | 232.4144 | 73.6713 | 0 | 73.6713 | 57.02 | 73.6713 | 3/13/11:00
3 | 13 | 1900-01-11 | 14.4 | 286 | 1 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 286 | 0 | 0 | 39.791 | 72.4583 | -3.3424 | 86.148 | -75 | -10.0899 | 158.6255 | -0.75163 | 285.2484 | 90.4188 | 0 | 90.4188 | 57.92 | 90.4188 | 3/13/12:00
3 | 13 | 1900-01-12 | 14.4 | 315 | 2 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 315 | 0 | 0 | 39.791 | 72.5 | -3.3262 | 86.148 | -75 | -10.0782 | 173.6285 | -1.599 | 313.401 | 99.3427 | 0 | 99.3427 | 57.92 | 99.3427 | 3/13/13:00
3 | 13 | 1900-01-13 | 14.4 | 378 | 174 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 378 | 0 | 0 | 39.791 | 72.5417 | -3.31 | 86.148 | -75 | -10.0664 | 188.6314 | -138.3937 | 239.6063 | 75.951 | 0 | 75.951 | 57.92 | 75.951 | 3/13/14:00
3 | 13 | 1900-01-14 | 15 | 332 | 6 | 59 | 0 | 1 | 0 | 59 | 0 | 332 | 0 | 0 | 39.791 | 72.5833 | -3.2938 | 86.148 | -75 | -10.0547 | 203.6343 | -4.4373 | 327.5627 | 103.8317 | 0 | 103.8317 | 59 | 103.8317 | 3/13/15:00
3 | 13 | 1900-01-15 | 15.6 | 251 | 71 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 251 | 0 | 0 | 39.791 | 72.625 | -3.2776 | 86.148 | -75 | -10.043 | 218.6372 | -45.1421 | 205.8579 | 65.2533 | 0 | 65.2533 | 60.08 | 65.2533 | 3/13/16:00
3 | 13 | 1900-01-16 | 16.1 | 197 | 8 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 197 | 0 | 0 | 39.791 | 72.6667 | -3.2614 | 86.148 | -75 | -10.0313 | 233.6402 | -3.9297 | 193.0703 | 61.1999 | 0 | 61.1999 | 60.98 | 61.1999 | 3/13/17:00
3 | 13 | 1900-01-17 | 15.6 | 87 | 120 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 87 | 0 | 0 | 39.791 | 72.7083 | -3.2452 | 86.148 | -75 | -10.0195 | 248.6431 | -37.8728 | 49.1272 | 15.5725 | 0 | 15.5725 | 60.08 | 15.5725 | 3/13/18:00
3 | 13 | 1900-01-18 | 14.4 | 34 | 42 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 34 | 0 | 0 | 39.791 | 72.75 | -3.2289 | 86.148 | -75 | -10.0078 | 263.6461 | -5.0799 | 28.9201 | 9.1672 | 0 | 9.1672 | 57.92 | 9.1672 | 3/13/19:00
3 | 13 | 1900-01-19 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 72.7917 | -3.2127 | 86.148 | -75 | -9.996 | 278.649 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 3/13/20:00
3 | 13 | 1900-01-20 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 72.8333 | -3.1965 | 86.148 | -75 | -9.9842 | 293.6519 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 3/13/21:00
3 | 13 | 1900-01-21 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72.875 | -3.1803 | 86.148 | -75 | -9.9724 | 308.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/22:00
3 | 13 | 1900-01-22 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72.9167 | -3.1641 | 86.148 | -75 | -9.9606 | 323.6578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/23:00
3 | 13 | 1900-01-23 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 72.9583 | -3.1478 | 86.148 | -75 | -9.9488 | 338.6608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/13/24:00
3 | 14 | 1899-12-31 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73 | -3.1316 | 86.148 | -75 | -9.937 | -6.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/1:00
3 | 14 | 1900-01-01 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.0417 | -3.1154 | 86.148 | -75 | -9.9252 | 8.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/2:00
3 | 14 | 1900-01-02 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.0833 | -3.0992 | 86.148 | -75 | -9.9134 | 23.6697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/3:00
3 | 14 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.125 | -3.0829 | 86.148 | -75 | -9.9015 | 38.6726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/4:00
3 | 14 | 1900-01-04 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.1667 | -3.0667 | 86.148 | -75 | -9.8897 | 53.6756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/5:00
3 | 14 | 1900-01-05 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.2083 | -3.0505 | 86.148 | -75 | -9.8778 | 68.6785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/6:00
3 | 14 | 1900-01-06 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.25 | -3.0343 | 86.148 | -75 | -9.8659 | 83.6815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/7:00
3 | 14 | 1900-01-07 | 7.2 | 24 | 69 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 24 | 0 | 0 | 39.791 | 73.2917 | -3.018 | 86.148 | -75 | -9.8541 | 98.6845 | -10.3193 | 13.6807 | 4.3365 | 4.3365 | 0 | 0 | 0 | 3/14/8:00
3 | 14 | 1900-01-08 | 7.8 | 81 | 3 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 81 | 0 | 0 | 39.791 | 73.3333 | -3.0018 | 86.148 | -75 | -9.8422 | 113.6875 | -1.0254 | 79.9746 | 25.3506 | 25.3506 | 0 | 0 | 0 | 3/14/9:00
3 | 14 | 1900-01-09 | 8.9 | 175 | 11 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 175 | 0 | 0 | 39.791 | 73.375 | -2.9856 | 86.148 | -75 | -9.8303 | 128.6904 | -5.6431 | 169.3569 | 53.6832 | 53.6832 | 0 | 0 | 0 | 3/14/10:00
3 | 14 | 1900-01-10 | 10 | 226 | 50 | 50 | 1 | 0 | 50 | 0 | 0 | 226 | 0 | 0 | 39.791 | 73.4167 | -2.9693 | 86.148 | -75 | -9.8184 | 143.6934 | -32.5765 | 193.4235 | 61.3119 | 61.3119 | 0 | 0 | 0 | 3/14/11:00
3 | 14 | 1900-01-11 | 10.6 | 338 | 279 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 338 | 0 | 0 | 39.791 | 73.4583 | -2.9531 | 86.148 | -75 | -9.8065 | 158.6964 | -208.664 | 129.336 | 40.9973 | 40.9973 | 0 | 0 | 0 | 3/14/12:00
3 | 14 | 1900-01-12 | 12.2 | 241 | 611 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 241 | 0 | 0 | 39.791 | 73.5 | -2.9368 | 86.148 | -75 | -9.7945 | 173.6994 | -486.0686 | -245.0686 | -77.6825 | -77.6825 | 0 | 0 | 0 | 3/14/13:00
3 | 14 | 1900-01-13 | 13.3 | 162 | 786 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 162 | 0 | 0 | 39.791 | 73.5417 | -2.9206 | 86.148 | -75 | -9.7826 | 188.7023 | -621.8521 | -459.8521 | -145.7651 | 0 | -145.7651 | 55.94 | -145.7651 | 3/14/14:00
3 | 14 | 1900-01-14 | 13.9 | 155 | 822 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 155 | 0 | 0 | 39.791 | 73.5833 | -2.9044 | 86.148 | -75 | -9.7707 | 203.7053 | -604.2322 | -449.2322 | -142.3988 | 0 | -142.3988 | 57.02 | -142.3988 | 3/14/15:00
3 | 14 | 1900-01-15 | 13.9 | 89 | 781 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 89 | 0 | 0 | 39.791 | 73.625 | -2.8881 | 86.148 | -75 | -9.7587 | 218.7083 | -492.8776 | -403.8776 | -128.0222 | 0 | -128.0222 | 57.02 | -128.0222 | 3/14/16:00
3 | 14 | 1900-01-16 | 13.9 | 79 | 674 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 79 | 0 | 0 | 39.791 | 73.6667 | -2.8719 | 86.148 | -75 | -9.7468 | 233.7113 | -327.7428 | -248.7428 | -78.8471 | 0 | -78.8471 | 57.02 | -78.8471 | 3/14/17:00
3 | 14 | 1900-01-17 | 11.7 | 81 | 258 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 81 | 0 | 0 | 39.791 | 73.7083 | -2.8556 | 86.148 | -75 | -9.7348 | 248.7143 | -80.1026 | 0.89736 | 0.28445 | 0.28445 | 0 | 0 | 0 | 3/14/18:00
3 | 14 | 1900-01-18 | 10 | 32 | 22 | 50 | 1 | 0 | 50 | 0 | 0 | 32 | 0 | 0 | 39.791 | 73.75 | -2.8394 | 86.148 | -75 | -9.7228 | 263.7173 | -2.5451 | 29.4549 | 9.3367 | 9.3367 | 0 | 0 | 0 | 3/14/19:00
3 | 14 | 1900-01-19 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.7917 | -2.8231 | 86.148 | -75 | -9.7108 | 278.7203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/20:00
3 | 14 | 1900-01-20 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.8333 | -2.8069 | 86.148 | -75 | -9.6988 | 293.7233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/21:00
3 | 14 | 1900-01-21 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.875 | -2.7906 | 86.148 | -75 | -9.6868 | 308.7263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/22:00
3 | 14 | 1900-01-22 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.9167 | -2.7744 | 86.148 | -75 | -9.6748 | 323.7293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/23:00
3 | 14 | 1900-01-23 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 73.9583 | -2.7581 | 86.148 | -75 | -9.6628 | 338.7323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/14/24:00
3 | 15 | 1899-12-31 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74 | -2.7419 | 86.148 | -75 | -9.6508 | -6.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/1:00
3 | 15 | 1900-01-01 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.0417 | -2.7256 | 86.148 | -75 | -9.6387 | 8.7383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/2:00
3 | 15 | 1900-01-02 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.0833 | -2.7094 | 86.148 | -75 | -9.6267 | 23.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/3:00
3 | 15 | 1900-01-03 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.125 | -2.6931 | 86.148 | -75 | -9.6147 | 38.7443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/4:00
3 | 15 | 1900-01-04 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.1667 | -2.6769 | 86.148 | -75 | -9.6026 | 53.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/5:00
3 | 15 | 1900-01-05 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.2083 | -2.6606 | 86.148 | -75 | -9.5905 | 68.7504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/6:00
3 | 15 | 1900-01-06 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.25 | -2.6443 | 86.148 | -75 | -9.5784 | 83.7534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/7:00
3 | 15 | 1900-01-07 | 3.9 | 37 | 19 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 37 | 0 | 0 | 39.791 | 74.2917 | -2.6281 | 86.148 | -75 | -9.5664 | 98.7564 | -2.7777 | 34.2223 | 10.8479 | 10.8479 | 0 | 0 | 0 | 3/15/8:00
3 | 15 | 1900-01-08 | 4.4 | 101 | 63 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 101 | 0 | 0 | 39.791 | 74.3333 | -2.6118 | 86.148 | -75 | -9.5543 | 113.7594 | -21.3206 | 79.6794 | 25.257 | 25.257 | 0 | 0 | 0 | 3/15/9:00
3 | 15 | 1900-01-09 | 5 | 157 | 19 | 41 | 1 | 0 | 41 | 0 | 0 | 157 | 0 | 0 | 39.791 | 74.375 | -2.5955 | 86.148 | -75 | -9.5422 | 128.7625 | -9.6818 | 147.3182 | 46.6973 | 46.6973 | 0 | 0 | 0 | 3/15/10:00
3 | 15 | 1900-01-10 | 5 | 262 | 2 | 41 | 1 | 0 | 41 | 0 | 0 | 262 | 0 | 0 | 39.791 | 74.4167 | -2.5793 | 86.148 | -75 | -9.53 | 143.7655 | -1.2959 | 260.7041 | 82.6386 | 82.6386 | 0 | 0 | 0 | 3/15/11:00
3 | 15 | 1900-01-11 | 5 | 264 | 12 | 41 | 1 | 0 | 41 | 0 | 0 | 264 | 0 | 0 | 39.791 | 74.4583 | -2.563 | 86.148 | -75 | -9.5179 | 158.7685 | -8.9296 | 255.0704 | 80.8529 | 80.8529 | 0 | 0 | 0 | 3/15/12:00
3 | 15 | 1900-01-12 | 5.6 | 317 | 4 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 317 | 0 | 0 | 39.791 | 74.5 | -2.5468 | 86.148 | -75 | -9.5058 | 173.7716 | -3.1661 | 313.8339 | 99.4799 | 99.4799 | 0 | 0 | 0 | 3/15/13:00
3 | 15 | 1900-01-13 | 5.6 | 315 | 1 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 315 | 0 | 0 | 39.791 | 74.5417 | -2.5305 | 86.148 | -75 | -9.4937 | 188.7746 | -0.78691 | 314.2131 | 99.6001 | 99.6001 | 0 | 0 | 0 | 3/15/14:00
3 | 15 | 1900-01-14 | 5.6 | 275 | 4 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 275 | 0 | 0 | 39.791 | 74.5833 | -2.5142 | 86.148 | -75 | -9.4815 | 203.7776 | -2.9222 | 272.0778 | 86.2439 | 86.2439 | 0 | 0 | 0 | 3/15/15:00
3 | 15 | 1900-01-15 | 5 | 263 | 3 | 41 | 1 | 0 | 41 | 0 | 0 | 263 | 0 | 0 | 39.791 | 74.625 | -2.4979 | 86.148 | -75 | -9.4694 | 218.7807 | -1.879 | 261.121 | 82.7708 | 82.7708 | 0 | 0 | 0 | 3/15/16:00
3 | 15 | 1900-01-16 | 5 | 178 | 4 | 41 | 1 | 0 | 41 | 0 | 0 | 178 | 0 | 0 | 39.791 | 74.6667 | -2.4817 | 86.148 | -75 | -9.4572 | 233.7837 | -1.9251 | 176.0749 | 55.8127 | 55.8127 | 0 | 0 | 0 | 3/15/17:00
3 | 15 | 1900-01-17 | 4.4 | 97 | 2 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 97 | 0 | 0 | 39.791 | 74.7083 | -2.4654 | 86.148 | -75 | -9.445 | 248.7867 | -0.61061 | 96.3894 | 30.5538 | 30.5538 | 0 | 0 | 0 | 3/15/18:00
3 | 15 | 1900-01-18 | 4.4 | 26 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 26 | 0 | 0 | 39.791 | 74.75 | -2.4491 | 86.148 | -75 | -9.4328 | 263.7898 | 0 | 26 | 8.2415 | 8.2415 | 0 | 0 | 0 | 3/15/19:00
3 | 15 | 1900-01-19 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.7917 | -2.4328 | 86.148 | -75 | -9.4207 | 278.7928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/20:00
3 | 15 | 1900-01-20 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.8333 | -2.4166 | 86.148 | -75 | -9.4085 | 293.7959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/21:00
3 | 15 | 1900-01-21 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.875 | -2.4003 | 86.148 | -75 | -9.3963 | 308.7989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/22:00
3 | 15 | 1900-01-22 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.9167 | -2.384 | 86.148 | -75 | -9.384 | 323.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/23:00
3 | 15 | 1900-01-23 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 74.9583 | -2.3677 | 86.148 | -75 | -9.3718 | 338.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/15/24:00
3 | 16 | 1899-12-31 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75 | -2.3515 | 86.148 | -75 | -9.3596 | -6.1919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/1:00
3 | 16 | 1900-01-01 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.0417 | -2.3352 | 86.148 | -75 | -9.3474 | 8.8112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/2:00
3 | 16 | 1900-01-02 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.0833 | -2.3189 | 86.148 | -75 | -9.3351 | 23.8142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/3:00
3 | 16 | 1900-01-03 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.125 | -2.3026 | 86.148 | -75 | -9.3229 | 38.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/4:00
3 | 16 | 1900-01-04 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.1667 | -2.2863 | 86.148 | -75 | -9.3106 | 53.8203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/5:00
3 | 16 | 1900-01-05 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.2083 | -2.27 | 86.148 | -75 | -9.2983 | 68.8234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/6:00
3 | 16 | 1900-01-06 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.25 | -2.2538 | 86.148 | -75 | -9.2861 | 83.8265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/7:00
3 | 16 | 1900-01-07 | 3.3 | 40 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 40 | 0 | 0 | 39.791 | 75.2917 | -2.2375 | 86.148 | -75 | -9.2738 | 98.8296 | 0 | 40 | 12.6793 | 12.6793 | 0 | 0 | 0 | 3/16/8:00
3 | 16 | 1900-01-08 | 3.3 | 126 | 1 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 126 | 0 | 0 | 39.791 | 75.3333 | -2.2212 | 86.148 | -75 | -9.2615 | 113.8326 | -0.33505 | 125.665 | 39.8336 | 39.8336 | 0 | 0 | 0 | 3/16/9:00
3 | 16 | 1900-01-09 | 3.9 | 230 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 230 | 0 | 0 | 39.791 | 75.375 | -2.2049 | 86.148 | -75 | -9.2492 | 128.8357 | 0 | 230 | 72.906 | 72.906 | 0 | 0 | 0 | 3/16/10:00
3 | 16 | 1900-01-10 | 4.4 | 280 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 280 | 0 | 0 | 39.791 | 75.4167 | -2.1886 | 86.148 | -75 | -9.2369 | 143.8388 | -0.64435 | 279.3556 | 88.5509 | 88.5509 | 0 | 0 | 0 | 3/16/11:00
3 | 16 | 1900-01-11 | 4.4 | 335 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 335 | 0 | 0 | 39.791 | 75.4583 | -2.1723 | 86.148 | -75 | -9.2246 | 158.8419 | -0.74033 | 334.2597 | 105.9545 | 105.9545 | 0 | 0 | 0 | 3/16/12:00
3 | 16 | 1900-01-12 | 4.4 | 404 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 404 | 0 | 0 | 39.791 | 75.5 | -2.156 | 86.148 | -75 | -9.2123 | 173.8449 | 0 | 404 | 128.0609 | 128.0609 | 0 | 0 | 0 | 3/16/13:00
3 | 16 | 1900-01-13 | 4.4 | 364 | 2 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 364 | 0 | 0 | 39.791 | 75.5417 | -2.1397 | 86.148 | -75 | -9.1999 | 188.848 | -1.5652 | 362.4348 | 114.8855 | 114.8855 | 0 | 0 | 0 | 3/16/14:00
3 | 16 | 1900-01-14 | 5 | 358 | 2 | 41 | 1 | 0 | 41 | 0 | 0 | 358 | 0 | 0 | 39.791 | 75.5833 | -2.1234 | 86.148 | -75 | -9.1876 | 203.8511 | -1.452 | 356.548 | 113.0195 | 113.0195 | 0 | 0 | 0 | 3/16/15:00
3 | 16 | 1900-01-15 | 5 | 296 | 2 | 41 | 1 | 0 | 41 | 0 | 0 | 296 | 0 | 0 | 39.791 | 75.625 | -2.1071 | 86.148 | -75 | -9.1753 | 218.8542 | -1.243 | 294.757 | 93.4328 | 93.4328 | 0 | 0 | 0 | 3/16/16:00
3 | 16 | 1900-01-16 | 5 | 203 | 1 | 41 | 1 | 0 | 41 | 0 | 0 | 203 | 0 | 0 | 39.791 | 75.6667 | -2.0908 | 86.148 | -75 | -9.1629 | 233.8573 | -0.47624 | 202.5238 | 64.1965 | 64.1965 | 0 | 0 | 0 | 3/16/17:00
3 | 16 | 1900-01-17 | 4.4 | 118 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 118 | 0 | 0 | 39.791 | 75.7083 | -2.0745 | 86.148 | -75 | -9.1506 | 248.8604 | -0.3001 | 117.6999 | 37.3088 | 37.3088 | 0 | 0 | 0 | 3/16/18:00
3 | 16 | 1900-01-18 | 3.9 | 29 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 29 | 0 | 0 | 39.791 | 75.75 | -2.0582 | 86.148 | -75 | -9.1382 | 263.8635 | 0 | 29 | 9.1925 | 9.1925 | 0 | 0 | 0 | 3/16/19:00
3 | 16 | 1900-01-19 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.7917 | -2.042 | 86.148 | -75 | -9.1258 | 278.8665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/20:00
3 | 16 | 1900-01-20 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.8333 | -2.0257 | 86.148 | -75 | -9.1134 | 293.8696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/21:00
3 | 16 | 1900-01-21 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.875 | -2.0094 | 86.148 | -75 | -9.101 | 308.8727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/22:00
3 | 16 | 1900-01-22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.9167 | -1.9931 | 86.148 | -75 | -9.0887 | 323.8758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/23:00
3 | 16 | 1900-01-23 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 75.9583 | -1.9767 | 86.148 | -75 | -9.0763 | 338.8789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/16/24:00
3 | 17 | 1899-12-31 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76 | -1.9604 | 86.148 | -75 | -9.0638 | -6.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/1:00
3 | 17 | 1900-01-01 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.0417 | -1.9441 | 86.148 | -75 | -9.0514 | 8.8851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/2:00
3 | 17 | 1900-01-02 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.0833 | -1.9278 | 86.148 | -75 | -9.039 | 23.8882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/3:00
3 | 17 | 1900-01-03 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.125 | -1.9115 | 86.148 | -75 | -9.0266 | 38.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/4:00
3 | 17 | 1900-01-04 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.1667 | -1.8952 | 86.148 | -75 | -9.0141 | 53.8945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/5:00
3 | 17 | 1900-01-05 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.2083 | -1.8789 | 86.148 | -75 | -9.0017 | 68.8976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/6:00
3 | 17 | 1900-01-06 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.25 | -1.8626 | 86.148 | -75 | -8.9892 | 83.9007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/7:00
3 | 17 | 1900-01-07 | 1.1 | 36 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 36 | 0 | 0 | 39.791 | 76.2917 | -1.8463 | 86.148 | -75 | -8.9768 | 98.9038 | 0 | 36 | 11.4114 | 11.4114 | 0 | 0 | 0 | 3/17/8:00
3 | 17 | 1900-01-08 | 3.9 | 97 | 102 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 97 | 0 | 0 | 39.791 | 76.3333 | -1.83 | 86.148 | -75 | -8.9643 | 113.9069 | -33.8301 | 63.1699 | 20.0237 | 20.0237 | 0 | 0 | 0 | 3/17/9:00
3 | 17 | 1900-01-09 | 4.4 | 212 | 203 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 212 | 0 | 0 | 39.791 | 76.375 | -1.8137 | 86.148 | -75 | -8.9518 | 128.91 | -102.0349 | 109.9651 | 34.857 | 34.857 | 0 | 0 | 0 | 3/17/10:00
3 | 17 | 1900-01-10 | 7.2 | 239 | 407 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 239 | 0 | 0 | 39.791 | 76.4167 | -1.7974 | 86.148 | -75 | -8.9394 | 143.9132 | -260.7723 | -21.7723 | -6.9014 | -6.9014 | 0 | 0 | 0 | 3/17/11:00
3 | 17 | 1900-01-11 | 8.3 | 261 | 586 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 261 | 0 | 0 | 39.791 | 76.4583 | -1.7811 | 86.148 | -75 | -8.9269 | 158.9163 | -431.5831 | -170.5831 | -54.0719 | -54.0719 | 0 | 0 | 0 | 3/17/12:00
3 | 17 | 1900-01-12 | 9.4 | 265 | 600 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 265 | 0 | 0 | 39.791 | 76.5 | -1.7648 | 86.148 | -75 | -8.9144 | 173.9194 | -470.0446 | -205.0446 | -64.9956 | -64.9956 | 0 | 0 | 0 | 3/17/13:00
3 | 17 | 1900-01-13 | 10.6 | 220 | 675 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 220 | 0 | 0 | 39.791 | 76.5417 | -1.7484 | 86.148 | -75 | -8.9019 | 188.9225 | -525.325 | -305.325 | -96.7827 | -96.7827 | 0 | 0 | 0 | 3/17/14:00
3 | 17 | 1900-01-14 | 11.7 | 210 | 622 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 210 | 0 | 0 | 39.791 | 76.5833 | -1.7321 | 86.148 | -75 | -8.8894 | 203.9257 | -448.6999 | -238.6999 | -75.6637 | -75.6637 | 0 | 0 | 0 | 3/17/15:00
3 | 17 | 1900-01-15 | 12.2 | 261 | 410 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 261 | 0 | 0 | 39.791 | 76.625 | -1.7158 | 86.148 | -75 | -8.8768 | 218.9288 | -252.8231 | 8.1769 | 2.5919 | 2.5919 | 0 | 0 | 0 | 3/17/16:00
3 | 17 | 1900-01-16 | 12.8 | 181 | 389 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 181 | 0 | 0 | 39.791 | 76.6667 | -1.6995 | 86.148 | -75 | -8.8643 | 233.9319 | -183.283 | -2.283 | -0.72368 | 0 | -0.72368 | 55.04 | -0.72368 | 3/17/17:00
3 | 17 | 1900-01-17 | 11.7 | 110 | 72 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 110 | 0 | 0 | 39.791 | 76.7083 | -1.6832 | 86.148 | -75 | -8.8518 | 248.9351 | -21.2297 | 88.7703 | 28.1386 | 28.1386 | 0 | 0 | 0 | 3/17/18:00
3 | 17 | 1900-01-18 | 10.6 | 33 | 4 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 33 | 0 | 0 | 39.791 | 76.75 | -1.6669 | 86.148 | -75 | -8.8393 | 263.9382 | -0.3989 | 32.6011 | 10.334 | 10.334 | 0 | 0 | 0 | 3/17/19:00
3 | 17 | 1900-01-19 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.7917 | -1.6505 | 86.148 | -75 | -8.8267 | 278.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/20:00
3 | 17 | 1900-01-20 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.8333 | -1.6342 | 86.148 | -75 | -8.8142 | 293.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/21:00
3 | 17 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.875 | -1.6179 | 86.148 | -75 | -8.8016 | 308.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/22:00
3 | 17 | 1900-01-22 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.9167 | -1.6016 | 86.148 | -75 | -8.789 | 323.9507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/23:00
3 | 17 | 1900-01-23 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 76.9583 | -1.5853 | 86.148 | -75 | -8.7765 | 338.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/17/24:00
3 | 18 | 1899-12-31 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 77 | -1.5689 | 86.148 | -75 | -8.7639 | -6.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/18/1:00
3 | 18 | 1900-01-01 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 77.0417 | -1.5526 | 86.148 | -75 | -8.7513 | 8.9602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/18/2:00
3 | 18 | 1900-01-02 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 77.0833 | -1.5363 | 86.148 | -75 | -8.7387 | 23.9633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/18/3:00
3 | 18 | 1900-01-03 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 77.125 | -1.52 | 86.148 | -75 | -8.7261 | 38.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/18/4:00
3 | 18 | 1900-01-04 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 77.1667 | -1.5037 | 86.148 | -75 | -8.7135 | 53.9696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/18/5:00
3 | 18 | 1900-01-05 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 77.2083 | -1.4873 | 86.148 | -75 | -8.7009 | 68.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/18/6:00
3 | 18 | 1900-01-06 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 77.25 | -1.471 | 86.148 | -75 | -8.6883 | 83.9759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/18/7:00
3 | 18 | 1900-01-07 | 6.7 | 22 | 12 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 22 | 0 | 0 | 39.791 | 77.2917 | -1.4547 | 86.148 | -75 | -8.6757 | 98.9791 | -1.6336 | 20.3664 | 6.4558 | 6.4558 | 0 | 0 | 0 | 3/18/8:00
3 | 18 | 1900-01-08 | 8.3 | 95 | 4 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 95 | 0 | 0 | 39.791 | 77.3333 | -1.4384 | 86.148 | -75 | -8.663 | 113.9822 | -1.3131 | 93.6869 | 29.6971 | 29.6971 | 0 | 0 | 0 | 3/18/9:00
3 | 18 | 1900-01-09 | 8.9 | 177 | 4 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 177 | 0 | 0 | 39.791 | 77.375 | -1.422 | 86.148 | -75 | -8.6504 | 128.9854 | -1.9966 | 175.0034 | 55.473 | 55.473 | 0 | 0 | 0 | 3/18/10:00
3 | 18 | 1900-01-10 | 10.6 | 299 | 8 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 299 | 0 | 0 | 39.791 | 77.4167 | -1.4057 | 86.148 | -75 | -8.6378 | 143.9886 | -5.0965 | 293.9035 | 93.1623 | 93.1623 | 0 | 0 | 0 | 3/18/11:00
3 | 18 | 1900-01-11 | 13.9 | 263 | 341 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 263 | 0 | 0 | 39.791 | 77.4583 | -1.3894 | 86.148 | -75 | -8.6251 | 158.9917 | -249.8218 | 13.1782 | 4.1773 | 0 | 4.1773 | 57.02 | 4.1773 | 3/18/12:00
3 | 18 | 1900-01-12 | 16.7 | 278 | 5 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 278 | 0 | 0 | 39.791 | 77.5 | -1.373 | 86.148 | -75 | -8.6125 | 173.9949 | -3.8964 | 274.1036 | 86.886 | 0 | 86.886 | 62.06 | 86.886 | 3/18/13:00
3 | 18 | 1900-01-13 | 17.2 | 265 | 14 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 265 | 0 | 0 | 39.791 | 77.5417 | -1.3567 | 86.148 | -75 | -8.5998 | 188.998 | -10.8342 | 254.1658 | 80.5661 | 0 | 80.5661 | 62.96 | 80.5661 | 3/18/14:00
3 | 18 | 1900-01-14 | 18.3 | 171 | 20 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 171 | 0 | 0 | 39.791 | 77.5833 | -1.3404 | 86.148 | -75 | -8.5871 | 204.0012 | -14.3345 | 156.6655 | 49.6602 | 0 | 49.6602 | 64.94 | 49.6602 | 3/18/15:00
3 | 18 | 1900-01-15 | 15 | 136 | 6 | 59 | 0 | 1 | 0 | 59 | 0 | 136 | 0 | 0 | 39.791 | 77.625 | -1.3241 | 86.148 | -75 | -8.5745 | 219.0044 | -3.6704 | 132.3296 | 41.9462 | 0 | 41.9462 | 59 | 41.9462 | 3/18/16:00
3 | 18 | 1900-01-16 | 11.7 | 108 | 7 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 108 | 0 | 0 | 39.791 | 77.6667 | -1.3077 | 86.148 | -75 | -8.5618 | 234.0076 | -3.2624 | 104.7376 | 33.2 | 33.2 | 0 | 0 | 0 | 3/18/17:00
3 | 18 | 1900-01-17 | 11.1 | 63 | 4 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 63 | 0 | 0 | 39.791 | 77.7083 | -1.2914 | 86.148 | -75 | -8.5491 | 249.0107 | -1.1583 | 61.8417 | 19.6027 | 19.6027 | 0 | 0 | 0 | 3/18/18:00
3 | 18 | 1900-01-18 | 11.7 | 14 | 1 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 14 | 0 | 0 | 39.791 | 77.75 | -1.2751 | 86.148 | -75 | -8.5364 | 264.0139 | -0.094354 | 13.9056 | 4.4078 | 4.4078 | 0 | 0 | 0 | 3/18/19:00
3 | 18 | 1900-01-19 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 77.7917 | -1.2587 | 86.148 | -75 | -8.5237 | 279.0171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/18/20:00
3 | 18 | 1900-01-20 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 77.8333 | -1.2424 | 86.148 | -75 | -8.511 | 294.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/18/21:00
3 | 18 | 1900-01-21 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 77.875 | -1.2261 | 86.148 | -75 | -8.4983 | 309.0234 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 3/18/22:00
3 | 18 | 1900-01-22 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 77.9167 | -1.2097 | 86.148 | -75 | -8.4856 | 324.0266 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 3/18/23:00
3 | 18 | 1900-01-23 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 77.9583 | -1.1934 | 86.148 | -75 | -8.4729 | 339.0298 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 3/18/24:00
3 | 19 | 1899-12-31 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 78 | -1.1771 | 86.148 | -75 | -8.4601 | -5.967 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 3/19/1:00
3 | 19 | 1900-01-01 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 78.0417 | -1.1607 | 86.148 | -75 | -8.4474 | 9.0361 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 3/19/2:00
3 | 19 | 1900-01-02 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 78.0833 | -1.1444 | 86.148 | -75 | -8.4347 | 24.0393 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 3/19/3:00
3 | 19 | 1900-01-03 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 78.125 | -1.128 | 86.148 | -75 | -8.4219 | 39.0425 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 3/19/4:00
3 | 19 | 1900-01-04 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 78.1667 | -1.1117 | 86.148 | -75 | -8.4092 | 54.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/19/5:00
3 | 19 | 1900-01-05 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 78.2083 | -1.0954 | 86.148 | -75 | -8.3964 | 69.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/19/6:00
3 | 19 | 1900-01-06 | 10 | 1 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 1 | 0 | 0 | 39.791 | 78.25 | -1.079 | 86.148 | -75 | -8.3837 | 84.0521 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 3/19/7:00
3 | 19 | 1900-01-07 | 10 | 34 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 34 | 0 | 0 | 39.791 | 78.2917 | -1.0627 | 86.148 | -75 | -8.3709 | 99.0553 | 0 | 34 | 10.7774 | 10.7774 | 0 | 0 | 0 | 3/19/8:00
3 | 19 | 1900-01-08 | 7.8 | 114 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 114 | 0 | 0 | 39.791 | 78.3333 | -1.0464 | 86.148 | -75 | -8.3581 | 114.0585 | 0 | 114 | 36.136 | 36.136 | 0 | 0 | 0 | 3/19/9:00
3 | 19 | 1900-01-09 | 6.7 | 121 | 1 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 121 | 0 | 0 | 39.791 | 78.375 | -1.03 | 86.148 | -75 | -8.3453 | 129.0617 | -0.49563 | 120.5044 | 38.1978 | 38.1978 | 0 | 0 | 0 | 3/19/10:00
3 | 19 | 1900-01-10 | 5.6 | 313 | 1 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 313 | 0 | 0 | 39.791 | 78.4167 | -1.0137 | 86.148 | -75 | -8.3326 | 144.0649 | -0.63337 | 312.3666 | 99.0148 | 99.0148 | 0 | 0 | 0 | 3/19/11:00
3 | 19 | 1900-01-11 | 5 | 203 | 1 | 41 | 1 | 0 | 41 | 0 | 0 | 203 | 0 | 0 | 39.791 | 78.4583 | -0.99733 | 86.148 | -75 | -8.3198 | 159.0681 | -0.72871 | 202.2713 | 64.1165 | 64.1165 | 0 | 0 | 0 | 3/19/12:00
3 | 19 | 1900-01-12 | 4.4 | 359 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 359 | 0 | 0 | 39.791 | 78.5 | -0.98099 | 86.148 | -75 | -8.307 | 174.0713 | -0.77512 | 358.2249 | 113.551 | 113.551 | 0 | 0 | 0 | 3/19/13:00
3 | 19 | 1900-01-13 | 4.4 | 203 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 203 | 0 | 0 | 39.791 | 78.5417 | -0.96465 | 86.148 | -75 | -8.2942 | 189.0745 | -0.76943 | 202.2306 | 64.1036 | 64.1036 | 0 | 0 | 0 | 3/19/14:00
3 | 19 | 1900-01-14 | 4.4 | 331 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 331 | 0 | 0 | 39.791 | 78.5833 | -0.9483 | 86.148 | -75 | -8.2814 | 204.0777 | -0.71203 | 330.288 | 104.6955 | 104.6955 | 0 | 0 | 0 | 3/19/15:00
3 | 19 | 1900-01-15 | 4.4 | 258 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 258 | 0 | 0 | 39.791 | 78.625 | -0.93196 | 86.148 | -75 | -8.2685 | 219.0809 | -0.60679 | 257.3932 | 81.5892 | 81.5892 | 0 | 0 | 0 | 3/19/16:00
3 | 19 | 1900-01-16 | 5 | 196 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 196 | 0 | 0 | 39.791 | 78.6667 | -0.91562 | 86.148 | -75 | -8.2557 | 234.0841 | 0 | 196 | 62.1286 | 62.1286 | 0 | 0 | 0 | 3/19/17:00
3 | 19 | 1900-01-17 | 5 | 94 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 94 | 0 | 0 | 39.791 | 78.7083 | -0.89928 | 86.148 | -75 | -8.2429 | 249.0873 | 0 | 94 | 29.7964 | 29.7964 | 0 | 0 | 0 | 3/19/18:00
3 | 19 | 1900-01-18 | 3.9 | 17 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 17 | 0 | 0 | 39.791 | 78.75 | -0.88293 | 86.148 | -75 | -8.2301 | 264.0905 | 0 | 17 | 5.3887 | 5.3887 | 0 | 0 | 0 | 3/19/19:00
3 | 19 | 1900-01-19 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 78.7917 | -0.86659 | 86.148 | -75 | -8.2172 | 279.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/19/20:00
3 | 19 | 1900-01-20 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 78.8333 | -0.85024 | 86.148 | -75 | -8.2044 | 294.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/19/21:00
3 | 19 | 1900-01-21 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 78.875 | -0.8339 | 86.148 | -75 | -8.1916 | 309.1001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/19/22:00
3 | 19 | 1900-01-22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 78.9167 | -0.81756 | 86.148 | -75 | -8.1787 | 324.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/19/23:00
3 | 19 | 1900-01-23 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 78.9583 | -0.80121 | 86.148 | -75 | -8.1658 | 339.1065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/19/24:00
3 | 20 | 1899-12-31 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79 | -0.78486 | 86.148 | -75 | -8.153 | -5.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/1:00
3 | 20 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.0417 | -0.76852 | 86.148 | -75 | -8.1401 | 9.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/2:00
3 | 20 | 1900-01-02 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.0833 | -0.75217 | 86.148 | -75 | -8.1272 | 24.1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/3:00
3 | 20 | 1900-01-03 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.125 | -0.73582 | 86.148 | -75 | -8.1144 | 39.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/4:00
3 | 20 | 1900-01-04 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.1667 | -0.71948 | 86.148 | -75 | -8.1015 | 54.1226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/5:00
3 | 20 | 1900-01-05 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.2083 | -0.70313 | 86.148 | -75 | -8.0886 | 69.1258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/6:00
3 | 20 | 1900-01-06 | -4.4 | 1 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 1 | 0 | 0 | 39.791 | 79.25 | -0.68678 | 86.148 | -75 | -8.0757 | 84.1291 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 3/20/7:00
3 | 20 | 1900-01-07 | -5 | 39 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 39 | 0 | 0 | 39.791 | 79.2917 | -0.67043 | 86.148 | -75 | -8.0628 | 99.1323 | 0 | 39 | 12.3623 | 12.3623 | 0 | 0 | 0 | 3/20/8:00
3 | 20 | 1900-01-08 | -5 | 112 | 99 | 23 | 1 | 0 | 23 | 0 | 0 | 112 | 0 | 0 | 39.791 | 79.3333 | -0.65409 | 86.148 | -75 | -8.0499 | 114.1355 | -31.826 | 80.174 | 25.4138 | 25.4138 | 0 | 0 | 0 | 3/20/9:00
3 | 20 | 1900-01-09 | -5 | 211 | 241 | 23 | 1 | 0 | 23 | 0 | 0 | 211 | 0 | 0 | 39.791 | 79.375 | -0.63774 | 86.148 | -75 | -8.037 | 129.1387 | -118.5955 | 92.4045 | 29.2906 | 29.2906 | 0 | 0 | 0 | 3/20/10:00
3 | 20 | 1900-01-10 | -6.1 | 237 | 459 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 237 | 0 | 0 | 39.791 | 79.4167 | -0.62139 | 86.148 | -75 | -8.0241 | 144.142 | -289.0126 | -52.0126 | -16.4871 | -16.4871 | 0 | 0 | 0 | 3/20/11:00
3 | 20 | 1900-01-11 | -4.4 | 328 | 80 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 328 | 0 | 0 | 39.791 | 79.4583 | -0.60504 | 86.148 | -75 | -8.0112 | 159.1452 | -57.981 | 270.019 | 85.5913 | 85.5913 | 0 | 0 | 0 | 3/20/12:00
3 | 20 | 1900-01-12 | -3.9 | 373 | 140 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 373 | 0 | 0 | 39.791 | 79.5 | -0.58869 | 86.148 | -75 | -7.9982 | 174.1484 | -107.9282 | 265.0718 | 84.0231 | 84.0231 | 0 | 0 | 0 | 3/20/13:00
3 | 20 | 1900-01-13 | -2.8 | 315 | 5 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 315 | 0 | 0 | 39.791 | 79.5417 | -0.57234 | 86.148 | -75 | -7.9853 | 189.1517 | -3.8248 | 311.1752 | 98.6371 | 98.6371 | 0 | 0 | 0 | 3/20/14:00
3 | 20 | 1900-01-14 | -4.4 | 278 | 5 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 278 | 0 | 0 | 39.791 | 79.5833 | -0.55599 | 86.148 | -75 | -7.9724 | 204.1549 | -3.5364 | 274.4636 | 87.0002 | 87.0002 | 0 | 0 | 0 | 3/20/15:00
3 | 20 | 1900-01-15 | -4.4 | 216 | 3 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 216 | 0 | 0 | 39.791 | 79.625 | -0.53964 | 86.148 | -75 | -7.9595 | 219.1581 | -1.8054 | 214.1946 | 67.8959 | 67.8959 | 0 | 0 | 0 | 3/20/16:00
3 | 20 | 1900-01-16 | -3.9 | 157 | 4 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 157 | 0 | 0 | 39.791 | 79.6667 | -0.52329 | 86.148 | -75 | -7.9465 | 234.1614 | -1.8229 | 155.1771 | 49.1884 | 49.1884 | 0 | 0 | 0 | 3/20/17:00
3 | 20 | 1900-01-17 | -4.4 | 96 | 3 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 96 | 0 | 0 | 39.791 | 79.7083 | -0.50694 | 86.148 | -75 | -7.9336 | 249.1646 | -0.83686 | 95.1631 | 30.1651 | 30.1651 | 0 | 0 | 0 | 3/20/18:00
3 | 20 | 1900-01-18 | -4.4 | 21 | 1 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 21 | 0 | 0 | 39.791 | 79.75 | -0.49059 | 86.148 | -75 | -7.9206 | 264.1678 | -0.083556 | 20.9164 | 6.6301 | 6.6301 | 0 | 0 | 0 | 3/20/19:00
3 | 20 | 1900-01-19 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.7917 | -0.47424 | 86.148 | -75 | -7.9077 | 279.1711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/20:00
3 | 20 | 1900-01-20 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.8333 | -0.45789 | 86.148 | -75 | -7.8947 | 294.1743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/21:00
3 | 20 | 1900-01-21 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.875 | -0.44154 | 86.148 | -75 | -7.8817 | 309.1776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/22:00
3 | 20 | 1900-01-22 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.9167 | -0.42518 | 86.148 | -75 | -7.8688 | 324.1808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/23:00
3 | 20 | 1900-01-23 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 79.9583 | -0.40883 | 86.148 | -75 | -7.8558 | 339.1841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/20/24:00
3 | 21 | 1899-12-31 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80 | -0.39248 | 86.148 | -75 | -7.8428 | -5.8127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/1:00
3 | 21 | 1900-01-01 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.0417 | -0.37613 | 86.148 | -75 | -7.8298 | 9.1905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/2:00
3 | 21 | 1900-01-02 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.0833 | -0.35978 | 86.148 | -75 | -7.8168 | 24.1938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/3:00
3 | 21 | 1900-01-03 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.125 | -0.34342 | 86.148 | -75 | -7.8038 | 39.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/4:00
3 | 21 | 1900-01-04 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.1667 | -0.32707 | 86.148 | -75 | -7.7908 | 54.2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/5:00
3 | 21 | 1900-01-05 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.2083 | -0.31072 | 86.148 | -75 | -7.7778 | 69.2035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/6:00
3 | 21 | 1900-01-06 | -8.9 | 1 | 2 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 1 | 0 | 0 | 39.791 | 80.25 | -0.29437 | 86.148 | -75 | -7.7648 | 84.2068 | 0.14854 | 1.1485 | 0.36407 | 0.36407 | 0 | 0 | 0 | 3/21/7:00
3 | 21 | 1900-01-07 | -7.2 | 38 | 246 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 38 | 0 | 0 | 39.791 | 80.2917 | -0.27801 | 86.148 | -75 | -7.7518 | 99.21 | -31.0174 | 6.9826 | 2.2134 | 2.2134 | 0 | 0 | 0 | 3/21/8:00
3 | 21 | 1900-01-08 | -6.1 | 72 | 584 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 72 | 0 | 0 | 39.791 | 80.3333 | -0.26166 | 86.148 | -75 | -7.7388 | 114.2133 | -185.7473 | -113.7473 | -36.0559 | -36.0559 | 0 | 0 | 0 | 3/21/9:00
3 | 21 | 1900-01-09 | -5 | 142 | 612 | 23 | 1 | 0 | 23 | 0 | 0 | 142 | 0 | 0 | 39.791 | 80.375 | -0.24531 | 86.148 | -75 | -7.7258 | 129.2166 | -298.9919 | -156.9919 | -49.7637 | -49.7637 | 0 | 0 | 0 | 3/21/10:00
3 | 21 | 1900-01-10 | -3.9 | 155 | 679 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 155 | 0 | 0 | 39.791 | 80.4167 | -0.22895 | 86.148 | -75 | -7.7128 | 144.2198 | -424.9972 | -269.9972 | -85.5844 | -85.5844 | 0 | 0 | 0 | 3/21/11:00
3 | 21 | 1900-01-11 | -2.8 | 132 | 870 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 132 | 0 | 0 | 39.791 | 80.4583 | -0.2126 | 86.148 | -75 | -7.6997 | 159.2231 | -627.0827 | -495.0827 | -156.9326 | -156.9326 | 0 | 0 | 0 | 3/21/12:00
3 | 21 | 1900-01-12 | -1.7 | 138 | 882 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 138 | 0 | 0 | 39.791 | 80.5 | -0.19625 | 86.148 | -75 | -7.6867 | 174.2263 | -676.2062 | -538.2062 | -170.602 | -170.602 | 0 | 0 | 0 | 3/21/13:00
3 | 21 | 1900-01-13 | -0.6 | 137 | 886 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 137 | 0 | 0 | 39.791 | 80.5417 | -0.17989 | 86.148 | -75 | -7.6737 | 189.2296 | -673.7515 | -536.7515 | -170.1409 | -170.1409 | 0 | 0 | 0 | 3/21/14:00
3 | 21 | 1900-01-14 | 0 | 130 | 856 | 32 | 1 | 0 | 32 | 0 | 0 | 130 | 0 | 0 | 39.791 | 80.5833 | -0.16354 | 86.148 | -75 | -7.6606 | 204.2328 | -601.3415 | -471.3415 | -149.407 | -149.407 | 0 | 0 | 0 | 3/21/15:00
3 | 21 | 1900-01-15 | 0 | 115 | 809 | 32 | 1 | 0 | 32 | 0 | 0 | 115 | 0 | 0 | 39.791 | 80.625 | -0.14719 | 86.148 | -75 | -7.6476 | 219.2361 | -482.8039 | -367.8039 | -116.5874 | -116.5874 | 0 | 0 | 0 | 3/21/16:00
3 | 21 | 1900-01-16 | 0.6 | 93 | 718 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 93 | 0 | 0 | 39.791 | 80.6667 | -0.13083 | 86.148 | -75 | -7.6345 | 234.2394 | -323.4619 | -230.4619 | -73.0524 | -73.0524 | 0 | 0 | 0 | 3/21/17:00
3 | 21 | 1900-01-17 | 0.6 | 65 | 529 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 65 | 0 | 0 | 39.791 | 80.7083 | -0.11448 | 86.148 | -75 | -7.6215 | 249.2426 | -144.7356 | -79.7356 | -25.2748 | -25.2748 | 0 | 0 | 0 | 3/21/18:00
3 | 21 | 1900-01-18 | -1.1 | 29 | 146 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 29 | 0 | 0 | 39.791 | 80.75 | -0.098124 | 86.148 | -75 | -7.6084 | 264.2459 | -11.4075 | 17.5925 | 5.5765 | 5.5765 | 0 | 0 | 0 | 3/21/19:00
3 | 21 | 1900-01-19 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.7917 | -0.08177 | 86.148 | -75 | -7.5954 | 279.2492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/20:00
3 | 21 | 1900-01-20 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.8333 | -0.065416 | 86.148 | -75 | -7.5823 | 294.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/21:00
3 | 21 | 1900-01-21 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.875 | -0.049062 | 86.148 | -75 | -7.5692 | 309.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/22:00
3 | 21 | 1900-01-22 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.9167 | -0.032708 | 86.148 | -75 | -7.5562 | 324.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/23:00
3 | 21 | 1900-01-23 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 80.9583 | -0.016354 | 86.148 | -75 | -7.5431 | 339.2622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/21/24:00
3 | 22 | 1899-12-31 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81 | 1.8406e-13 | 86.148 | -75 | -7.53 | -5.7345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/1:00
3 | 22 | 1900-01-01 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.0417 | 0.016354 | 86.148 | -75 | -7.5169 | 9.2688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/2:00
3 | 22 | 1900-01-02 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.0833 | 0.032708 | 86.148 | -75 | -7.5038 | 24.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/3:00
3 | 22 | 1900-01-03 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.125 | 0.049062 | 86.148 | -75 | -7.4907 | 39.2753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/4:00
3 | 22 | 1900-01-04 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.1667 | 0.065416 | 86.148 | -75 | -7.4776 | 54.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/5:00
3 | 22 | 1900-01-05 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.2083 | 0.08177 | 86.148 | -75 | -7.4645 | 69.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/6:00
3 | 22 | 1900-01-06 | -6.1 | 2 | 3 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 2 | 0 | 0 | 39.791 | 81.25 | 0.098124 | 86.148 | -75 | -7.4514 | 84.2851 | 0.23283 | 2.2328 | 0.70777 | 0.70777 | 0 | 0 | 0 | 3/22/7:00
3 | 22 | 1900-01-07 | -3.3 | 49 | 216 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 49 | 0 | 0 | 39.791 | 81.2917 | 0.11448 | 86.148 | -75 | -7.4383 | 99.2884 | -26.5122 | 22.4878 | 7.1282 | 7.1282 | 0 | 0 | 0 | 3/22/8:00
3 | 22 | 1900-01-08 | -1.1 | 72 | 597 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 72 | 0 | 0 | 39.791 | 81.3333 | 0.13083 | 86.148 | -75 | -7.4252 | 114.2917 | -187.8385 | -115.8385 | -36.7188 | -36.7188 | 0 | 0 | 0 | 3/22/9:00
3 | 22 | 1900-01-09 | 0 | 99 | 748 | 32 | 1 | 0 | 32 | 0 | 0 | 99 | 0 | 0 | 39.791 | 81.375 | 0.14719 | 86.148 | -75 | -7.4121 | 129.295 | -362.7665 | -263.7665 | -83.6094 | -83.6094 | 0 | 0 | 0 | 3/22/10:00
3 | 22 | 1900-01-10 | 2.2 | 119 | 827 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 119 | 0 | 0 | 39.791 | 81.4167 | 0.16354 | 86.148 | -75 | -7.399 | 144.2983 | -514.5173 | -395.5173 | -125.3721 | -125.3721 | 0 | 0 | 0 | 3/22/11:00
3 | 22 | 1900-01-11 | 3.9 | 131 | 869 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 131 | 0 | 0 | 39.791 | 81.4583 | 0.17989 | 86.148 | -75 | -7.3859 | 159.3015 | -622.8772 | -491.8772 | -155.9165 | -155.9165 | 0 | 0 | 0 | 3/22/12:00
3 | 22 | 1900-01-12 | 5 | 136 | 885 | 41 | 1 | 0 | 41 | 0 | 0 | 136 | 0 | 0 | 39.791 | 81.5 | 0.19625 | 86.148 | -75 | -7.3727 | 174.3048 | -674.7193 | -538.7193 | -170.7646 | -170.7646 | 0 | 0 | 0 | 3/22/13:00
3 | 22 | 1900-01-13 | 6.7 | 136 | 884 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 136 | 0 | 0 | 39.791 | 81.5417 | 0.2126 | 86.148 | -75 | -7.3596 | 189.3081 | -668.2038 | -532.2038 | -168.6993 | -168.6993 | 0 | 0 | 0 | 3/22/14:00
3 | 22 | 1900-01-14 | 8.3 | 128 | 860 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 128 | 0 | 0 | 39.791 | 81.5833 | 0.22895 | 86.148 | -75 | -7.3465 | 204.3114 | -600.0065 | -472.0065 | -149.6178 | -149.6178 | 0 | 0 | 0 | 3/22/15:00
3 | 22 | 1900-01-15 | 8.9 | 157 | 678 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 157 | 0 | 0 | 39.791 | 81.625 | 0.24531 | 86.148 | -75 | -7.3333 | 219.3147 | -401.1973 | -244.1973 | -77.4063 | -77.4063 | 0 | 0 | 0 | 3/22/16:00
3 | 22 | 1900-01-16 | 9.4 | 117 | 610 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 117 | 0 | 0 | 39.791 | 81.6667 | 0.26166 | 86.148 | -75 | -7.3202 | 234.318 | -271.6091 | -154.6091 | -49.0084 | -49.0084 | 0 | 0 | 0 | 3/22/17:00
3 | 22 | 1900-01-17 | 7.8 | 108 | 308 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 108 | 0 | 0 | 39.791 | 81.7083 | 0.27801 | 86.148 | -75 | -7.3071 | 249.3212 | -82.6147 | 25.3853 | 8.0467 | 8.0467 | 0 | 0 | 0 | 3/22/18:00
3 | 22 | 1900-01-18 | 5.6 | 38 | 57 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 38 | 0 | 0 | 39.791 | 81.75 | 0.29437 | 86.148 | -75 | -7.2939 | 264.3245 | -4.1439 | 33.8561 | 10.7318 | 10.7318 | 0 | 0 | 0 | 3/22/19:00
3 | 22 | 1900-01-19 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.7917 | 0.31072 | 86.148 | -75 | -7.2808 | 279.3278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/20:00
3 | 22 | 1900-01-20 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.8333 | 0.32707 | 86.148 | -75 | -7.2676 | 294.3311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/21:00
3 | 22 | 1900-01-21 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.875 | 0.34342 | 86.148 | -75 | -7.2545 | 309.3344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/22:00
3 | 22 | 1900-01-22 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.9167 | 0.35978 | 86.148 | -75 | -7.2413 | 324.3377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/23:00
3 | 22 | 1900-01-23 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 81.9583 | 0.37613 | 86.148 | -75 | -7.2281 | 339.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/22/24:00
3 | 23 | 1899-12-31 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82 | 0.39248 | 86.148 | -75 | -7.215 | -5.6557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/1:00
3 | 23 | 1900-01-01 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.0417 | 0.40883 | 86.148 | -75 | -7.2018 | 9.3476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/2:00
3 | 23 | 1900-01-02 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.0833 | 0.42518 | 86.148 | -75 | -7.1886 | 24.3508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/3:00
3 | 23 | 1900-01-03 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.125 | 0.44154 | 86.148 | -75 | -7.1754 | 39.3541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/4:00
3 | 23 | 1900-01-04 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.1667 | 0.45789 | 86.148 | -75 | -7.1623 | 54.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/5:00
3 | 23 | 1900-01-05 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.2083 | 0.47424 | 86.148 | -75 | -7.1491 | 69.3607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/6:00
3 | 23 | 1900-01-06 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.25 | 0.49059 | 86.148 | -75 | -7.1359 | 84.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/7:00
3 | 23 | 1900-01-07 | 4.4 | 39 | 103 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 39 | 0 | 0 | 39.791 | 82.2917 | 0.50694 | 86.148 | -75 | -7.1227 | 99.3673 | -12.2979 | 26.7021 | 8.4641 | 8.4641 | 0 | 0 | 0 | 3/23/8:00
3 | 23 | 1900-01-08 | 6.1 | 166 | 164 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 166 | 0 | 0 | 39.791 | 82.3333 | 0.52329 | 86.148 | -75 | -7.1095 | 114.3706 | -51.0377 | 114.9623 | 36.441 | 36.441 | 0 | 0 | 0 | 3/23/9:00
3 | 23 | 1900-01-09 | 7.8 | 188 | 424 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 188 | 0 | 0 | 39.791 | 82.375 | 0.53964 | 86.148 | -75 | -7.0963 | 129.3739 | -204.1124 | -16.1124 | -5.1074 | -5.1074 | 0 | 0 | 0 | 3/23/10:00
3 | 23 | 1900-01-10 | 9.4 | 241 | 526 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 241 | 0 | 0 | 39.791 | 82.4167 | 0.55599 | 86.148 | -75 | -7.0831 | 144.3772 | -325.2553 | -84.2553 | -26.7075 | -26.7075 | 0 | 0 | 0 | 3/23/11:00
3 | 23 | 1900-01-11 | 11.7 | 231 | 719 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 231 | 0 | 0 | 39.791 | 82.4583 | 0.57234 | 86.148 | -75 | -7.0699 | 159.3805 | -512.4547 | -281.4547 | -89.2162 | -89.2162 | 0 | 0 | 0 | 3/23/12:00
3 | 23 | 1900-01-12 | 13.3 | 272 | 595 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 272 | 0 | 0 | 39.791 | 82.5 | 0.58869 | 86.148 | -75 | -7.0567 | 174.3838 | -451.0575 | -179.0575 | -56.7581 | 0 | -56.7581 | 55.94 | -56.7581 | 3/23/13:00
3 | 23 | 1900-01-13 | 15.6 | 310 | 348 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 310 | 0 | 0 | 39.791 | 82.5417 | 0.60504 | 86.148 | -75 | -7.0435 | 189.3871 | -261.4504 | 48.5496 | 15.3894 | 0 | 15.3894 | 60.08 | 15.3894 | 3/23/14:00
3 | 23 | 1900-01-14 | 15.6 | 292 | 478 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 292 | 0 | 0 | 39.791 | 82.5833 | 0.62139 | 86.148 | -75 | -7.0303 | 204.3904 | -331.1708 | -39.1708 | -12.4165 | 0 | -12.4165 | 60.08 | -12.4165 | 3/23/15:00
3 | 23 | 1900-01-15 | 15.6 | 217 | 456 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 217 | 0 | 0 | 39.791 | 82.625 | 0.63774 | 86.148 | -75 | -7.0171 | 219.3937 | -267.5122 | -50.5122 | -16.0115 | 0 | -16.0115 | 60.08 | -16.0115 | 3/23/16:00
3 | 23 | 1900-01-16 | 15 | 182 | 303 | 59 | 0 | 1 | 0 | 59 | 0 | 182 | 0 | 0 | 39.791 | 82.6667 | 0.65409 | 86.148 | -75 | -7.0039 | 234.397 | -133.3174 | 48.6826 | 15.4315 | 0 | 15.4315 | 59 | 15.4315 | 3/23/17:00
3 | 23 | 1900-01-17 | 14.4 | 130 | 111 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 130 | 0 | 0 | 39.791 | 82.7083 | 0.67043 | 86.148 | -75 | -6.9907 | 249.4003 | -29.1751 | 100.8249 | 31.9597 | 0 | 31.9597 | 57.92 | 31.9597 | 3/23/18:00
3 | 23 | 1900-01-18 | 11.7 | 39 | 43 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 39 | 0 | 0 | 39.791 | 82.75 | 0.68678 | 86.148 | -75 | -6.9775 | 264.4036 | -2.892 | 36.108 | 11.4456 | 11.4456 | 0 | 0 | 0 | 3/23/19:00
3 | 23 | 1900-01-19 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.7917 | 0.70313 | 86.148 | -75 | -6.9642 | 279.4069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/20:00
3 | 23 | 1900-01-20 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.8333 | 0.71948 | 86.148 | -75 | -6.951 | 294.4102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/21:00
3 | 23 | 1900-01-21 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.875 | 0.73582 | 86.148 | -75 | -6.9378 | 309.4136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/22:00
3 | 23 | 1900-01-22 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.9167 | 0.75217 | 86.148 | -75 | -6.9246 | 324.4169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/23:00
3 | 23 | 1900-01-23 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 82.9583 | 0.76852 | 86.148 | -75 | -6.9113 | 339.4202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/23/24:00
3 | 24 | 1899-12-31 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83 | 0.78486 | 86.148 | -75 | -6.8981 | -5.5765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/1:00
3 | 24 | 1900-01-01 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.0417 | 0.80121 | 86.148 | -75 | -6.8849 | 9.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/2:00
3 | 24 | 1900-01-02 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.0833 | 0.81756 | 86.148 | -75 | -6.8716 | 24.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/3:00
3 | 24 | 1900-01-03 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.125 | 0.8339 | 86.148 | -75 | -6.8584 | 39.4334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/4:00
3 | 24 | 1900-01-04 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.1667 | 0.85024 | 86.148 | -75 | -6.8451 | 54.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/5:00
3 | 24 | 1900-01-05 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.2083 | 0.86659 | 86.148 | -75 | -6.8319 | 69.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/6:00
3 | 24 | 1900-01-06 | -1.1 | 4 | 14 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 4 | 0 | 0 | 39.791 | 83.25 | 0.88293 | 86.148 | -75 | -6.8186 | 84.4433 | 1.1796 | 5.1796 | 1.6418 | 1.6418 | 0 | 0 | 0 | 3/24/7:00
3 | 24 | 1900-01-07 | 1.1 | 35 | 377 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 35 | 0 | 0 | 39.791 | 83.2917 | 0.89928 | 86.148 | -75 | -6.8054 | 99.4467 | -43.7525 | -8.7525 | -2.7744 | -2.7744 | 0 | 0 | 0 | 3/24/8:00
3 | 24 | 1900-01-08 | 3.3 | 60 | 666 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 60 | 0 | 0 | 39.791 | 83.3333 | 0.91562 | 86.148 | -75 | -6.7921 | 114.45 | -204.9718 | -144.9718 | -45.9535 | -45.9535 | 0 | 0 | 0 | 3/24/9:00
3 | 24 | 1900-01-09 | 5 | 102 | 771 | 41 | 1 | 0 | 41 | 0 | 0 | 102 | 0 | 0 | 39.791 | 83.375 | 0.93196 | 86.148 | -75 | -6.7789 | 129.4533 | -368.3797 | -266.3797 | -84.4377 | -84.4377 | 0 | 0 | 0 | 3/24/10:00
3 | 24 | 1900-01-10 | 7.2 | 96 | 868 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 96 | 0 | 0 | 39.791 | 83.4167 | 0.9483 | 86.148 | -75 | -6.7656 | 144.4566 | -533.4186 | -437.4186 | -138.6541 | -138.6541 | 0 | 0 | 0 | 3/24/11:00
3 | 24 | 1900-01-11 | 8.3 | 106 | 910 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 106 | 0 | 0 | 39.791 | 83.4583 | 0.96465 | 86.148 | -75 | -6.7524 | 159.4599 | -644.8797 | -538.8797 | -170.8155 | -170.8155 | 0 | 0 | 0 | 3/24/12:00
3 | 24 | 1900-01-12 | 10 | 160 | 880 | 50 | 1 | 0 | 50 | 0 | 0 | 160 | 0 | 0 | 39.791 | 83.5 | 0.98099 | 86.148 | -75 | -6.7391 | 174.4632 | -663.2824 | -503.2824 | -159.5317 | -159.5317 | 0 | 0 | 0 | 3/24/13:00
3 | 24 | 1900-01-13 | 11.1 | 149 | 884 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 149 | 0 | 0 | 39.791 | 83.5417 | 0.99733 | 86.148 | -75 | -6.7258 | 189.4665 | -660.0525 | -511.0525 | -161.9947 | -161.9947 | 0 | 0 | 0 | 3/24/14:00
3 | 24 | 1900-01-14 | 12.8 | 140 | 871 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 140 | 0 | 0 | 39.791 | 83.5833 | 1.0137 | 86.148 | -75 | -6.7126 | 204.4699 | -599.1921 | -459.1921 | -145.5559 | 0 | -145.5559 | 55.04 | -145.5559 | 3/24/15:00
3 | 24 | 1900-01-15 | 13.3 | 115 | 838 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 115 | 0 | 0 | 39.791 | 83.625 | 1.03 | 86.148 | -75 | -6.6993 | 219.4732 | -487.3242 | -372.3242 | -118.0203 | 0 | -118.0203 | 55.94 | -118.0203 | 3/24/16:00
3 | 24 | 1900-01-16 | 14.4 | 76 | 787 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 76 | 0 | 0 | 39.791 | 83.6667 | 1.0464 | 86.148 | -75 | -6.686 | 234.4765 | -342.1074 | -266.1074 | -84.3514 | 0 | -84.3514 | 57.92 | -84.3514 | 3/24/17:00
3 | 24 | 1900-01-17 | 14.4 | 54 | 626 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 54 | 0 | 0 | 39.791 | 83.7083 | 1.0627 | 86.148 | -75 | -6.6727 | 249.4798 | -161.1521 | -107.1521 | -33.9654 | 0 | -33.9654 | 57.92 | -33.9654 | 3/24/18:00
3 | 24 | 1900-01-18 | 11.7 | 27 | 241 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 27 | 0 | 0 | 39.791 | 83.75 | 1.079 | 86.148 | -75 | -6.6595 | 264.4831 | -14.8954 | 12.1046 | 3.837 | 3.837 | 0 | 0 | 0 | 3/24/19:00
3 | 24 | 1900-01-19 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.7917 | 1.0954 | 86.148 | -75 | -6.6462 | 279.4865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/20:00
3 | 24 | 1900-01-20 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.8333 | 1.1117 | 86.148 | -75 | -6.6329 | 294.4898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/21:00
3 | 24 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.875 | 1.128 | 86.148 | -75 | -6.6196 | 309.4931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/22:00
3 | 24 | 1900-01-22 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.9167 | 1.1444 | 86.148 | -75 | -6.6063 | 324.4964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/23:00
3 | 24 | 1900-01-23 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 83.9583 | 1.1607 | 86.148 | -75 | -6.5931 | 339.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/24/24:00
3 | 25 | 1899-12-31 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 84 | 1.1771 | 86.148 | -75 | -6.5798 | -5.4969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/25/1:00
3 | 25 | 1900-01-01 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 84.0417 | 1.1934 | 86.148 | -75 | -6.5665 | 9.5064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/25/2:00
3 | 25 | 1900-01-02 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 84.0833 | 1.2097 | 86.148 | -75 | -6.5532 | 24.5097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/25/3:00
3 | 25 | 1900-01-03 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 84.125 | 1.2261 | 86.148 | -75 | -6.5399 | 39.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/25/4:00
3 | 25 | 1900-01-04 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 84.1667 | 1.2424 | 86.148 | -75 | -6.5266 | 54.5163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/25/5:00
3 | 25 | 1900-01-05 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 84.2083 | 1.2587 | 86.148 | -75 | -6.5133 | 69.5197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/25/6:00
3 | 25 | 1900-01-06 | 7.2 | 6 | 13 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 6 | 0 | 0 | 39.791 | 84.25 | 1.2751 | 86.148 | -75 | -6.5 | 84.523 | 1.1383 | 7.1383 | 2.2627 | 2.2627 | 0 | 0 | 0 | 3/25/7:00
3 | 25 | 1900-01-07 | 10 | 45 | 347 | 50 | 1 | 0 | 50 | 0 | 0 | 45 | 0 | 0 | 39.791 | 84.2917 | 1.2914 | 86.148 | -75 | -6.4867 | 99.5263 | -39.1112 | 5.8888 | 1.8667 | 1.8667 | 0 | 0 | 0 | 3/25/8:00
3 | 25 | 1900-01-08 | 14.4 | 78 | 576 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 78 | 0 | 0 | 39.791 | 84.3333 | 1.3077 | 86.148 | -75 | -6.4734 | 114.5296 | -175.2863 | -97.2863 | -30.8381 | 0 | -30.8381 | 57.92 | -30.8381 | 3/25/9:00
3 | 25 | 1900-01-09 | 17.8 | 110 | 723 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 110 | 0 | 0 | 39.791 | 84.375 | 1.3241 | 86.148 | -75 | -6.4601 | 129.533 | -342.8283 | -232.8283 | -73.8025 | 0 | -73.8025 | 64.04 | -73.8025 | 3/25/10:00
3 | 25 | 1900-01-10 | 20 | 139 | 755 | 68 | 0 | 1 | 0 | 68 | 0 | 139 | 0 | 0 | 39.791 | 84.4167 | 1.3404 | 86.148 | -75 | -6.4468 | 144.5363 | -461.074 | -322.074 | -102.0918 | 0 | -102.0918 | 68 | -102.0918 | 3/25/11:00
3 | 25 | 1900-01-11 | 21.1 | 135 | 797 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 135 | 0 | 0 | 39.791 | 84.4583 | 1.3567 | 86.148 | -75 | -6.4335 | 159.5396 | -561.5305 | -426.5305 | -135.2027 | 0 | -135.2027 | 69.98 | -135.2027 | 3/25/12:00
3 | 25 | 1900-01-12 | 22.8 | 166 | 852 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 166 | 0 | 0 | 39.791 | 84.5 | 1.373 | 86.148 | -75 | -6.4202 | 174.5429 | -638.4434 | -472.4434 | -149.7563 | 0 | -149.7563 | 73.04 | -149.7563 | 3/25/13:00
3 | 25 | 1900-01-13 | 22.8 | 102 | 912 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 102 | 0 | 0 | 39.791 | 84.5417 | 1.3894 | 86.148 | -75 | -6.4069 | 189.5463 | -676.7068 | -574.7068 | -182.172 | 0 | -182.172 | 73.04 | -182.172 | 3/25/14:00
3 | 25 | 1900-01-14 | 23.3 | 97 | 899 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 97 | 0 | 0 | 39.791 | 84.5833 | 1.4057 | 86.148 | -75 | -6.3936 | 204.5496 | -614.029 | -517.029 | -163.8892 | 0 | -163.8892 | 73.94 | -163.8892 | 3/25/15:00
3 | 25 | 1900-01-15 | 23.3 | 86 | 865 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 86 | 0 | 0 | 39.791 | 84.625 | 1.422 | 86.148 | -75 | -6.3803 | 219.5529 | -498.5752 | -412.5752 | -130.7791 | 0 | -130.7791 | 73.94 | -130.7791 | 3/25/16:00
3 | 25 | 1900-01-16 | 23.3 | 70 | 788 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 70 | 0 | 0 | 39.791 | 84.6667 | 1.4384 | 86.148 | -75 | -6.367 | 234.5563 | -338.3542 | -268.3542 | -85.0636 | 0 | -85.0636 | 73.94 | -85.0636 | 3/25/17:00
3 | 25 | 1900-01-17 | 21.7 | 72 | 573 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 72 | 0 | 0 | 39.791 | 84.7083 | 1.4547 | 86.148 | -75 | -6.3536 | 249.5596 | -144.4027 | -72.4027 | -22.9504 | 0 | -22.9504 | 71.06 | -22.9504 | 3/25/18:00
3 | 25 | 1900-01-18 | 20.6 | 42 | 100 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 42 | 0 | 0 | 39.791 | 84.75 | 1.471 | 86.148 | -75 | -6.3403 | 264.5629 | -5.6353 | 36.3647 | 11.527 | 0 | 11.527 | 69.08 | 11.527 | 3/25/19:00
3 | 25 | 1900-01-19 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 84.7917 | 1.4873 | 86.148 | -75 | -6.327 | 279.5662 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 3/25/20:00
3 | 25 | 1900-01-20 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 84.8333 | 1.5037 | 86.148 | -75 | -6.3137 | 294.5696 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 3/25/21:00
3 | 25 | 1900-01-21 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 84.875 | 1.52 | 86.148 | -75 | -6.3004 | 309.5729 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 3/25/22:00
3 | 25 | 1900-01-22 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 84.9167 | 1.5363 | 86.148 | -75 | -6.2871 | 324.5762 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 3/25/23:00
3 | 25 | 1900-01-23 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 84.9583 | 1.5526 | 86.148 | -75 | -6.2737 | 339.5796 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 3/25/24:00
3 | 26 | 1899-12-31 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 85 | 1.5689 | 86.148 | -75 | -6.2604 | -5.4171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/26/1:00
3 | 26 | 1900-01-01 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 85.0417 | 1.5853 | 86.148 | -75 | -6.2471 | 9.5862 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 3/26/2:00
3 | 26 | 1900-01-02 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 85.0833 | 1.6016 | 86.148 | -75 | -6.2338 | 24.5896 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 3/26/3:00
3 | 26 | 1900-01-03 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 85.125 | 1.6179 | 86.148 | -75 | -6.2204 | 39.5929 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 3/26/4:00
3 | 26 | 1900-01-04 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 85.1667 | 1.6342 | 86.148 | -75 | -6.2071 | 54.5962 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 3/26/5:00
3 | 26 | 1900-01-05 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 85.2083 | 1.6505 | 86.148 | -75 | -6.1938 | 69.5996 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 3/26/6:00
3 | 26 | 1900-01-06 | 12.2 | 6 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 6 | 0 | 0 | 39.791 | 85.25 | 1.6669 | 86.148 | -75 | -6.1805 | 84.6029 | 0 | 6 | 1.9019 | 1.9019 | 0 | 0 | 0 | 3/26/7:00
3 | 26 | 1900-01-07 | 13.3 | 62 | 41 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 62 | 0 | 0 | 39.791 | 85.2917 | 1.6832 | 86.148 | -75 | -6.1671 | 99.6062 | -4.4842 | 57.5158 | 18.2315 | 0 | 18.2315 | 55.94 | 18.2315 | 3/26/8:00
3 | 26 | 1900-01-08 | 17.2 | 165 | 261 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 165 | 0 | 0 | 39.791 | 85.3333 | 1.6995 | 86.148 | -75 | -6.1538 | 114.6095 | -78.5241 | 86.4759 | 27.4113 | 0 | 27.4113 | 62.96 | 27.4113 | 3/26/9:00
3 | 26 | 1900-01-09 | 16.1 | 281 | 32 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 281 | 0 | 0 | 39.791 | 85.375 | 1.7158 | 86.148 | -75 | -6.1405 | 129.6129 | -15.0572 | 265.9428 | 84.2992 | 0 | 84.2992 | 60.98 | 84.2992 | 3/26/10:00
3 | 26 | 1900-01-10 | 16.1 | 274 | 71 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 274 | 0 | 0 | 39.791 | 85.4167 | 1.7321 | 86.148 | -75 | -6.1271 | 144.6162 | -43.0847 | 230.9153 | 73.1961 | 0 | 73.1961 | 60.98 | 73.1961 | 3/26/11:00
3 | 26 | 1900-01-11 | 15 | 322 | 26 | 59 | 0 | 1 | 0 | 59 | 0 | 322 | 0 | 0 | 39.791 | 85.4583 | 1.7484 | 86.148 | -75 | -6.1138 | 159.6195 | -18.211 | 303.789 | 96.2958 | 0 | 96.2958 | 59 | 96.2958 | 3/26/12:00
3 | 26 | 1900-01-12 | 12.2 | 167 | 3 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 167 | 0 | 0 | 39.791 | 85.5 | 1.7648 | 86.148 | -75 | -6.1005 | 174.6229 | -2.2348 | 164.7652 | 52.2277 | 52.2277 | 0 | 0 | 0 | 3/26/13:00
3 | 26 | 1900-01-13 | 11.7 | 213 | 1 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 213 | 0 | 0 | 39.791 | 85.5417 | 1.7811 | 86.148 | -75 | -6.0871 | 189.6262 | -0.73731 | 212.2627 | 67.2836 | 67.2836 | 0 | 0 | 0 | 3/26/14:00
3 | 26 | 1900-01-14 | 11.7 | 332 | 7 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 332 | 0 | 0 | 39.791 | 85.5833 | 1.7974 | 86.148 | -75 | -6.0738 | 204.6295 | -4.7464 | 327.2536 | 103.7337 | 103.7337 | 0 | 0 | 0 | 3/26/15:00
3 | 26 | 1900-01-15 | 12.2 | 271 | 2 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 271 | 0 | 0 | 39.791 | 85.625 | 1.8137 | 86.148 | -75 | -6.0605 | 219.6329 | -1.1424 | 269.8576 | 85.5401 | 85.5401 | 0 | 0 | 0 | 3/26/16:00
3 | 26 | 1900-01-16 | 12.2 | 176 | 5 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 176 | 0 | 0 | 39.791 | 85.6667 | 1.83 | 86.148 | -75 | -6.0471 | 234.6362 | -2.1203 | 173.8797 | 55.1168 | 55.1168 | 0 | 0 | 0 | 3/26/17:00
3 | 26 | 1900-01-17 | 13.3 | 118 | 164 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 118 | 0 | 0 | 39.791 | 85.7083 | 1.8463 | 86.148 | -75 | -6.0338 | 249.6396 | -40.4394 | 77.5606 | 24.5854 | 0 | 24.5854 | 55.94 | 24.5854 | 3/26/18:00
3 | 26 | 1900-01-18 | 11.7 | 28 | 42 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 28 | 0 | 0 | 39.791 | 85.75 | 1.8626 | 86.148 | -75 | -6.0205 | 264.6429 | -2.1378 | 25.8622 | 8.1979 | 8.1979 | 0 | 0 | 0 | 3/26/19:00
3 | 26 | 1900-01-19 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 85.7917 | 1.8789 | 86.148 | -75 | -6.0071 | 279.6462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/26/20:00
3 | 26 | 1900-01-20 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 85.8333 | 1.8952 | 86.148 | -75 | -5.9938 | 294.6496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/26/21:00
3 | 26 | 1900-01-21 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 85.875 | 1.9115 | 86.148 | -75 | -5.9804 | 309.6529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/26/22:00
3 | 26 | 1900-01-22 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 85.9167 | 1.9278 | 86.148 | -75 | -5.9671 | 324.6562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/26/23:00
3 | 26 | 1900-01-23 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 85.9583 | 1.9441 | 86.148 | -75 | -5.9538 | 339.6596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/26/24:00
3 | 27 | 1899-12-31 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86 | 1.9604 | 86.148 | -75 | -5.9404 | -5.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/1:00
3 | 27 | 1900-01-01 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.0417 | 1.9767 | 86.148 | -75 | -5.9271 | 9.6662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/2:00
3 | 27 | 1900-01-02 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.0833 | 1.9931 | 86.148 | -75 | -5.9137 | 24.6696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/3:00
3 | 27 | 1900-01-03 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.125 | 2.0094 | 86.148 | -75 | -5.9004 | 39.6729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/4:00
3 | 27 | 1900-01-04 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.1667 | 2.0257 | 86.148 | -75 | -5.887 | 54.6762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/5:00
3 | 27 | 1900-01-05 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.2083 | 2.042 | 86.148 | -75 | -5.8737 | 69.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/6:00
3 | 27 | 1900-01-06 | 0 | 6 | 3 | 32 | 1 | 0 | 32 | 0 | 0 | 6 | 0 | 0 | 39.791 | 86.25 | 2.0582 | 86.148 | -75 | -5.8604 | 84.6829 | 0.28243 | 6.2824 | 1.9914 | 1.9914 | 0 | 0 | 0 | 3/27/7:00
3 | 27 | 1900-01-07 | 1.7 | 51 | 229 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 51 | 0 | 0 | 39.791 | 86.2917 | 2.0745 | 86.148 | -75 | -5.847 | 99.6862 | -24.281 | 26.719 | 8.4695 | 8.4695 | 0 | 0 | 0 | 3/27/8:00
3 | 27 | 1900-01-08 | 3.3 | 91 | 524 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 91 | 0 | 0 | 39.791 | 86.3333 | 2.0908 | 86.148 | -75 | -5.8337 | 114.6896 | -155.8336 | -64.8336 | -20.5511 | -20.5511 | 0 | 0 | 0 | 3/27/9:00
3 | 27 | 1900-01-09 | 4.4 | 126 | 676 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 126 | 0 | 0 | 39.791 | 86.375 | 2.1071 | 86.148 | -75 | -5.8203 | 129.6929 | -315.6128 | -189.6128 | -60.104 | -60.104 | 0 | 0 | 0 | 3/27/10:00
3 | 27 | 1900-01-10 | 5.6 | 150 | 757 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 150 | 0 | 0 | 39.791 | 86.4167 | 2.1234 | 86.148 | -75 | -5.807 | 144.6963 | -456.4213 | -306.4213 | -97.1302 | -97.1302 | 0 | 0 | 0 | 3/27/11:00
3 | 27 | 1900-01-11 | 7.8 | 165 | 801 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 165 | 0 | 0 | 39.791 | 86.4583 | 2.1397 | 86.148 | -75 | -5.7936 | 159.6996 | -557.7039 | -392.7039 | -124.4803 | -124.4803 | 0 | 0 | 0 | 3/27/12:00
3 | 27 | 1900-01-12 | 8.3 | 172 | 823 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 172 | 0 | 0 | 39.791 | 86.5 | 2.156 | 86.148 | -75 | -5.7803 | 174.7029 | -609.4184 | -437.4184 | -138.654 | -138.654 | 0 | 0 | 0 | 3/27/13:00
3 | 27 | 1900-01-13 | 10 | 171 | 817 | 50 | 1 | 0 | 50 | 0 | 0 | 171 | 0 | 0 | 39.791 | 86.5417 | 2.1723 | 86.148 | -75 | -5.7669 | 189.7063 | -598.5192 | -427.5192 | -135.5161 | -135.5161 | 0 | 0 | 0 | 3/27/14:00
3 | 27 | 1900-01-14 | 10.6 | 178 | 781 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 178 | 0 | 0 | 39.791 | 86.5833 | 2.1886 | 86.148 | -75 | -5.7536 | 204.7096 | -525.6752 | -347.6752 | -110.207 | -110.207 | 0 | 0 | 0 | 3/27/15:00
3 | 27 | 1900-01-15 | 10.6 | 150 | 734 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 150 | 0 | 0 | 39.791 | 86.625 | 2.2049 | 86.148 | -75 | -5.7402 | 219.7129 | -415.4612 | -265.4612 | -84.1466 | -84.1466 | 0 | 0 | 0 | 3/27/16:00
3 | 27 | 1900-01-16 | 11.1 | 120 | 637 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 120 | 0 | 0 | 39.791 | 86.6667 | 2.2212 | 86.148 | -75 | -5.7269 | 234.7163 | -266.7124 | -146.7124 | -46.5053 | -46.5053 | 0 | 0 | 0 | 3/27/17:00
3 | 27 | 1900-01-17 | 11.1 | 80 | 461 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 80 | 0 | 0 | 39.791 | 86.7083 | 2.2375 | 86.148 | -75 | -5.7136 | 249.7196 | -111.1674 | -31.1674 | -9.8795 | -9.8795 | 0 | 0 | 0 | 3/27/18:00
3 | 27 | 1900-01-18 | 8.9 | 35 | 114 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 35 | 0 | 0 | 39.791 | 86.75 | 2.2538 | 86.148 | -75 | -5.7002 | 264.7229 | -5.181 | 29.819 | 9.4521 | 9.4521 | 0 | 0 | 0 | 3/27/19:00
3 | 27 | 1900-01-19 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.7917 | 2.27 | 86.148 | -75 | -5.6869 | 279.7263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/20:00
3 | 27 | 1900-01-20 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.8333 | 2.2863 | 86.148 | -75 | -5.6735 | 294.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/21:00
3 | 27 | 1900-01-21 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.875 | 2.3026 | 86.148 | -75 | -5.6602 | 309.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/22:00
3 | 27 | 1900-01-22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.9167 | 2.3189 | 86.148 | -75 | -5.6468 | 324.7363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/23:00
3 | 27 | 1900-01-23 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 86.9583 | 2.3352 | 86.148 | -75 | -5.6335 | 339.7396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/27/24:00
3 | 28 | 1899-12-31 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 87 | 2.3515 | 86.148 | -75 | -5.6201 | -5.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/28/1:00
3 | 28 | 1900-01-01 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 87.0417 | 2.3677 | 86.148 | -75 | -5.6068 | 9.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/28/2:00
3 | 28 | 1900-01-02 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 87.0833 | 2.384 | 86.148 | -75 | -5.5935 | 24.7496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/28/3:00
3 | 28 | 1900-01-03 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 87.125 | 2.4003 | 86.148 | -75 | -5.5801 | 39.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/28/4:00
3 | 28 | 1900-01-04 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 87.1667 | 2.4166 | 86.148 | -75 | -5.5668 | 54.7563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/28/5:00
3 | 28 | 1900-01-05 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 87.2083 | 2.4328 | 86.148 | -75 | -5.5534 | 69.7596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/28/6:00
3 | 28 | 1900-01-06 | 2.8 | 8 | 4 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 8 | 0 | 0 | 39.791 | 87.25 | 2.4491 | 86.148 | -75 | -5.5401 | 84.763 | 0.38968 | 8.3897 | 2.6594 | 2.6594 | 0 | 0 | 0 | 3/28/7:00
3 | 28 | 1900-01-07 | 5 | 48 | 372 | 41 | 1 | 0 | 41 | 0 | 0 | 48 | 0 | 0 | 39.791 | 87.2917 | 2.4654 | 86.148 | -75 | -5.5267 | 99.7663 | -38.2009 | 9.7991 | 3.1061 | 3.1061 | 0 | 0 | 0 | 3/28/8:00
3 | 28 | 1900-01-08 | 7.8 | 65 | 698 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 65 | 0 | 0 | 39.791 | 87.3333 | 2.4817 | 86.148 | -75 | -5.5134 | 114.7697 | -205.1544 | -140.1544 | -44.4265 | -44.4265 | 0 | 0 | 0 | 3/28/9:00
3 | 28 | 1900-01-09 | 10.6 | 94 | 798 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 94 | 0 | 0 | 39.791 | 87.375 | 2.4979 | 86.148 | -75 | -5.5001 | 129.773 | -369.6429 | -275.6429 | -87.374 | -87.374 | 0 | 0 | 0 | 3/28/10:00
3 | 28 | 1900-01-10 | 13.3 | 115 | 805 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 115 | 0 | 0 | 39.791 | 87.4167 | 2.5142 | 86.148 | -75 | -5.4867 | 144.7763 | -482.2105 | -367.2105 | -116.3993 | 0 | -116.3993 | 55.94 | -116.3993 | 3/28/11:00
3 | 28 | 1900-01-11 | 16.1 | 153 | 858 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 153 | 0 | 0 | 39.791 | 87.4583 | 2.5305 | 86.148 | -75 | -5.4734 | 159.7797 | -593.7958 | -440.7958 | -139.7246 | 0 | -139.7246 | 60.98 | -139.7246 | 3/28/12:00
3 | 28 | 1900-01-12 | 17.8 | 134 | 844 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 134 | 0 | 0 | 39.791 | 87.5 | 2.5468 | 86.148 | -75 | -5.46 | 174.783 | -621.1904 | -487.1904 | -154.4308 | 0 | -154.4308 | 64.04 | -154.4308 | 3/28/13:00
3 | 28 | 1900-01-13 | 19.4 | 125 | 876 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 125 | 0 | 0 | 39.791 | 87.5417 | 2.563 | 86.148 | -75 | -5.4467 | 189.7863 | -637.5758 | -512.5758 | -162.4776 | 0 | -162.4776 | 66.92 | -162.4776 | 3/28/14:00
3 | 28 | 1900-01-14 | 20.6 | 138 | 791 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 138 | 0 | 0 | 39.791 | 87.5833 | 2.5793 | 86.148 | -75 | -5.4334 | 204.7897 | -528.4454 | -390.4454 | -123.7644 | 0 | -123.7644 | 69.08 | -123.7644 | 3/28/15:00
3 | 28 | 1900-01-15 | 21.1 | 140 | 798 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 140 | 0 | 0 | 39.791 | 87.625 | 2.5955 | 86.148 | -75 | -5.42 | 219.793 | -447.5257 | -307.5257 | -97.4803 | 0 | -97.4803 | 69.98 | -97.4803 | 3/28/16:00
3 | 28 | 1900-01-16 | 20.6 | 112 | 731 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 112 | 0 | 0 | 39.791 | 87.6667 | 2.6118 | 86.148 | -75 | -5.4067 | 234.7963 | -302.15 | -190.15 | -60.2742 | 0 | -60.2742 | 69.08 | -60.2742 | 3/28/17:00
3 | 28 | 1900-01-17 | 19.4 | 82 | 391 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 82 | 0 | 0 | 39.791 | 87.7083 | 2.6281 | 86.148 | -75 | -5.3933 | 249.7997 | -92.1594 | -10.1594 | -3.2203 | 0 | -3.2203 | 66.92 | -3.2203 | 3/28/18:00
3 | 28 | 1900-01-18 | 16.1 | 38 | 153 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 38 | 0 | 0 | 39.791 | 87.75 | 2.6443 | 86.148 | -75 | -5.38 | 264.803 | -6.12 | 31.88 | 10.1054 | 0 | 10.1054 | 60.98 | 10.1054 | 3/28/19:00
3 | 28 | 1900-01-19 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 87.7917 | 2.6606 | 86.148 | -75 | -5.3667 | 279.8063 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 3/28/20:00
3 | 28 | 1900-01-20 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 87.8333 | 2.6769 | 86.148 | -75 | -5.3533 | 294.8097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/28/21:00
3 | 28 | 1900-01-21 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 87.875 | 2.6931 | 86.148 | -75 | -5.34 | 309.813 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 3/28/22:00
3 | 28 | 1900-01-22 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 87.9167 | 2.7094 | 86.148 | -75 | -5.3267 | 324.8163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/28/23:00
3 | 28 | 1900-01-23 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 87.9583 | 2.7256 | 86.148 | -75 | -5.3133 | 339.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/28/24:00
3 | 29 | 1899-12-31 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 88 | 2.7419 | 86.148 | -75 | -5.3 | -5.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/29/1:00
3 | 29 | 1900-01-01 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 88.0417 | 2.7581 | 86.148 | -75 | -5.2867 | 9.8263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/29/2:00
3 | 29 | 1900-01-02 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 88.0833 | 2.7744 | 86.148 | -75 | -5.2734 | 24.8297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/29/3:00
3 | 29 | 1900-01-03 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 88.125 | 2.7906 | 86.148 | -75 | -5.26 | 39.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/29/4:00
3 | 29 | 1900-01-04 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 88.1667 | 2.8069 | 86.148 | -75 | -5.2467 | 54.8363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/29/5:00
3 | 29 | 1900-01-05 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 88.2083 | 2.8231 | 86.148 | -75 | -5.2334 | 69.8397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/29/6:00
3 | 29 | 1900-01-06 | 10 | 7 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 7 | 0 | 0 | 39.791 | 88.25 | 2.8394 | 86.148 | -75 | -5.22 | 84.843 | 0 | 7 | 2.2189 | 2.2189 | 0 | 0 | 0 | 3/29/7:00
3 | 29 | 1900-01-07 | 12.8 | 54 | 146 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 54 | 0 | 0 | 39.791 | 88.2917 | 2.8556 | 86.148 | -75 | -5.2067 | 99.8463 | -14.5053 | 39.4947 | 12.5191 | 0 | 12.5191 | 55.04 | 12.5191 | 3/29/8:00
3 | 29 | 1900-01-08 | 17.2 | 116 | 367 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 116 | 0 | 0 | 39.791 | 88.3333 | 2.8719 | 86.148 | -75 | -5.1934 | 114.8497 | -106.5892 | 9.4108 | 2.983 | 0 | 2.983 | 62.96 | 2.983 | 3/29/9:00
3 | 29 | 1900-01-09 | 20.6 | 146 | 619 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 146 | 0 | 0 | 39.791 | 88.375 | 2.8881 | 86.148 | -75 | -5.1801 | 129.853 | -284.4453 | -138.4453 | -43.8847 | 0 | -43.8847 | 69.08 | -43.8847 | 3/29/10:00
3 | 29 | 1900-01-10 | 22.2 | 175 | 699 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 175 | 0 | 0 | 39.791 | 88.4167 | 2.9044 | 86.148 | -75 | -5.1668 | 144.8563 | -415.9619 | -240.9619 | -76.3807 | 0 | -76.3807 | 71.96 | -76.3807 | 3/29/11:00
3 | 29 | 1900-01-11 | 22.8 | 193 | 749 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 193 | 0 | 0 | 39.791 | 88.4583 | 2.9206 | 86.148 | -75 | -5.1534 | 159.8596 | -515.2019 | -322.2019 | -102.1324 | 0 | -102.1324 | 73.04 | -102.1324 | 3/29/12:00
3 | 29 | 1900-01-12 | 23.9 | 201 | 760 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 201 | 0 | 0 | 39.791 | 88.5 | 2.9368 | 86.148 | -75 | -5.1401 | 174.863 | -555.9421 | -354.9421 | -112.5104 | 0 | -112.5104 | 75.02 | -112.5104 | 3/29/13:00
3 | 29 | 1900-01-13 | 25 | 206 | 754 | 77 | 0 | 1 | 0 | 77 | 0 | 206 | 0 | 0 | 39.791 | 88.5417 | 2.9531 | 86.148 | -75 | -5.1268 | 189.8663 | -545.1748 | -339.1748 | -107.5125 | 0 | -107.5125 | 77 | -107.5125 | 3/29/14:00
3 | 29 | 1900-01-14 | 25.6 | 203 | 713 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 203 | 0 | 0 | 39.791 | 88.5833 | 2.9693 | 86.148 | -75 | -5.1135 | 204.8696 | -472.7485 | -269.7485 | -85.5056 | 0 | -85.5056 | 78.08 | -85.5056 | 3/29/15:00
3 | 29 | 1900-01-15 | 25.6 | 189 | 652 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 189 | 0 | 0 | 39.791 | 88.625 | 2.9856 | 86.148 | -75 | -5.1002 | 219.873 | -362.2357 | -173.2357 | -54.9127 | 0 | -54.9127 | 78.08 | -54.9127 | 3/29/16:00
3 | 29 | 1900-01-16 | 25.6 | 158 | 544 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 158 | 0 | 0 | 39.791 | 88.6667 | 3.0018 | 86.148 | -75 | -5.0869 | 234.8763 | -221.9324 | -63.9324 | -20.2655 | 0 | -20.2655 | 78.08 | -20.2655 | 3/29/17:00
3 | 29 | 1900-01-17 | 24.4 | 97 | 328 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 97 | 0 | 0 | 39.791 | 88.7083 | 3.018 | 86.148 | -75 | -5.0735 | 249.8796 | -75.5244 | 21.4756 | 6.8074 | 0 | 6.8074 | 75.92 | 6.8074 | 3/29/18:00
3 | 29 | 1900-01-18 | 22.2 | 35 | 41 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 35 | 0 | 0 | 39.791 | 88.75 | 3.0343 | 86.148 | -75 | -5.0602 | 264.8829 | -1.417 | 33.583 | 10.6452 | 0 | 10.6452 | 71.96 | 10.6452 | 3/29/19:00
3 | 29 | 1900-01-19 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 88.7917 | 3.0505 | 86.148 | -75 | -5.0469 | 279.8863 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 3/29/20:00
3 | 29 | 1900-01-20 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 88.8333 | 3.0667 | 86.148 | -75 | -5.0336 | 294.8896 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 3/29/21:00
3 | 29 | 1900-01-21 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 88.875 | 3.0829 | 86.148 | -75 | -5.0203 | 309.8929 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 3/29/22:00
3 | 29 | 1900-01-22 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 88.9167 | 3.0992 | 86.148 | -75 | -5.007 | 324.8962 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 3/29/23:00
3 | 29 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 88.9583 | 3.1154 | 86.148 | -75 | -4.9937 | 339.8996 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 3/29/24:00
3 | 30 | 1899-12-31 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 89 | 3.1316 | 86.148 | -75 | -4.9804 | -5.0971 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 3/30/1:00
3 | 30 | 1900-01-01 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 89.0417 | 3.1478 | 86.148 | -75 | -4.9671 | 9.9062 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 3/30/2:00
3 | 30 | 1900-01-02 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 89.0833 | 3.1641 | 86.148 | -75 | -4.9538 | 24.9095 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 3/30/3:00
3 | 30 | 1900-01-03 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 89.125 | 3.1803 | 86.148 | -75 | -4.9405 | 39.9129 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 3/30/4:00
3 | 30 | 1900-01-04 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 89.1667 | 3.1965 | 86.148 | -75 | -4.9272 | 54.9162 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 3/30/5:00
3 | 30 | 1900-01-05 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 89.2083 | 3.2127 | 86.148 | -75 | -4.9139 | 69.9195 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 3/30/6:00
3 | 30 | 1900-01-06 | 14.4 | 9 | 46 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 9 | 0 | 0 | 39.791 | 89.25 | 3.2289 | 86.148 | -75 | -4.9006 | 84.9228 | 4.7812 | 13.7812 | 4.3684 | 0 | 4.3684 | 57.92 | 4.3684 | 3/30/7:00
3 | 30 | 1900-01-07 | 16.1 | 55 | 196 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 55 | 0 | 0 | 39.791 | 89.2917 | 3.2452 | 86.148 | -75 | -4.8873 | 99.9262 | -18.8184 | 36.1816 | 11.4689 | 0 | 11.4689 | 60.98 | 11.4689 | 3/30/8:00
3 | 30 | 1900-01-08 | 18.9 | 129 | 290 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 129 | 0 | 0 | 39.791 | 89.3333 | 3.2614 | 86.148 | -75 | -4.874 | 114.9295 | -83.2131 | 45.7869 | 14.5136 | 0 | 14.5136 | 66.02 | 14.5136 | 3/30/9:00
3 | 30 | 1900-01-09 | 20.6 | 68 | 860 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 68 | 0 | 0 | 39.791 | 89.375 | 3.2776 | 86.148 | -75 | -4.8608 | 129.9328 | -392.0053 | -324.0053 | -102.704 | 0 | -102.704 | 69.08 | -102.704 | 3/30/10:00
3 | 30 | 1900-01-10 | 23.3 | 80 | 904 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 80 | 0 | 0 | 39.791 | 89.4167 | 3.2938 | 86.148 | -75 | -4.8475 | 144.9361 | -534.374 | -454.374 | -144.0286 | 0 | -144.0286 | 73.94 | -144.0286 | 3/30/11:00
3 | 30 | 1900-01-11 | 25 | 85 | 877 | 77 | 0 | 1 | 0 | 77 | 0 | 85 | 0 | 0 | 39.791 | 89.4583 | 3.31 | 86.148 | -75 | -4.8342 | 159.9395 | -599.5267 | -514.5267 | -163.096 | 0 | -163.096 | 77 | -163.096 | 3/30/12:00
3 | 30 | 1900-01-12 | 26.1 | 183 | 622 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 183 | 0 | 0 | 39.791 | 89.5 | 3.3262 | 86.148 | -75 | -4.8209 | 174.9428 | -452.1759 | -269.1759 | -85.3241 | 0 | -85.3241 | 78.98 | -85.3241 | 3/30/13:00
3 | 30 | 1900-01-13 | 27.2 | 220 | 707 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 220 | 0 | 0 | 39.791 | 89.5417 | 3.3424 | 86.148 | -75 | -4.8076 | 189.9461 | -507.7922 | -287.7922 | -91.2251 | 0 | -91.2251 | 80.96 | -91.2251 | 3/30/14:00
3 | 30 | 1900-01-14 | 27.8 | 226 | 614 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 226 | 0 | 0 | 39.791 | 89.5833 | 3.3586 | 86.148 | -75 | -4.7944 | 204.9494 | -404.0048 | -178.0048 | -56.4244 | 0 | -56.4244 | 82.04 | -56.4244 | 3/30/15:00
3 | 30 | 1900-01-15 | 27.2 | 274 | 359 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 274 | 0 | 0 | 39.791 | 89.625 | 3.3748 | 86.148 | -75 | -4.7811 | 219.9527 | -197.5676 | 76.4324 | 24.2277 | 0 | 24.2277 | 80.96 | 24.2277 | 3/30/16:00
3 | 30 | 1900-01-16 | 27.2 | 129 | 592 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 129 | 0 | 0 | 39.791 | 89.6667 | 3.391 | 86.148 | -75 | -4.7678 | 234.956 | -238.3285 | -109.3285 | -34.6552 | 0 | -34.6552 | 80.96 | -34.6552 | 3/30/17:00
3 | 30 | 1900-01-17 | 25.6 | 105 | 312 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 105 | 0 | 0 | 39.791 | 89.7083 | 3.4072 | 86.148 | -75 | -4.7545 | 249.9594 | -70.1418 | 34.8582 | 11.0494 | 0 | 11.0494 | 78.08 | 11.0494 | 3/30/18:00
3 | 30 | 1900-01-18 | 22.2 | 36 | 129 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 36 | 0 | 0 | 39.791 | 89.75 | 3.4234 | 86.148 | -75 | -4.7413 | 264.9627 | -3.7579 | 32.2421 | 10.2202 | 0 | 10.2202 | 71.96 | 10.2202 | 3/30/19:00
3 | 30 | 1900-01-19 | 21.1 | 2 | 2 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 2 | 0 | 0 | 39.791 | 89.7917 | 3.4396 | 86.148 | -75 | -4.728 | 279.966 | 0.34227 | 2.3423 | 0.74246 | 0 | 0.74246 | 69.98 | 0.74246 | 3/30/20:00
3 | 30 | 1900-01-20 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 89.8333 | 3.4558 | 86.148 | -75 | -4.7147 | 294.9693 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 3/30/21:00
3 | 30 | 1900-01-21 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 89.875 | 3.472 | 86.148 | -75 | -4.7015 | 309.9726 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 3/30/22:00
3 | 30 | 1900-01-22 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 89.9167 | 3.4882 | 86.148 | -75 | -4.6882 | 324.9759 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 3/30/23:00
3 | 30 | 1900-01-23 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 89.9583 | 3.5044 | 86.148 | -75 | -4.675 | 339.9793 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 3/30/24:00
3 | 31 | 1899-12-31 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 90 | 3.5206 | 86.148 | -75 | -4.6617 | -5.0174 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 3/31/1:00
3 | 31 | 1900-01-01 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 90.0417 | 3.5368 | 86.148 | -75 | -4.6484 | 9.9859 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 3/31/2:00
3 | 31 | 1900-01-02 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 90.0833 | 3.553 | 86.148 | -75 | -4.6352 | 24.9892 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 3/31/3:00
3 | 31 | 1900-01-03 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 90.125 | 3.5691 | 86.148 | -75 | -4.6219 | 39.9925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/31/4:00
3 | 31 | 1900-01-04 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 90.1667 | 3.5853 | 86.148 | -75 | -4.6087 | 54.9958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/31/5:00
3 | 31 | 1900-01-05 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 90.2083 | 3.6015 | 86.148 | -75 | -4.5955 | 69.9991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/31/6:00
3 | 31 | 1900-01-06 | 11.1 | 10 | 60 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 10 | 0 | 0 | 39.791 | 90.25 | 3.6177 | 86.148 | -75 | -4.5822 | 85.0024 | 6.4311 | 16.4311 | 5.2084 | 5.2084 | 0 | 0 | 0 | 3/31/7:00
3 | 31 | 1900-01-07 | 13.9 | 37 | 485 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 37 | 0 | 0 | 39.791 | 90.2917 | 3.6339 | 86.148 | -75 | -4.569 | 100.0058 | -44.9466 | -7.9466 | -2.5189 | 0 | -2.5189 | 57.02 | -2.5189 | 3/31/8:00
3 | 31 | 1900-01-08 | 17.8 | 60 | 721 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 60 | 0 | 0 | 39.791 | 90.3333 | 3.65 | 86.148 | -75 | -4.5557 | 115.0091 | -204.3612 | -144.3612 | -45.76 | 0 | -45.76 | 64.04 | -45.76 | 3/31/9:00
3 | 31 | 1900-01-09 | 20 | 75 | 825 | 68 | 0 | 1 | 0 | 68 | 0 | 75 | 0 | 0 | 39.791 | 90.375 | 3.6662 | 86.148 | -75 | -4.5425 | 130.0124 | -372.9829 | -297.9829 | -94.4554 | 0 | -94.4554 | 68 | -94.4554 | 3/31/10:00
3 | 31 | 1900-01-10 | 23.9 | 83 | 899 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 83 | 0 | 0 | 39.791 | 90.4167 | 3.6824 | 86.148 | -75 | -4.5293 | 145.0157 | -527.8394 | -444.8394 | -141.0063 | 0 | -141.0063 | 75.02 | -141.0063 | 3/31/11:00
3 | 31 | 1900-01-11 | 26.1 | 91 | 925 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 91 | 0 | 0 | 39.791 | 90.4583 | 3.6986 | 86.148 | -75 | -4.516 | 160.019 | -628.3932 | -537.3932 | -170.3443 | 0 | -170.3443 | 78.98 | -170.3443 | 3/31/12:00
3 | 31 | 1900-01-12 | 27.8 | 200 | 715 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 200 | 0 | 0 | 39.791 | 90.5 | 3.7147 | 86.148 | -75 | -4.5028 | 175.0223 | -516.5258 | -316.5258 | -100.3332 | 0 | -100.3332 | 82.04 | -100.3332 | 3/31/13:00
3 | 31 | 1900-01-13 | 27.8 | 218 | 566 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 218 | 0 | 0 | 39.791 | 90.5417 | 3.7309 | 86.148 | -75 | -4.4896 | 190.0256 | -403.7861 | -185.7861 | -58.8909 | 0 | -58.8909 | 82.04 | -58.8909 | 3/31/14:00
3 | 31 | 1900-01-14 | 28.3 | 120 | 808 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 120 | 0 | 0 | 39.791 | 90.5833 | 3.7471 | 86.148 | -75 | -4.4764 | 205.0289 | -527.5558 | -407.5558 | -129.1881 | 0 | -129.1881 | 82.94 | -129.1881 | 3/31/15:00
3 | 31 | 1900-01-15 | 27.8 | 112 | 716 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 112 | 0 | 0 | 39.791 | 90.625 | 3.7632 | 86.148 | -75 | -4.4631 | 220.0322 | -390.2667 | -278.2667 | -88.2057 | 0 | -88.2057 | 82.04 | -88.2057 | 3/31/16:00
3 | 31 | 1900-01-16 | 25.6 | 135 | 562 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 135 | 0 | 0 | 39.791 | 90.6667 | 3.7794 | 86.148 | -75 | -4.4499 | 235.0355 | -223.2231 | -88.2231 | -27.9652 | 0 | -27.9652 | 78.08 | -27.9652 | 3/31/17:00
3 | 31 | 1900-01-17 | 25.6 | 97 | 334 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 97 | 0 | 0 | 39.791 | 90.7083 | 3.7956 | 86.148 | -75 | -4.4367 | 250.0388 | -73.2706 | 23.7294 | 7.5218 | 0 | 7.5218 | 78.08 | 7.5218 | 3/31/18:00
3 | 31 | 1900-01-18 | 23.3 | 29 | 262 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 29 | 0 | 0 | 39.791 | 90.75 | 3.8117 | 86.148 | -75 | -4.4235 | 265.0421 | -6.2131 | 22.7869 | 7.223 | 0 | 7.223 | 73.94 | 7.223 | 3/31/19:00
3 | 31 | 1900-01-19 | 20.6 | 1 | 6 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 1 | 0 | 0 | 39.791 | 90.7917 | 3.8279 | 86.148 | -75 | -4.4103 | 280.0454 | 1.0587 | 2.0587 | 0.65258 | 0 | 0.65258 | 69.08 | 0.65258 | 3/31/20:00
3 | 31 | 1900-01-20 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 90.8333 | 3.844 | 86.148 | -75 | -4.3971 | 295.0487 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 3/31/21:00
3 | 31 | 1900-01-21 | 16 | 0 | 0 | 60.8 | 0 | 1 | 0 | 60.8 | 0 | 0 | 0 | 0 | 39.791 | 90.875 | 3.8602 | 86.148 | -75 | -4.3839 | 310.052 | 0 | 0 | 0 | 0 | 0 | 60.8 | 0 | 3/31/22:00
3 | 31 | 1900-01-22 | 13.2 | 0 | 0 | 55.76 | 0 | 1 | 0 | 55.76 | 0 | 0 | 0 | 0 | 39.791 | 90.9167 | 3.8763 | 86.148 | -75 | -4.3707 | 325.0553 | 0 | 0 | 0 | 0 | 0 | 55.76 | 0 | 3/31/23:00
3 | 31 | 1900-01-23 | 10.3 | 0 | 0 | 50.54 | 1 | 0 | 50.54 | 0 | 0 | 0 | 0 | 0 | 39.791 | 90.9583 | 3.8925 | 86.148 | -75 | -4.3575 | 340.0586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3/31/24:00
4 | 1 | 1899-12-31 | 7.5 | 0 | 0 | 45.5 | 1 | 0 | 45.5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91 | 3.9086 | 86.148 | -75 | -4.3443 | -4.9381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/1:00
4 | 1 | 1900-01-01 | 4.6 | 0 | 0 | 40.28 | 1 | 0 | 40.28 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91.0417 | 3.9248 | 86.148 | -75 | -4.3311 | 10.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/2:00
4 | 1 | 1900-01-02 | 1.8 | 0 | 0 | 35.24 | 1 | 0 | 35.24 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91.0833 | 3.9409 | 86.148 | -75 | -4.3179 | 25.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/3:00
4 | 1 | 1900-01-03 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91.125 | 3.9571 | 86.148 | -75 | -4.3047 | 40.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/4:00
4 | 1 | 1900-01-04 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91.1667 | 3.9732 | 86.148 | -75 | -4.2915 | 55.0751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/5:00
4 | 1 | 1900-01-05 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91.2083 | 3.9894 | 86.148 | -75 | -4.2784 | 70.0784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/6:00
4 | 1 | 1900-01-06 | 0 | 10 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 10 | 0 | 0 | 39.791 | 91.25 | 4.0055 | 86.148 | -75 | -4.2652 | 85.0817 | 0 | 10 | 3.1698 | 3.1698 | 0 | 0 | 0 | 4/1/7:00
4 | 1 | 1900-01-07 | 1.1 | 90 | 27 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 90 | 0 | 0 | 39.791 | 91.2917 | 4.0217 | 86.148 | -75 | -4.252 | 100.085 | -2.412 | 87.588 | 27.7639 | 27.7639 | 0 | 0 | 0 | 4/1/8:00
4 | 1 | 1900-01-08 | 2.8 | 145 | 72 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 145 | 0 | 0 | 39.791 | 91.3333 | 4.0378 | 86.148 | -75 | -4.2388 | 115.0883 | -20.1552 | 124.8448 | 39.5736 | 39.5736 | 0 | 0 | 0 | 4/1/9:00
4 | 1 | 1900-01-09 | 6.1 | 314 | 164 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 314 | 0 | 0 | 39.791 | 91.375 | 4.0539 | 86.148 | -75 | -4.2257 | 130.0916 | -73.532 | 240.468 | 76.2242 | 76.2242 | 0 | 0 | 0 | 4/1/10:00
4 | 1 | 1900-01-10 | 7.2 | 290 | 8 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 290 | 0 | 0 | 39.791 | 91.4167 | 4.0701 | 86.148 | -75 | -4.2125 | 145.0949 | -4.6651 | 285.3349 | 90.4462 | 90.4462 | 0 | 0 | 0 | 4/1/11:00
4 | 1 | 1900-01-11 | 9.4 | 267 | 26 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 267 | 0 | 0 | 39.791 | 91.4583 | 4.0862 | 86.148 | -75 | -4.1994 | 160.0982 | -17.5514 | 249.4486 | 79.0709 | 79.0709 | 0 | 0 | 0 | 4/1/12:00
4 | 1 | 1900-01-12 | 11.1 | 379 | 1 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 379 | 0 | 0 | 39.791 | 91.5 | 4.1023 | 86.148 | -75 | -4.1862 | 175.1015 | -0.71783 | 378.2822 | 119.9088 | 119.9088 | 0 | 0 | 0 | 4/1/13:00
4 | 1 | 1900-01-13 | 12.2 | 469 | 93 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 469 | 0 | 0 | 39.791 | 91.5417 | 4.1185 | 86.148 | -75 | -4.173 | 190.1047 | -65.895 | 403.105 | 127.7772 | 127.7772 | 0 | 0 | 0 | 4/1/14:00
4 | 1 | 1900-01-14 | 12.2 | 274 | 7 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 274 | 0 | 0 | 39.791 | 91.5833 | 4.1346 | 86.148 | -75 | -4.1599 | 205.108 | -4.5348 | 269.4652 | 85.4158 | 85.4158 | 0 | 0 | 0 | 4/1/15:00
4 | 1 | 1900-01-15 | 11.7 | 191 | 5 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 191 | 0 | 0 | 39.791 | 91.625 | 4.1507 | 86.148 | -75 | -4.1467 | 220.1113 | -2.699 | 188.301 | 59.6881 | 59.6881 | 0 | 0 | 0 | 4/1/16:00
4 | 1 | 1900-01-16 | 9.4 | 87 | 4 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 87 | 0 | 0 | 39.791 | 91.6667 | 4.1668 | 86.148 | -75 | -4.1336 | 235.1146 | -1.5672 | 85.4328 | 27.0807 | 27.0807 | 0 | 0 | 0 | 4/1/17:00
4 | 1 | 1900-01-17 | 8.9 | 86 | 3 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 86 | 0 | 0 | 39.791 | 91.7083 | 4.1829 | 86.148 | -75 | -4.1205 | 250.1179 | -0.64182 | 85.3582 | 27.0571 | 27.0571 | 0 | 0 | 0 | 4/1/18:00
4 | 1 | 1900-01-18 | 8.3 | 21 | 1 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 21 | 0 | 0 | 39.791 | 91.75 | 4.1991 | 86.148 | -75 | -4.1073 | 265.1212 | -0.018314 | 20.9817 | 6.6508 | 6.6508 | 0 | 0 | 0 | 4/1/19:00
4 | 1 | 1900-01-19 | 7.8 | 1 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 1 | 0 | 0 | 39.791 | 91.7917 | 4.2152 | 86.148 | -75 | -4.0942 | 280.1245 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 4/1/20:00
4 | 1 | 1900-01-20 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91.8333 | 4.2313 | 86.148 | -75 | -4.0811 | 295.1277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/21:00
4 | 1 | 1900-01-21 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91.875 | 4.2474 | 86.148 | -75 | -4.0679 | 310.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/22:00
4 | 1 | 1900-01-22 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91.9167 | 4.2635 | 86.148 | -75 | -4.0548 | 325.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/23:00
4 | 1 | 1900-01-23 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 91.9583 | 4.2796 | 86.148 | -75 | -4.0417 | 340.1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/1/24:00
4 | 2 | 1899-12-31 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92 | 4.2957 | 86.148 | -75 | -4.0286 | -4.8591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/1:00
4 | 2 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.0417 | 4.3118 | 86.148 | -75 | -4.0155 | 10.1441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/2:00
4 | 2 | 1900-01-02 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.0833 | 4.3279 | 86.148 | -75 | -4.0023 | 25.1474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/3:00
4 | 2 | 1900-01-03 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.125 | 4.3441 | 86.148 | -75 | -3.9892 | 40.1507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/4:00
4 | 2 | 1900-01-04 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.1667 | 4.3602 | 86.148 | -75 | -3.9761 | 55.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/5:00
4 | 2 | 1900-01-05 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.2083 | 4.3763 | 86.148 | -75 | -3.963 | 70.1572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/6:00
4 | 2 | 1900-01-06 | -1.7 | 12 | 24 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 12 | 0 | 0 | 39.791 | 92.25 | 4.3923 | 86.148 | -75 | -3.9499 | 85.1605 | 2.7276 | 14.7276 | 4.6684 | 4.6684 | 0 | 0 | 0 | 4/2/7:00
4 | 2 | 1900-01-07 | -1.1 | 52 | 367 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 52 | 0 | 0 | 39.791 | 92.2917 | 4.4084 | 86.148 | -75 | -3.9368 | 100.1638 | -31.5608 | 20.4392 | 6.4789 | 6.4789 | 0 | 0 | 0 | 4/2/8:00
4 | 2 | 1900-01-08 | 0 | 123 | 530 | 32 | 1 | 0 | 32 | 0 | 0 | 123 | 0 | 0 | 39.791 | 92.3333 | 4.4245 | 86.148 | -75 | -3.9238 | 115.1671 | -146.5004 | -23.5004 | -7.4492 | -7.4492 | 0 | 0 | 0 | 4/2/9:00
4 | 2 | 1900-01-09 | 0.6 | 248 | 416 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 248 | 0 | 0 | 39.791 | 92.375 | 4.4406 | 86.148 | -75 | -3.9107 | 130.1703 | -184.9602 | 63.0398 | 19.9825 | 19.9825 | 0 | 0 | 0 | 4/2/10:00
4 | 2 | 1900-01-10 | 2.2 | 286 | 125 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 286 | 0 | 0 | 39.791 | 92.4167 | 4.4567 | 86.148 | -75 | -3.8976 | 145.1736 | -72.3897 | 213.6103 | 67.7107 | 67.7107 | 0 | 0 | 0 | 4/2/11:00
4 | 2 | 1900-01-11 | 2.8 | 411 | 340 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 411 | 0 | 0 | 39.791 | 92.4583 | 4.4728 | 86.148 | -75 | -3.8845 | 160.1769 | -228.052 | 182.948 | 57.9913 | 57.9913 | 0 | 0 | 0 | 4/2/12:00
4 | 2 | 1900-01-12 | 2.8 | 373 | 51 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 373 | 0 | 0 | 39.791 | 92.5 | 4.4889 | 86.148 | -75 | -3.8714 | 175.1801 | -36.3747 | 336.6253 | 106.7043 | 106.7043 | 0 | 0 | 0 | 4/2/13:00
4 | 2 | 1900-01-13 | 2.8 | 327 | 5 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 327 | 0 | 0 | 39.791 | 92.5417 | 4.505 | 86.148 | -75 | -3.8584 | 190.1834 | -3.5184 | 323.4816 | 102.538 | 102.538 | 0 | 0 | 0 | 4/2/14:00
4 | 2 | 1900-01-14 | 2.8 | 249 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 249 | 0 | 0 | 39.791 | 92.5833 | 4.521 | 86.148 | -75 | -3.8453 | 205.1867 | 0 | 249 | 78.9287 | 78.9287 | 0 | 0 | 0 | 4/2/15:00
4 | 2 | 1900-01-15 | 2.8 | 324 | 99 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 324 | 0 | 0 | 39.791 | 92.625 | 4.5371 | 86.148 | -75 | -3.8322 | 220.1899 | -52.9165 | 271.0835 | 85.9287 | 85.9287 | 0 | 0 | 0 | 4/2/16:00
4 | 2 | 1900-01-16 | 2.8 | 246 | 5 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 246 | 0 | 0 | 39.791 | 92.6667 | 4.5532 | 86.148 | -75 | -3.8192 | 235.1932 | -1.9321 | 244.0679 | 77.3653 | 77.3653 | 0 | 0 | 0 | 4/2/17:00
4 | 2 | 1900-01-17 | 2.2 | 77 | 6 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 77 | 0 | 0 | 39.791 | 92.7083 | 4.5693 | 86.148 | -75 | -3.8061 | 250.1965 | -1.2511 | 75.7489 | 24.0111 | 24.0111 | 0 | 0 | 0 | 4/2/18:00
4 | 2 | 1900-01-18 | 1.7 | 38 | 35 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 38 | 0 | 0 | 39.791 | 92.75 | 4.5854 | 86.148 | -75 | -3.7931 | 265.1997 | -0.45259 | 37.5474 | 11.9019 | 11.9019 | 0 | 0 | 0 | 4/2/19:00
4 | 2 | 1900-01-19 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.7917 | 4.6014 | 86.148 | -75 | -3.78 | 280.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/20:00
4 | 2 | 1900-01-20 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.8333 | 4.6175 | 86.148 | -75 | -3.767 | 295.2062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/21:00
4 | 2 | 1900-01-21 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.875 | 4.6336 | 86.148 | -75 | -3.754 | 310.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/22:00
4 | 2 | 1900-01-22 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.9167 | 4.6496 | 86.148 | -75 | -3.7409 | 325.2128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/23:00
4 | 2 | 1900-01-23 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 92.9583 | 4.6657 | 86.148 | -75 | -3.7279 | 340.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/2/24:00
4 | 3 | 1899-12-31 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93 | 4.6818 | 86.148 | -75 | -3.7149 | -4.7807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/1:00
4 | 3 | 1900-01-01 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.0417 | 4.6978 | 86.148 | -75 | -3.7019 | 10.2225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/2:00
4 | 3 | 1900-01-02 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.0833 | 4.7139 | 86.148 | -75 | -3.6888 | 25.2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/3:00
4 | 3 | 1900-01-03 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.125 | 4.7299 | 86.148 | -75 | -3.6758 | 40.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/4:00
4 | 3 | 1900-01-04 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.1667 | 4.746 | 86.148 | -75 | -3.6628 | 55.2323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/5:00
4 | 3 | 1900-01-05 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.2083 | 4.762 | 86.148 | -75 | -3.6498 | 70.2355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/6:00
4 | 3 | 1900-01-06 | -5.6 | 12 | 44 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 12 | 0 | 0 | 39.791 | 93.25 | 4.7781 | 86.148 | -75 | -3.6368 | 85.2388 | 5.1421 | 17.1421 | 5.4337 | 5.4337 | 0 | 0 | 0 | 4/3/7:00
4 | 3 | 1900-01-07 | -1.7 | 44 | 467 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 44 | 0 | 0 | 39.791 | 93.2917 | 4.7941 | 86.148 | -75 | -3.6238 | 100.242 | -38.6015 | 5.3985 | 1.7112 | 1.7112 | 0 | 0 | 0 | 4/3/8:00
4 | 3 | 1900-01-08 | 0 | 96 | 622 | 32 | 1 | 0 | 32 | 0 | 0 | 96 | 0 | 0 | 39.791 | 93.3333 | 4.8102 | 86.148 | -75 | -3.6108 | 115.2453 | -169.7384 | -73.7384 | -23.3738 | -23.3738 | 0 | 0 | 0 | 4/3/9:00
4 | 3 | 1900-01-09 | 0.6 | 236 | 230 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 236 | 0 | 0 | 39.791 | 93.375 | 4.8262 | 86.148 | -75 | -3.5979 | 130.2485 | -101.3959 | 134.6041 | 42.6672 | 42.6672 | 0 | 0 | 0 | 4/3/10:00
4 | 3 | 1900-01-10 | 1.1 | 326 | 10 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 326 | 0 | 0 | 39.791 | 93.4167 | 4.8422 | 86.148 | -75 | -3.5849 | 145.2518 | -5.7508 | 320.2492 | 101.5134 | 101.5134 | 0 | 0 | 0 | 4/3/11:00
4 | 3 | 1900-01-11 | 2.8 | 344 | 1 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 344 | 0 | 0 | 39.791 | 93.4583 | 4.8583 | 86.148 | -75 | -3.5719 | 160.255 | -0.66641 | 343.3336 | 108.8308 | 108.8308 | 0 | 0 | 0 | 4/3/12:00
4 | 3 | 1900-01-12 | 2.8 | 360 | 9 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 360 | 0 | 0 | 39.791 | 93.5 | 4.8743 | 86.148 | -75 | -3.5589 | 175.2583 | -6.3774 | 353.6226 | 112.0922 | 112.0922 | 0 | 0 | 0 | 4/3/13:00
4 | 3 | 1900-01-13 | 2.8 | 310 | 3 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 310 | 0 | 0 | 39.791 | 93.5417 | 4.8904 | 86.148 | -75 | -3.546 | 190.2615 | -2.0963 | 307.9037 | 97.6001 | 97.6001 | 0 | 0 | 0 | 4/3/14:00
4 | 3 | 1900-01-14 | 2.2 | 281 | 6 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 281 | 0 | 0 | 39.791 | 93.5833 | 4.9064 | 86.148 | -75 | -3.533 | 205.2648 | -3.8256 | 277.1744 | 87.8594 | 87.8594 | 0 | 0 | 0 | 4/3/15:00
4 | 3 | 1900-01-15 | 1.7 | 249 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 249 | 0 | 0 | 39.791 | 93.625 | 4.9224 | 86.148 | -75 | -3.52 | 220.268 | 0 | 249 | 78.9287 | 78.9287 | 0 | 0 | 0 | 4/3/16:00
4 | 3 | 1900-01-16 | 2.8 | 176 | 116 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 176 | 0 | 0 | 39.791 | 93.6667 | 4.9384 | 86.148 | -75 | -3.5071 | 235.2712 | -44.1988 | 131.8012 | 41.7787 | 41.7787 | 0 | 0 | 0 | 4/3/17:00
4 | 3 | 1900-01-17 | 2.8 | 122 | 67 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 122 | 0 | 0 | 39.791 | 93.7083 | 4.9545 | 86.148 | -75 | -3.4941 | 250.2745 | -13.6077 | 108.3923 | 34.3585 | 34.3585 | 0 | 0 | 0 | 4/3/18:00
4 | 3 | 1900-01-18 | 1.7 | 40 | 100 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 40 | 0 | 0 | 39.791 | 93.75 | 4.9705 | 86.148 | -75 | -3.4812 | 265.2777 | -0.757 | 39.243 | 12.4393 | 12.4393 | 0 | 0 | 0 | 4/3/19:00
4 | 3 | 1900-01-19 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.7917 | 4.9865 | 86.148 | -75 | -3.4683 | 280.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/20:00
4 | 3 | 1900-01-20 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.8333 | 5.0025 | 86.148 | -75 | -3.4553 | 295.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/21:00
4 | 3 | 1900-01-21 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.875 | 5.0185 | 86.148 | -75 | -3.4424 | 310.2874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/22:00
4 | 3 | 1900-01-22 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.9167 | 5.0346 | 86.148 | -75 | -3.4295 | 325.2906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/23:00
4 | 3 | 1900-01-23 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 93.9583 | 5.0506 | 86.148 | -75 | -3.4165 | 340.2939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/3/24:00
4 | 4 | 1899-12-31 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94 | 5.0666 | 86.148 | -75 | -3.4036 | -4.7029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/1:00
4 | 4 | 1900-01-01 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.0417 | 5.0826 | 86.148 | -75 | -3.3907 | 10.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/2:00
4 | 4 | 1900-01-02 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.0833 | 5.0986 | 86.148 | -75 | -3.3778 | 25.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/3:00
4 | 4 | 1900-01-03 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.125 | 5.1146 | 86.148 | -75 | -3.3649 | 40.3068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/4:00
4 | 4 | 1900-01-04 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.1667 | 5.1306 | 86.148 | -75 | -3.352 | 55.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/5:00
4 | 4 | 1900-01-05 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.2083 | 5.1466 | 86.148 | -75 | -3.3391 | 70.3132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/6:00
4 | 4 | 1900-01-06 | -1.7 | 10 | 1 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 10 | 0 | 0 | 39.791 | 94.25 | 5.1626 | 86.148 | -75 | -3.3262 | 85.3164 | 0.12007 | 10.1201 | 3.2079 | 3.2079 | 0 | 0 | 0 | 4/4/7:00
4 | 4 | 1900-01-07 | -1.1 | 82 | 48 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 82 | 0 | 0 | 39.791 | 94.2917 | 5.1786 | 86.148 | -75 | -3.3133 | 100.3197 | -3.8074 | 78.1926 | 24.7857 | 24.7857 | 0 | 0 | 0 | 4/4/8:00
4 | 4 | 1900-01-08 | 0 | 150 | 25 | 32 | 1 | 0 | 32 | 0 | 0 | 150 | 0 | 0 | 39.791 | 94.3333 | 5.1946 | 86.148 | -75 | -3.3005 | 115.3229 | -6.734 | 143.266 | 45.4128 | 45.4128 | 0 | 0 | 0 | 4/4/9:00
4 | 4 | 1900-01-09 | 1.1 | 301 | 295 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 301 | 0 | 0 | 39.791 | 94.375 | 5.2106 | 86.148 | -75 | -3.2876 | 130.3261 | -128.9367 | 172.0633 | 54.5411 | 54.5411 | 0 | 0 | 0 | 4/4/10:00
4 | 4 | 1900-01-10 | 1.7 | 341 | 88 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 341 | 0 | 0 | 39.791 | 94.4167 | 5.2266 | 86.148 | -75 | -3.2747 | 145.3293 | -50.2497 | 290.7503 | 92.1628 | 92.1628 | 0 | 0 | 0 | 4/4/11:00
4 | 4 | 1900-01-11 | 3.3 | 241 | 612 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 241 | 0 | 0 | 39.791 | 94.4583 | 5.2425 | 86.148 | -75 | -3.2619 | 160.3325 | -405.1771 | -164.1771 | -52.0413 | -52.0413 | 0 | 0 | 0 | 4/4/12:00
4 | 4 | 1900-01-12 | 3.9 | 337 | 351 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 337 | 0 | 0 | 39.791 | 94.5 | 5.2585 | 86.148 | -75 | -3.249 | 175.3357 | -247.0904 | 89.9096 | 28.4998 | 28.4998 | 0 | 0 | 0 | 4/4/13:00
4 | 4 | 1900-01-13 | 6.7 | 260 | 543 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 260 | 0 | 0 | 39.791 | 94.5417 | 5.2745 | 86.148 | -75 | -3.2362 | 190.339 | -376.7739 | -116.7739 | -37.0153 | -37.0153 | 0 | 0 | 0 | 4/4/14:00
4 | 4 | 1900-01-14 | 7.8 | 253 | 518 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 253 | 0 | 0 | 39.791 | 94.5833 | 5.2905 | 86.148 | -75 | -3.2233 | 205.3422 | -327.6205 | -74.6205 | -23.6534 | -23.6534 | 0 | 0 | 0 | 4/4/15:00
4 | 4 | 1900-01-15 | 8.3 | 208 | 705 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 208 | 0 | 0 | 39.791 | 94.625 | 5.3065 | 86.148 | -75 | -3.2105 | 220.3454 | -369.371 | -161.371 | -51.1518 | -51.1518 | 0 | 0 | 0 | 4/4/16:00
4 | 4 | 1900-01-16 | 7.8 | 151 | 546 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 151 | 0 | 0 | 39.791 | 94.6667 | 5.3224 | 86.148 | -75 | -3.1976 | 235.3486 | -205.0995 | -54.0995 | -17.1486 | -17.1486 | 0 | 0 | 0 | 4/4/17:00
4 | 4 | 1900-01-17 | 6.7 | 101 | 513 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 101 | 0 | 0 | 39.791 | 94.7083 | 5.3384 | 86.148 | -75 | -3.1848 | 250.3518 | -101.4204 | -0.4204 | -0.13326 | -0.13326 | 0 | 0 | 0 | 4/4/18:00
4 | 4 | 1900-01-18 | 5 | 52 | 107 | 41 | 1 | 0 | 41 | 0 | 0 | 52 | 0 | 0 | 39.791 | 94.75 | 5.3544 | 86.148 | -75 | -3.172 | 265.355 | -0.23889 | 51.7611 | 16.4074 | 16.4074 | 0 | 0 | 0 | 4/4/19:00
4 | 4 | 1900-01-19 | 3.9 | 0 | 1 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.7917 | 5.3703 | 86.148 | -75 | -3.1592 | 280.3582 | 0.19745 | 0.19745 | 0.062588 | 0.062588 | 0 | 0 | 0 | 4/4/20:00
4 | 4 | 1900-01-20 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.8333 | 5.3863 | 86.148 | -75 | -3.1464 | 295.3614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/21:00
4 | 4 | 1900-01-21 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.875 | 5.4023 | 86.148 | -75 | -3.1335 | 310.3646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/22:00
4 | 4 | 1900-01-22 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.9167 | 5.4182 | 86.148 | -75 | -3.1207 | 325.3678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/23:00
4 | 4 | 1900-01-23 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 94.9583 | 5.4342 | 86.148 | -75 | -3.1079 | 340.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/4/24:00
4 | 5 | 1899-12-31 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95 | 5.4501 | 86.148 | -75 | -3.0952 | -4.6258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/1:00
4 | 5 | 1900-01-01 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95.0417 | 5.4661 | 86.148 | -75 | -3.0824 | 10.3774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/2:00
4 | 5 | 1900-01-02 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95.0833 | 5.482 | 86.148 | -75 | -3.0696 | 25.3806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/3:00
4 | 5 | 1900-01-03 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95.125 | 5.498 | 86.148 | -75 | -3.0568 | 40.3838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/4:00
4 | 5 | 1900-01-04 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95.1667 | 5.5139 | 86.148 | -75 | -3.044 | 55.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/5:00
4 | 5 | 1900-01-05 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95.2083 | 5.5299 | 86.148 | -75 | -3.0313 | 70.3902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/6:00
4 | 5 | 1900-01-06 | 3.9 | 14 | 3 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 14 | 0 | 0 | 39.791 | 95.25 | 5.5458 | 86.148 | -75 | -3.0185 | 85.3934 | 0.36982 | 14.3698 | 4.555 | 4.555 | 0 | 0 | 0 | 4/5/7:00
4 | 5 | 1900-01-07 | 4.4 | 71 | 5 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 71 | 0 | 0 | 39.791 | 95.2917 | 5.5618 | 86.148 | -75 | -3.0058 | 100.3966 | -0.37992 | 70.6201 | 22.3853 | 22.3853 | 0 | 0 | 0 | 4/5/8:00
4 | 5 | 1900-01-08 | 5.6 | 177 | 8 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 177 | 0 | 0 | 39.791 | 95.3333 | 5.5777 | 86.148 | -75 | -2.993 | 115.3997 | -2.1266 | 174.8734 | 55.4318 | 55.4318 | 0 | 0 | 0 | 4/5/9:00
4 | 5 | 1900-01-09 | 5.6 | 212 | 10 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 212 | 0 | 0 | 39.791 | 95.375 | 5.5936 | 86.148 | -75 | -2.9803 | 130.4029 | -4.3328 | 207.6672 | 65.8269 | 65.8269 | 0 | 0 | 0 | 4/5/10:00
4 | 5 | 1900-01-10 | 6.1 | 307 | 4 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 307 | 0 | 0 | 39.791 | 95.4167 | 5.6096 | 86.148 | -75 | -2.9675 | 145.4061 | -2.2678 | 304.7322 | 96.5948 | 96.5948 | 0 | 0 | 0 | 4/5/11:00
4 | 5 | 1900-01-11 | 6.1 | 380 | 2 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 380 | 0 | 0 | 39.791 | 95.4583 | 5.6255 | 86.148 | -75 | -2.9548 | 160.4093 | -1.3154 | 378.6846 | 120.0364 | 120.0364 | 0 | 0 | 0 | 4/5/12:00
4 | 5 | 1900-01-12 | 7.2 | 397 | 1 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 397 | 0 | 0 | 39.791 | 95.5 | 5.6414 | 86.148 | -75 | -2.9421 | 175.4125 | -0.6993 | 396.3007 | 125.6204 | 125.6204 | 0 | 0 | 0 | 4/5/13:00
4 | 5 | 1900-01-13 | 8.3 | 350 | 4 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 350 | 0 | 0 | 39.791 | 95.5417 | 5.6573 | 86.148 | -75 | -2.9294 | 190.4157 | -2.7558 | 347.2442 | 110.0703 | 110.0703 | 0 | 0 | 0 | 4/5/14:00
4 | 5 | 1900-01-14 | 8.9 | 382 | 2 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 382 | 0 | 0 | 39.791 | 95.5833 | 5.6733 | 86.148 | -75 | -2.9166 | 205.4188 | -1.2547 | 380.7453 | 120.6896 | 120.6896 | 0 | 0 | 0 | 4/5/15:00
4 | 5 | 1900-01-15 | 10 | 306 | 157 | 50 | 1 | 0 | 50 | 0 | 0 | 306 | 0 | 0 | 39.791 | 95.625 | 5.6892 | 86.148 | -75 | -2.9039 | 220.422 | -81.4262 | 224.5738 | 71.186 | 71.186 | 0 | 0 | 0 | 4/5/16:00
4 | 5 | 1900-01-16 | 10.6 | 166 | 127 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 166 | 0 | 0 | 39.791 | 95.6667 | 5.7051 | 86.148 | -75 | -2.8912 | 235.4252 | -47.0235 | 118.9765 | 37.7135 | 37.7135 | 0 | 0 | 0 | 4/5/17:00
4 | 5 | 1900-01-17 | 10 | 130 | 53 | 50 | 1 | 0 | 50 | 0 | 0 | 130 | 0 | 0 | 39.791 | 95.7083 | 5.721 | 86.148 | -75 | -2.8785 | 250.4284 | -10.1929 | 119.8071 | 37.9768 | 37.9768 | 0 | 0 | 0 | 4/5/18:00
4 | 5 | 1900-01-18 | 9.4 | 47 | 12 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 47 | 0 | 0 | 39.791 | 95.75 | 5.7369 | 86.148 | -75 | -2.8658 | 265.4315 | 0.03694 | 47.0369 | 14.9099 | 14.9099 | 0 | 0 | 0 | 4/5/19:00
4 | 5 | 1900-01-19 | 8.9 | 2 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 2 | 0 | 0 | 39.791 | 95.7917 | 5.7528 | 86.148 | -75 | -2.8532 | 280.4347 | 0 | 2 | 0.63397 | 0.63397 | 0 | 0 | 0 | 4/5/20:00
4 | 5 | 1900-01-20 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95.8333 | 5.7687 | 86.148 | -75 | -2.8405 | 295.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/21:00
4 | 5 | 1900-01-21 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95.875 | 5.7846 | 86.148 | -75 | -2.8278 | 310.441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/22:00
4 | 5 | 1900-01-22 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95.9167 | 5.8005 | 86.148 | -75 | -2.8151 | 325.4442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/23:00
4 | 5 | 1900-01-23 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 95.9583 | 5.8164 | 86.148 | -75 | -2.8025 | 340.4474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/5/24:00
4 | 6 | 1899-12-31 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96 | 5.8323 | 86.148 | -75 | -2.7898 | -4.5495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/1:00
4 | 6 | 1900-01-01 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96.0417 | 5.8482 | 86.148 | -75 | -2.7772 | 10.4537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/2:00
4 | 6 | 1900-01-02 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96.0833 | 5.8641 | 86.148 | -75 | -2.7645 | 25.4569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/3:00
4 | 6 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96.125 | 5.88 | 86.148 | -75 | -2.7519 | 40.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/4:00
4 | 6 | 1900-01-04 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96.1667 | 5.8959 | 86.148 | -75 | -2.7393 | 55.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/5:00
4 | 6 | 1900-01-05 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96.2083 | 5.9118 | 86.148 | -75 | -2.7267 | 70.4663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/6:00
4 | 6 | 1900-01-06 | 5.6 | 13 | 1 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 13 | 0 | 0 | 39.791 | 96.25 | 5.9276 | 86.148 | -75 | -2.714 | 85.4695 | 0.12646 | 13.1265 | 4.1609 | 4.1609 | 0 | 0 | 0 | 4/6/7:00
4 | 6 | 1900-01-07 | 5.6 | 79 | 3 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 79 | 0 | 0 | 39.791 | 96.2917 | 5.9435 | 86.148 | -75 | -2.7014 | 100.4726 | -0.21794 | 78.7821 | 24.9725 | 24.9725 | 0 | 0 | 0 | 4/6/8:00
4 | 6 | 1900-01-08 | 6.1 | 140 | 6 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 140 | 0 | 0 | 39.791 | 96.3333 | 5.9594 | 86.148 | -75 | -2.6888 | 115.4758 | -1.5736 | 138.4264 | 43.8787 | 43.8787 | 0 | 0 | 0 | 4/6/9:00
4 | 6 | 1900-01-09 | 6.7 | 149 | 2 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 149 | 0 | 0 | 39.791 | 96.375 | 5.9753 | 86.148 | -75 | -2.6762 | 130.4789 | -0.85896 | 148.141 | 46.9581 | 46.9581 | 0 | 0 | 0 | 4/6/10:00
4 | 6 | 1900-01-10 | 7.8 | 168 | 7 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 168 | 0 | 0 | 39.791 | 96.4167 | 5.9911 | 86.148 | -75 | -2.6636 | 145.4821 | -3.94 | 164.06 | 52.0042 | 52.0042 | 0 | 0 | 0 | 4/6/11:00
4 | 6 | 1900-01-11 | 7.8 | 190 | 4 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 190 | 0 | 0 | 39.791 | 96.4583 | 6.007 | 86.148 | -75 | -2.651 | 160.4852 | -2.6132 | 187.3868 | 59.3984 | 59.3984 | 0 | 0 | 0 | 4/6/12:00
4 | 6 | 1900-01-12 | 8.9 | 389 | 4 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 389 | 0 | 0 | 39.791 | 96.5 | 6.0229 | 86.148 | -75 | -2.6385 | 175.4884 | -2.7785 | 386.2215 | 122.4255 | 122.4255 | 0 | 0 | 0 | 4/6/13:00
4 | 6 | 1900-01-13 | 8.9 | 214 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 214 | 0 | 0 | 39.791 | 96.5417 | 6.0387 | 86.148 | -75 | -2.6259 | 190.4915 | 0 | 214 | 67.8343 | 67.8343 | 0 | 0 | 0 | 4/6/14:00
4 | 6 | 1900-01-14 | 10 | 384 | 2 | 50 | 1 | 0 | 50 | 0 | 0 | 384 | 0 | 0 | 39.791 | 96.5833 | 6.0546 | 86.148 | -75 | -2.6133 | 205.4947 | -1.2444 | 382.7556 | 121.3268 | 121.3268 | 0 | 0 | 0 | 4/6/15:00
4 | 6 | 1900-01-15 | 10 | 338 | 1 | 50 | 1 | 0 | 50 | 0 | 0 | 338 | 0 | 0 | 39.791 | 96.625 | 6.0704 | 86.148 | -75 | -2.6008 | 220.4978 | -0.51335 | 337.4867 | 106.9774 | 106.9774 | 0 | 0 | 0 | 4/6/16:00
4 | 6 | 1900-01-16 | 10.6 | 248 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 248 | 0 | 0 | 39.791 | 96.6667 | 6.0863 | 86.148 | -75 | -2.5882 | 235.5009 | 0 | 248 | 78.6117 | 78.6117 | 0 | 0 | 0 | 4/6/17:00
4 | 6 | 1900-01-17 | 10 | 132 | 1 | 50 | 1 | 0 | 50 | 0 | 0 | 132 | 0 | 0 | 39.791 | 96.7083 | 6.1021 | 86.148 | -75 | -2.5757 | 250.5041 | -0.18696 | 131.813 | 41.7824 | 41.7824 | 0 | 0 | 0 | 4/6/18:00
4 | 6 | 1900-01-18 | 9.4 | 48 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 48 | 0 | 0 | 39.791 | 96.75 | 6.118 | 86.148 | -75 | -2.5631 | 265.5072 | 0.0083603 | 48.0084 | 15.2178 | 15.2178 | 0 | 0 | 0 | 4/6/19:00
4 | 6 | 1900-01-19 | 8.9 | 3 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 3 | 0 | 0 | 39.791 | 96.7917 | 6.1338 | 86.148 | -75 | -2.5506 | 280.5104 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 4/6/20:00
4 | 6 | 1900-01-20 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96.8333 | 6.1497 | 86.148 | -75 | -2.5381 | 295.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/21:00
4 | 6 | 1900-01-21 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96.875 | 6.1655 | 86.148 | -75 | -2.5255 | 310.5166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/22:00
4 | 6 | 1900-01-22 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96.9167 | 6.1814 | 86.148 | -75 | -2.513 | 325.5197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/23:00
4 | 6 | 1900-01-23 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 96.9583 | 6.1972 | 86.148 | -75 | -2.5005 | 340.5229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/6/24:00
4 | 7 | 1899-12-31 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97 | 6.213 | 86.148 | -75 | -2.488 | -4.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/1:00
4 | 7 | 1900-01-01 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97.0417 | 6.2289 | 86.148 | -75 | -2.4755 | 10.5291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/2:00
4 | 7 | 1900-01-02 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97.0833 | 6.2447 | 86.148 | -75 | -2.463 | 25.5322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/3:00
4 | 7 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97.125 | 6.2605 | 86.148 | -75 | -2.4505 | 40.5354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/4:00
4 | 7 | 1900-01-04 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97.1667 | 6.2763 | 86.148 | -75 | -2.4381 | 55.5385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/5:00
4 | 7 | 1900-01-05 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97.2083 | 6.2921 | 86.148 | -75 | -2.4256 | 70.5416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/6:00
4 | 7 | 1900-01-06 | 6.1 | 16 | 5 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 16 | 0 | 0 | 39.791 | 97.25 | 6.308 | 86.148 | -75 | -2.4131 | 85.5447 | 0.64822 | 16.6482 | 5.2772 | 5.2772 | 0 | 0 | 0 | 4/7/7:00
4 | 7 | 1900-01-07 | 8.3 | 80 | 73 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 80 | 0 | 0 | 39.791 | 97.2917 | 6.3238 | 86.148 | -75 | -2.4007 | 100.5478 | -5.0596 | 74.9404 | 23.7548 | 23.7548 | 0 | 0 | 0 | 4/7/8:00
4 | 7 | 1900-01-08 | 10 | 142 | 71 | 50 | 1 | 0 | 50 | 0 | 0 | 142 | 0 | 0 | 39.791 | 97.3333 | 6.3396 | 86.148 | -75 | -2.3882 | 115.5509 | -18.3691 | 123.6309 | 39.1888 | 39.1888 | 0 | 0 | 0 | 4/7/9:00
4 | 7 | 1900-01-09 | 11.7 | 272 | 202 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 272 | 0 | 0 | 39.791 | 97.375 | 6.3554 | 86.148 | -75 | -2.3758 | 130.554 | -85.9838 | 186.0162 | 58.9639 | 58.9639 | 0 | 0 | 0 | 4/7/10:00
4 | 7 | 1900-01-10 | 13.3 | 267 | 558 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 267 | 0 | 0 | 39.791 | 97.4167 | 6.3712 | 86.148 | -75 | -2.3634 | 145.5572 | -311.7805 | -44.7805 | -14.1946 | 0 | -14.1946 | 55.94 | -14.1946 | 4/7/11:00
4 | 7 | 1900-01-11 | 16.1 | 311 | 510 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 311 | 0 | 0 | 39.791 | 97.4583 | 6.387 | 86.148 | -75 | -2.3509 | 160.5603 | -330.933 | -19.933 | -6.3184 | 0 | -6.3184 | 60.98 | -6.3184 | 4/7/12:00
4 | 7 | 1900-01-12 | 17.2 | 357 | 448 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 357 | 0 | 0 | 39.791 | 97.5 | 6.4028 | 86.148 | -75 | -2.3385 | 175.5634 | -309.0901 | 47.9099 | 15.1866 | 0 | 15.1866 | 62.96 | 15.1866 | 4/7/13:00
4 | 7 | 1900-01-13 | 18.9 | 377 | 146 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 377 | 0 | 0 | 39.791 | 97.5417 | 6.4186 | 86.148 | -75 | -2.3261 | 190.5665 | -99.1449 | 277.8551 | 88.0752 | 0 | 88.0752 | 66.02 | 88.0752 | 4/7/14:00
4 | 7 | 1900-01-14 | 19.4 | 271 | 469 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 271 | 0 | 0 | 39.791 | 97.5833 | 6.4344 | 86.148 | -75 | -2.3137 | 205.5696 | -289.3933 | -18.3933 | -5.8304 | 0 | -5.8304 | 66.92 | -5.8304 | 4/7/15:00
4 | 7 | 1900-01-15 | 20 | 242 | 468 | 68 | 0 | 1 | 0 | 68 | 0 | 242 | 0 | 0 | 39.791 | 97.625 | 6.4502 | 86.148 | -75 | -2.3013 | 220.5727 | -237.7721 | 4.2279 | 1.3402 | 0 | 1.3402 | 68 | 1.3402 | 4/7/16:00
4 | 7 | 1900-01-16 | 20 | 124 | 633 | 68 | 0 | 1 | 0 | 68 | 0 | 124 | 0 | 0 | 39.791 | 97.6667 | 6.466 | 86.148 | -75 | -2.2889 | 235.5758 | -227.5923 | -103.5923 | -32.837 | 0 | -32.837 | 68 | -32.837 | 4/7/17:00
4 | 7 | 1900-01-17 | 18.9 | 87 | 496 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 87 | 0 | 0 | 39.791 | 97.7083 | 6.4817 | 86.148 | -75 | -2.2765 | 250.5789 | -90.0812 | -3.0812 | -0.97668 | 0 | -0.97668 | 66.02 | -0.97668 | 4/7/18:00
4 | 7 | 1900-01-18 | 17.2 | 44 | 177 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 44 | 0 | 0 | 39.791 | 97.75 | 6.4975 | 86.148 | -75 | -2.2642 | 265.582 | 2.4091 | 46.4091 | 14.7109 | 0 | 14.7109 | 62.96 | 14.7109 | 4/7/19:00
4 | 7 | 1900-01-19 | 15 | 3 | 1 | 59 | 0 | 1 | 0 | 59 | 0 | 3 | 0 | 0 | 39.791 | 97.7917 | 6.5133 | 86.148 | -75 | -2.2518 | 280.5851 | 0.21283 | 3.2128 | 1.0184 | 0 | 1.0184 | 59 | 1.0184 | 4/7/20:00
4 | 7 | 1900-01-20 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97.8333 | 6.5291 | 86.148 | -75 | -2.2394 | 295.5881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/21:00
4 | 7 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97.875 | 6.5449 | 86.148 | -75 | -2.2271 | 310.5912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/22:00
4 | 7 | 1900-01-22 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97.9167 | 6.5606 | 86.148 | -75 | -2.2147 | 325.5943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/23:00
4 | 7 | 1900-01-23 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 97.9583 | 6.5764 | 86.148 | -75 | -2.2024 | 340.5974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/7/24:00
4 | 8 | 1899-12-31 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98 | 6.5922 | 86.148 | -75 | -2.1901 | -4.3995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/1:00
4 | 8 | 1900-01-01 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98.0417 | 6.6079 | 86.148 | -75 | -2.1777 | 10.6036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/2:00
4 | 8 | 1900-01-02 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98.0833 | 6.6237 | 86.148 | -75 | -2.1654 | 25.6066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/3:00
4 | 8 | 1900-01-03 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98.125 | 6.6394 | 86.148 | -75 | -2.1531 | 40.6097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/4:00
4 | 8 | 1900-01-04 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98.1667 | 6.6552 | 86.148 | -75 | -2.1408 | 55.6128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/5:00
4 | 8 | 1900-01-05 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98.2083 | 6.6709 | 86.148 | -75 | -2.1285 | 70.6159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/6:00
4 | 8 | 1900-01-06 | 1.1 | 19 | 30 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 19 | 0 | 0 | 39.791 | 98.25 | 6.6867 | 86.148 | -75 | -2.1162 | 85.6189 | 3.9845 | 22.9845 | 7.2857 | 7.2857 | 0 | 0 | 0 | 4/8/7:00
4 | 8 | 1900-01-07 | 3.3 | 62 | 360 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 62 | 0 | 0 | 39.791 | 98.2917 | 6.7024 | 86.148 | -75 | -2.1039 | 100.622 | -23.7502 | 38.2498 | 12.1245 | 12.1245 | 0 | 0 | 0 | 4/8/8:00
4 | 8 | 1900-01-08 | 6.1 | 99 | 599 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 99 | 0 | 0 | 39.791 | 98.3333 | 6.7182 | 86.148 | -75 | -2.0916 | 115.6251 | -152.8408 | -53.8408 | -17.0666 | -17.0666 | 0 | 0 | 0 | 4/8/9:00
4 | 8 | 1900-01-09 | 9.4 | 130 | 716 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 130 | 0 | 0 | 39.791 | 98.375 | 6.7339 | 86.148 | -75 | -2.0794 | 130.6282 | -302.0342 | -172.0342 | -54.5318 | -54.5318 | 0 | 0 | 0 | 4/8/10:00
4 | 8 | 1900-01-10 | 12.2 | 151 | 788 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 151 | 0 | 0 | 39.791 | 98.4167 | 6.7496 | 86.148 | -75 | -2.0671 | 145.6312 | -437.0453 | -286.0453 | -90.6714 | -90.6714 | 0 | 0 | 0 | 4/8/11:00
4 | 8 | 1900-01-11 | 14.4 | 164 | 827 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 164 | 0 | 0 | 39.791 | 98.4583 | 6.7654 | 86.148 | -75 | -2.0549 | 160.6343 | -532.9759 | -368.9759 | -116.9589 | 0 | -116.9589 | 57.92 | -116.9589 | 4/8/12:00
4 | 8 | 1900-01-12 | 15.6 | 170 | 842 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 170 | 0 | 0 | 39.791 | 98.5 | 6.7811 | 86.148 | -75 | -2.0426 | 175.6373 | -576.964 | -406.964 | -129.0005 | 0 | -129.0005 | 60.08 | -129.0005 | 4/8/13:00
4 | 8 | 1900-01-13 | 16.1 | 169 | 837 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 169 | 0 | 0 | 39.791 | 98.5417 | 6.7968 | 86.148 | -75 | -2.0304 | 190.6404 | -564.2406 | -395.2406 | -125.2844 | 0 | -125.2844 | 60.98 | -125.2844 | 4/8/14:00
4 | 8 | 1900-01-14 | 17.2 | 160 | 817 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 160 | 0 | 0 | 39.791 | 98.5833 | 6.8126 | 86.148 | -75 | -2.0182 | 205.6435 | -499.9178 | -339.9178 | -107.748 | 0 | -107.748 | 62.96 | -107.748 | 4/8/15:00
4 | 8 | 1900-01-15 | 17.2 | 143 | 772 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 143 | 0 | 0 | 39.791 | 98.625 | 6.8283 | 86.148 | -75 | -2.0059 | 220.6465 | -388.1459 | -245.1459 | -77.707 | 0 | -77.707 | 62.96 | -77.707 | 4/8/16:00
4 | 8 | 1900-01-16 | 17.8 | 118 | 684 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 118 | 0 | 0 | 39.791 | 98.6667 | 6.844 | 86.148 | -75 | -1.9937 | 235.6496 | -242.2786 | -124.2786 | -39.3941 | 0 | -39.3941 | 64.04 | -39.3941 | 4/8/17:00
4 | 8 | 1900-01-17 | 16.7 | 84 | 523 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 84 | 0 | 0 | 39.791 | 98.7083 | 6.8597 | 86.148 | -75 | -1.9815 | 250.6526 | -92.2049 | -8.2049 | -2.6008 | 0 | -2.6008 | 62.06 | -2.6008 | 4/8/18:00
4 | 8 | 1900-01-18 | 14.4 | 44 | 202 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 44 | 0 | 0 | 39.791 | 98.75 | 6.8754 | 86.148 | -75 | -1.9693 | 265.6557 | 3.803 | 47.803 | 15.1527 | 0 | 15.1527 | 57.92 | 15.1527 | 4/8/19:00
4 | 8 | 1900-01-19 | 12.8 | 3 | 1 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 3 | 0 | 0 | 39.791 | 98.7917 | 6.8911 | 86.148 | -75 | -1.9571 | 280.6587 | 0.21788 | 3.2179 | 1.02 | 0 | 1.02 | 55.04 | 1.02 | 4/8/20:00
4 | 8 | 1900-01-20 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98.8333 | 6.9068 | 86.148 | -75 | -1.9449 | 295.6618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/21:00
4 | 8 | 1900-01-21 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98.875 | 6.9225 | 86.148 | -75 | -1.9328 | 310.6648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/22:00
4 | 8 | 1900-01-22 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98.9167 | 6.9382 | 86.148 | -75 | -1.9206 | 325.6679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/23:00
4 | 8 | 1900-01-23 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 98.9583 | 6.9539 | 86.148 | -75 | -1.9084 | 340.6709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/8/24:00
4 | 9 | 1899-12-31 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 99 | 6.9696 | 86.148 | -75 | -1.8963 | -4.3261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/9/1:00
4 | 9 | 1900-01-01 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 99.0417 | 6.9853 | 86.148 | -75 | -1.8841 | 10.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/9/2:00
4 | 9 | 1900-01-02 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 99.0833 | 7.001 | 86.148 | -75 | -1.872 | 25.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/9/3:00
4 | 9 | 1900-01-03 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 99.125 | 7.0167 | 86.148 | -75 | -1.8599 | 40.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/9/4:00
4 | 9 | 1900-01-04 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 99.1667 | 7.0324 | 86.148 | -75 | -1.8478 | 55.6861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/9/5:00
4 | 9 | 1900-01-05 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 99.2083 | 7.048 | 86.148 | -75 | -1.8356 | 70.6891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/9/6:00
4 | 9 | 1900-01-06 | 3.9 | 17 | 119 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 17 | 0 | 0 | 39.791 | 99.25 | 7.0637 | 86.148 | -75 | -1.8235 | 85.6921 | 16.1818 | 33.1818 | 10.518 | 10.518 | 0 | 0 | 0 | 4/9/7:00
4 | 9 | 1900-01-07 | 7.2 | 43 | 558 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 43 | 0 | 0 | 39.791 | 99.2917 | 7.0794 | 86.148 | -75 | -1.8114 | 100.6951 | -34.9515 | 8.0485 | 2.5512 | 2.5512 | 0 | 0 | 0 | 4/9/8:00
4 | 9 | 1900-01-08 | 10 | 64 | 759 | 50 | 1 | 0 | 50 | 0 | 0 | 64 | 0 | 0 | 39.791 | 99.3333 | 7.095 | 86.148 | -75 | -1.7994 | 115.6982 | -190.9602 | -126.9602 | -40.2442 | -40.2442 | 0 | 0 | 0 | 4/9/9:00
4 | 9 | 1900-01-09 | 12.2 | 82 | 851 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 82 | 0 | 0 | 39.791 | 99.375 | 7.1107 | 86.148 | -75 | -1.7873 | 130.7012 | -355.7162 | -273.7162 | -86.7632 | -86.7632 | 0 | 0 | 0 | 4/9/10:00
4 | 9 | 1900-01-10 | 13.9 | 95 | 905 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 95 | 0 | 0 | 39.791 | 99.4167 | 7.1264 | 86.148 | -75 | -1.7752 | 145.7042 | -498.196 | -403.196 | -127.8061 | 0 | -127.8061 | 57.02 | -127.8061 | 4/9/11:00
4 | 9 | 1900-01-11 | 15.6 | 103 | 934 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 103 | 0 | 0 | 39.791 | 99.4583 | 7.142 | 86.148 | -75 | -1.7631 | 160.7072 | -597.7946 | -494.7946 | -156.8412 | 0 | -156.8412 | 60.08 | -156.8412 | 4/9/12:00
4 | 9 | 1900-01-12 | 16.7 | 107 | 944 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 107 | 0 | 0 | 39.791 | 99.5 | 7.1577 | 86.148 | -75 | -1.7511 | 175.7102 | -642.4083 | -535.4083 | -169.7151 | 0 | -169.7151 | 62.06 | -169.7151 | 4/9/13:00
4 | 9 | 1900-01-13 | 17.8 | 106 | 943 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 106 | 0 | 0 | 39.791 | 99.5417 | 7.1733 | 86.148 | -75 | -1.739 | 190.7132 | -631.0228 | -525.0228 | -166.4231 | 0 | -166.4231 | 64.04 | -166.4231 | 4/9/14:00
4 | 9 | 1900-01-14 | 18.3 | 100 | 925 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 100 | 0 | 0 | 39.791 | 99.5833 | 7.189 | 86.148 | -75 | -1.727 | 205.7163 | -561.2407 | -461.2407 | -146.2052 | 0 | -146.2052 | 64.94 | -146.2052 | 4/9/15:00
4 | 9 | 1900-01-15 | 18.3 | 90 | 890 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 90 | 0 | 0 | 39.791 | 99.625 | 7.2046 | 86.148 | -75 | -1.715 | 220.7193 | -442.7826 | -352.7826 | -111.8259 | 0 | -111.8259 | 64.94 | -111.8259 | 4/9/16:00
4 | 9 | 1900-01-16 | 18.3 | 75 | 826 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 75 | 0 | 0 | 39.791 | 99.6667 | 7.2203 | 86.148 | -75 | -1.7029 | 235.7223 | -288.1827 | -213.1827 | -67.5752 | 0 | -67.5752 | 64.94 | -67.5752 | 4/9/17:00
4 | 9 | 1900-01-17 | 17.8 | 55 | 697 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 55 | 0 | 0 | 39.791 | 99.7083 | 7.2359 | 86.148 | -75 | -1.6909 | 250.7253 | -119.1955 | -64.1955 | -20.3489 | 0 | -20.3489 | 64.04 | -20.3489 | 4/9/18:00
4 | 9 | 1900-01-18 | 16.7 | 33 | 403 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 33 | 0 | 0 | 39.791 | 99.75 | 7.2516 | 86.148 | -75 | -1.6789 | 265.7283 | 9.6746 | 42.6746 | 13.5271 | 0 | 13.5271 | 62.06 | 13.5271 | 4/9/19:00
4 | 9 | 1900-01-19 | 15 | 5 | 17 | 59 | 0 | 1 | 0 | 59 | 0 | 5 | 0 | 0 | 39.791 | 99.7917 | 7.2672 | 86.148 | -75 | -1.6669 | 280.7313 | 3.789 | 8.789 | 2.786 | 0 | 2.786 | 59 | 2.786 | 4/9/20:00
4 | 9 | 1900-01-20 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 99.8333 | 7.2828 | 86.148 | -75 | -1.6549 | 295.7343 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 4/9/21:00
4 | 9 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 99.875 | 7.2984 | 86.148 | -75 | -1.643 | 310.7373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/9/22:00
4 | 9 | 1900-01-22 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 99.9167 | 7.3141 | 86.148 | -75 | -1.631 | 325.7403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/9/23:00
4 | 9 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 99.9583 | 7.3297 | 86.148 | -75 | -1.619 | 340.7432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/9/24:00
4 | 10 | 1899-12-31 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 100 | 7.3453 | 86.148 | -75 | -1.6071 | -4.2538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/10/1:00
4 | 10 | 1900-01-01 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 100.0417 | 7.3609 | 86.148 | -75 | -1.5951 | 10.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/10/2:00
4 | 10 | 1900-01-02 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 100.0833 | 7.3765 | 86.148 | -75 | -1.5832 | 25.7522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/10/3:00
4 | 10 | 1900-01-03 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 100.125 | 7.3921 | 86.148 | -75 | -1.5712 | 40.7552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/10/4:00
4 | 10 | 1900-01-04 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 100.1667 | 7.4077 | 86.148 | -75 | -1.5593 | 55.7582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/10/5:00
4 | 10 | 1900-01-05 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 100.2083 | 7.4233 | 86.148 | -75 | -1.5474 | 70.7611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/10/6:00
4 | 10 | 1900-01-06 | 5 | 21 | 26 | 41 | 1 | 0 | 41 | 0 | 0 | 21 | 0 | 0 | 39.791 | 100.25 | 7.4389 | 86.148 | -75 | -1.5355 | 85.7641 | 3.6175 | 24.6175 | 7.8033 | 7.8033 | 0 | 0 | 0 | 4/10/7:00
4 | 10 | 1900-01-07 | 8.3 | 68 | 338 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 68 | 0 | 0 | 39.791 | 100.2917 | 7.4545 | 86.148 | -75 | -1.5236 | 100.7671 | -20.0442 | 47.9558 | 15.2011 | 15.2011 | 0 | 0 | 0 | 4/10/8:00
4 | 10 | 1900-01-08 | 11.7 | 130 | 538 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 130 | 0 | 0 | 39.791 | 100.3333 | 7.4701 | 86.148 | -75 | -1.5117 | 115.7701 | -133.4367 | -3.4367 | -1.0894 | -1.0894 | 0 | 0 | 0 | 4/10/9:00
4 | 10 | 1900-01-09 | 15 | 201 | 575 | 59 | 0 | 1 | 0 | 59 | 0 | 201 | 0 | 0 | 39.791 | 100.375 | 7.4857 | 86.148 | -75 | -1.4998 | 130.773 | -238.1366 | -37.1366 | -11.7716 | 0 | -11.7716 | 59 | -11.7716 | 4/10/10:00
4 | 10 | 1900-01-10 | 17.8 | 216 | 665 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 216 | 0 | 0 | 39.791 | 100.4167 | 7.5013 | 86.148 | -75 | -1.488 | 145.776 | -363.3213 | -147.3213 | -46.6983 | 0 | -46.6983 | 64.04 | -46.6983 | 4/10/11:00
4 | 10 | 1900-01-11 | 19.4 | 303 | 416 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 303 | 0 | 0 | 39.791 | 100.4583 | 7.5169 | 86.148 | -75 | -1.4761 | 160.779 | -264.407 | 38.593 | 12.2333 | 0 | 12.2333 | 66.92 | 12.2333 | 4/10/12:00
4 | 10 | 1900-01-12 | 20 | 307 | 631 | 68 | 0 | 1 | 0 | 68 | 0 | 307 | 0 | 0 | 39.791 | 100.5 | 7.5324 | 86.148 | -75 | -1.4642 | 175.7819 | -426.427 | -119.427 | -37.8563 | 0 | -37.8563 | 68 | -37.8563 | 4/10/13:00
4 | 10 | 1900-01-13 | 21.1 | 297 | 646 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 297 | 0 | 0 | 39.791 | 100.5417 | 7.548 | 86.148 | -75 | -1.4524 | 190.7849 | -429.076 | -132.076 | -41.8658 | 0 | -41.8658 | 69.98 | -41.8658 | 4/10/14:00
4 | 10 | 1900-01-14 | 21.7 | 268 | 623 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 268 | 0 | 0 | 39.791 | 100.5833 | 7.5636 | 86.148 | -75 | -1.4406 | 205.7879 | -374.7982 | -106.7982 | -33.8532 | 0 | -33.8532 | 71.06 | -33.8532 | 4/10/15:00
4 | 10 | 1900-01-15 | 22.2 | 329 | 257 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 329 | 0 | 0 | 39.791 | 100.625 | 7.5792 | 86.148 | -75 | -1.4287 | 220.7908 | -126.508 | 202.492 | 64.1864 | 0 | 64.1864 | 71.96 | 64.1864 | 4/10/16:00
4 | 10 | 1900-01-16 | 21.7 | 206 | 101 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 206 | 0 | 0 | 39.791 | 100.6667 | 7.5947 | 86.148 | -75 | -1.4169 | 235.7938 | -34.7027 | 171.2973 | 54.2982 | 0 | 54.2982 | 71.06 | 54.2982 | 4/10/17:00
4 | 10 | 1900-01-17 | 20.6 | 113 | 20 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 113 | 0 | 0 | 39.791 | 100.7083 | 7.6103 | 86.148 | -75 | -1.4051 | 250.7967 | -3.3151 | 109.6849 | 34.7682 | 0 | 34.7682 | 69.08 | 34.7682 | 4/10/18:00
4 | 10 | 1900-01-18 | 18.3 | 45 | 16 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 45 | 0 | 0 | 39.791 | 100.75 | 7.6258 | 86.148 | -75 | -1.3933 | 265.7997 | 0.46635 | 45.4664 | 14.412 | 0 | 14.412 | 64.94 | 14.412 | 4/10/19:00
4 | 10 | 1900-01-19 | 16.1 | 2 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 2 | 0 | 0 | 39.791 | 100.7917 | 7.6414 | 86.148 | -75 | -1.3815 | 280.8026 | 0 | 2 | 0.63397 | 0 | 0.63397 | 60.98 | 0.63397 | 4/10/20:00
4 | 10 | 1900-01-20 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 100.8333 | 7.6569 | 86.148 | -75 | -1.3697 | 295.8056 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 4/10/21:00
4 | 10 | 1900-01-21 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 100.875 | 7.6725 | 86.148 | -75 | -1.358 | 310.8085 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 4/10/22:00
4 | 10 | 1900-01-22 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 100.9167 | 7.688 | 86.148 | -75 | -1.3462 | 325.8115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/10/23:00
4 | 10 | 1900-01-23 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 100.9583 | 7.7036 | 86.148 | -75 | -1.3344 | 340.8144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/10/24:00
4 | 11 | 1899-12-31 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101 | 7.7191 | 86.148 | -75 | -1.3227 | -4.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/1:00
4 | 11 | 1900-01-01 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101.0417 | 7.7346 | 86.148 | -75 | -1.3109 | 10.8203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/2:00
4 | 11 | 1900-01-02 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101.0833 | 7.7502 | 86.148 | -75 | -1.2992 | 25.8232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/3:00
4 | 11 | 1900-01-03 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101.125 | 7.7657 | 86.148 | -75 | -1.2875 | 40.8261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/4:00
4 | 11 | 1900-01-04 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101.1667 | 7.7812 | 86.148 | -75 | -1.2758 | 55.8291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/5:00
4 | 11 | 1900-01-05 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101.2083 | 7.7967 | 86.148 | -75 | -1.2641 | 70.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/6:00
4 | 11 | 1900-01-06 | 6.1 | 6 | 1 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 6 | 0 | 0 | 39.791 | 101.25 | 7.8123 | 86.148 | -75 | -1.2524 | 85.8349 | 0.14228 | 6.1423 | 1.947 | 1.947 | 0 | 0 | 0 | 4/11/7:00
4 | 11 | 1900-01-07 | 6.7 | 62 | 5 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 62 | 0 | 0 | 39.791 | 101.2917 | 7.8278 | 86.148 | -75 | -1.2407 | 100.8378 | -0.27984 | 61.7202 | 19.5642 | 19.5642 | 0 | 0 | 0 | 4/11/8:00
4 | 11 | 1900-01-08 | 7.8 | 174 | 10 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 174 | 0 | 0 | 39.791 | 101.3333 | 7.8433 | 86.148 | -75 | -1.229 | 115.8407 | -2.4445 | 171.5555 | 54.3801 | 54.3801 | 0 | 0 | 0 | 4/11/9:00
4 | 11 | 1900-01-09 | 10.6 | 189 | 475 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 189 | 0 | 0 | 39.791 | 101.375 | 7.8588 | 86.148 | -75 | -1.2174 | 130.8437 | -194.8898 | -5.8898 | -1.867 | -1.867 | 0 | 0 | 0 | 4/11/10:00
4 | 11 | 1900-01-10 | 12.2 | 138 | 774 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 138 | 0 | 0 | 39.791 | 101.4167 | 7.8743 | 86.148 | -75 | -1.2057 | 145.8466 | -419.6568 | -281.6568 | -89.2803 | -89.2803 | 0 | 0 | 0 | 4/11/11:00
4 | 11 | 1900-01-11 | 14.4 | 113 | 858 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 113 | 0 | 0 | 39.791 | 101.4583 | 7.8898 | 86.148 | -75 | -1.1941 | 160.8495 | -541.5186 | -428.5186 | -135.8329 | 0 | -135.8329 | 57.92 | -135.8329 | 4/11/12:00
4 | 11 | 1900-01-12 | 15.6 | 262 | 613 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 262 | 0 | 0 | 39.791 | 101.5 | 7.9053 | 86.148 | -75 | -1.1824 | 175.8524 | -411.3642 | -149.3642 | -47.3458 | 0 | -47.3458 | 60.08 | -47.3458 | 4/11/13:00
4 | 11 | 1900-01-13 | 16.1 | 338 | 328 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 338 | 0 | 0 | 39.791 | 101.5417 | 7.9208 | 86.148 | -75 | -1.1708 | 190.8553 | -216.2314 | 121.7686 | 38.5985 | 0 | 38.5985 | 60.98 | 38.5985 | 4/11/14:00
4 | 11 | 1900-01-14 | 14.4 | 179 | 5 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 179 | 0 | 0 | 39.791 | 101.5833 | 7.9363 | 86.148 | -75 | -1.1592 | 205.8582 | -2.9823 | 176.0177 | 55.7945 | 0 | 55.7945 | 57.92 | 55.7945 | 4/11/15:00
4 | 11 | 1900-01-15 | 15 | 207 | 13 | 59 | 0 | 1 | 0 | 59 | 0 | 207 | 0 | 0 | 39.791 | 101.625 | 7.9518 | 86.148 | -75 | -1.1476 | 220.8611 | -6.3311 | 200.6689 | 63.6086 | 0 | 63.6086 | 59 | 63.6086 | 4/11/16:00
4 | 11 | 1900-01-16 | 14.4 | 177 | 162 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 177 | 0 | 0 | 39.791 | 101.6667 | 7.9672 | 86.148 | -75 | -1.136 | 235.864 | -54.8073 | 122.1927 | 38.7329 | 0 | 38.7329 | 57.92 | 38.7329 | 4/11/17:00
4 | 11 | 1900-01-17 | 13.3 | 76 | 115 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 76 | 0 | 0 | 39.791 | 101.7083 | 7.9827 | 86.148 | -75 | -1.1244 | 250.8669 | -18.4609 | 57.5391 | 18.2389 | 0 | 18.2389 | 55.94 | 18.2389 | 4/11/18:00
4 | 11 | 1900-01-18 | 12.2 | 35 | 3 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 35 | 0 | 0 | 39.791 | 101.75 | 7.9982 | 86.148 | -75 | -1.1128 | 265.8698 | 0.10274 | 35.1027 | 11.127 | 11.127 | 0 | 0 | 0 | 4/11/19:00
4 | 11 | 1900-01-19 | 10 | 2 | 1 | 50 | 1 | 0 | 50 | 0 | 0 | 2 | 0 | 0 | 39.791 | 101.7917 | 8.0137 | 86.148 | -75 | -1.1012 | 280.8727 | 0.23274 | 2.2327 | 0.70774 | 0.70774 | 0 | 0 | 0 | 4/11/20:00
4 | 11 | 1900-01-20 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101.8333 | 8.0291 | 86.148 | -75 | -1.0897 | 295.8756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/21:00
4 | 11 | 1900-01-21 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101.875 | 8.0446 | 86.148 | -75 | -1.0781 | 310.8785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/22:00
4 | 11 | 1900-01-22 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101.9167 | 8.06 | 86.148 | -75 | -1.0666 | 325.8814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/23:00
4 | 11 | 1900-01-23 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 101.9583 | 8.0755 | 86.148 | -75 | -1.055 | 340.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/11/24:00
4 | 12 | 1899-12-31 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102 | 8.091 | 86.148 | -75 | -1.0435 | -4.1129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/1:00
4 | 12 | 1900-01-01 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102.0417 | 8.1064 | 86.148 | -75 | -1.032 | 10.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/2:00
4 | 12 | 1900-01-02 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102.0833 | 8.1218 | 86.148 | -75 | -1.0205 | 25.8929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/3:00
4 | 12 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102.125 | 8.1373 | 86.148 | -75 | -1.009 | 40.8958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/4:00
4 | 12 | 1900-01-04 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102.1667 | 8.1527 | 86.148 | -75 | -0.9975 | 55.8986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/5:00
4 | 12 | 1900-01-05 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102.2083 | 8.1682 | 86.148 | -75 | -0.98602 | 70.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/6:00
4 | 12 | 1900-01-06 | 4.4 | 24 | 21 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 24 | 0 | 0 | 39.791 | 102.25 | 8.1836 | 86.148 | -75 | -0.97455 | 85.9044 | 3.0538 | 27.0538 | 8.5756 | 8.5756 | 0 | 0 | 0 | 4/12/7:00
4 | 12 | 1900-01-07 | 5.6 | 50 | 1 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 50 | 0 | 0 | 39.791 | 102.2917 | 8.199 | 86.148 | -75 | -0.96309 | 100.9072 | -0.052637 | 49.9474 | 15.8324 | 15.8324 | 0 | 0 | 0 | 4/12/8:00
4 | 12 | 1900-01-08 | 7.8 | 171 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 171 | 0 | 0 | 39.791 | 102.3333 | 8.2144 | 86.148 | -75 | -0.95165 | 115.9101 | 0 | 171 | 54.204 | 54.204 | 0 | 0 | 0 | 4/12/9:00
4 | 12 | 1900-01-09 | 8.9 | 226 | 406 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 226 | 0 | 0 | 39.791 | 102.375 | 8.2299 | 86.148 | -75 | -0.94021 | 130.9129 | -165.0107 | 60.9893 | 19.3326 | 19.3326 | 0 | 0 | 0 | 4/12/10:00
4 | 12 | 1900-01-10 | 10 | 352 | 74 | 50 | 1 | 0 | 50 | 0 | 0 | 352 | 0 | 0 | 39.791 | 102.4167 | 8.2453 | 86.148 | -75 | -0.92878 | 145.9158 | -39.814 | 312.186 | 98.9575 | 98.9575 | 0 | 0 | 0 | 4/12/11:00
4 | 12 | 1900-01-11 | 12.2 | 326 | 474 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 326 | 0 | 0 | 39.791 | 102.4583 | 8.2607 | 86.148 | -75 | -0.91736 | 160.9187 | -297.046 | 28.954 | 9.1779 | 9.1779 | 0 | 0 | 0 | 4/12/12:00
4 | 12 | 1900-01-12 | 13.3 | 271 | 11 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 271 | 0 | 0 | 39.791 | 102.5 | 8.2761 | 86.148 | -75 | -0.90595 | 175.9215 | -7.3297 | 263.6703 | 83.5789 | 0 | 83.5789 | 55.94 | 83.5789 | 4/12/13:00
4 | 12 | 1900-01-13 | 12.8 | 375 | 35 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 375 | 0 | 0 | 39.791 | 102.5417 | 8.2915 | 86.148 | -75 | -0.89455 | 190.9244 | -22.8998 | 352.1002 | 111.6096 | 0 | 111.6096 | 55.04 | 111.6096 | 4/12/14:00
4 | 12 | 1900-01-14 | 13.3 | 325 | 467 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 325 | 0 | 0 | 39.791 | 102.5833 | 8.3069 | 86.148 | -75 | -0.88316 | 205.9272 | -276.1527 | 48.8473 | 15.4837 | 0 | 15.4837 | 55.94 | 15.4837 | 4/12/15:00
4 | 12 | 1900-01-15 | 14.4 | 260 | 386 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 260 | 0 | 0 | 39.791 | 102.625 | 8.3223 | 86.148 | -75 | -0.87178 | 220.9301 | -185.9654 | 74.0346 | 23.4677 | 0 | 23.4677 | 57.92 | 23.4677 | 4/12/16:00
4 | 12 | 1900-01-16 | 15 | 216 | 412 | 59 | 0 | 1 | 0 | 59 | 0 | 216 | 0 | 0 | 39.791 | 102.6667 | 8.3377 | 86.148 | -75 | -0.86041 | 235.9329 | -137.2241 | 78.7759 | 24.9706 | 0 | 24.9706 | 59 | 24.9706 | 4/12/17:00
4 | 12 | 1900-01-17 | 13.9 | 136 | 316 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 136 | 0 | 0 | 39.791 | 102.7083 | 8.3531 | 86.148 | -75 | -0.84905 | 250.9357 | -49.0876 | 86.9124 | 27.5497 | 0 | 27.5497 | 57.02 | 27.5497 | 4/12/18:00
4 | 12 | 1900-01-18 | 11.7 | 35 | 16 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 35 | 0 | 0 | 39.791 | 102.75 | 8.3685 | 86.148 | -75 | -0.8377 | 265.9386 | 0.62882 | 35.6288 | 11.2937 | 11.2937 | 0 | 0 | 0 | 4/12/19:00
4 | 12 | 1900-01-19 | 11.1 | 5 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 5 | 0 | 0 | 39.791 | 102.7917 | 8.3839 | 86.148 | -75 | -0.82636 | 280.9414 | 0 | 5 | 1.5849 | 1.5849 | 0 | 0 | 0 | 4/12/20:00
4 | 12 | 1900-01-20 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102.8333 | 8.3992 | 86.148 | -75 | -0.81503 | 295.9442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/21:00
4 | 12 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102.875 | 8.4146 | 86.148 | -75 | -0.80371 | 310.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/22:00
4 | 12 | 1900-01-22 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102.9167 | 8.43 | 86.148 | -75 | -0.7924 | 325.9499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/23:00
4 | 12 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 102.9583 | 8.4454 | 86.148 | -75 | -0.7811 | 340.9527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/12/24:00
4 | 13 | 1899-12-31 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 103 | 8.4607 | 86.148 | -75 | -0.76981 | -4.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/13/1:00
4 | 13 | 1900-01-01 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 103.0417 | 8.4761 | 86.148 | -75 | -0.75853 | 10.9584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/13/2:00
4 | 13 | 1900-01-02 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 103.0833 | 8.4914 | 86.148 | -75 | -0.74726 | 25.9612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/13/3:00
4 | 13 | 1900-01-03 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 103.125 | 8.5068 | 86.148 | -75 | -0.736 | 40.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/13/4:00
4 | 13 | 1900-01-04 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 103.1667 | 8.5221 | 86.148 | -75 | -0.72475 | 55.9668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/13/5:00
4 | 13 | 1900-01-05 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 103.2083 | 8.5375 | 86.148 | -75 | -0.71351 | 70.9696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/13/6:00
4 | 13 | 1900-01-06 | 8.3 | 29 | 7 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 29 | 0 | 0 | 39.791 | 103.25 | 8.5528 | 86.148 | -75 | -0.70228 | 85.9724 | 1.0398 | 30.0398 | 9.5221 | 9.5221 | 0 | 0 | 0 | 4/13/7:00
4 | 13 | 1900-01-07 | 10 | 109 | 98 | 50 | 1 | 0 | 50 | 0 | 0 | 109 | 0 | 0 | 39.791 | 103.2917 | 8.5682 | 86.148 | -75 | -0.69106 | 100.9752 | -4.832 | 104.168 | 33.0194 | 33.0194 | 0 | 0 | 0 | 4/13/8:00
4 | 13 | 1900-01-08 | 11.7 | 236 | 103 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 236 | 0 | 0 | 39.791 | 103.3333 | 8.5835 | 86.148 | -75 | -0.67985 | 115.978 | -24.4403 | 211.5597 | 67.0607 | 67.0607 | 0 | 0 | 0 | 4/13/9:00
4 | 13 | 1900-01-09 | 12.8 | 259 | 10 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 259 | 0 | 0 | 39.791 | 103.375 | 8.5988 | 86.148 | -75 | -0.66866 | 130.9808 | -4.0256 | 254.9744 | 80.8224 | 0 | 80.8224 | 55.04 | 80.8224 | 4/13/10:00
4 | 13 | 1900-01-10 | 12.8 | 242 | 8 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 242 | 0 | 0 | 39.791 | 103.4167 | 8.6142 | 86.148 | -75 | -0.65747 | 145.9836 | -4.2708 | 237.7292 | 75.356 | 0 | 75.356 | 55.04 | 75.356 | 4/13/11:00
4 | 13 | 1900-01-11 | 13.3 | 425 | 12 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 425 | 0 | 0 | 39.791 | 103.4583 | 8.6295 | 86.148 | -75 | -0.64629 | 160.9864 | -7.4665 | 417.5335 | 132.3508 | 0 | 132.3508 | 55.94 | 132.3508 | 4/13/12:00
4 | 13 | 1900-01-12 | 12.2 | 217 | 1 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 217 | 0 | 0 | 39.791 | 103.5 | 8.6448 | 86.148 | -75 | -0.63512 | 175.9892 | -0.6616 | 216.3384 | 68.5755 | 68.5755 | 0 | 0 | 0 | 4/13/13:00
4 | 13 | 1900-01-13 | 10 | 196 | 4 | 50 | 1 | 0 | 50 | 0 | 0 | 196 | 0 | 0 | 39.791 | 103.5417 | 8.6601 | 86.148 | -75 | -0.62396 | 190.992 | -2.5973 | 193.4027 | 61.3053 | 61.3053 | 0 | 0 | 0 | 4/13/14:00
4 | 13 | 1900-01-14 | 11.1 | 209 | 4 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 209 | 0 | 0 | 39.791 | 103.5833 | 8.6754 | 86.148 | -75 | -0.61282 | 205.9948 | -2.3449 | 206.6551 | 65.5061 | 65.5061 | 0 | 0 | 0 | 4/13/15:00
4 | 13 | 1900-01-15 | 12.2 | 257 | 1 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 257 | 0 | 0 | 39.791 | 103.625 | 8.6907 | 86.148 | -75 | -0.60168 | 220.9976 | -0.47657 | 256.5234 | 81.3134 | 81.3134 | 0 | 0 | 0 | 4/13/16:00
4 | 13 | 1900-01-16 | 12.8 | 213 | 147 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 213 | 0 | 0 | 39.791 | 103.6667 | 8.706 | 86.148 | -75 | -0.59055 | 236.0004 | -48.1937 | 164.8063 | 52.2407 | 0 | 52.2407 | 55.04 | 52.2407 | 4/13/17:00
4 | 13 | 1900-01-17 | 13.3 | 142 | 87 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 142 | 0 | 0 | 39.791 | 103.7083 | 8.7213 | 86.148 | -75 | -0.57944 | 251.0031 | -13.0664 | 128.9336 | 40.8697 | 0 | 40.8697 | 55.94 | 40.8697 | 4/13/18:00
4 | 13 | 1900-01-18 | 13.3 | 44 | 2 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 44 | 0 | 0 | 39.791 | 103.75 | 8.7366 | 86.148 | -75 | -0.56833 | 266.0059 | 0.08862 | 44.0886 | 13.9753 | 0 | 13.9753 | 55.94 | 13.9753 | 4/13/19:00
4 | 13 | 1900-01-19 | 12.8 | 3 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 3 | 0 | 0 | 39.791 | 103.7917 | 8.7519 | 86.148 | -75 | -0.55724 | 281.0087 | 0 | 3 | 0.95095 | 0 | 0.95095 | 55.04 | 0.95095 | 4/13/20:00
4 | 13 | 1900-01-20 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 103.8333 | 8.7672 | 86.148 | -75 | -0.54615 | 296.0115 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 4/13/21:00
4 | 13 | 1900-01-21 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 103.875 | 8.7825 | 86.148 | -75 | -0.53508 | 311.0142 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 4/13/22:00
4 | 13 | 1900-01-22 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 103.9167 | 8.7978 | 86.148 | -75 | -0.52402 | 326.017 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 4/13/23:00
4 | 13 | 1900-01-23 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 103.9583 | 8.813 | 86.148 | -75 | -0.51296 | 341.0198 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 4/13/24:00
4 | 14 | 1899-12-31 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 104 | 8.8283 | 86.148 | -75 | -0.50192 | -3.9775 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 4/14/1:00
4 | 14 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 104.0417 | 8.8436 | 86.148 | -75 | -0.49089 | 11.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/14/2:00
4 | 14 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 104.0833 | 8.8588 | 86.148 | -75 | -0.47987 | 26.028 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 4/14/3:00
4 | 14 | 1900-01-03 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 104.125 | 8.8741 | 86.148 | -75 | -0.46886 | 41.0308 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 4/14/4:00
4 | 14 | 1900-01-04 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 104.1667 | 8.8894 | 86.148 | -75 | -0.45786 | 56.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/14/5:00
4 | 14 | 1900-01-05 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 104.2083 | 8.9046 | 86.148 | -75 | -0.44687 | 71.0363 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 4/14/6:00
4 | 14 | 1900-01-06 | 13.9 | 24 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 24 | 0 | 0 | 39.791 | 104.25 | 8.9199 | 86.148 | -75 | -0.43589 | 86.039 | 0 | 24 | 7.6076 | 0 | 7.6076 | 57.02 | 7.6076 | 4/14/7:00
4 | 14 | 1900-01-07 | 15 | 44 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 44 | 0 | 0 | 39.791 | 104.2917 | 8.9351 | 86.148 | -75 | -0.42492 | 101.0418 | 0 | 44 | 13.9472 | 0 | 13.9472 | 59 | 13.9472 | 4/14/8:00
4 | 14 | 1900-01-08 | 16.1 | 130 | 4 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 130 | 0 | 0 | 39.791 | 104.3333 | 8.9503 | 86.148 | -75 | -0.41396 | 116.0445 | -0.93479 | 129.0652 | 40.9114 | 0 | 40.9114 | 60.98 | 40.9114 | 4/14/9:00
4 | 14 | 1900-01-09 | 17.8 | 117 | 8 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 117 | 0 | 0 | 39.791 | 104.375 | 8.9656 | 86.148 | -75 | -0.40302 | 131.0472 | -3.1895 | 113.8105 | 36.076 | 0 | 36.076 | 64.04 | 36.076 | 4/14/10:00
4 | 14 | 1900-01-10 | 17.8 | 292 | 84 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 292 | 0 | 0 | 39.791 | 104.4167 | 8.9808 | 86.148 | -75 | -0.39208 | 146.05 | -44.4927 | 247.5073 | 78.4555 | 0 | 78.4555 | 64.04 | 78.4555 | 4/14/11:00
4 | 14 | 1900-01-11 | 20.6 | 376 | 101 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 376 | 0 | 0 | 39.791 | 104.4583 | 8.996 | 86.148 | -75 | -0.38116 | 161.0527 | -62.3916 | 313.6084 | 99.4084 | 0 | 99.4084 | 69.08 | 99.4084 | 4/14/12:00
4 | 14 | 1900-01-12 | 20 | 387 | 115 | 68 | 0 | 1 | 0 | 68 | 0 | 387 | 0 | 0 | 39.791 | 104.5 | 9.0113 | 86.148 | -75 | -0.37024 | 176.0554 | -75.5391 | 311.4609 | 98.7277 | 0 | 98.7277 | 68 | 98.7277 | 4/14/13:00
4 | 14 | 1900-01-13 | 13.3 | 171 | 5 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 171 | 0 | 0 | 39.791 | 104.5417 | 9.0265 | 86.148 | -75 | -0.35934 | 191.0582 | -3.2218 | 167.7782 | 53.1827 | 0 | 53.1827 | 55.94 | 53.1827 | 4/14/14:00
4 | 14 | 1900-01-14 | 12.2 | 190 | 7 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 190 | 0 | 0 | 39.791 | 104.5833 | 9.0417 | 86.148 | -75 | -0.34845 | 206.0609 | -4.0678 | 185.9322 | 58.9373 | 58.9373 | 0 | 0 | 0 | 4/14/15:00
4 | 14 | 1900-01-15 | 11.7 | 131 | 7 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 131 | 0 | 0 | 39.791 | 104.625 | 9.0569 | 86.148 | -75 | -0.33756 | 221.0636 | -3.2997 | 127.7003 | 40.4788 | 40.4788 | 0 | 0 | 0 | 4/14/16:00
4 | 14 | 1900-01-16 | 11.7 | 106 | 4 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 106 | 0 | 0 | 39.791 | 104.6667 | 9.0721 | 86.148 | -75 | -0.32669 | 236.0663 | -1.2906 | 104.7094 | 33.191 | 33.191 | 0 | 0 | 0 | 4/14/17:00
4 | 14 | 1900-01-17 | 11.1 | 72 | 4 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 72 | 0 | 0 | 39.791 | 104.7083 | 9.0873 | 86.148 | -75 | -0.31583 | 251.069 | -0.58031 | 71.4197 | 22.6388 | 22.6388 | 0 | 0 | 0 | 4/14/18:00
4 | 14 | 1900-01-18 | 11.1 | 29 | 1 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 29 | 0 | 0 | 39.791 | 104.75 | 9.1025 | 86.148 | -75 | -0.30499 | 266.0718 | 0.04927 | 29.0493 | 9.2081 | 9.2081 | 0 | 0 | 0 | 4/14/19:00
4 | 14 | 1900-01-19 | 11.1 | 6 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 6 | 0 | 0 | 39.791 | 104.7917 | 9.1177 | 86.148 | -75 | -0.29415 | 281.0745 | 0 | 6 | 1.9019 | 1.9019 | 0 | 0 | 0 | 4/14/20:00
4 | 14 | 1900-01-20 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 104.8333 | 9.1329 | 86.148 | -75 | -0.28332 | 296.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/14/21:00
4 | 14 | 1900-01-21 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 104.875 | 9.1481 | 86.148 | -75 | -0.27251 | 311.0799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/14/22:00
4 | 14 | 1900-01-22 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 104.9167 | 9.1633 | 86.148 | -75 | -0.2617 | 326.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/14/23:00
4 | 14 | 1900-01-23 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 104.9583 | 9.1785 | 86.148 | -75 | -0.25091 | 341.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/14/24:00
4 | 15 | 1899-12-31 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105 | 9.1936 | 86.148 | -75 | -0.24012 | -3.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/1:00
4 | 15 | 1900-01-01 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105.0417 | 9.2088 | 86.148 | -75 | -0.22935 | 11.0907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/2:00
4 | 15 | 1900-01-02 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105.0833 | 9.224 | 86.148 | -75 | -0.21859 | 26.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/3:00
4 | 15 | 1900-01-03 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105.125 | 9.2391 | 86.148 | -75 | -0.20784 | 41.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/4:00
4 | 15 | 1900-01-04 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105.1667 | 9.2543 | 86.148 | -75 | -0.1971 | 56.0987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/5:00
4 | 15 | 1900-01-05 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105.2083 | 9.2695 | 86.148 | -75 | -0.18638 | 71.1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/6:00
4 | 15 | 1900-01-06 | 10.6 | 23 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 23 | 0 | 0 | 39.791 | 105.25 | 9.2846 | 86.148 | -75 | -0.17566 | 86.1041 | 0 | 23 | 7.2906 | 7.2906 | 0 | 0 | 0 | 4/15/7:00
4 | 15 | 1900-01-07 | 10.6 | 68 | 4 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 68 | 0 | 0 | 39.791 | 105.2917 | 9.2997 | 86.148 | -75 | -0.16496 | 101.1068 | -0.17061 | 67.8294 | 21.5007 | 21.5007 | 0 | 0 | 0 | 4/15/8:00
4 | 15 | 1900-01-08 | 11.7 | 206 | 4 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 206 | 0 | 0 | 39.791 | 105.3333 | 9.3149 | 86.148 | -75 | -0.15426 | 116.1094 | -0.92043 | 205.0796 | 65.0066 | 65.0066 | 0 | 0 | 0 | 4/15/9:00
4 | 15 | 1900-01-09 | 11.7 | 279 | 169 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 279 | 0 | 0 | 39.791 | 105.375 | 9.33 | 86.148 | -75 | -0.14358 | 131.1121 | -66.7211 | 212.2789 | 67.2887 | 67.2887 | 0 | 0 | 0 | 4/15/10:00
4 | 15 | 1900-01-10 | 12.8 | 286 | 26 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 286 | 0 | 0 | 39.791 | 105.4167 | 9.3452 | 86.148 | -75 | -0.13291 | 146.1148 | -13.6627 | 272.3373 | 86.3262 | 0 | 86.3262 | 55.04 | 86.3262 | 4/15/11:00
4 | 15 | 1900-01-11 | 14.4 | 363 | 8 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 363 | 0 | 0 | 39.791 | 105.4583 | 9.3603 | 86.148 | -75 | -0.12225 | 161.1174 | -4.9061 | 358.0939 | 113.5095 | 0 | 113.5095 | 57.92 | 113.5095 | 4/15/12:00
4 | 15 | 1900-01-12 | 12.8 | 211 | 6 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 211 | 0 | 0 | 39.791 | 105.5 | 9.3754 | 86.148 | -75 | -0.1116 | 176.1201 | -3.9128 | 207.0872 | 65.643 | 0 | 65.643 | 55.04 | 65.643 | 4/15/13:00
4 | 15 | 1900-01-13 | 12.8 | 250 | 13 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 250 | 0 | 0 | 39.791 | 105.5417 | 9.3905 | 86.148 | -75 | -0.10096 | 191.1228 | -8.3125 | 241.6875 | 76.6107 | 0 | 76.6107 | 55.04 | 76.6107 | 4/15/14:00
4 | 15 | 1900-01-14 | 13.9 | 306 | 8 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 306 | 0 | 0 | 39.791 | 105.5833 | 9.4057 | 86.148 | -75 | -0.090338 | 206.1254 | -4.6081 | 301.3919 | 95.536 | 0 | 95.536 | 57.02 | 95.536 | 4/15/15:00
4 | 15 | 1900-01-15 | 12.8 | 168 | 308 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 168 | 0 | 0 | 39.791 | 105.625 | 9.4208 | 86.148 | -75 | -0.079724 | 221.1281 | -143.5948 | 24.4052 | 7.736 | 0 | 7.736 | 55.04 | 7.736 | 4/15/16:00
4 | 15 | 1900-01-16 | 12.2 | 128 | 7 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 128 | 0 | 0 | 39.791 | 105.6667 | 9.4359 | 86.148 | -75 | -0.069121 | 236.1307 | -2.2225 | 125.7775 | 39.8693 | 39.8693 | 0 | 0 | 0 | 4/15/17:00
4 | 15 | 1900-01-17 | 12.8 | 119 | 7 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 119 | 0 | 0 | 39.791 | 105.7083 | 9.451 | 86.148 | -75 | -0.058529 | 251.1334 | -0.98006 | 118.0199 | 37.4103 | 0 | 37.4103 | 55.04 | 37.4103 | 4/15/18:00
4 | 15 | 1900-01-18 | 12.2 | 55 | 20 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 55 | 0 | 0 | 39.791 | 105.75 | 9.4661 | 86.148 | -75 | -0.047949 | 266.136 | 1.0836 | 56.0836 | 17.7775 | 17.7775 | 0 | 0 | 0 | 4/15/19:00
4 | 15 | 1900-01-19 | 11.7 | 2 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 2 | 0 | 0 | 39.791 | 105.7917 | 9.4812 | 86.148 | -75 | -0.03738 | 281.1387 | 0 | 2 | 0.63397 | 0.63397 | 0 | 0 | 0 | 4/15/20:00
4 | 15 | 1900-01-20 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105.8333 | 9.4963 | 86.148 | -75 | -0.026823 | 296.1413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/21:00
4 | 15 | 1900-01-21 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105.875 | 9.5114 | 86.148 | -75 | -0.016277 | 311.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/22:00
4 | 15 | 1900-01-22 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105.9167 | 9.5264 | 86.148 | -75 | -0.005743 | 326.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/23:00
4 | 15 | 1900-01-23 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 105.9583 | 9.5415 | 86.148 | -75 | 0.0047798 | 341.1492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/15/24:00
4 | 16 | 1899-12-31 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106 | 9.5566 | 86.148 | -75 | 0.015291 | -3.8482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/1:00
4 | 16 | 1900-01-01 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106.0417 | 9.5717 | 86.148 | -75 | 0.025791 | 11.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/2:00
4 | 16 | 1900-01-02 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106.0833 | 9.5867 | 86.148 | -75 | 0.036279 | 26.1571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/3:00
4 | 16 | 1900-01-03 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106.125 | 9.6018 | 86.148 | -75 | 0.046755 | 41.1597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/4:00
4 | 16 | 1900-01-04 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106.1667 | 9.6168 | 86.148 | -75 | 0.05722 | 56.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/5:00
4 | 16 | 1900-01-05 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106.2083 | 9.6319 | 86.148 | -75 | 0.067674 | 71.1649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/6:00
4 | 16 | 1900-01-06 | 8.9 | 14 | 1 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 14 | 0 | 0 | 39.791 | 106.25 | 9.6469 | 86.148 | -75 | 0.078115 | 86.1675 | 0.15788 | 14.1579 | 4.4878 | 4.4878 | 0 | 0 | 0 | 4/16/7:00
4 | 16 | 1900-01-07 | 8.9 | 62 | 7 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 62 | 0 | 0 | 39.791 | 106.2917 | 9.662 | 86.148 | -75 | 0.088545 | 101.1701 | -0.27531 | 61.7247 | 19.5656 | 19.5656 | 0 | 0 | 0 | 4/16/8:00
4 | 16 | 1900-01-08 | 9.4 | 162 | 6 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 162 | 0 | 0 | 39.791 | 106.3333 | 9.677 | 86.148 | -75 | 0.098963 | 116.1727 | -1.3591 | 160.6409 | 50.9204 | 50.9204 | 0 | 0 | 0 | 4/16/9:00
4 | 16 | 1900-01-09 | 10 | 135 | 9 | 50 | 1 | 0 | 50 | 0 | 0 | 135 | 0 | 0 | 39.791 | 106.375 | 9.6921 | 86.148 | -75 | 0.10937 | 131.1753 | -3.5182 | 131.4818 | 41.6774 | 41.6774 | 0 | 0 | 0 | 4/16/10:00
4 | 16 | 1900-01-10 | 10 | 183 | 5 | 50 | 1 | 0 | 50 | 0 | 0 | 183 | 0 | 0 | 39.791 | 106.4167 | 9.7071 | 86.148 | -75 | 0.11976 | 146.1779 | -2.6065 | 180.3935 | 57.1816 | 57.1816 | 0 | 0 | 0 | 4/16/11:00
4 | 16 | 1900-01-11 | 10.6 | 206 | 1 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 206 | 0 | 0 | 39.791 | 106.4583 | 9.7221 | 86.148 | -75 | 0.13015 | 161.1805 | -0.60879 | 205.3912 | 65.1054 | 65.1054 | 0 | 0 | 0 | 4/16/12:00
4 | 16 | 1900-01-12 | 11.1 | 228 | 5 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 228 | 0 | 0 | 39.791 | 106.5 | 9.7371 | 86.148 | -75 | 0.14052 | 176.1831 | -3.237 | 224.763 | 71.246 | 71.246 | 0 | 0 | 0 | 4/16/13:00
4 | 16 | 1900-01-13 | 11.7 | 234 | 3 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 234 | 0 | 0 | 39.791 | 106.5417 | 9.7522 | 86.148 | -75 | 0.15088 | 191.1857 | -1.9035 | 232.0965 | 73.5705 | 73.5705 | 0 | 0 | 0 | 4/16/14:00
4 | 16 | 1900-01-14 | 12.2 | 372 | 1 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 372 | 0 | 0 | 39.791 | 106.5833 | 9.7672 | 86.148 | -75 | 0.16123 | 206.1883 | -0.57094 | 371.4291 | 117.7365 | 117.7365 | 0 | 0 | 0 | 4/16/15:00
4 | 16 | 1900-01-15 | 13.3 | 345 | 1 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 345 | 0 | 0 | 39.791 | 106.625 | 9.7822 | 86.148 | -75 | 0.17156 | 221.1909 | -0.46108 | 344.5389 | 109.2128 | 0 | 109.2128 | 55.94 | 109.2128 | 4/16/16:00
4 | 16 | 1900-01-16 | 12.8 | 233 | 1 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 233 | 0 | 0 | 39.791 | 106.6667 | 9.7972 | 86.148 | -75 | 0.18189 | 236.1935 | -0.31239 | 232.6876 | 73.7579 | 0 | 73.7579 | 55.04 | 73.7579 | 4/16/17:00
4 | 16 | 1900-01-17 | 12.8 | 143 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 143 | 0 | 0 | 39.791 | 106.7083 | 9.8122 | 86.148 | -75 | 0.1922 | 251.196 | 0 | 143 | 45.3285 | 0 | 45.3285 | 55.04 | 45.3285 | 4/16/18:00
4 | 16 | 1900-01-18 | 12.2 | 61 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 61 | 0 | 0 | 39.791 | 106.75 | 9.8272 | 86.148 | -75 | 0.2025 | 266.1986 | 0 | 61 | 19.3359 | 19.3359 | 0 | 0 | 0 | 4/16/19:00
4 | 16 | 1900-01-19 | 12.2 | 7 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 7 | 0 | 0 | 39.791 | 106.7917 | 9.8422 | 86.148 | -75 | 0.21279 | 281.2012 | 0 | 7 | 2.2189 | 2.2189 | 0 | 0 | 0 | 4/16/20:00
4 | 16 | 1900-01-20 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106.8333 | 9.8572 | 86.148 | -75 | 0.22306 | 296.2038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/21:00
4 | 16 | 1900-01-21 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106.875 | 9.8721 | 86.148 | -75 | 0.23333 | 311.2063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/22:00
4 | 16 | 1900-01-22 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106.9167 | 9.8871 | 86.148 | -75 | 0.24358 | 326.2089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/23:00
4 | 16 | 1900-01-23 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 106.9583 | 9.9021 | 86.148 | -75 | 0.25382 | 341.2115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/16/24:00
4 | 17 | 1899-12-31 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107 | 9.9171 | 86.148 | -75 | 0.26405 | -3.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/1:00
4 | 17 | 1900-01-01 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107.0417 | 9.932 | 86.148 | -75 | 0.27427 | 11.2166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/2:00
4 | 17 | 1900-01-02 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107.0833 | 9.947 | 86.148 | -75 | 0.28447 | 26.2191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/3:00
4 | 17 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107.125 | 9.9619 | 86.148 | -75 | 0.29466 | 41.2217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/4:00
4 | 17 | 1900-01-04 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107.1667 | 9.9769 | 86.148 | -75 | 0.30484 | 56.2242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/5:00
4 | 17 | 1900-01-05 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107.2083 | 9.9918 | 86.148 | -75 | 0.31501 | 71.2268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/6:00
4 | 17 | 1900-01-06 | 10 | 31 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 31 | 0 | 0 | 39.791 | 107.25 | 10.0068 | 86.148 | -75 | 0.32517 | 86.2293 | 0 | 31 | 9.8265 | 9.8265 | 0 | 0 | 0 | 4/17/7:00
4 | 17 | 1900-01-07 | 10 | 119 | 140 | 50 | 1 | 0 | 50 | 0 | 0 | 119 | 0 | 0 | 39.791 | 107.2917 | 10.0217 | 86.148 | -75 | 0.33531 | 101.2318 | -5.0414 | 113.9586 | 36.1229 | 36.1229 | 0 | 0 | 0 | 4/17/8:00
4 | 17 | 1900-01-08 | 11.1 | 172 | 5 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 172 | 0 | 0 | 39.791 | 107.3333 | 10.0367 | 86.148 | -75 | 0.34544 | 116.2344 | -1.1146 | 170.8854 | 54.1677 | 54.1677 | 0 | 0 | 0 | 4/17/9:00
4 | 17 | 1900-01-09 | 12.2 | 255 | 63 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 255 | 0 | 0 | 39.791 | 107.375 | 10.0516 | 86.148 | -75 | 0.35556 | 131.2369 | -24.3825 | 230.6175 | 73.1017 | 73.1017 | 0 | 0 | 0 | 4/17/10:00
4 | 17 | 1900-01-10 | 12.8 | 340 | 80 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 340 | 0 | 0 | 39.791 | 107.4167 | 10.0665 | 86.148 | -75 | 0.36567 | 146.2394 | -41.3688 | 298.6312 | 94.6609 | 0 | 94.6609 | 55.04 | 94.6609 | 4/17/11:00
4 | 17 | 1900-01-11 | 13.9 | 421 | 160 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 421 | 0 | 0 | 39.791 | 107.4583 | 10.0814 | 86.148 | -75 | 0.37576 | 161.2419 | -96.6894 | 324.3106 | 102.8008 | 0 | 102.8008 | 57.02 | 102.8008 | 4/17/12:00
4 | 17 | 1900-01-12 | 15 | 441 | 170 | 59 | 0 | 1 | 0 | 59 | 0 | 441 | 0 | 0 | 39.791 | 107.5 | 10.0963 | 86.148 | -75 | 0.38585 | 176.2445 | -109.2536 | 331.7464 | 105.1578 | 0 | 105.1578 | 59 | 105.1578 | 4/17/13:00
4 | 17 | 1900-01-13 | 15.6 | 401 | 6 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 401 | 0 | 0 | 39.791 | 107.5417 | 10.1113 | 86.148 | -75 | 0.39592 | 191.247 | -3.7774 | 397.2226 | 125.9126 | 0 | 125.9126 | 60.08 | 125.9126 | 4/17/14:00
4 | 17 | 1900-01-14 | 15.6 | 396 | 10 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 396 | 0 | 0 | 39.791 | 107.5833 | 10.1262 | 86.148 | -75 | 0.40598 | 206.2495 | -5.6589 | 390.3411 | 123.7313 | 0 | 123.7313 | 60.08 | 123.7313 | 4/17/15:00
4 | 17 | 1900-01-15 | 15.6 | 247 | 1 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 247 | 0 | 0 | 39.791 | 107.625 | 10.1411 | 86.148 | -75 | 0.41602 | 221.252 | -0.45597 | 246.544 | 78.1501 | 0 | 78.1501 | 60.08 | 78.1501 | 4/17/16:00
4 | 17 | 1900-01-16 | 14.4 | 267 | 11 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 267 | 0 | 0 | 39.791 | 107.6667 | 10.156 | 86.148 | -75 | 0.42606 | 236.2545 | -3.3804 | 263.6196 | 83.5628 | 0 | 83.5628 | 57.92 | 83.5628 | 4/17/17:00
4 | 17 | 1900-01-17 | 14.4 | 148 | 4 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 148 | 0 | 0 | 39.791 | 107.7083 | 10.1708 | 86.148 | -75 | 0.43608 | 251.257 | -0.52003 | 147.48 | 46.7486 | 0 | 46.7486 | 57.92 | 46.7486 | 4/17/18:00
4 | 17 | 1900-01-18 | 14.4 | 62 | 3 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 62 | 0 | 0 | 39.791 | 107.75 | 10.1857 | 86.148 | -75 | 0.44609 | 266.2595 | 0.19151 | 62.1915 | 19.7136 | 0 | 19.7136 | 57.92 | 19.7136 | 4/17/19:00
4 | 17 | 1900-01-19 | 13.3 | 10 | 2 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 10 | 0 | 0 | 39.791 | 107.7917 | 10.2006 | 86.148 | -75 | 0.45608 | 281.262 | 0.52206 | 10.5221 | 3.3353 | 0 | 3.3353 | 55.94 | 3.3353 | 4/17/20:00
4 | 17 | 1900-01-20 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107.8333 | 10.2155 | 86.148 | -75 | 0.46607 | 296.2645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/21:00
4 | 17 | 1900-01-21 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107.875 | 10.2304 | 86.148 | -75 | 0.47604 | 311.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/22:00
4 | 17 | 1900-01-22 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107.9167 | 10.2452 | 86.148 | -75 | 0.486 | 326.2695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/23:00
4 | 17 | 1900-01-23 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 107.9583 | 10.2601 | 86.148 | -75 | 0.49595 | 341.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/17/24:00
4 | 18 | 1899-12-31 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 108 | 10.275 | 86.148 | -75 | 0.50588 | -3.7255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/18/1:00
4 | 18 | 1900-01-01 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 108.0417 | 10.2898 | 86.148 | -75 | 0.51581 | 11.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/18/2:00
4 | 18 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 108.0833 | 10.3047 | 86.148 | -75 | 0.52572 | 26.2794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/18/3:00
4 | 18 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 108.125 | 10.3195 | 86.148 | -75 | 0.53561 | 41.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/18/4:00
4 | 18 | 1900-01-04 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 108.1667 | 10.3344 | 86.148 | -75 | 0.5455 | 56.2844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/18/5:00
4 | 18 | 1900-01-05 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 108.2083 | 10.3492 | 86.148 | -75 | 0.55537 | 71.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/18/6:00
4 | 18 | 1900-01-06 | 8.9 | 24 | 186 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 24 | 0 | 0 | 39.791 | 108.25 | 10.364 | 86.148 | -75 | 0.56523 | 86.2893 | 30.5137 | 54.5137 | 17.2799 | 17.2799 | 0 | 0 | 0 | 4/18/7:00
4 | 18 | 1900-01-07 | 12.2 | 45 | 620 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 45 | 0 | 0 | 39.791 | 108.2917 | 10.3789 | 86.148 | -75 | 0.57508 | 101.2918 | -20.2703 | 24.7297 | 7.8389 | 7.8389 | 0 | 0 | 0 | 4/18/8:00
4 | 18 | 1900-01-08 | 15 | 64 | 771 | 59 | 0 | 1 | 0 | 59 | 0 | 64 | 0 | 0 | 39.791 | 108.3333 | 10.3937 | 86.148 | -75 | 0.58491 | 116.2942 | -169.1062 | -105.1062 | -33.3168 | 0 | -33.3168 | 59 | -33.3168 | 4/18/9:00
4 | 18 | 1900-01-09 | 17.2 | 80 | 857 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 80 | 0 | 0 | 39.791 | 108.375 | 10.4085 | 86.148 | -75 | 0.59473 | 131.2967 | -328.3452 | -248.3452 | -78.7211 | 0 | -78.7211 | 62.96 | -78.7211 | 4/18/10:00
4 | 18 | 1900-01-10 | 18.9 | 92 | 899 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 92 | 0 | 0 | 39.791 | 108.4167 | 10.4233 | 86.148 | -75 | 0.60454 | 146.2991 | -461.1138 | -369.1138 | -117.0026 | 0 | -117.0026 | 66.02 | -117.0026 | 4/18/11:00
4 | 18 | 1900-01-11 | 20 | 192 | 703 | 68 | 0 | 1 | 0 | 68 | 0 | 192 | 0 | 0 | 39.791 | 108.4583 | 10.4381 | 86.148 | -75 | 0.61434 | 161.3016 | -421.6836 | -229.6836 | -72.8057 | 0 | -72.8057 | 68 | -72.8057 | 4/18/12:00
4 | 18 | 1900-01-12 | 21.1 | 237 | 622 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 237 | 0 | 0 | 39.791 | 108.5 | 10.4529 | 86.148 | -75 | 0.62412 | 176.304 | -396.8043 | -159.8043 | -50.6552 | 0 | -50.6552 | 69.98 | -50.6552 | 4/18/13:00
4 | 18 | 1900-01-13 | 21.7 | 257 | 642 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 257 | 0 | 0 | 39.791 | 108.5417 | 10.4677 | 86.148 | -75 | 0.63389 | 191.3065 | -401.0303 | -144.0303 | -45.6551 | 0 | -45.6551 | 71.06 | -45.6551 | 4/18/14:00
4 | 18 | 1900-01-14 | 21.1 | 317 | 563 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 317 | 0 | 0 | 39.791 | 108.5833 | 10.4825 | 86.148 | -75 | 0.64365 | 206.3089 | -315.7646 | 1.2354 | 0.39161 | 0 | 0.39161 | 69.98 | 0.39161 | 4/18/15:00
4 | 18 | 1900-01-15 | 22.8 | 330 | 324 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 330 | 0 | 0 | 39.791 | 108.625 | 10.4973 | 86.148 | -75 | 0.6534 | 221.3113 | -146.0917 | 183.9083 | 58.2957 | 0 | 58.2957 | 73.04 | 58.2957 | 4/18/16:00
4 | 18 | 1900-01-16 | 21.7 | 192 | 374 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 192 | 0 | 0 | 39.791 | 108.6667 | 10.5121 | 86.148 | -75 | 0.66313 | 236.3138 | -113.0473 | 78.9527 | 25.0266 | 0 | 25.0266 | 71.06 | 25.0266 | 4/18/17:00
4 | 18 | 1900-01-17 | 21.1 | 154 | 230 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 154 | 0 | 0 | 39.791 | 108.7083 | 10.5269 | 86.148 | -75 | 0.67285 | 251.3162 | -28.7687 | 125.2313 | 39.6961 | 0 | 39.6961 | 69.98 | 39.6961 | 4/18/18:00
4 | 18 | 1900-01-18 | 20.6 | 76 | 120 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 76 | 0 | 0 | 39.791 | 108.75 | 10.5416 | 86.148 | -75 | 0.68256 | 266.3186 | 8.2299 | 84.2299 | 26.6994 | 0 | 26.6994 | 69.08 | 26.6994 | 4/18/19:00
4 | 18 | 1900-01-19 | 18.3 | 10 | 8 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 10 | 0 | 0 | 39.791 | 108.7917 | 10.5564 | 86.148 | -75 | 0.69225 | 281.3211 | 2.1243 | 12.1243 | 3.8432 | 0 | 3.8432 | 64.94 | 3.8432 | 4/18/20:00
4 | 18 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 108.8333 | 10.5712 | 86.148 | -75 | 0.70194 | 296.3235 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 4/18/21:00
4 | 18 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 108.875 | 10.5859 | 86.148 | -75 | 0.71161 | 311.3259 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 4/18/22:00
4 | 18 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 108.9167 | 10.6007 | 86.148 | -75 | 0.72126 | 326.3283 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 4/18/23:00
4 | 18 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 108.9583 | 10.6154 | 86.148 | -75 | 0.73091 | 341.3307 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 4/18/24:00
4 | 19 | 1899-12-31 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 109 | 10.6302 | 86.148 | -75 | 0.74054 | -3.6669 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 4/19/1:00
4 | 19 | 1900-01-01 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 109.0417 | 10.6449 | 86.148 | -75 | 0.75015 | 11.3355 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 4/19/2:00
4 | 19 | 1900-01-02 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 109.0833 | 10.6597 | 86.148 | -75 | 0.75976 | 26.3379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/19/3:00
4 | 19 | 1900-01-03 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 109.125 | 10.6744 | 86.148 | -75 | 0.76935 | 41.3403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/19/4:00
4 | 19 | 1900-01-04 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 109.1667 | 10.6891 | 86.148 | -75 | 0.77893 | 56.3427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/19/5:00
4 | 19 | 1900-01-05 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 109.2083 | 10.7038 | 86.148 | -75 | 0.7885 | 71.3451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/19/6:00
4 | 19 | 1900-01-06 | 11.1 | 27 | 140 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 27 | 0 | 0 | 39.791 | 109.25 | 10.7186 | 86.148 | -75 | 0.79805 | 86.3475 | 23.3974 | 50.3974 | 15.9751 | 15.9751 | 0 | 0 | 0 | 4/19/7:00
4 | 19 | 1900-01-07 | 15 | 60 | 505 | 59 | 0 | 1 | 0 | 59 | 0 | 60 | 0 | 0 | 39.791 | 109.2917 | 10.7333 | 86.148 | -75 | 0.80759 | 101.3499 | -14.8382 | 45.1618 | 14.3155 | 0 | 14.3155 | 59 | 14.3155 | 4/19/8:00
4 | 19 | 1900-01-08 | 17.2 | 88 | 697 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 88 | 0 | 0 | 39.791 | 109.3333 | 10.748 | 86.148 | -75 | 0.81712 | 116.3523 | -150.3725 | -62.3725 | -19.771 | 0 | -19.771 | 62.96 | -19.771 | 4/19/9:00
4 | 19 | 1900-01-09 | 19.4 | 111 | 787 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 111 | 0 | 0 | 39.791 | 109.375 | 10.7627 | 86.148 | -75 | 0.82663 | 131.3547 | -298.4635 | -187.4635 | -59.4226 | 0 | -59.4226 | 66.92 | -59.4226 | 4/19/10:00
4 | 19 | 1900-01-10 | 21.7 | 127 | 834 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 127 | 0 | 0 | 39.791 | 109.4167 | 10.7774 | 86.148 | -75 | 0.83613 | 146.357 | -424.2785 | -297.2785 | -94.2321 | 0 | -94.2321 | 71.06 | -94.2321 | 4/19/11:00
4 | 19 | 1900-01-11 | 22.2 | 133 | 867 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 133 | 0 | 0 | 39.791 | 109.4583 | 10.7921 | 86.148 | -75 | 0.84562 | 161.3594 | -516.1805 | -383.1805 | -121.4615 | 0 | -121.4615 | 71.96 | -121.4615 | 4/19/12:00
4 | 19 | 1900-01-12 | 22.8 | 140 | 870 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 140 | 0 | 0 | 39.791 | 109.5 | 10.8068 | 86.148 | -75 | 0.85509 | 176.3618 | -550.9184 | -410.9184 | -130.254 | 0 | -130.254 | 73.04 | -130.254 | 4/19/13:00
4 | 19 | 1900-01-13 | 23.3 | 139 | 871 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 139 | 0 | 0 | 39.791 | 109.5417 | 10.8214 | 86.148 | -75 | 0.86455 | 191.3641 | -539.8163 | -400.8163 | -127.0518 | 0 | -127.0518 | 73.94 | -127.0518 | 4/19/14:00
4 | 19 | 1900-01-14 | 23.9 | 132 | 854 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 132 | 0 | 0 | 39.791 | 109.5833 | 10.8361 | 86.148 | -75 | 0.874 | 206.3665 | -474.7011 | -342.7011 | -108.6303 | 0 | -108.6303 | 75.02 | -108.6303 | 4/19/15:00
4 | 19 | 1900-01-15 | 23.9 | 119 | 820 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 119 | 0 | 0 | 39.791 | 109.625 | 10.8508 | 86.148 | -75 | 0.88344 | 221.3689 | -365.6053 | -246.6053 | -78.1696 | 0 | -78.1696 | 75.02 | -78.1696 | 4/19/16:00
4 | 19 | 1900-01-16 | 23.9 | 100 | 747 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 100 | 0 | 0 | 39.791 | 109.6667 | 10.8655 | 86.148 | -75 | 0.89286 | 236.3712 | -222.0604 | -122.0604 | -38.691 | 0 | -38.691 | 75.02 | -38.691 | 4/19/17:00
4 | 19 | 1900-01-17 | 23.3 | 74 | 618 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 74 | 0 | 0 | 39.791 | 109.7083 | 10.8801 | 86.148 | -75 | 0.90227 | 251.3736 | -74.2876 | -0.28764 | -0.091176 | 0 | -0.091176 | 73.94 | -0.091176 | 4/19/18:00
4 | 19 | 1900-01-18 | 21.1 | 45 | 347 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 45 | 0 | 0 | 39.791 | 109.75 | 10.8948 | 86.148 | -75 | 0.91167 | 266.3759 | 25.4239 | 70.4239 | 22.3231 | 0 | 22.3231 | 69.98 | 22.3231 | 4/19/19:00
4 | 19 | 1900-01-19 | 20.6 | 10 | 18 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 10 | 0 | 0 | 39.791 | 109.7917 | 10.9094 | 86.148 | -75 | 0.92105 | 281.3783 | 4.8595 | 14.8595 | 4.7102 | 0 | 4.7102 | 69.08 | 4.7102 | 4/19/20:00
4 | 19 | 1900-01-20 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 109.8333 | 10.9241 | 86.148 | -75 | 0.93042 | 296.3806 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 4/19/21:00
4 | 19 | 1900-01-21 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 109.875 | 10.9387 | 86.148 | -75 | 0.93977 | 311.3829 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 4/19/22:00
4 | 19 | 1900-01-22 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 109.9167 | 10.9534 | 86.148 | -75 | 0.94912 | 326.3853 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 4/19/23:00
4 | 19 | 1900-01-23 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 109.9583 | 10.968 | 86.148 | -75 | 0.95845 | 341.3876 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 4/19/24:00
4 | 20 | 1899-12-31 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 110 | 10.9826 | 86.148 | -75 | 0.96776 | -3.6101 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 4/20/1:00
4 | 20 | 1900-01-01 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 110.0417 | 10.9973 | 86.148 | -75 | 0.97707 | 11.3923 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 4/20/2:00
4 | 20 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 110.0833 | 11.0119 | 86.148 | -75 | 0.98636 | 26.3946 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 4/20/3:00
4 | 20 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 110.125 | 11.0265 | 86.148 | -75 | 0.99563 | 41.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/20/4:00
4 | 20 | 1900-01-04 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 110.1667 | 11.0411 | 86.148 | -75 | 1.0049 | 56.3992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/20/5:00
4 | 20 | 1900-01-05 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 110.2083 | 11.0557 | 86.148 | -75 | 1.0141 | 71.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/20/6:00
4 | 20 | 1900-01-06 | 11.1 | 26 | 200 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 26 | 0 | 0 | 39.791 | 110.25 | 11.0703 | 86.148 | -75 | 1.0234 | 86.4038 | 34.0371 | 60.0371 | 19.0307 | 19.0307 | 0 | 0 | 0 | 4/20/7:00
4 | 20 | 1900-01-07 | 16.7 | 53 | 577 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 53 | 0 | 0 | 39.791 | 110.2917 | 11.0849 | 86.148 | -75 | 1.0326 | 101.4062 | -15.046 | 37.954 | 12.0308 | 0 | 12.0308 | 62.06 | 12.0308 | 4/20/8:00
4 | 20 | 1900-01-08 | 19.4 | 76 | 742 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 76 | 0 | 0 | 39.791 | 110.3333 | 11.0995 | 86.148 | -75 | 1.0418 | 116.4085 | -157.4177 | -81.4177 | -25.808 | 0 | -25.808 | 66.92 | -25.808 | 4/20/9:00
4 | 20 | 1900-01-09 | 22.2 | 95 | 824 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 95 | 0 | 0 | 39.791 | 110.375 | 11.1141 | 86.148 | -75 | 1.051 | 131.4108 | -309.2896 | -214.2896 | -67.9261 | 0 | -67.9261 | 71.96 | -67.9261 | 4/20/10:00
4 | 20 | 1900-01-10 | 23.9 | 109 | 873 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 109 | 0 | 0 | 39.791 | 110.4167 | 11.1286 | 86.148 | -75 | 1.0602 | 146.413 | -440.4617 | -331.4617 | -105.0676 | 0 | -105.0676 | 75.02 | -105.0676 | 4/20/11:00
4 | 20 | 1900-01-11 | 25.6 | 117 | 902 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 117 | 0 | 0 | 39.791 | 110.4583 | 11.1432 | 86.148 | -75 | 1.0694 | 161.4153 | -532.9912 | -415.9912 | -131.8619 | 0 | -131.8619 | 78.08 | -131.8619 | 4/20/12:00
4 | 20 | 1900-01-12 | 26.1 | 121 | 912 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 121 | 0 | 0 | 39.791 | 110.5 | 11.1578 | 86.148 | -75 | 1.0785 | 176.4176 | -573.2301 | -452.2301 | -143.349 | 0 | -143.349 | 78.98 | -143.349 | 4/20/13:00
4 | 20 | 1900-01-13 | 26.7 | 119 | 909 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 119 | 0 | 0 | 39.791 | 110.5417 | 11.1723 | 86.148 | -75 | 1.0877 | 191.4199 | -558.9382 | -439.9382 | -139.4527 | 0 | -139.4527 | 80.06 | -139.4527 | 4/20/14:00
4 | 20 | 1900-01-14 | 27.8 | 113 | 888 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 113 | 0 | 0 | 39.791 | 110.5833 | 11.1869 | 86.148 | -75 | 1.0968 | 206.4222 | -489.1808 | -376.1808 | -119.2427 | 0 | -119.2427 | 82.04 | -119.2427 | 4/20/15:00
4 | 20 | 1900-01-15 | 26.7 | 103 | 856 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 103 | 0 | 0 | 39.791 | 110.625 | 11.2015 | 86.148 | -75 | 1.1059 | 221.4245 | -377.3734 | -274.3734 | -86.9716 | 0 | -86.9716 | 80.06 | -86.9716 | 4/20/16:00
4 | 20 | 1900-01-16 | 27.2 | 91 | 783 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 91 | 0 | 0 | 39.791 | 110.6667 | 11.216 | 86.148 | -75 | 1.115 | 236.4268 | -228.8862 | -137.8862 | -43.7075 | 0 | -43.7075 | 80.96 | -43.7075 | 4/20/17:00
4 | 20 | 1900-01-17 | 26.1 | 68 | 661 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 68 | 0 | 0 | 39.791 | 110.7083 | 11.2306 | 86.148 | -75 | 1.1241 | 251.429 | -76.27 | -8.27 | -2.6215 | 0 | -2.6215 | 78.98 | -2.6215 | 4/20/18:00
4 | 20 | 1900-01-18 | 24.4 | 46 | 385 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 46 | 0 | 0 | 39.791 | 110.75 | 11.2451 | 86.148 | -75 | 1.1332 | 266.4313 | 29.9883 | 75.9883 | 24.087 | 0 | 24.087 | 75.92 | 24.087 | 4/20/19:00
4 | 20 | 1900-01-19 | 23.3 | 11 | 29 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 11 | 0 | 0 | 39.791 | 110.7917 | 11.2596 | 86.148 | -75 | 1.1422 | 281.4336 | 7.9561 | 18.9561 | 6.0087 | 0 | 6.0087 | 73.94 | 6.0087 | 4/20/20:00
4 | 20 | 1900-01-20 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 110.8333 | 11.2741 | 86.148 | -75 | 1.1513 | 296.4358 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 4/20/21:00
4 | 20 | 1900-01-21 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 110.875 | 11.2887 | 86.148 | -75 | 1.1603 | 311.4381 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 4/20/22:00
4 | 20 | 1900-01-22 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 110.9167 | 11.3032 | 86.148 | -75 | 1.1693 | 326.4403 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 4/20/23:00
4 | 20 | 1900-01-23 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 110.9583 | 11.3177 | 86.148 | -75 | 1.1783 | 341.4426 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 4/20/24:00
4 | 21 | 1899-12-31 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 111 | 11.3322 | 86.148 | -75 | 1.1873 | -3.5552 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 4/21/1:00
4 | 21 | 1900-01-01 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 111.0417 | 11.3467 | 86.148 | -75 | 1.1963 | 11.4471 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 4/21/2:00
4 | 21 | 1900-01-02 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 111.0833 | 11.3612 | 86.148 | -75 | 1.2053 | 26.4493 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 4/21/3:00
4 | 21 | 1900-01-03 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 111.125 | 11.3757 | 86.148 | -75 | 1.2142 | 41.4516 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 4/21/4:00
4 | 21 | 1900-01-04 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 111.1667 | 11.3902 | 86.148 | -75 | 1.2232 | 56.4538 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 4/21/5:00
4 | 21 | 1900-01-05 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 111.2083 | 11.4047 | 86.148 | -75 | 1.2321 | 71.456 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 4/21/6:00
4 | 21 | 1900-01-06 | 15 | 34 | 46 | 59 | 0 | 1 | 0 | 59 | 0 | 34 | 0 | 0 | 39.791 | 111.25 | 11.4191 | 86.148 | -75 | 1.241 | 86.4582 | 7.9689 | 41.9689 | 13.3034 | 0 | 13.3034 | 59 | 13.3034 | 4/21/7:00
4 | 21 | 1900-01-07 | 18.3 | 106 | 265 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 106 | 0 | 0 | 39.791 | 111.2917 | 11.4336 | 86.148 | -75 | 1.2499 | 101.4605 | -6.0355 | 99.9645 | 31.687 | 0 | 31.687 | 64.94 | 31.687 | 4/21/8:00
4 | 21 | 1900-01-08 | 21.1 | 146 | 501 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 146 | 0 | 0 | 39.791 | 111.3333 | 11.4481 | 86.148 | -75 | 1.2588 | 116.4627 | -104.4918 | 41.5082 | 13.1574 | 0 | 13.1574 | 69.98 | 13.1574 | 4/21/9:00
4 | 21 | 1900-01-09 | 23.9 | 279 | 351 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 279 | 0 | 0 | 39.791 | 111.375 | 11.4625 | 86.148 | -75 | 1.2676 | 131.4649 | -130.3835 | 148.6165 | 47.1088 | 0 | 47.1088 | 75.02 | 47.1088 | 4/21/10:00
4 | 21 | 1900-01-10 | 26.7 | 299 | 529 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 299 | 0 | 0 | 39.791 | 111.4167 | 11.477 | 86.148 | -75 | 1.2765 | 146.4671 | -264.6866 | 34.3134 | 10.8767 | 0 | 10.8767 | 80.06 | 10.8767 | 4/21/11:00
4 | 21 | 1900-01-11 | 27.2 | 293 | 611 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 293 | 0 | 0 | 39.791 | 111.4583 | 11.4914 | 86.148 | -75 | 1.2853 | 161.4693 | -358.3164 | -65.3164 | -20.7042 | 0 | -20.7042 | 80.96 | -20.7042 | 4/21/12:00
4 | 21 | 1900-01-12 | 27.8 | 317 | 610 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 317 | 0 | 0 | 39.791 | 111.5 | 11.5059 | 86.148 | -75 | 1.2942 | 176.4715 | -380.5533 | -63.5533 | -20.1453 | 0 | -20.1453 | 82.04 | -20.1453 | 4/21/13:00
4 | 21 | 1900-01-13 | 28.3 | 306 | 657 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 306 | 0 | 0 | 39.791 | 111.5417 | 11.5203 | 86.148 | -75 | 1.303 | 191.4737 | -400.7979 | -94.7979 | -30.0493 | 0 | -30.0493 | 82.94 | -30.0493 | 4/21/14:00
4 | 21 | 1900-01-14 | 28.3 | 350 | 535 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 350 | 0 | 0 | 39.791 | 111.5833 | 11.5348 | 86.148 | -75 | 1.3118 | 206.4759 | -292.0739 | 57.9261 | 18.3616 | 0 | 18.3616 | 82.94 | 18.3616 | 4/21/15:00
4 | 21 | 1900-01-15 | 28.3 | 259 | 495 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 259 | 0 | 0 | 39.791 | 111.625 | 11.5492 | 86.148 | -75 | 1.3206 | 221.4781 | -215.7668 | 43.2332 | 13.7042 | 0 | 13.7042 | 82.94 | 13.7042 | 4/21/16:00
4 | 21 | 1900-01-16 | 27.8 | 251 | 218 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 251 | 0 | 0 | 39.791 | 111.6667 | 11.5636 | 86.148 | -75 | 1.3293 | 236.4803 | -62.657 | 188.343 | 59.7014 | 0 | 59.7014 | 82.04 | 59.7014 | 4/21/17:00
4 | 21 | 1900-01-17 | 26.1 | 148 | 100 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 148 | 0 | 0 | 39.791 | 111.7083 | 11.578 | 86.148 | -75 | 1.3381 | 251.4825 | -11.0621 | 136.9379 | 43.4069 | 0 | 43.4069 | 78.98 | 43.4069 | 4/21/18:00
4 | 21 | 1900-01-18 | 25 | 82 | 70 | 77 | 0 | 1 | 0 | 77 | 0 | 82 | 0 | 0 | 39.791 | 111.75 | 11.5924 | 86.148 | -75 | 1.3468 | 266.4847 | 5.7717 | 87.7717 | 27.8221 | 0 | 27.8221 | 77 | 27.8221 | 4/21/19:00
4 | 21 | 1900-01-19 | 23.9 | 11 | 3 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 11 | 0 | 0 | 39.791 | 111.7917 | 11.6068 | 86.148 | -75 | 1.3556 | 281.4869 | 0.83596 | 11.836 | 3.7518 | 0 | 3.7518 | 75.02 | 3.7518 | 4/21/20:00
4 | 21 | 1900-01-20 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 111.8333 | 11.6212 | 86.148 | -75 | 1.3643 | 296.4891 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 4/21/21:00
4 | 21 | 1900-01-21 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 111.875 | 11.6356 | 86.148 | -75 | 1.373 | 311.4912 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 4/21/22:00
4 | 21 | 1900-01-22 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 111.9167 | 11.65 | 86.148 | -75 | 1.3817 | 326.4934 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 4/21/23:00
4 | 21 | 1900-01-23 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 111.9583 | 11.6644 | 86.148 | -75 | 1.3903 | 341.4956 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 4/21/24:00
4 | 22 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 112 | 11.6788 | 86.148 | -75 | 1.399 | -3.5022 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 4/22/1:00
4 | 22 | 1900-01-01 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 112.0417 | 11.6932 | 86.148 | -75 | 1.4077 | 11.4999 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 4/22/2:00
4 | 22 | 1900-01-02 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 112.0833 | 11.7075 | 86.148 | -75 | 1.4163 | 26.5021 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 4/22/3:00
4 | 22 | 1900-01-03 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 112.125 | 11.7219 | 86.148 | -75 | 1.4249 | 41.5042 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 4/22/4:00
4 | 22 | 1900-01-04 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 112.1667 | 11.7363 | 86.148 | -75 | 1.4335 | 56.5064 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 4/22/5:00
4 | 22 | 1900-01-05 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 112.2083 | 11.7506 | 86.148 | -75 | 1.4421 | 71.5085 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 4/22/6:00
4 | 22 | 1900-01-06 | 13.9 | 19 | 3 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 19 | 0 | 0 | 39.791 | 112.25 | 11.765 | 86.148 | -75 | 1.4507 | 86.5107 | 0.52883 | 19.5288 | 6.1903 | 0 | 6.1903 | 57.02 | 6.1903 | 4/22/7:00
4 | 22 | 1900-01-07 | 14.4 | 110 | 2 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 110 | 0 | 0 | 39.791 | 112.2917 | 11.7793 | 86.148 | -75 | 1.4592 | 101.5128 | -0.038962 | 109.961 | 34.8557 | 0 | 34.8557 | 57.92 | 34.8557 | 4/22/8:00
4 | 22 | 1900-01-08 | 16.1 | 189 | 4 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 189 | 0 | 0 | 39.791 | 112.3333 | 11.7936 | 86.148 | -75 | 1.4678 | 116.5149 | -0.81993 | 188.1801 | 59.6498 | 0 | 59.6498 | 60.98 | 59.6498 | 4/22/9:00
4 | 22 | 1900-01-09 | 17.2 | 316 | 8 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 316 | 0 | 0 | 39.791 | 112.375 | 11.808 | 86.148 | -75 | 1.4763 | 131.5171 | -2.9406 | 313.0594 | 99.2344 | 0 | 99.2344 | 62.96 | 99.2344 | 4/22/10:00
4 | 22 | 1900-01-10 | 19.4 | 285 | 8 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 285 | 0 | 0 | 39.791 | 112.4167 | 11.8223 | 86.148 | -75 | 1.4848 | 146.5192 | -3.9694 | 281.0306 | 89.0818 | 0 | 89.0818 | 66.92 | 89.0818 | 4/22/11:00
4 | 22 | 1900-01-11 | 20 | 409 | 6 | 68 | 0 | 1 | 0 | 68 | 0 | 409 | 0 | 0 | 39.791 | 112.4583 | 11.8366 | 86.148 | -75 | 1.4933 | 161.5213 | -3.492 | 405.508 | 128.539 | 0 | 128.539 | 68 | 128.539 | 4/22/12:00
4 | 22 | 1900-01-12 | 18.3 | 226 | 4 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 226 | 0 | 0 | 39.791 | 112.5 | 11.8509 | 86.148 | -75 | 1.5018 | 176.5235 | -2.4768 | 223.5232 | 70.853 | 0 | 70.853 | 64.94 | 70.853 | 4/22/13:00
4 | 22 | 1900-01-13 | 17.8 | 374 | 3 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 374 | 0 | 0 | 39.791 | 112.5417 | 11.8653 | 86.148 | -75 | 1.5103 | 191.5256 | -1.8156 | 372.1844 | 117.9759 | 0 | 117.9759 | 64.04 | 117.9759 | 4/22/14:00
4 | 22 | 1900-01-14 | 18.3 | 429 | 3 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 429 | 0 | 0 | 39.791 | 112.5833 | 11.8796 | 86.148 | -75 | 1.5188 | 206.5277 | -1.6231 | 427.3769 | 135.471 | 0 | 135.471 | 64.94 | 135.471 | 4/22/15:00
4 | 22 | 1900-01-15 | 18.9 | 322 | 1 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 322 | 0 | 0 | 39.791 | 112.625 | 11.8939 | 86.148 | -75 | 1.5272 | 221.5298 | -0.43097 | 321.569 | 101.9318 | 0 | 101.9318 | 66.02 | 101.9318 | 4/22/16:00
4 | 22 | 1900-01-16 | 17.8 | 151 | 1 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 151 | 0 | 0 | 39.791 | 112.6667 | 11.9082 | 86.148 | -75 | 1.5356 | 236.5319 | -0.28257 | 150.7174 | 47.7748 | 0 | 47.7748 | 64.04 | 47.7748 | 4/22/17:00
4 | 22 | 1900-01-17 | 16.1 | 98 | 1 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 98 | 0 | 0 | 39.791 | 112.7083 | 11.9224 | 86.148 | -75 | 1.5441 | 251.534 | -0.10592 | 97.8941 | 31.0307 | 0 | 31.0307 | 60.98 | 31.0307 | 4/22/18:00
4 | 22 | 1900-01-18 | 13.3 | 46 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 46 | 0 | 0 | 39.791 | 112.75 | 11.9367 | 86.148 | -75 | 1.5525 | 266.5361 | 0 | 46 | 14.5812 | 0 | 14.5812 | 55.94 | 14.5812 | 4/22/19:00
4 | 22 | 1900-01-19 | 12.8 | 11 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 11 | 0 | 0 | 39.791 | 112.7917 | 11.951 | 86.148 | -75 | 1.5609 | 281.5382 | 0 | 11 | 3.4868 | 0 | 3.4868 | 55.04 | 3.4868 | 4/22/20:00
4 | 22 | 1900-01-20 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 112.8333 | 11.9653 | 86.148 | -75 | 1.5692 | 296.5403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/22/21:00
4 | 22 | 1900-01-21 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 112.875 | 11.9795 | 86.148 | -75 | 1.5776 | 311.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/22/22:00
4 | 22 | 1900-01-22 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 112.9167 | 11.9938 | 86.148 | -75 | 1.5859 | 326.5445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/22/23:00
4 | 22 | 1900-01-23 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 112.9583 | 12.0081 | 86.148 | -75 | 1.5943 | 341.5466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/22/24:00
4 | 23 | 1899-12-31 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113 | 12.0223 | 86.148 | -75 | 1.6026 | -3.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/1:00
4 | 23 | 1900-01-01 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113.0417 | 12.0366 | 86.148 | -75 | 1.6109 | 11.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/2:00
4 | 23 | 1900-01-02 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113.0833 | 12.0508 | 86.148 | -75 | 1.6192 | 26.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/3:00
4 | 23 | 1900-01-03 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113.125 | 12.065 | 86.148 | -75 | 1.6275 | 41.5549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/4:00
4 | 23 | 1900-01-04 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113.1667 | 12.0793 | 86.148 | -75 | 1.6357 | 56.5569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/5:00
4 | 23 | 1900-01-05 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113.2083 | 12.0935 | 86.148 | -75 | 1.644 | 71.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/6:00
4 | 23 | 1900-01-06 | 7.2 | 34 | 59 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 34 | 0 | 0 | 39.791 | 113.25 | 12.1077 | 86.148 | -75 | 1.6522 | 86.561 | 10.5789 | 44.5789 | 14.1307 | 14.1307 | 0 | 0 | 0 | 4/23/7:00
4 | 23 | 1900-01-07 | 10.6 | 70 | 1 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 70 | 0 | 0 | 39.791 | 113.2917 | 12.1219 | 86.148 | -75 | 1.6604 | 101.5631 | -0.016193 | 69.9838 | 22.1836 | 22.1836 | 0 | 0 | 0 | 4/23/8:00
4 | 23 | 1900-01-08 | 13.3 | 218 | 240 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 218 | 0 | 0 | 39.791 | 113.3333 | 12.1361 | 86.148 | -75 | 1.6686 | 116.5652 | -48.3372 | 169.6628 | 53.7801 | 0 | 53.7801 | 55.94 | 53.7801 | 4/23/9:00
4 | 23 | 1900-01-09 | 13.9 | 298 | 4 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 298 | 0 | 0 | 39.791 | 113.375 | 12.1503 | 86.148 | -75 | 1.6768 | 131.5672 | -1.4548 | 296.5452 | 93.9997 | 0 | 93.9997 | 57.02 | 93.9997 | 4/23/10:00
4 | 23 | 1900-01-10 | 15 | 296 | 4 | 59 | 0 | 1 | 0 | 59 | 0 | 296 | 0 | 0 | 39.791 | 113.4167 | 12.1645 | 86.148 | -75 | 1.685 | 146.5692 | -1.968 | 294.032 | 93.203 | 0 | 93.203 | 59 | 93.203 | 4/23/11:00
4 | 23 | 1900-01-11 | 13.9 | 420 | 11 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 420 | 0 | 0 | 39.791 | 113.4583 | 12.1787 | 86.148 | -75 | 1.6931 | 161.5713 | -6.3532 | 413.6468 | 131.1188 | 0 | 131.1188 | 57.02 | 131.1188 | 4/23/12:00
4 | 23 | 1900-01-12 | 12.8 | 199 | 4 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 199 | 0 | 0 | 39.791 | 113.5 | 12.1929 | 86.148 | -75 | 1.7013 | 176.5733 | -2.4582 | 196.5418 | 62.3003 | 0 | 62.3003 | 55.04 | 62.3003 | 4/23/13:00
4 | 23 | 1900-01-13 | 13.9 | 317 | 2 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 317 | 0 | 0 | 39.791 | 113.5417 | 12.2071 | 86.148 | -75 | 1.7094 | 191.5754 | -1.2008 | 315.7992 | 100.1028 | 0 | 100.1028 | 57.02 | 100.1028 | 4/23/14:00
4 | 23 | 1900-01-14 | 14.4 | 365 | 192 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 365 | 0 | 0 | 39.791 | 113.5833 | 12.2212 | 86.148 | -75 | 1.7175 | 206.5774 | -102.9387 | 262.0613 | 83.0689 | 0 | 83.0689 | 57.92 | 83.0689 | 4/23/15:00
4 | 23 | 1900-01-15 | 15 | 292 | 273 | 59 | 0 | 1 | 0 | 59 | 0 | 292 | 0 | 0 | 39.791 | 113.625 | 12.2354 | 86.148 | -75 | 1.7256 | 221.5794 | -116.323 | 175.677 | 55.6865 | 0 | 55.6865 | 59 | 55.6865 | 4/23/16:00
4 | 23 | 1900-01-16 | 13.9 | 232 | 67 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 232 | 0 | 0 | 39.791 | 113.6667 | 12.2496 | 86.148 | -75 | 1.7337 | 236.5814 | -18.6104 | 213.3896 | 67.6408 | 0 | 67.6408 | 57.02 | 67.6408 | 4/23/17:00
4 | 23 | 1900-01-17 | 13.3 | 190 | 56 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 190 | 0 | 0 | 39.791 | 113.7083 | 12.2637 | 86.148 | -75 | 1.7418 | 251.5834 | -5.6711 | 184.3289 | 58.429 | 0 | 58.429 | 55.94 | 58.429 | 4/23/18:00
4 | 23 | 1900-01-18 | 12.8 | 66 | 57 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 66 | 0 | 0 | 39.791 | 113.75 | 12.2779 | 86.148 | -75 | 1.7498 | 266.5855 | 5.2085 | 71.2085 | 22.5719 | 0 | 22.5719 | 55.04 | 22.5719 | 4/23/19:00
4 | 23 | 1900-01-19 | 11.7 | 14 | 1 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 14 | 0 | 0 | 39.791 | 113.7917 | 12.292 | 86.148 | -75 | 1.7579 | 281.5875 | 0.28705 | 14.2871 | 4.5287 | 4.5287 | 0 | 0 | 0 | 4/23/20:00
4 | 23 | 1900-01-20 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113.8333 | 12.3061 | 86.148 | -75 | 1.7659 | 296.5895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/21:00
4 | 23 | 1900-01-21 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113.875 | 12.3203 | 86.148 | -75 | 1.7739 | 311.5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/22:00
4 | 23 | 1900-01-22 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113.9167 | 12.3344 | 86.148 | -75 | 1.7819 | 326.5935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/23:00
4 | 23 | 1900-01-23 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 113.9583 | 12.3485 | 86.148 | -75 | 1.7899 | 341.5955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/23/24:00
4 | 24 | 1899-12-31 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114 | 12.3626 | 86.148 | -75 | 1.7979 | -3.4025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/1:00
4 | 24 | 1900-01-01 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114.0417 | 12.3767 | 86.148 | -75 | 1.8058 | 11.5995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/2:00
4 | 24 | 1900-01-02 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114.0833 | 12.3909 | 86.148 | -75 | 1.8138 | 26.6014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/3:00
4 | 24 | 1900-01-03 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114.125 | 12.405 | 86.148 | -75 | 1.8217 | 41.6034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/4:00
4 | 24 | 1900-01-04 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114.1667 | 12.419 | 86.148 | -75 | 1.8296 | 56.6054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/5:00
4 | 24 | 1900-01-05 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114.2083 | 12.4331 | 86.148 | -75 | 1.8375 | 71.6074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/6:00
4 | 24 | 1900-01-06 | 8.3 | 19 | 2 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 19 | 0 | 0 | 39.791 | 114.25 | 12.4472 | 86.148 | -75 | 1.8454 | 86.6093 | 0.36464 | 19.3646 | 6.1383 | 6.1383 | 0 | 0 | 0 | 4/24/7:00
4 | 24 | 1900-01-07 | 9.4 | 93 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 93 | 0 | 0 | 39.791 | 114.2917 | 12.4613 | 86.148 | -75 | 1.8532 | 101.6113 | 0 | 93 | 29.4794 | 29.4794 | 0 | 0 | 0 | 4/24/8:00
4 | 24 | 1900-01-08 | 10.6 | 167 | 9 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 167 | 0 | 0 | 39.791 | 114.3333 | 12.4754 | 86.148 | -75 | 1.8611 | 116.6133 | -1.7805 | 165.2195 | 52.3717 | 52.3717 | 0 | 0 | 0 | 4/24/9:00
4 | 24 | 1900-01-09 | 11.1 | 267 | 5 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 267 | 0 | 0 | 39.791 | 114.375 | 12.4894 | 86.148 | -75 | 1.8689 | 131.6152 | -1.7991 | 265.2009 | 84.064 | 84.064 | 0 | 0 | 0 | 4/24/10:00
4 | 24 | 1900-01-10 | 11.7 | 291 | 9 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 291 | 0 | 0 | 39.791 | 114.4167 | 12.5035 | 86.148 | -75 | 1.8767 | 146.6172 | -4.3905 | 286.6095 | 90.8502 | 90.8502 | 0 | 0 | 0 | 4/24/11:00
4 | 24 | 1900-01-11 | 12.8 | 385 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 385 | 0 | 0 | 39.791 | 114.4583 | 12.5175 | 86.148 | -75 | 1.8845 | 161.6191 | 0 | 385 | 122.0383 | 0 | 122.0383 | 55.04 | 122.0383 | 4/24/12:00
4 | 24 | 1900-01-12 | 14.4 | 294 | 522 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 294 | 0 | 0 | 39.791 | 114.5 | 12.5316 | 86.148 | -75 | 1.8923 | 176.6211 | -318.3737 | -24.3737 | -7.726 | 0 | -7.726 | 57.92 | -7.726 | 4/24/13:00
4 | 24 | 1900-01-13 | 15.6 | 264 | 668 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 264 | 0 | 0 | 39.791 | 114.5417 | 12.5456 | 86.148 | -75 | 1.9001 | 191.623 | -397.8883 | -133.8883 | -42.4403 | 0 | -42.4403 | 60.08 | -42.4403 | 4/24/14:00
4 | 24 | 1900-01-14 | 15 | 403 | 120 | 59 | 0 | 1 | 0 | 59 | 0 | 403 | 0 | 0 | 39.791 | 114.5833 | 12.5597 | 86.148 | -75 | 1.9079 | 206.625 | -63.7556 | 339.2444 | 107.5345 | 0 | 107.5345 | 59 | 107.5345 | 4/24/15:00
4 | 24 | 1900-01-15 | 15.6 | 296 | 257 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 296 | 0 | 0 | 39.791 | 114.625 | 12.5737 | 86.148 | -75 | 1.9156 | 221.6269 | -108.2636 | 187.7364 | 59.5092 | 0 | 59.5092 | 60.08 | 59.5092 | 4/24/16:00
4 | 24 | 1900-01-16 | 16.1 | 206 | 358 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 206 | 0 | 0 | 39.791 | 114.6667 | 12.5877 | 86.148 | -75 | 1.9233 | 236.6288 | -97.7423 | 108.2577 | 34.3158 | 0 | 34.3158 | 60.98 | 34.3158 | 4/24/17:00
4 | 24 | 1900-01-17 | 15.6 | 87 | 592 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 87 | 0 | 0 | 39.791 | 114.7083 | 12.6017 | 86.148 | -75 | 1.9311 | 251.6308 | -57.2386 | 29.7614 | 9.4339 | 0 | 9.4339 | 60.08 | 9.4339 | 4/24/18:00
4 | 24 | 1900-01-18 | 13.9 | 52 | 325 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 52 | 0 | 0 | 39.791 | 114.75 | 12.6157 | 86.148 | -75 | 1.9388 | 266.6327 | 31.1149 | 83.1149 | 26.346 | 0 | 26.346 | 57.02 | 26.346 | 4/24/19:00
4 | 24 | 1900-01-19 | 12.2 | 12 | 16 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 12 | 0 | 0 | 39.791 | 114.7917 | 12.6297 | 86.148 | -75 | 1.9465 | 281.6346 | 4.6583 | 16.6583 | 5.2804 | 5.2804 | 0 | 0 | 0 | 4/24/20:00
4 | 24 | 1900-01-20 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114.8333 | 12.6437 | 86.148 | -75 | 1.9541 | 296.6365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/21:00
4 | 24 | 1900-01-21 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114.875 | 12.6577 | 86.148 | -75 | 1.9618 | 311.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/22:00
4 | 24 | 1900-01-22 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114.9167 | 12.6717 | 86.148 | -75 | 1.9694 | 326.6404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/23:00
4 | 24 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 114.9583 | 12.6857 | 86.148 | -75 | 1.977 | 341.6423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/24/24:00
4 | 25 | 1899-12-31 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 115 | 12.6997 | 86.148 | -75 | 1.9847 | -3.3558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/25/1:00
4 | 25 | 1900-01-01 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 115.0417 | 12.7137 | 86.148 | -75 | 1.9923 | 11.6461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/25/2:00
4 | 25 | 1900-01-02 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 115.0833 | 12.7276 | 86.148 | -75 | 1.9998 | 26.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/25/3:00
4 | 25 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 115.125 | 12.7416 | 86.148 | -75 | 2.0074 | 41.6499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/25/4:00
4 | 25 | 1900-01-04 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 115.1667 | 12.7555 | 86.148 | -75 | 2.015 | 56.6517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/25/5:00
4 | 25 | 1900-01-05 | 3.3 | 1 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 1 | 0 | 0 | 39.791 | 115.2083 | 12.7695 | 86.148 | -75 | 2.0225 | 71.6536 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 4/25/6:00
4 | 25 | 1900-01-06 | 4.4 | 33 | 138 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 33 | 0 | 0 | 39.791 | 115.25 | 12.7834 | 86.148 | -75 | 2.03 | 86.6555 | 25.5747 | 58.5747 | 18.5672 | 18.5672 | 0 | 0 | 0 | 4/25/7:00
4 | 25 | 1900-01-07 | 7.2 | 75 | 486 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 75 | 0 | 0 | 39.791 | 115.2917 | 12.7974 | 86.148 | -75 | 2.0375 | 101.6574 | -4.6861 | 70.3139 | 22.2883 | 22.2883 | 0 | 0 | 0 | 4/25/8:00
4 | 25 | 1900-01-08 | 8.9 | 109 | 668 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 109 | 0 | 0 | 39.791 | 115.3333 | 12.8113 | 86.148 | -75 | 2.045 | 116.6593 | -129.7704 | -20.7704 | -6.5839 | -6.5839 | 0 | 0 | 0 | 4/25/9:00
4 | 25 | 1900-01-09 | 11.1 | 136 | 765 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 136 | 0 | 0 | 39.791 | 115.375 | 12.8252 | 86.148 | -75 | 2.0525 | 131.6611 | -272.3072 | -136.3072 | -43.207 | -43.207 | 0 | 0 | 0 | 4/25/10:00
4 | 25 | 1900-01-10 | 12.8 | 154 | 820 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 154 | 0 | 0 | 39.791 | 115.4167 | 12.8391 | 86.148 | -75 | 2.0599 | 146.663 | -396.6205 | -242.6205 | -76.9064 | 0 | -76.9064 | 55.04 | -76.9064 | 4/25/11:00
4 | 25 | 1900-01-11 | 13.9 | 165 | 855 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 165 | 0 | 0 | 39.791 | 115.4583 | 12.853 | 86.148 | -75 | 2.0674 | 161.6648 | -486.2672 | -321.2672 | -101.8361 | 0 | -101.8361 | 57.02 | -101.8361 | 4/25/12:00
4 | 25 | 1900-01-12 | 15 | 170 | 864 | 59 | 0 | 1 | 0 | 59 | 0 | 170 | 0 | 0 | 39.791 | 115.5 | 12.8669 | 86.148 | -75 | 2.0748 | 176.6667 | -522.9833 | -352.9833 | -111.8895 | 0 | -111.8895 | 59 | -111.8895 | 4/25/13:00
4 | 25 | 1900-01-13 | 16.1 | 168 | 859 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 168 | 0 | 0 | 39.791 | 115.5417 | 12.8808 | 86.148 | -75 | 2.0822 | 191.6686 | -507.5825 | -339.5825 | -107.6417 | 0 | -107.6417 | 60.98 | -107.6417 | 4/25/14:00
4 | 25 | 1900-01-14 | 17.2 | 160 | 837 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 160 | 0 | 0 | 39.791 | 115.5833 | 12.8947 | 86.148 | -75 | 2.0896 | 206.6704 | -440.6759 | -280.6759 | -88.9694 | 0 | -88.9694 | 62.96 | -88.9694 | 4/25/15:00
4 | 25 | 1900-01-15 | 17.8 | 145 | 795 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 145 | 0 | 0 | 39.791 | 115.625 | 12.9086 | 86.148 | -75 | 2.097 | 221.6723 | -331.0981 | -186.0981 | -58.9898 | 0 | -58.9898 | 64.04 | -58.9898 | 4/25/16:00
4 | 25 | 1900-01-16 | 18.3 | 121 | 719 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 121 | 0 | 0 | 39.791 | 115.6667 | 12.9225 | 86.148 | -75 | 2.1044 | 236.6741 | -192.9338 | -71.9338 | -22.8018 | 0 | -22.8018 | 64.94 | -22.8018 | 4/25/17:00
4 | 25 | 1900-01-17 | 17.8 | 90 | 583 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 90 | 0 | 0 | 39.791 | 115.7083 | 12.9364 | 86.148 | -75 | 2.1117 | 251.6759 | -53.734 | 36.266 | 11.4957 | 0 | 11.4957 | 64.04 | 11.4957 | 4/25/18:00
4 | 25 | 1900-01-18 | 16.1 | 54 | 315 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 54 | 0 | 0 | 39.791 | 115.75 | 12.9503 | 86.148 | -75 | 2.1191 | 266.6778 | 31.509 | 85.509 | 27.1048 | 0 | 27.1048 | 60.98 | 27.1048 | 4/25/19:00
4 | 25 | 1900-01-19 | 14.4 | 13 | 16 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 13 | 0 | 0 | 39.791 | 115.7917 | 12.9641 | 86.148 | -75 | 2.1264 | 281.6796 | 4.7226 | 17.7226 | 5.6177 | 0 | 5.6177 | 57.92 | 5.6177 | 4/25/20:00
4 | 25 | 1900-01-20 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 115.8333 | 12.978 | 86.148 | -75 | 2.1337 | 296.6814 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 4/25/21:00
4 | 25 | 1900-01-21 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 115.875 | 12.9918 | 86.148 | -75 | 2.141 | 311.6832 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 4/25/22:00
4 | 25 | 1900-01-22 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 115.9167 | 13.0057 | 86.148 | -75 | 2.1483 | 326.6851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/25/23:00
4 | 25 | 1900-01-23 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 115.9583 | 13.0195 | 86.148 | -75 | 2.1555 | 341.6869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/25/24:00
4 | 26 | 1899-12-31 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 116 | 13.0334 | 86.148 | -75 | 2.1628 | -3.3113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/26/1:00
4 | 26 | 1900-01-01 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 116.0417 | 13.0472 | 86.148 | -75 | 2.17 | 11.6905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/26/2:00
4 | 26 | 1900-01-02 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 116.0833 | 13.061 | 86.148 | -75 | 2.1772 | 26.6923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/26/3:00
4 | 26 | 1900-01-03 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 116.125 | 13.0748 | 86.148 | -75 | 2.1844 | 41.6941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/26/4:00
4 | 26 | 1900-01-04 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 116.1667 | 13.0886 | 86.148 | -75 | 2.1916 | 56.6959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/26/5:00
4 | 26 | 1900-01-05 | 5.6 | 1 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 1 | 0 | 0 | 39.791 | 116.2083 | 13.1024 | 86.148 | -75 | 2.1988 | 71.6977 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 4/26/6:00
4 | 26 | 1900-01-06 | 7.2 | 38 | 67 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 38 | 0 | 0 | 39.791 | 116.25 | 13.1162 | 86.148 | -75 | 2.2059 | 86.6995 | 12.6171 | 50.6171 | 16.0447 | 16.0447 | 0 | 0 | 0 | 4/26/7:00
4 | 26 | 1900-01-07 | 9.4 | 94 | 367 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 94 | 0 | 0 | 39.791 | 116.2917 | 13.13 | 86.148 | -75 | 2.2131 | 101.7013 | -2.3416 | 91.6584 | 29.0541 | 29.0541 | 0 | 0 | 0 | 4/26/8:00
4 | 26 | 1900-01-08 | 11.7 | 141 | 556 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 141 | 0 | 0 | 39.791 | 116.3333 | 13.1438 | 86.148 | -75 | 2.2202 | 116.703 | -106.0345 | 34.9655 | 11.0834 | 11.0834 | 0 | 0 | 0 | 4/26/9:00
4 | 26 | 1900-01-09 | 14.4 | 178 | 667 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 178 | 0 | 0 | 39.791 | 116.375 | 13.1576 | 86.148 | -75 | 2.2273 | 131.7048 | -234.8506 | -56.8506 | -18.0206 | 0 | -18.0206 | 57.92 | -18.0206 | 4/26/10:00
4 | 26 | 1900-01-10 | 16.1 | 204 | 737 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 204 | 0 | 0 | 39.791 | 116.4167 | 13.1714 | 86.148 | -75 | 2.2344 | 146.7066 | -353.4231 | -149.4231 | -47.3645 | 0 | -47.3645 | 60.98 | -47.3645 | 4/26/11:00
4 | 26 | 1900-01-11 | 17.8 | 220 | 767 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 220 | 0 | 0 | 39.791 | 116.4583 | 13.1851 | 86.148 | -75 | 2.2415 | 161.7084 | -432.8533 | -212.8533 | -67.4708 | 0 | -67.4708 | 64.04 | -67.4708 | 4/26/12:00
4 | 26 | 1900-01-12 | 18.3 | 226 | 780 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 226 | 0 | 0 | 39.791 | 116.5 | 13.1989 | 86.148 | -75 | 2.2485 | 176.7101 | -468.5641 | -242.5641 | -76.8886 | 0 | -76.8886 | 64.94 | -76.8886 | 4/26/13:00
4 | 26 | 1900-01-13 | 19.4 | 223 | 774 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 223 | 0 | 0 | 39.791 | 116.5417 | 13.2126 | 86.148 | -75 | 2.2556 | 191.7119 | -453.7115 | -230.7115 | -73.1315 | 0 | -73.1315 | 66.92 | -73.1315 | 4/26/14:00
4 | 26 | 1900-01-14 | 20 | 212 | 746 | 68 | 0 | 1 | 0 | 68 | 0 | 212 | 0 | 0 | 39.791 | 116.5833 | 13.2264 | 86.148 | -75 | 2.2626 | 206.7137 | -389.2137 | -177.2137 | -56.1736 | 0 | -56.1736 | 68 | -56.1736 | 4/26/15:00
4 | 26 | 1900-01-15 | 21.1 | 190 | 696 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 190 | 0 | 0 | 39.791 | 116.625 | 13.2401 | 86.148 | -75 | 2.2696 | 221.7154 | -286.573 | -96.573 | -30.612 | 0 | -30.612 | 69.98 | -30.612 | 4/26/16:00
4 | 26 | 1900-01-16 | 20.6 | 158 | 611 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 158 | 0 | 0 | 39.791 | 116.6667 | 13.2539 | 86.148 | -75 | 2.2766 | 236.7172 | -161.126 | -3.126 | -0.99089 | 0 | -0.99089 | 69.08 | -0.99089 | 4/26/17:00
4 | 26 | 1900-01-17 | 20 | 115 | 462 | 68 | 0 | 1 | 0 | 68 | 0 | 115 | 0 | 0 | 39.791 | 116.7083 | 13.2676 | 86.148 | -75 | 2.2836 | 251.7189 | -40.5247 | 74.4753 | 23.6074 | 0 | 23.6074 | 68 | 23.6074 | 4/26/18:00
4 | 26 | 1900-01-18 | 18.9 | 70 | 188 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 70 | 0 | 0 | 39.791 | 116.75 | 13.2813 | 86.148 | -75 | 2.2906 | 266.7206 | 19.5984 | 89.5984 | 28.4011 | 0 | 28.4011 | 66.02 | 28.4011 | 4/26/19:00
4 | 26 | 1900-01-19 | 17.2 | 13 | 2 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 13 | 0 | 0 | 39.791 | 116.7917 | 13.295 | 86.148 | -75 | 2.2975 | 281.7224 | 0.59821 | 13.5982 | 4.3104 | 0 | 4.3104 | 62.96 | 4.3104 | 4/26/20:00
4 | 26 | 1900-01-20 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 116.8333 | 13.3087 | 86.148 | -75 | 2.3045 | 296.7241 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 4/26/21:00
4 | 26 | 1900-01-21 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 116.875 | 13.3225 | 86.148 | -75 | 2.3114 | 311.7258 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 4/26/22:00
4 | 26 | 1900-01-22 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 116.9167 | 13.3362 | 86.148 | -75 | 2.3183 | 326.7276 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 4/26/23:00
4 | 26 | 1900-01-23 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 116.9583 | 13.3498 | 86.148 | -75 | 2.3252 | 341.7293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/26/24:00
4 | 27 | 1899-12-31 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 117 | 13.3635 | 86.148 | -75 | 2.3321 | -3.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/27/1:00
4 | 27 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 117.0417 | 13.3772 | 86.148 | -75 | 2.3389 | 11.7327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/27/2:00
4 | 27 | 1900-01-02 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 117.0833 | 13.3909 | 86.148 | -75 | 2.3458 | 26.7344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/27/3:00
4 | 27 | 1900-01-03 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 117.125 | 13.4046 | 86.148 | -75 | 2.3526 | 41.7362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/27/4:00
4 | 27 | 1900-01-04 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 117.1667 | 13.4182 | 86.148 | -75 | 2.3594 | 56.7379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/27/5:00
4 | 27 | 1900-01-05 | 9.4 | 1 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 1 | 0 | 0 | 39.791 | 117.2083 | 13.4319 | 86.148 | -75 | 2.3662 | 71.7396 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 4/27/6:00
4 | 27 | 1900-01-06 | 10.6 | 37 | 11 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 37 | 0 | 0 | 39.791 | 117.25 | 13.4455 | 86.148 | -75 | 2.373 | 86.7412 | 2.1042 | 39.1042 | 12.3954 | 12.3954 | 0 | 0 | 0 | 4/27/7:00
4 | 27 | 1900-01-07 | 12.2 | 113 | 233 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 113 | 0 | 0 | 39.791 | 117.2917 | 13.4592 | 86.148 | -75 | 2.3798 | 101.7429 | -0.72897 | 112.271 | 35.588 | 35.588 | 0 | 0 | 0 | 4/27/8:00
4 | 27 | 1900-01-08 | 13.9 | 147 | 505 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 147 | 0 | 0 | 39.791 | 117.3333 | 13.4728 | 86.148 | -75 | 2.3865 | 116.7446 | -94.5165 | 52.4835 | 16.6364 | 0 | 16.6364 | 57.02 | 16.6364 | 4/27/9:00
4 | 27 | 1900-01-09 | 17.2 | 161 | 659 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 161 | 0 | 0 | 39.791 | 117.375 | 13.4864 | 86.148 | -75 | 2.3932 | 131.7463 | -229.4988 | -68.4988 | -21.7129 | 0 | -21.7129 | 62.96 | -21.7129 | 4/27/10:00
4 | 27 | 1900-01-10 | 19.4 | 206 | 700 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 206 | 0 | 0 | 39.791 | 117.4167 | 13.5001 | 86.148 | -75 | 2.4 | 146.748 | -332.7916 | -126.7916 | -40.1907 | 0 | -40.1907 | 66.92 | -40.1907 | 4/27/11:00
4 | 27 | 1900-01-11 | 21.1 | 193 | 789 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 193 | 0 | 0 | 39.791 | 117.4583 | 13.5137 | 86.148 | -75 | 2.4067 | 161.7497 | -441.8227 | -248.8227 | -78.8725 | 0 | -78.8725 | 69.98 | -78.8725 | 4/27/12:00
4 | 27 | 1900-01-12 | 22.2 | 198 | 775 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 198 | 0 | 0 | 39.791 | 117.5 | 13.5273 | 86.148 | -75 | 2.4134 | 176.7513 | -462.0308 | -264.0308 | -83.6931 | 0 | -83.6931 | 71.96 | -83.6931 | 4/27/13:00
4 | 27 | 1900-01-13 | 22.8 | 191 | 753 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 191 | 0 | 0 | 39.791 | 117.5417 | 13.5409 | 86.148 | -75 | 2.42 | 191.753 | -437.8825 | -246.8825 | -78.2574 | 0 | -78.2574 | 73.04 | -78.2574 | 4/27/14:00
4 | 27 | 1900-01-14 | 21.1 | 391 | 142 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 391 | 0 | 0 | 39.791 | 117.5833 | 13.5545 | 86.148 | -75 | 2.4267 | 206.7547 | -73.4166 | 317.5834 | 100.6684 | 0 | 100.6684 | 69.98 | 100.6684 | 4/27/15:00
4 | 27 | 1900-01-15 | 20 | 176 | 675 | 68 | 0 | 1 | 0 | 68 | 0 | 176 | 0 | 0 | 39.791 | 117.625 | 13.5681 | 86.148 | -75 | 2.4333 | 221.7563 | -274.7677 | -98.7677 | -31.3076 | 0 | -31.3076 | 68 | -31.3076 | 4/27/16:00
4 | 27 | 1900-01-16 | 20 | 219 | 450 | 68 | 0 | 1 | 0 | 68 | 0 | 219 | 0 | 0 | 39.791 | 117.6667 | 13.5817 | 86.148 | -75 | 2.4399 | 236.758 | -116.614 | 102.386 | 32.4546 | 0 | 32.4546 | 68 | 32.4546 | 4/27/17:00
4 | 27 | 1900-01-17 | 19.4 | 165 | 339 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 165 | 0 | 0 | 39.791 | 117.7083 | 13.5952 | 86.148 | -75 | 2.4466 | 251.7596 | -28.2494 | 136.7506 | 43.3475 | 0 | 43.3475 | 66.92 | 43.3475 | 4/27/18:00
4 | 27 | 1900-01-18 | 17.8 | 72 | 144 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 72 | 0 | 0 | 39.791 | 117.75 | 13.6088 | 86.148 | -75 | 2.4531 | 266.7613 | 15.6085 | 87.6085 | 27.7704 | 0 | 27.7704 | 64.04 | 27.7704 | 4/27/19:00
4 | 27 | 1900-01-19 | 14.4 | 12 | 2 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 12 | 0 | 0 | 39.791 | 117.7917 | 13.6224 | 86.148 | -75 | 2.4597 | 281.7629 | 0.60594 | 12.6059 | 3.9959 | 0 | 3.9959 | 57.92 | 3.9959 | 4/27/20:00
4 | 27 | 1900-01-20 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 117.8333 | 13.6359 | 86.148 | -75 | 2.4663 | 296.7646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/27/21:00
4 | 27 | 1900-01-21 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 117.875 | 13.6495 | 86.148 | -75 | 2.4728 | 311.7662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/27/22:00
4 | 27 | 1900-01-22 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 117.9167 | 13.663 | 86.148 | -75 | 2.4794 | 326.7678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/27/23:00
4 | 27 | 1900-01-23 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 117.9583 | 13.6766 | 86.148 | -75 | 2.4859 | 341.7695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/27/24:00
4 | 28 | 1899-12-31 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 118 | 13.6901 | 86.148 | -75 | 2.4924 | -3.2289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/28/1:00
4 | 28 | 1900-01-01 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 118.0417 | 13.7037 | 86.148 | -75 | 2.4989 | 11.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/28/2:00
4 | 28 | 1900-01-02 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 118.0833 | 13.7172 | 86.148 | -75 | 2.5053 | 26.7743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/28/3:00
4 | 28 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 118.125 | 13.7307 | 86.148 | -75 | 2.5118 | 41.7759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/28/4:00
4 | 28 | 1900-01-04 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 118.1667 | 13.7442 | 86.148 | -75 | 2.5182 | 56.7776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/28/5:00
4 | 28 | 1900-01-05 | 4.4 | 1 | 5 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 1 | 0 | 0 | 39.791 | 118.2083 | 13.7577 | 86.148 | -75 | 2.5246 | 71.7792 | 1.9278 | 2.9278 | 0.92807 | 0.92807 | 0 | 0 | 0 | 4/28/6:00
4 | 28 | 1900-01-06 | 6.7 | 43 | 161 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 43 | 0 | 0 | 39.791 | 118.25 | 13.7712 | 86.148 | -75 | 2.531 | 86.7808 | 31.2752 | 74.2752 | 23.5439 | 23.5439 | 0 | 0 | 0 | 4/28/7:00
4 | 28 | 1900-01-07 | 8.3 | 103 | 358 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 103 | 0 | 0 | 39.791 | 118.2917 | 13.7847 | 86.148 | -75 | 2.5374 | 101.7824 | 0.040061 | 103.0401 | 32.6619 | 32.6619 | 0 | 0 | 0 | 4/28/8:00
4 | 28 | 1900-01-08 | 11.1 | 90 | 764 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 90 | 0 | 0 | 39.791 | 118.3333 | 13.7982 | 86.148 | -75 | 2.5438 | 116.7839 | -140.2885 | -50.2885 | -15.9406 | -15.9406 | 0 | 0 | 0 | 4/28/9:00
4 | 28 | 1900-01-09 | 12.8 | 98 | 861 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 98 | 0 | 0 | 39.791 | 118.375 | 13.8117 | 86.148 | -75 | 2.5501 | 131.7855 | -296.5446 | -198.5446 | -62.9352 | 0 | -62.9352 | 55.04 | -62.9352 | 4/28/10:00
4 | 28 | 1900-01-10 | 13.9 | 104 | 901 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 104 | 0 | 0 | 39.791 | 118.4167 | 13.8251 | 86.148 | -75 | 2.5565 | 146.7871 | -424.6472 | -320.6472 | -101.6396 | 0 | -101.6396 | 57.02 | -101.6396 | 4/28/11:00
4 | 28 | 1900-01-11 | 13.9 | 111 | 929 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 111 | 0 | 0 | 39.791 | 118.4583 | 13.8386 | 86.148 | -75 | 2.5628 | 161.7887 | -516.1824 | -405.1824 | -128.4358 | 0 | -128.4358 | 57.02 | -128.4358 | 4/28/12:00
4 | 28 | 1900-01-12 | 15.6 | 199 | 876 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 199 | 0 | 0 | 39.791 | 118.5 | 13.852 | 86.148 | -75 | 2.5691 | 176.7903 | -518.2799 | -319.2799 | -101.2061 | 0 | -101.2061 | 60.08 | -101.2061 | 4/28/13:00
4 | 28 | 1900-01-13 | 16.1 | 177 | 804 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 177 | 0 | 0 | 39.791 | 118.5417 | 13.8655 | 86.148 | -75 | 2.5754 | 191.7918 | -463.813 | -286.813 | -90.9147 | 0 | -90.9147 | 60.98 | -90.9147 | 4/28/14:00
4 | 28 | 1900-01-14 | 16.7 | 105 | 873 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 105 | 0 | 0 | 39.791 | 118.5833 | 13.8789 | 86.148 | -75 | 2.5817 | 206.7934 | -447.2806 | -342.2806 | -108.497 | 0 | -108.497 | 62.06 | -108.497 | 4/28/15:00
4 | 28 | 1900-01-15 | 16.7 | 97 | 881 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 97 | 0 | 0 | 39.791 | 118.625 | 13.8924 | 86.148 | -75 | 2.5879 | 221.795 | -354.5488 | -257.5488 | -81.6385 | 0 | -81.6385 | 62.06 | -81.6385 | 4/28/16:00
4 | 28 | 1900-01-16 | 16.7 | 82 | 829 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 82 | 0 | 0 | 39.791 | 118.6667 | 13.9058 | 86.148 | -75 | 2.5942 | 236.7965 | -211.0959 | -129.0959 | -40.9212 | 0 | -40.9212 | 62.06 | -40.9212 | 4/28/17:00
4 | 28 | 1900-01-17 | 16.7 | 70 | 701 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 70 | 0 | 0 | 39.791 | 118.7083 | 13.9192 | 86.148 | -75 | 2.6004 | 251.7981 | -55.3913 | 14.6087 | 4.6307 | 0 | 4.6307 | 62.06 | 4.6307 | 4/28/18:00
4 | 28 | 1900-01-18 | 15 | 44 | 472 | 59 | 0 | 1 | 0 | 59 | 0 | 44 | 0 | 0 | 39.791 | 118.75 | 13.9327 | 86.148 | -75 | 2.6066 | 266.7997 | 53.0823 | 97.0823 | 30.7734 | 0 | 30.7734 | 59 | 30.7734 | 4/28/19:00
4 | 28 | 1900-01-19 | 12.2 | 14 | 72 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 14 | 0 | 0 | 39.791 | 118.7917 | 13.9461 | 86.148 | -75 | 2.6128 | 281.8012 | 22.0866 | 36.0866 | 11.4388 | 11.4388 | 0 | 0 | 0 | 4/28/20:00
4 | 28 | 1900-01-20 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 118.8333 | 13.9595 | 86.148 | -75 | 2.619 | 296.8027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/28/21:00
4 | 28 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 118.875 | 13.9729 | 86.148 | -75 | 2.6252 | 311.8043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/28/22:00
4 | 28 | 1900-01-22 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 118.9167 | 13.9863 | 86.148 | -75 | 2.6313 | 326.8058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/28/23:00
4 | 28 | 1900-01-23 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 118.9583 | 13.9996 | 86.148 | -75 | 2.6374 | 341.8074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/28/24:00
4 | 29 | 1899-12-31 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 119 | 14.013 | 86.148 | -75 | 2.6435 | -3.1911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/29/1:00
4 | 29 | 1900-01-01 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 119.0417 | 14.0264 | 86.148 | -75 | 2.6496 | 11.8104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/29/2:00
4 | 29 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 119.0833 | 14.0398 | 86.148 | -75 | 2.6557 | 26.8119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/29/3:00
4 | 29 | 1900-01-03 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 119.125 | 14.0531 | 86.148 | -75 | 2.6618 | 41.8134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/29/4:00
4 | 29 | 1900-01-04 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 119.1667 | 14.0665 | 86.148 | -75 | 2.6678 | 56.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/29/5:00
4 | 29 | 1900-01-05 | 11.1 | 2 | 6 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 2 | 0 | 0 | 39.791 | 119.2083 | 14.0798 | 86.148 | -75 | 2.6739 | 71.8165 | 2.3296 | 4.3296 | 1.3724 | 1.3724 | 0 | 0 | 0 | 4/29/6:00
4 | 29 | 1900-01-06 | 12.8 | 36 | 261 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 36 | 0 | 0 | 39.791 | 119.25 | 14.0932 | 86.148 | -75 | 2.6799 | 86.818 | 51.4705 | 87.4705 | 27.7266 | 0 | 27.7266 | 55.04 | 27.7266 | 4/29/7:00
4 | 29 | 1900-01-07 | 14.4 | 76 | 562 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 76 | 0 | 0 | 39.791 | 119.2917 | 14.1065 | 86.148 | -75 | 2.6859 | 101.8195 | 1.8773 | 77.8773 | 24.6857 | 0 | 24.6857 | 57.92 | 24.6857 | 4/29/8:00
4 | 29 | 1900-01-08 | 16.7 | 199 | 222 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 199 | 0 | 0 | 39.791 | 119.3333 | 14.1198 | 86.148 | -75 | 2.6919 | 116.821 | -39.9817 | 159.0183 | 50.406 | 0 | 50.406 | 62.06 | 50.406 | 4/29/9:00
4 | 29 | 1900-01-09 | 19.4 | 225 | 471 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 225 | 0 | 0 | 39.791 | 119.375 | 14.1331 | 86.148 | -75 | 2.6979 | 131.8225 | -160.4218 | 64.5782 | 20.4702 | 0 | 20.4702 | 66.92 | 20.4702 | 4/29/10:00
4 | 29 | 1900-01-10 | 21.7 | 227 | 536 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 227 | 0 | 0 | 39.791 | 119.4167 | 14.1465 | 86.148 | -75 | 2.7038 | 146.824 | -250.4269 | -23.4269 | -7.4259 | 0 | -7.4259 | 71.06 | -7.4259 | 4/29/11:00
4 | 29 | 1900-01-11 | 23.9 | 249 | 593 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 249 | 0 | 0 | 39.791 | 119.4583 | 14.1598 | 86.148 | -75 | 2.7097 | 161.8254 | -326.9272 | -77.9272 | -24.7016 | 0 | -24.7016 | 75.02 | -24.7016 | 4/29/12:00
4 | 29 | 1900-01-12 | 25 | 187 | 734 | 77 | 0 | 1 | 0 | 77 | 0 | 187 | 0 | 0 | 39.791 | 119.5 | 14.1731 | 86.148 | -75 | 2.7157 | 176.8269 | -430.9683 | -243.9683 | -77.3337 | 0 | -77.3337 | 77 | -77.3337 | 4/29/13:00
4 | 29 | 1900-01-13 | 26.7 | 100 | 932 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 100 | 0 | 0 | 39.791 | 119.5417 | 14.1864 | 86.148 | -75 | 2.7216 | 191.8284 | -533.371 | -433.371 | -137.371 | 0 | -137.371 | 80.06 | -137.371 | 4/29/14:00
4 | 29 | 1900-01-14 | 27.8 | 97 | 905 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 97 | 0 | 0 | 39.791 | 119.5833 | 14.1996 | 86.148 | -75 | 2.7275 | 206.8299 | -459.4943 | -362.4943 | -114.9044 | 0 | -114.9044 | 82.04 | -114.9044 | 4/29/15:00
4 | 29 | 1900-01-15 | 28.3 | 77 | 837 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 77 | 0 | 0 | 39.791 | 119.625 | 14.2129 | 86.148 | -75 | 2.7333 | 221.8313 | -333.0193 | -256.0193 | -81.1536 | 0 | -81.1536 | 82.94 | -81.1536 | 4/29/16:00
4 | 29 | 1900-01-16 | 28.9 | 159 | 557 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 159 | 0 | 0 | 39.791 | 119.6667 | 14.2262 | 86.148 | -75 | 2.7392 | 236.8328 | -139.3622 | 19.6378 | 6.2248 | 0 | 6.2248 | 84.02 | 6.2248 | 4/29/17:00
4 | 29 | 1900-01-17 | 28.3 | 94 | 465 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 94 | 0 | 0 | 39.791 | 119.7083 | 14.2395 | 86.148 | -75 | 2.745 | 251.8343 | -34.7705 | 59.2295 | 18.7747 | 0 | 18.7747 | 82.94 | 18.7747 | 4/29/18:00
4 | 29 | 1900-01-18 | 27.2 | 99 | 73 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 99 | 0 | 0 | 39.791 | 119.75 | 14.2527 | 86.148 | -75 | 2.7509 | 266.8357 | 8.5013 | 107.5013 | 34.076 | 0 | 34.076 | 80.96 | 34.076 | 4/29/19:00
4 | 29 | 1900-01-19 | 25.6 | 16 | 40 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 16 | 0 | 0 | 39.791 | 119.7917 | 14.266 | 86.148 | -75 | 2.7567 | 281.8372 | 12.4187 | 28.4187 | 9.0082 | 0 | 9.0082 | 78.08 | 9.0082 | 4/29/20:00
4 | 29 | 1900-01-20 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 119.8333 | 14.2792 | 86.148 | -75 | 2.7625 | 296.8386 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 4/29/21:00
4 | 29 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 119.875 | 14.2925 | 86.148 | -75 | 2.7682 | 311.8401 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 4/29/22:00
4 | 29 | 1900-01-22 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 119.9167 | 14.3057 | 86.148 | -75 | 2.774 | 326.8415 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 4/29/23:00
4 | 29 | 1900-01-23 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 119.9583 | 14.3189 | 86.148 | -75 | 2.7797 | 341.8429 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 4/29/24:00
4 | 30 | 1899-12-31 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 120 | 14.3321 | 86.148 | -75 | 2.7855 | -3.1556 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 4/30/1:00
4 | 30 | 1900-01-01 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 120.0417 | 14.3454 | 86.148 | -75 | 2.7912 | 11.8458 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 4/30/2:00
4 | 30 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 120.0833 | 14.3586 | 86.148 | -75 | 2.7969 | 26.8472 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 4/30/3:00
4 | 30 | 1900-01-03 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 120.125 | 14.3718 | 86.148 | -75 | 2.8025 | 41.8486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/30/4:00
4 | 30 | 1900-01-04 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 120.1667 | 14.385 | 86.148 | -75 | 2.8082 | 56.8501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/30/5:00
4 | 30 | 1900-01-05 | 7.8 | 1 | 2 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 1 | 0 | 0 | 39.791 | 120.2083 | 14.3981 | 86.148 | -75 | 2.8139 | 71.8515 | 0.78192 | 1.7819 | 0.56484 | 0.56484 | 0 | 0 | 0 | 4/30/6:00
4 | 30 | 1900-01-06 | 9.4 | 33 | 287 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 33 | 0 | 0 | 39.791 | 120.25 | 14.4113 | 86.148 | -75 | 2.8195 | 86.8529 | 57.4397 | 90.4397 | 28.6678 | 28.6678 | 0 | 0 | 0 | 4/30/7:00
4 | 30 | 1900-01-07 | 9.4 | 61 | 616 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 61 | 0 | 0 | 39.791 | 120.2917 | 14.4245 | 86.148 | -75 | 2.8251 | 101.8543 | 4.0383 | 65.0383 | 20.616 | 20.616 | 0 | 0 | 0 | 4/30/8:00
4 | 30 | 1900-01-08 | 10 | 85 | 769 | 50 | 1 | 0 | 50 | 0 | 0 | 85 | 0 | 0 | 39.791 | 120.3333 | 14.4377 | 86.148 | -75 | 2.8307 | 116.8557 | -135.794 | -50.794 | -16.1008 | -16.1008 | 0 | 0 | 0 | 4/30/9:00
4 | 30 | 1900-01-09 | 11.7 | 105 | 838 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 105 | 0 | 0 | 39.791 | 120.375 | 14.4508 | 86.148 | -75 | 2.8363 | 131.8571 | -282.2327 | -177.2327 | -56.1797 | -56.1797 | 0 | 0 | 0 | 4/30/10:00
4 | 30 | 1900-01-10 | 12.8 | 125 | 879 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 125 | 0 | 0 | 39.791 | 120.4167 | 14.464 | 86.148 | -75 | 2.8418 | 146.8585 | -407.1021 | -282.1021 | -89.4214 | 0 | -89.4214 | 55.04 | -89.4214 | 4/30/11:00
4 | 30 | 1900-01-11 | 13.9 | 169 | 880 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 169 | 0 | 0 | 39.791 | 120.4583 | 14.4771 | 86.148 | -75 | 2.8474 | 161.8598 | -481.3734 | -312.3734 | -99.0169 | 0 | -99.0169 | 57.02 | -99.0169 | 4/30/12:00
4 | 30 | 1900-01-12 | 15 | 137 | 834 | 59 | 0 | 1 | 0 | 59 | 0 | 137 | 0 | 0 | 39.791 | 120.5 | 14.4903 | 86.148 | -75 | 2.8529 | 176.8612 | -485.9642 | -348.9642 | -110.6156 | 0 | -110.6156 | 59 | -110.6156 | 4/30/13:00
4 | 30 | 1900-01-13 | 16.1 | 159 | 887 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 159 | 0 | 0 | 39.791 | 120.5417 | 14.5034 | 86.148 | -75 | 2.8584 | 191.8626 | -503.5797 | -344.5797 | -109.2258 | 0 | -109.2258 | 60.98 | -109.2258 | 4/30/14:00
4 | 30 | 1900-01-14 | 16.7 | 198 | 830 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 198 | 0 | 0 | 39.791 | 120.5833 | 14.5165 | 86.148 | -75 | 2.8639 | 206.864 | -417.6223 | -219.6223 | -69.6164 | 0 | -69.6164 | 62.06 | -69.6164 | 4/30/15:00
4 | 30 | 1900-01-15 | 17.2 | 202 | 785 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 202 | 0 | 0 | 39.791 | 120.625 | 14.5296 | 86.148 | -75 | 2.8694 | 221.8654 | -308.792 | -106.792 | -33.8512 | 0 | -33.8512 | 62.96 | -33.8512 | 4/30/16:00
4 | 30 | 1900-01-16 | 17.2 | 126 | 752 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 126 | 0 | 0 | 39.791 | 120.6667 | 14.5427 | 86.148 | -75 | 2.8749 | 236.8667 | -184.865 | -58.865 | -18.6592 | 0 | -18.6592 | 62.96 | -18.6592 | 4/30/17:00
4 | 30 | 1900-01-17 | 17.2 | 90 | 657 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 90 | 0 | 0 | 39.791 | 120.7083 | 14.5558 | 86.148 | -75 | 2.8803 | 251.8681 | -46.3883 | 43.6117 | 13.8241 | 0 | 13.8241 | 62.96 | 13.8241 | 4/30/18:00
4 | 30 | 1900-01-18 | 16.1 | 58 | 365 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 58 | 0 | 0 | 39.791 | 120.75 | 14.5689 | 86.148 | -75 | 2.8858 | 266.8694 | 43.936 | 101.936 | 32.3119 | 0 | 32.3119 | 60.98 | 32.3119 | 4/30/19:00
4 | 30 | 1900-01-19 | 14.4 | 16 | 35 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 16 | 0 | 0 | 39.791 | 120.7917 | 14.582 | 86.148 | -75 | 2.8912 | 281.8708 | 10.9934 | 26.9934 | 8.5564 | 0 | 8.5564 | 57.92 | 8.5564 | 4/30/20:00
4 | 30 | 1900-01-20 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 120.8333 | 14.5951 | 86.148 | -75 | 2.8966 | 296.8721 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 4/30/21:00
4 | 30 | 1900-01-21 | 12.7 | 0 | 0 | 54.86 | 1 | 0 | 54.86 | 0 | 0 | 0 | 0 | 0 | 39.791 | 120.875 | 14.6082 | 86.148 | -75 | 2.902 | 311.8735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/30/22:00
4 | 30 | 1900-01-22 | 12 | 0 | 0 | 53.6 | 1 | 0 | 53.6 | 0 | 0 | 0 | 0 | 0 | 39.791 | 120.9167 | 14.6213 | 86.148 | -75 | 2.9073 | 326.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/30/23:00
4 | 30 | 1900-01-23 | 11.4 | 0 | 0 | 52.52 | 1 | 0 | 52.52 | 0 | 0 | 0 | 0 | 0 | 39.791 | 120.9583 | 14.6343 | 86.148 | -75 | 2.9127 | 341.8762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4/30/24:00
5 | 1 | 1899-12-31 | 10.8 | 0 | 0 | 51.44 | 1 | 0 | 51.44 | 0 | 0 | 0 | 0 | 0 | 39.791 | 121 | 14.6474 | 86.148 | -75 | 2.918 | -3.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/1/1:00
5 | 1 | 1900-01-01 | 10.2 | 0 | 0 | 50.36 | 1 | 0 | 50.36 | 0 | 0 | 0 | 0 | 0 | 39.791 | 121.0417 | 14.6604 | 86.148 | -75 | 2.9233 | 11.8788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/1/2:00
5 | 1 | 1900-01-02 | 9.5 | 0 | 0 | 49.1 | 1 | 0 | 49.1 | 0 | 0 | 0 | 0 | 0 | 39.791 | 121.0833 | 14.6735 | 86.148 | -75 | 2.9286 | 26.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/1/3:00
5 | 1 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 121.125 | 14.6865 | 86.148 | -75 | 2.9339 | 41.8815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/1/4:00
5 | 1 | 1900-01-04 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 121.1667 | 14.6995 | 86.148 | -75 | 2.9392 | 56.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/1/5:00
5 | 1 | 1900-01-05 | 7.2 | 3 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 3 | 0 | 0 | 39.791 | 121.2083 | 14.7125 | 86.148 | -75 | 2.9444 | 71.8841 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 5/1/6:00
5 | 1 | 1900-01-06 | 7.8 | 47 | 62 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 47 | 0 | 0 | 39.791 | 121.25 | 14.7256 | 86.148 | -75 | 2.9497 | 86.8854 | 12.5895 | 59.5895 | 18.8888 | 18.8888 | 0 | 0 | 0 | 5/1/7:00
5 | 1 | 1900-01-07 | 10.6 | 110 | 316 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 110 | 0 | 0 | 39.791 | 121.2917 | 14.7386 | 86.148 | -75 | 2.9549 | 101.8867 | 3.0832 | 113.0832 | 35.8454 | 35.8454 | 0 | 0 | 0 | 5/1/8:00
5 | 1 | 1900-01-08 | 13.9 | 166 | 495 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 166 | 0 | 0 | 39.791 | 121.3333 | 14.7516 | 86.148 | -75 | 2.9601 | 116.888 | -85.6781 | 80.3219 | 25.4607 | 0 | 25.4607 | 57.02 | 25.4607 | 5/1/9:00
5 | 1 | 1900-01-09 | 16.1 | 275 | 455 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 275 | 0 | 0 | 39.791 | 121.375 | 14.7646 | 86.148 | -75 | 2.9653 | 131.8893 | -151.5175 | 123.4825 | 39.1418 | 0 | 39.1418 | 60.98 | 39.1418 | 5/1/10:00
5 | 1 | 1900-01-10 | 16.1 | 433 | 156 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 433 | 0 | 0 | 39.791 | 121.4167 | 14.7775 | 86.148 | -75 | 2.9704 | 146.8906 | -71.6184 | 361.3816 | 114.5517 | 0 | 114.5517 | 60.98 | 114.5517 | 5/1/11:00
5 | 1 | 1900-01-11 | 17.8 | 393 | 394 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 393 | 0 | 0 | 39.791 | 121.4583 | 14.7905 | 86.148 | -75 | 2.9756 | 161.8919 | -213.8428 | 179.1572 | 56.7897 | 0 | 56.7897 | 64.04 | 56.7897 | 5/1/12:00
5 | 1 | 1900-01-12 | 17.2 | 334 | 554 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 334 | 0 | 0 | 39.791 | 121.5 | 14.8035 | 86.148 | -75 | 2.9807 | 176.8932 | -320.3602 | 13.6398 | 4.3236 | 0 | 4.3236 | 62.96 | 4.3236 | 5/1/13:00
5 | 1 | 1900-01-13 | 17.8 | 398 | 1 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 398 | 0 | 0 | 39.791 | 121.5417 | 14.8165 | 86.148 | -75 | 2.9859 | 191.8945 | -0.56323 | 397.4368 | 125.9805 | 0 | 125.9805 | 64.04 | 125.9805 | 5/1/14:00
5 | 1 | 1900-01-14 | 18.3 | 300 | 63 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 300 | 0 | 0 | 39.791 | 121.5833 | 14.8294 | 86.148 | -75 | 2.991 | 206.8957 | -31.4146 | 268.5854 | 85.1369 | 0 | 85.1369 | 64.94 | 85.1369 | 5/1/15:00
5 | 1 | 1900-01-15 | 18.3 | 293 | 39 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 293 | 0 | 0 | 39.791 | 121.625 | 14.8424 | 86.148 | -75 | 2.996 | 221.897 | -15.1679 | 277.8321 | 88.0679 | 0 | 88.0679 | 64.94 | 88.0679 | 5/1/16:00
5 | 1 | 1900-01-16 | 18.9 | 255 | 1 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 255 | 0 | 0 | 39.791 | 121.6667 | 14.8553 | 86.148 | -75 | 3.0011 | 236.8983 | -0.24153 | 254.7585 | 80.754 | 0 | 80.754 | 66.02 | 80.754 | 5/1/17:00
5 | 1 | 1900-01-17 | 17.2 | 147 | 37 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 147 | 0 | 0 | 39.791 | 121.7083 | 14.8683 | 86.148 | -75 | 3.0062 | 251.8995 | -2.461 | 144.539 | 45.8164 | 0 | 45.8164 | 62.96 | 45.8164 | 5/1/18:00
5 | 1 | 1900-01-18 | 16.1 | 64 | 19 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 64 | 0 | 0 | 39.791 | 121.75 | 14.8812 | 86.148 | -75 | 3.0112 | 266.9008 | 2.36 | 66.36 | 21.035 | 0 | 21.035 | 60.98 | 21.035 | 5/1/19:00
5 | 1 | 1900-01-19 | 15 | 11 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 11 | 0 | 0 | 39.791 | 121.7917 | 14.8941 | 86.148 | -75 | 3.0162 | 281.9021 | 0 | 11 | 3.4868 | 0 | 3.4868 | 59 | 3.4868 | 5/1/20:00
5 | 1 | 1900-01-20 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 121.8333 | 14.907 | 86.148 | -75 | 3.0212 | 296.9033 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/1/21:00
5 | 1 | 1900-01-21 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 121.875 | 14.9199 | 86.148 | -75 | 3.0262 | 311.9046 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 5/1/22:00
5 | 1 | 1900-01-22 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 121.9167 | 14.9328 | 86.148 | -75 | 3.0312 | 326.9058 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/1/23:00
5 | 1 | 1900-01-23 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 121.9583 | 14.9457 | 86.148 | -75 | 3.0361 | 341.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/1/24:00
5 | 2 | 1899-12-31 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 122 | 14.9586 | 86.148 | -75 | 3.0411 | -3.0917 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/2/1:00
5 | 2 | 1900-01-01 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 122.0417 | 14.9715 | 86.148 | -75 | 3.046 | 11.9095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/2/2:00
5 | 2 | 1900-01-02 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 122.0833 | 14.9844 | 86.148 | -75 | 3.0509 | 26.9107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/2/3:00
5 | 2 | 1900-01-03 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 122.125 | 14.9972 | 86.148 | -75 | 3.0558 | 41.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/2/4:00
5 | 2 | 1900-01-04 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 122.1667 | 15.0101 | 86.148 | -75 | 3.0607 | 56.9132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/2/5:00
5 | 2 | 1900-01-05 | 10 | 1 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 1 | 0 | 0 | 39.791 | 122.2083 | 15.0229 | 86.148 | -75 | 3.0655 | 71.9144 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 5/2/6:00
5 | 2 | 1900-01-06 | 10.6 | 38 | 5 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 38 | 0 | 0 | 39.791 | 122.25 | 15.0358 | 86.148 | -75 | 3.0704 | 86.9156 | 1.0298 | 39.0298 | 12.3718 | 12.3718 | 0 | 0 | 0 | 5/2/7:00
5 | 2 | 1900-01-07 | 11.7 | 95 | 78 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 95 | 0 | 0 | 39.791 | 122.2917 | 15.0486 | 86.148 | -75 | 3.0752 | 101.9168 | 1.0095 | 96.0095 | 30.4333 | 30.4333 | 0 | 0 | 0 | 5/2/8:00
5 | 2 | 1900-01-08 | 13.9 | 233 | 33 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 233 | 0 | 0 | 39.791 | 122.3333 | 15.0615 | 86.148 | -75 | 3.08 | 116.918 | -5.597 | 227.403 | 72.0828 | 0 | 72.0828 | 57.02 | 72.0828 | 5/2/9:00
5 | 2 | 1900-01-09 | 17.2 | 291 | 10 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 291 | 0 | 0 | 39.791 | 122.375 | 15.0743 | 86.148 | -75 | 3.0848 | 131.9192 | -3.2924 | 287.7076 | 91.1983 | 0 | 91.1983 | 62.96 | 91.1983 | 5/2/10:00
5 | 2 | 1900-01-10 | 19.4 | 273 | 496 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 273 | 0 | 0 | 39.791 | 122.4167 | 15.0871 | 86.148 | -75 | 3.0895 | 146.9204 | -225.7127 | 47.2873 | 14.9893 | 0 | 14.9893 | 66.92 | 14.9893 | 5/2/11:00
5 | 2 | 1900-01-11 | 20 | 373 | 421 | 68 | 0 | 1 | 0 | 68 | 0 | 373 | 0 | 0 | 39.791 | 122.4583 | 15.0999 | 86.148 | -75 | 3.0943 | 161.9216 | -226.7135 | 146.2865 | 46.3703 | 0 | 46.3703 | 68 | 46.3703 | 5/2/12:00
5 | 2 | 1900-01-12 | 20 | 382 | 94 | 68 | 0 | 1 | 0 | 68 | 0 | 382 | 0 | 0 | 39.791 | 122.5 | 15.1127 | 86.148 | -75 | 3.099 | 176.9228 | -53.945 | 328.055 | 103.9877 | 0 | 103.9877 | 68 | 103.9877 | 5/2/13:00
5 | 2 | 1900-01-13 | 20.6 | 341 | 141 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 341 | 0 | 0 | 39.791 | 122.5417 | 15.1255 | 86.148 | -75 | 3.1038 | 191.9239 | -78.7858 | 262.2142 | 83.1173 | 0 | 83.1173 | 69.08 | 83.1173 | 5/2/14:00
5 | 2 | 1900-01-14 | 21.1 | 302 | 169 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 302 | 0 | 0 | 39.791 | 122.5833 | 15.1383 | 86.148 | -75 | 3.1085 | 206.9251 | -83.5171 | 218.4829 | 69.2553 | 0 | 69.2553 | 69.98 | 69.2553 | 5/2/15:00
5 | 2 | 1900-01-15 | 21.7 | 378 | 161 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 378 | 0 | 0 | 39.791 | 122.625 | 15.1511 | 86.148 | -75 | 3.1131 | 221.9263 | -61.9108 | 316.0892 | 100.1947 | 0 | 100.1947 | 71.06 | 100.1947 | 5/2/16:00
5 | 2 | 1900-01-16 | 21.1 | 247 | 252 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 247 | 0 | 0 | 39.791 | 122.6667 | 15.1638 | 86.148 | -75 | 3.1178 | 236.9275 | -59.7995 | 187.2005 | 59.3393 | 0 | 59.3393 | 69.98 | 59.3393 | 5/2/17:00
5 | 2 | 1900-01-17 | 20.6 | 184 | 220 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 184 | 0 | 0 | 39.791 | 122.7083 | 15.1766 | 86.148 | -75 | 3.1225 | 251.9286 | -13.7489 | 170.2511 | 53.9666 | 0 | 53.9666 | 69.08 | 53.9666 | 5/2/18:00
5 | 2 | 1900-01-18 | 18.9 | 81 | 179 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 81 | 0 | 0 | 39.791 | 122.75 | 15.1894 | 86.148 | -75 | 3.1271 | 266.9298 | 22.906 | 103.906 | 32.9364 | 0 | 32.9364 | 66.02 | 32.9364 | 5/2/19:00
5 | 2 | 1900-01-19 | 17.8 | 8 | 5 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 8 | 0 | 0 | 39.791 | 122.7917 | 15.2021 | 86.148 | -75 | 3.1317 | 281.9309 | 1.6056 | 9.6056 | 3.0448 | 0 | 3.0448 | 64.04 | 3.0448 | 5/2/20:00
5 | 2 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 122.8333 | 15.2149 | 86.148 | -75 | 3.1363 | 296.9321 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/2/21:00
5 | 2 | 1900-01-21 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 122.875 | 15.2276 | 86.148 | -75 | 3.1409 | 311.9332 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/2/22:00
5 | 2 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 122.9167 | 15.2403 | 86.148 | -75 | 3.1455 | 326.9344 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/2/23:00
5 | 2 | 1900-01-23 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 122.9583 | 15.253 | 86.148 | -75 | 3.1501 | 341.9355 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/2/24:00
5 | 3 | 1899-12-31 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 123 | 15.2658 | 86.148 | -75 | 3.1546 | -3.0634 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/3/1:00
5 | 3 | 1900-01-01 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 123.0417 | 15.2785 | 86.148 | -75 | 3.1591 | 11.9378 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/3/2:00
5 | 3 | 1900-01-02 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 123.0833 | 15.2912 | 86.148 | -75 | 3.1636 | 26.9389 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/3/3:00
5 | 3 | 1900-01-03 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 123.125 | 15.3039 | 86.148 | -75 | 3.1681 | 41.94 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/3/4:00
5 | 3 | 1900-01-04 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 123.1667 | 15.3165 | 86.148 | -75 | 3.1726 | 56.9411 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/3/5:00
5 | 3 | 1900-01-05 | 12.2 | 2 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 2 | 0 | 0 | 39.791 | 123.2083 | 15.3292 | 86.148 | -75 | 3.177 | 71.9423 | 0 | 2 | 0.63397 | 0.63397 | 0 | 0 | 0 | 5/3/6:00
5 | 3 | 1900-01-06 | 12.2 | 49 | 102 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 49 | 0 | 0 | 39.791 | 123.25 | 15.3419 | 86.148 | -75 | 3.1815 | 86.9434 | 21.3016 | 70.3016 | 22.2844 | 22.2844 | 0 | 0 | 0 | 5/3/7:00
5 | 3 | 1900-01-07 | 14.4 | 103 | 377 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 103 | 0 | 0 | 39.791 | 123.2917 | 15.3546 | 86.148 | -75 | 3.1859 | 101.9445 | 6.0744 | 109.0744 | 34.5747 | 0 | 34.5747 | 57.92 | 34.5747 | 5/3/8:00
5 | 3 | 1900-01-08 | 17.8 | 151 | 550 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 151 | 0 | 0 | 39.791 | 123.3333 | 15.3672 | 86.148 | -75 | 3.1903 | 116.9456 | -91.3769 | 59.6231 | 18.8995 | 0 | 18.8995 | 64.04 | 18.8995 | 5/3/9:00
5 | 3 | 1900-01-09 | 20 | 188 | 655 | 68 | 0 | 1 | 0 | 68 | 0 | 188 | 0 | 0 | 39.791 | 123.375 | 15.3799 | 86.148 | -75 | 3.1947 | 131.9467 | -213.1947 | -25.1947 | -7.9863 | 0 | -7.9863 | 68 | -7.9863 | 5/3/10:00
5 | 3 | 1900-01-10 | 21.7 | 214 | 717 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 214 | 0 | 0 | 39.791 | 123.4167 | 15.3925 | 86.148 | -75 | 3.199 | 146.9478 | -323.4139 | -109.4139 | -34.6823 | 0 | -34.6823 | 71.06 | -34.6823 | 5/3/11:00
5 | 3 | 1900-01-11 | 21.7 | 225 | 719 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 225 | 0 | 0 | 39.791 | 123.4583 | 15.4051 | 86.148 | -75 | 3.2034 | 161.9488 | -384.1674 | -159.1674 | -50.4533 | 0 | -50.4533 | 71.06 | -50.4533 | 5/3/12:00
5 | 3 | 1900-01-12 | 22.8 | 245 | 684 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 245 | 0 | 0 | 39.791 | 123.5 | 15.4178 | 86.148 | -75 | 3.2077 | 176.9499 | -389.5644 | -144.5644 | -45.8244 | 0 | -45.8244 | 73.04 | -45.8244 | 5/3/13:00
5 | 3 | 1900-01-13 | 23.9 | 396 | 381 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 396 | 0 | 0 | 39.791 | 123.5417 | 15.4304 | 86.148 | -75 | 3.2121 | 191.951 | -211.2083 | 184.7917 | 58.5757 | 0 | 58.5757 | 75.02 | 58.5757 | 5/3/14:00
5 | 3 | 1900-01-14 | 23.9 | 325 | 520 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 325 | 0 | 0 | 39.791 | 123.5833 | 15.443 | 86.148 | -75 | 3.2164 | 206.9521 | -254.6866 | 70.3134 | 22.2881 | 0 | 22.2881 | 75.02 | 22.2881 | 5/3/15:00
5 | 3 | 1900-01-15 | 23.9 | 310 | 254 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 310 | 0 | 0 | 39.791 | 123.625 | 15.4556 | 86.148 | -75 | 3.2206 | 221.9532 | -96.5769 | 213.4231 | 67.6514 | 0 | 67.6514 | 75.02 | 67.6514 | 5/3/16:00
5 | 3 | 1900-01-16 | 24.4 | 184 | 503 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 184 | 0 | 0 | 39.791 | 123.6667 | 15.4682 | 86.148 | -75 | 3.2249 | 236.9542 | -117.2706 | 66.7294 | 21.1521 | 0 | 21.1521 | 75.92 | 21.1521 | 5/3/17:00
5 | 3 | 1900-01-17 | 22.8 | 126 | 390 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 126 | 0 | 0 | 39.791 | 123.7083 | 15.4808 | 86.148 | -75 | 3.2292 | 251.9553 | -22.8368 | 103.1632 | 32.7009 | 0 | 32.7009 | 73.04 | 32.7009 | 5/3/18:00
5 | 3 | 1900-01-18 | 22.2 | 72 | 214 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 72 | 0 | 0 | 39.791 | 123.75 | 15.4934 | 86.148 | -75 | 3.2334 | 266.9563 | 28.1714 | 100.1714 | 31.7526 | 0 | 31.7526 | 71.96 | 31.7526 | 5/3/19:00
5 | 3 | 1900-01-19 | 20.6 | 12 | 1 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 12 | 0 | 0 | 39.791 | 123.7917 | 15.506 | 86.148 | -75 | 3.2376 | 281.9574 | 0.3245 | 12.3245 | 3.9067 | 0 | 3.9067 | 69.08 | 3.9067 | 5/3/20:00
5 | 3 | 1900-01-20 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 123.8333 | 15.5185 | 86.148 | -75 | 3.2418 | 296.9585 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 5/3/21:00
5 | 3 | 1900-01-21 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 123.875 | 15.5311 | 86.148 | -75 | 3.246 | 311.9595 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/3/22:00
5 | 3 | 1900-01-22 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 123.9167 | 15.5436 | 86.148 | -75 | 3.2502 | 326.9605 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/3/23:00
5 | 3 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 123.9583 | 15.5562 | 86.148 | -75 | 3.2543 | 341.9616 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/3/24:00
5 | 4 | 1899-12-31 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 124 | 15.5687 | 86.148 | -75 | 3.2585 | -3.0374 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/4/1:00
5 | 4 | 1900-01-01 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 124.0417 | 15.5812 | 86.148 | -75 | 3.2626 | 11.9636 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/4/2:00
5 | 4 | 1900-01-02 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 124.0833 | 15.5938 | 86.148 | -75 | 3.2667 | 26.9647 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/4/3:00
5 | 4 | 1900-01-03 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 124.125 | 15.6063 | 86.148 | -75 | 3.2708 | 41.9657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/4/4:00
5 | 4 | 1900-01-04 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 124.1667 | 15.6188 | 86.148 | -75 | 3.2748 | 56.9667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/4/5:00
5 | 4 | 1900-01-05 | 9.4 | 4 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 4 | 0 | 0 | 39.791 | 124.2083 | 15.6313 | 86.148 | -75 | 3.2789 | 71.9677 | 0 | 4 | 1.2679 | 1.2679 | 0 | 0 | 0 | 5/4/6:00
5 | 4 | 1900-01-06 | 10 | 50 | 107 | 50 | 1 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 39.791 | 124.25 | 15.6438 | 86.148 | -75 | 3.2829 | 86.9687 | 22.6524 | 72.6524 | 23.0295 | 23.0295 | 0 | 0 | 0 | 5/4/7:00
5 | 4 | 1900-01-07 | 14.4 | 104 | 383 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 104 | 0 | 0 | 39.791 | 124.2917 | 15.6563 | 86.148 | -75 | 3.2869 | 101.9697 | 7.3784 | 111.3784 | 35.305 | 0 | 35.305 | 57.92 | 35.305 | 5/4/8:00
5 | 4 | 1900-01-08 | 17.8 | 152 | 559 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 152 | 0 | 0 | 39.791 | 124.3333 | 15.6688 | 86.148 | -75 | 3.2909 | 116.9707 | -90.9459 | 61.0541 | 19.3531 | 0 | 19.3531 | 64.04 | 19.3531 | 5/4/9:00
5 | 4 | 1900-01-09 | 20.6 | 190 | 657 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 190 | 0 | 0 | 39.791 | 124.375 | 15.6812 | 86.148 | -75 | 3.2949 | 131.9717 | -211.3977 | -21.3977 | -6.7827 | 0 | -6.7827 | 69.08 | -6.7827 | 5/4/10:00
5 | 4 | 1900-01-10 | 23.3 | 215 | 716 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 215 | 0 | 0 | 39.791 | 124.4167 | 15.6937 | 86.148 | -75 | 3.2989 | 146.9727 | -320.1184 | -105.1184 | -33.3207 | 0 | -33.3207 | 73.94 | -33.3207 | 5/4/11:00
5 | 4 | 1900-01-11 | 25.6 | 231 | 749 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 231 | 0 | 0 | 39.791 | 124.4583 | 15.7061 | 86.148 | -75 | 3.3028 | 161.9737 | -397.0742 | -166.0742 | -52.6426 | 0 | -52.6426 | 78.08 | -52.6426 | 5/4/12:00
5 | 4 | 1900-01-12 | 27.8 | 237 | 767 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 237 | 0 | 0 | 39.791 | 124.5 | 15.7186 | 86.148 | -75 | 3.3068 | 176.9747 | -433.5371 | -196.5371 | -62.2988 | 0 | -62.2988 | 82.04 | -62.2988 | 5/4/13:00
5 | 4 | 1900-01-13 | 28.9 | 234 | 757 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 234 | 0 | 0 | 39.791 | 124.5417 | 15.731 | 86.148 | -75 | 3.3107 | 191.9757 | -416.3442 | -182.3442 | -57.7999 | 0 | -57.7999 | 84.02 | -57.7999 | 5/4/14:00
5 | 4 | 1900-01-14 | 28.9 | 215 | 682 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 215 | 0 | 0 | 39.791 | 124.5833 | 15.7435 | 86.148 | -75 | 3.3146 | 206.9766 | -331.0701 | -116.0701 | -36.7922 | 0 | -36.7922 | 84.02 | -36.7922 | 5/4/15:00
5 | 4 | 1900-01-15 | 28.9 | 169 | 714 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 169 | 0 | 0 | 39.791 | 124.625 | 15.7559 | 86.148 | -75 | 3.3185 | 221.9776 | -268.4475 | -99.4475 | -31.5231 | 0 | -31.5231 | 84.02 | -31.5231 | 5/4/16:00
5 | 4 | 1900-01-16 | 28.9 | 171 | 605 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 171 | 0 | 0 | 39.791 | 124.6667 | 15.7683 | 86.148 | -75 | 3.3223 | 236.9786 | -138.581 | 32.419 | 10.2763 | 0 | 10.2763 | 84.02 | 10.2763 | 5/4/17:00
5 | 4 | 1900-01-17 | 28.3 | 124 | 464 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 124 | 0 | 0 | 39.791 | 124.7083 | 15.7807 | 86.148 | -75 | 3.3262 | 251.9795 | -25.3791 | 98.6209 | 31.2611 | 0 | 31.2611 | 82.94 | 31.2611 | 5/4/18:00
5 | 4 | 1900-01-18 | 27.2 | 72 | 226 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 72 | 0 | 0 | 39.791 | 124.75 | 15.7931 | 86.148 | -75 | 3.33 | 266.9805 | 30.5631 | 102.5631 | 32.5107 | 0 | 32.5107 | 80.96 | 32.5107 | 5/4/19:00
5 | 4 | 1900-01-19 | 23.9 | 20 | 8 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 20 | 0 | 0 | 39.791 | 124.7917 | 15.8055 | 86.148 | -75 | 3.3338 | 281.9815 | 2.6224 | 22.6224 | 7.1709 | 0 | 7.1709 | 75.02 | 7.1709 | 5/4/20:00
5 | 4 | 1900-01-20 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 124.8333 | 15.8179 | 86.148 | -75 | 3.3376 | 296.9824 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/4/21:00
5 | 4 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 124.875 | 15.8303 | 86.148 | -75 | 3.3414 | 311.9833 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/4/22:00
5 | 4 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 124.9167 | 15.8427 | 86.148 | -75 | 3.3451 | 326.9843 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/4/23:00
5 | 4 | 1900-01-23 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 124.9583 | 15.855 | 86.148 | -75 | 3.3489 | 341.9852 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/4/24:00
5 | 5 | 1899-12-31 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 125 | 15.8674 | 86.148 | -75 | 3.3526 | -3.0138 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 5/5/1:00
5 | 5 | 1900-01-01 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 125.0417 | 15.8797 | 86.148 | -75 | 3.3563 | 11.9871 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/5/2:00
5 | 5 | 1900-01-02 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 125.0833 | 15.8921 | 86.148 | -75 | 3.36 | 26.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/5/3:00
5 | 5 | 1900-01-03 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 125.125 | 15.9044 | 86.148 | -75 | 3.3637 | 41.9889 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/5/4:00
5 | 5 | 1900-01-04 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 125.1667 | 15.9167 | 86.148 | -75 | 3.3674 | 56.9898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/5/5:00
5 | 5 | 1900-01-05 | 10.6 | 4 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 4 | 0 | 0 | 39.791 | 125.2083 | 15.9291 | 86.148 | -75 | 3.371 | 71.9908 | 0 | 4 | 1.2679 | 1.2679 | 0 | 0 | 0 | 5/5/6:00
5 | 5 | 1900-01-06 | 11.1 | 43 | 39 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 43 | 0 | 0 | 39.791 | 125.25 | 15.9414 | 86.148 | -75 | 3.3746 | 86.9917 | 8.3675 | 51.3675 | 16.2826 | 16.2826 | 0 | 0 | 0 | 5/5/7:00
5 | 5 | 1900-01-07 | 14.4 | 139 | 121 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 139 | 0 | 0 | 39.791 | 125.2917 | 15.9537 | 86.148 | -75 | 3.3783 | 101.9926 | 2.7102 | 141.7102 | 44.9197 | 0 | 44.9197 | 57.92 | 44.9197 | 5/5/8:00
5 | 5 | 1900-01-08 | 19.4 | 194 | 407 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 194 | 0 | 0 | 39.791 | 125.3333 | 15.966 | 86.148 | -75 | 3.3818 | 116.9935 | -64.8221 | 129.1779 | 40.9471 | 0 | 40.9471 | 66.92 | 40.9471 | 5/5/9:00
5 | 5 | 1900-01-09 | 24.4 | 278 | 438 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 278 | 0 | 0 | 39.791 | 125.375 | 15.9783 | 86.148 | -75 | 3.3854 | 131.9944 | -139.3104 | 138.6896 | 43.9622 | 0 | 43.9622 | 75.92 | 43.9622 | 5/5/10:00
5 | 5 | 1900-01-10 | 26.7 | 256 | 647 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 256 | 0 | 0 | 39.791 | 125.4167 | 15.9905 | 86.148 | -75 | 3.389 | 146.9952 | -286.718 | -30.718 | -9.7371 | 0 | -9.7371 | 80.06 | -9.7371 | 5/5/11:00
5 | 5 | 1900-01-11 | 28.3 | 275 | 686 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 275 | 0 | 0 | 39.791 | 125.4583 | 16.0028 | 86.148 | -75 | 3.3925 | 161.9961 | -360.841 | -85.841 | -27.2101 | 0 | -27.2101 | 82.94 | -27.2101 | 5/5/12:00
5 | 5 | 1900-01-12 | 28.9 | 298 | 660 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 298 | 0 | 0 | 39.791 | 125.5 | 16.0151 | 86.148 | -75 | 3.3961 | 176.997 | -370.2478 | -72.2478 | -22.9013 | 0 | -22.9013 | 84.02 | -22.9013 | 5/5/13:00
5 | 5 | 1900-01-13 | 29.4 | 349 | 569 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 349 | 0 | 0 | 39.791 | 125.5417 | 16.0273 | 86.148 | -75 | 3.3996 | 191.9979 | -310.4953 | 38.5047 | 12.2053 | 0 | 12.2053 | 84.92 | 12.2053 | 5/5/14:00
5 | 5 | 1900-01-14 | 29.4 | 410 | 444 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 410 | 0 | 0 | 39.791 | 125.5833 | 16.0396 | 86.148 | -75 | 3.4031 | 206.9988 | -213.6352 | 196.3648 | 62.2442 | 0 | 62.2442 | 84.92 | 62.2442 | 5/5/15:00
5 | 5 | 1900-01-15 | 29.4 | 307 | 426 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 307 | 0 | 0 | 39.791 | 125.625 | 16.0518 | 86.148 | -75 | 3.4065 | 221.9996 | -158.3866 | 148.6134 | 47.1079 | 0 | 47.1079 | 84.92 | 47.1079 | 5/5/16:00
5 | 5 | 1900-01-16 | 28.9 | 197 | 525 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 197 | 0 | 0 | 39.791 | 125.6667 | 16.0641 | 86.148 | -75 | 3.41 | 237.0005 | -118.1529 | 78.8471 | 24.9932 | 0 | 24.9932 | 84.02 | 24.9932 | 5/5/17:00
5 | 5 | 1900-01-17 | 27.8 | 142 | 382 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 142 | 0 | 0 | 39.791 | 125.7083 | 16.0763 | 86.148 | -75 | 3.4134 | 252.0014 | -19.4506 | 122.5494 | 38.846 | 0 | 38.846 | 82.04 | 38.846 | 5/5/18:00
5 | 5 | 1900-01-18 | 25.6 | 79 | 157 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 79 | 0 | 0 | 39.791 | 125.75 | 16.0885 | 86.148 | -75 | 3.4169 | 267.0022 | 21.7829 | 100.7829 | 31.9464 | 0 | 31.9464 | 78.08 | 31.9464 | 5/5/19:00
5 | 5 | 1900-01-19 | 20.6 | 20 | 3 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 20 | 0 | 0 | 39.791 | 125.7917 | 16.1007 | 86.148 | -75 | 3.4203 | 282.0031 | 0.99304 | 20.993 | 6.6544 | 0 | 6.6544 | 69.08 | 6.6544 | 5/5/20:00
5 | 5 | 1900-01-20 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 125.8333 | 16.1129 | 86.148 | -75 | 3.4236 | 297.0039 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/5/21:00
5 | 5 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 125.875 | 16.1251 | 86.148 | -75 | 3.427 | 312.0048 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/5/22:00
5 | 5 | 1900-01-22 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 125.9167 | 16.1373 | 86.148 | -75 | 3.4304 | 327.0056 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 5/5/23:00
5 | 5 | 1900-01-23 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 125.9583 | 16.1495 | 86.148 | -75 | 3.4337 | 342.0064 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/5/24:00
5 | 6 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 126 | 16.1617 | 86.148 | -75 | 3.437 | -2.9927 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 5/6/1:00
5 | 6 | 1900-01-01 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 126.0417 | 16.1738 | 86.148 | -75 | 3.4403 | 12.0081 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/6/2:00
5 | 6 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 126.0833 | 16.186 | 86.148 | -75 | 3.4436 | 27.0089 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/6/3:00
5 | 6 | 1900-01-03 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 126.125 | 16.1981 | 86.148 | -75 | 3.4469 | 42.0097 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/6/4:00
5 | 6 | 1900-01-04 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 126.1667 | 16.2103 | 86.148 | -75 | 3.4502 | 57.0105 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/6/5:00
5 | 6 | 1900-01-05 | 13.3 | 2 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 2 | 0 | 0 | 39.791 | 126.2083 | 16.2224 | 86.148 | -75 | 3.4534 | 72.0113 | 0 | 2 | 0.63397 | 0 | 0.63397 | 55.94 | 0.63397 | 5/6/6:00
5 | 6 | 1900-01-06 | 13.9 | 36 | 27 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 36 | 0 | 0 | 39.791 | 126.25 | 16.2345 | 86.148 | -75 | 3.4566 | 87.0122 | 5.8692 | 41.8692 | 13.2718 | 0 | 13.2718 | 57.02 | 13.2718 | 5/6/7:00
5 | 6 | 1900-01-07 | 14.4 | 140 | 146 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 140 | 0 | 0 | 39.791 | 126.2917 | 16.2467 | 86.148 | -75 | 3.4598 | 102.013 | 3.7248 | 143.7248 | 45.5582 | 0 | 45.5582 | 57.92 | 45.5582 | 5/6/8:00
5 | 6 | 1900-01-08 | 16.7 | 217 | 332 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 217 | 0 | 0 | 39.791 | 126.3333 | 16.2588 | 86.148 | -75 | 3.463 | 117.0138 | -51.7469 | 165.2531 | 52.3823 | 0 | 52.3823 | 62.06 | 52.3823 | 5/6/9:00
5 | 6 | 1900-01-09 | 18.9 | 192 | 656 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 192 | 0 | 0 | 39.791 | 126.375 | 16.2709 | 86.148 | -75 | 3.4662 | 132.0145 | -206.2362 | -14.2362 | -4.5126 | 0 | -4.5126 | 66.02 | -4.5126 | 5/6/10:00
5 | 6 | 1900-01-10 | 20.6 | 255 | 657 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 255 | 0 | 0 | 39.791 | 126.4167 | 16.283 | 86.148 | -75 | 3.4693 | 147.0153 | -288.5801 | -33.5801 | -10.6443 | 0 | -10.6443 | 69.08 | -10.6443 | 5/6/11:00
5 | 6 | 1900-01-11 | 22.2 | 239 | 736 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 239 | 0 | 0 | 39.791 | 126.4583 | 16.295 | 86.148 | -75 | 3.4725 | 162.0161 | -384.1292 | -145.1292 | -46.0034 | 0 | -46.0034 | 71.96 | -46.0034 | 5/6/12:00
5 | 6 | 1900-01-12 | 22.8 | 441 | 524 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 441 | 0 | 0 | 39.791 | 126.5 | 16.3071 | 86.148 | -75 | 3.4756 | 177.0169 | -291.749 | 149.251 | 47.3099 | 0 | 47.3099 | 73.04 | 47.3099 | 5/6/13:00
5 | 6 | 1900-01-13 | 23.9 | 437 | 505 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 437 | 0 | 0 | 39.791 | 126.5417 | 16.3192 | 86.148 | -75 | 3.4787 | 192.0177 | -273.425 | 163.575 | 51.8504 | 0 | 51.8504 | 75.02 | 51.8504 | 5/6/14:00
5 | 6 | 1900-01-14 | 24.4 | 246 | 717 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 246 | 0 | 0 | 39.791 | 126.5833 | 16.3313 | 86.148 | -75 | 3.4818 | 207.0184 | -341.9697 | -95.9697 | -30.4207 | 0 | -30.4207 | 75.92 | -30.4207 | 5/6/15:00
5 | 6 | 1900-01-15 | 24.4 | 203 | 692 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 203 | 0 | 0 | 39.791 | 126.625 | 16.3433 | 86.148 | -75 | 3.4848 | 222.0192 | -254.4443 | -51.4443 | -16.3069 | 0 | -16.3069 | 75.92 | -16.3069 | 5/6/16:00
5 | 6 | 1900-01-16 | 25 | 170 | 611 | 77 | 0 | 1 | 0 | 77 | 0 | 170 | 0 | 0 | 39.791 | 126.6667 | 16.3554 | 86.148 | -75 | 3.4879 | 237.02 | -135.1071 | 34.8929 | 11.0604 | 0 | 11.0604 | 77 | 11.0604 | 5/6/17:00
5 | 6 | 1900-01-17 | 23.9 | 123 | 449 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 123 | 0 | 0 | 39.791 | 126.7083 | 16.3674 | 86.148 | -75 | 3.4909 | 252.0207 | -21.2024 | 101.7976 | 32.268 | 0 | 32.268 | 75.02 | 32.268 | 5/6/18:00
5 | 6 | 1900-01-18 | 22.8 | 72 | 183 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 72 | 0 | 0 | 39.791 | 126.75 | 16.3794 | 86.148 | -75 | 3.4939 | 267.0215 | 26.0169 | 98.0169 | 31.0697 | 0 | 31.0697 | 73.04 | 31.0697 | 5/6/19:00
5 | 6 | 1900-01-19 | 18.3 | 21 | 10 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 21 | 0 | 0 | 39.791 | 126.7917 | 16.3915 | 86.148 | -75 | 3.4969 | 282.0222 | 3.3415 | 24.3415 | 7.7158 | 0 | 7.7158 | 64.94 | 7.7158 | 5/6/20:00
5 | 6 | 1900-01-20 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 126.8333 | 16.4035 | 86.148 | -75 | 3.4999 | 297.023 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/6/21:00
5 | 6 | 1900-01-21 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 126.875 | 16.4155 | 86.148 | -75 | 3.5029 | 312.0237 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/6/22:00
5 | 6 | 1900-01-22 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 126.9167 | 16.4275 | 86.148 | -75 | 3.5058 | 327.0245 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 5/6/23:00
5 | 6 | 1900-01-23 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 126.9583 | 16.4395 | 86.148 | -75 | 3.5087 | 342.0252 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 5/6/24:00
5 | 7 | 1899-12-31 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 127 | 16.4514 | 86.148 | -75 | 3.5117 | -2.9741 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/7/1:00
5 | 7 | 1900-01-01 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 127.0417 | 16.4634 | 86.148 | -75 | 3.5146 | 12.0266 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/7/2:00
5 | 7 | 1900-01-02 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 127.0833 | 16.4754 | 86.148 | -75 | 3.5174 | 27.0274 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/7/3:00
5 | 7 | 1900-01-03 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 127.125 | 16.4874 | 86.148 | -75 | 3.5203 | 42.0281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/7/4:00
5 | 7 | 1900-01-04 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 127.1667 | 16.4993 | 86.148 | -75 | 3.5231 | 57.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/7/5:00
5 | 7 | 1900-01-05 | 9.4 | 2 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 2 | 0 | 0 | 39.791 | 127.2083 | 16.5112 | 86.148 | -75 | 3.526 | 72.0295 | 0 | 2 | 0.63397 | 0.63397 | 0 | 0 | 0 | 5/7/6:00
5 | 7 | 1900-01-06 | 8.9 | 25 | 9 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 25 | 0 | 0 | 39.791 | 127.25 | 16.5232 | 86.148 | -75 | 3.5288 | 87.0302 | 1.9816 | 26.9816 | 8.5527 | 8.5527 | 0 | 0 | 0 | 5/7/7:00
5 | 7 | 1900-01-07 | 9.4 | 79 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 79 | 0 | 0 | 39.791 | 127.2917 | 16.5351 | 86.148 | -75 | 3.5316 | 102.0309 | 0 | 79 | 25.0416 | 25.0416 | 0 | 0 | 0 | 5/7/8:00
5 | 7 | 1900-01-08 | 9.4 | 203 | 28 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 203 | 0 | 0 | 39.791 | 127.3333 | 16.547 | 86.148 | -75 | 3.5344 | 117.0316 | -4.2695 | 198.7305 | 62.9941 | 62.9941 | 0 | 0 | 0 | 5/7/9:00
5 | 7 | 1900-01-09 | 10 | 291 | 7 | 50 | 1 | 0 | 50 | 0 | 0 | 291 | 0 | 0 | 39.791 | 127.375 | 16.5589 | 86.148 | -75 | 3.5371 | 132.0323 | -2.1752 | 288.8248 | 91.5524 | 91.5524 | 0 | 0 | 0 | 5/7/10:00
5 | 7 | 1900-01-10 | 10.6 | 277 | 1 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 277 | 0 | 0 | 39.791 | 127.4167 | 16.5708 | 86.148 | -75 | 3.5399 | 147.033 | -0.43536 | 276.5646 | 87.6662 | 87.6662 | 0 | 0 | 0 | 5/7/11:00
5 | 7 | 1900-01-11 | 12.2 | 384 | 398 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 384 | 0 | 0 | 39.791 | 127.4583 | 16.5827 | 86.148 | -75 | 3.5426 | 162.0336 | -206.1097 | 177.8903 | 56.3881 | 56.3881 | 0 | 0 | 0 | 5/7/12:00
5 | 7 | 1900-01-12 | 14.4 | 321 | 616 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 321 | 0 | 0 | 39.791 | 127.5 | 16.5946 | 86.148 | -75 | 3.5453 | 177.0343 | -340.4104 | -19.4104 | -6.1527 | 0 | -6.1527 | 57.92 | -6.1527 | 5/7/13:00
5 | 7 | 1900-01-13 | 16.1 | 172 | 841 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 172 | 0 | 0 | 39.791 | 127.5417 | 16.6065 | 86.148 | -75 | 3.548 | 192.035 | -451.8217 | -279.8217 | -88.6986 | 0 | -88.6986 | 60.98 | -88.6986 | 5/7/14:00
5 | 7 | 1900-01-14 | 16.7 | 150 | 850 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 150 | 0 | 0 | 39.791 | 127.5833 | 16.6184 | 86.148 | -75 | 3.5507 | 207.0357 | -401.8768 | -251.8768 | -79.8405 | 0 | -79.8405 | 62.06 | -79.8405 | 5/7/15:00
5 | 7 | 1900-01-15 | 16.1 | 190 | 709 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 190 | 0 | 0 | 39.791 | 127.625 | 16.6302 | 86.148 | -75 | 3.5533 | 222.0363 | -257.8365 | -67.8365 | -21.503 | 0 | -21.503 | 60.98 | -21.503 | 5/7/16:00
5 | 7 | 1900-01-16 | 15 | 109 | 775 | 59 | 0 | 1 | 0 | 59 | 0 | 109 | 0 | 0 | 39.791 | 127.6667 | 16.6421 | 86.148 | -75 | 3.556 | 237.037 | -168.3886 | -59.3886 | -18.8252 | 0 | -18.8252 | 59 | -18.8252 | 5/7/17:00
5 | 7 | 1900-01-17 | 15 | 81 | 654 | 59 | 0 | 1 | 0 | 59 | 0 | 81 | 0 | 0 | 39.791 | 127.7083 | 16.6539 | 86.148 | -75 | 3.5586 | 252.0376 | -28.5202 | 52.4798 | 16.6352 | 0 | 16.6352 | 59 | 16.6352 | 5/7/18:00
5 | 7 | 1900-01-18 | 13.9 | 53 | 460 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 53 | 0 | 0 | 39.791 | 127.75 | 16.6658 | 86.148 | -75 | 3.5612 | 267.0383 | 66.9337 | 119.9337 | 38.0169 | 0 | 38.0169 | 57.02 | 38.0169 | 5/7/19:00
5 | 7 | 1900-01-19 | 11.7 | 19 | 72 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 19 | 0 | 0 | 39.791 | 127.7917 | 16.6776 | 86.148 | -75 | 3.5638 | 282.0389 | 24.2779 | 43.2779 | 13.7183 | 13.7183 | 0 | 0 | 0 | 5/7/20:00
5 | 7 | 1900-01-20 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 127.8333 | 16.6894 | 86.148 | -75 | 3.5664 | 297.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/7/21:00
5 | 7 | 1900-01-21 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 127.875 | 16.7013 | 86.148 | -75 | 3.5689 | 312.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/7/22:00
5 | 7 | 1900-01-22 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 127.9167 | 16.7131 | 86.148 | -75 | 3.5714 | 327.0409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/7/23:00
5 | 7 | 1900-01-23 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 127.9583 | 16.7249 | 86.148 | -75 | 3.574 | 342.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/7/24:00
5 | 8 | 1899-12-31 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 128 | 16.7367 | 86.148 | -75 | 3.5765 | -2.9579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8/1:00
5 | 8 | 1900-01-01 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 128.0417 | 16.7484 | 86.148 | -75 | 3.579 | 12.0427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8/2:00
5 | 8 | 1900-01-02 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 128.0833 | 16.7602 | 86.148 | -75 | 3.5814 | 27.0434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8/3:00
5 | 8 | 1900-01-03 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 128.125 | 16.772 | 86.148 | -75 | 3.5839 | 42.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8/4:00
5 | 8 | 1900-01-04 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 128.1667 | 16.7837 | 86.148 | -75 | 3.5863 | 57.0446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8/5:00
5 | 8 | 1900-01-05 | 5.6 | 3 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 3 | 0 | 0 | 39.791 | 128.2083 | 16.7955 | 86.148 | -75 | 3.5887 | 72.0452 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 5/8/6:00
5 | 8 | 1900-01-06 | 6.1 | 50 | 82 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 50 | 0 | 0 | 39.791 | 128.25 | 16.8072 | 86.148 | -75 | 3.5911 | 87.0458 | 18.283 | 68.283 | 21.6445 | 21.6445 | 0 | 0 | 0 | 5/8/7:00
5 | 8 | 1900-01-07 | 7.2 | 122 | 121 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 122 | 0 | 0 | 39.791 | 128.2917 | 16.819 | 86.148 | -75 | 3.5935 | 102.0464 | 3.8327 | 125.8327 | 39.8868 | 39.8868 | 0 | 0 | 0 | 5/8/8:00
5 | 8 | 1900-01-08 | 9.4 | 148 | 531 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 148 | 0 | 0 | 39.791 | 128.3333 | 16.8307 | 86.148 | -75 | 3.5959 | 117.047 | -79.1871 | 68.8129 | 21.8125 | 21.8125 | 0 | 0 | 0 | 5/8/9:00
5 | 8 | 1900-01-09 | 11.1 | 313 | 6 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 313 | 0 | 0 | 39.791 | 128.375 | 16.8424 | 86.148 | -75 | 3.5982 | 132.0476 | -1.8427 | 311.1573 | 98.6314 | 98.6314 | 0 | 0 | 0 | 5/8/10:00
5 | 8 | 1900-01-10 | 12.2 | 256 | 560 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 256 | 0 | 0 | 39.791 | 128.4167 | 16.8541 | 86.148 | -75 | 3.6006 | 147.0481 | -241.652 | 14.348 | 4.5481 | 4.5481 | 0 | 0 | 0 | 5/8/11:00
5 | 8 | 1900-01-11 | 10 | 389 | 286 | 50 | 1 | 0 | 50 | 0 | 0 | 389 | 0 | 0 | 39.791 | 128.4583 | 16.8658 | 86.148 | -75 | 3.6029 | 162.0487 | -146.9628 | 242.0372 | 76.7216 | 76.7216 | 0 | 0 | 0 | 5/8/12:00
5 | 8 | 1900-01-12 | 11.7 | 397 | 226 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 397 | 0 | 0 | 39.791 | 128.5 | 16.8775 | 86.148 | -75 | 3.6052 | 177.0493 | -123.9627 | 273.0373 | 86.5481 | 86.5481 | 0 | 0 | 0 | 5/8/13:00
5 | 8 | 1900-01-13 | 13.3 | 521 | 130 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 521 | 0 | 0 | 39.791 | 128.5417 | 16.8892 | 86.148 | -75 | 3.6075 | 192.0499 | -69.3045 | 451.6955 | 143.1796 | 0 | 143.1796 | 55.94 | 143.1796 | 5/8/14:00
5 | 8 | 1900-01-14 | 12.8 | 360 | 55 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 360 | 0 | 0 | 39.791 | 128.5833 | 16.9009 | 86.148 | -75 | 3.6097 | 207.0504 | -25.7794 | 334.2206 | 105.9421 | 0 | 105.9421 | 55.04 | 105.9421 | 5/8/15:00
5 | 8 | 1900-01-15 | 12.8 | 329 | 254 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 329 | 0 | 0 | 39.791 | 128.625 | 16.9125 | 86.148 | -75 | 3.612 | 222.051 | -91.3653 | 237.6347 | 75.3261 | 0 | 75.3261 | 55.04 | 75.3261 | 5/8/16:00
5 | 8 | 1900-01-16 | 12.2 | 220 | 18 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 220 | 0 | 0 | 39.791 | 128.6667 | 16.9242 | 86.148 | -75 | 3.6142 | 237.0516 | -3.8431 | 216.1569 | 68.5179 | 68.5179 | 0 | 0 | 0 | 5/8/17:00
5 | 8 | 1900-01-17 | 12.2 | 169 | 124 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 169 | 0 | 0 | 39.791 | 128.7083 | 16.9358 | 86.148 | -75 | 3.6164 | 252.0521 | -4.9701 | 164.0299 | 51.9946 | 51.9946 | 0 | 0 | 0 | 5/8/18:00
5 | 8 | 1900-01-18 | 12.8 | 58 | 332 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 58 | 0 | 0 | 39.791 | 128.75 | 16.9475 | 86.148 | -75 | 3.6186 | 267.0527 | 49.3885 | 107.3885 | 34.0403 | 0 | 34.0403 | 55.04 | 34.0403 | 5/8/19:00
5 | 8 | 1900-01-19 | 8.3 | 21 | 129 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 21 | 0 | 0 | 39.791 | 128.7917 | 16.9591 | 86.148 | -75 | 3.6208 | 282.0532 | 43.8799 | 64.8799 | 20.5658 | 20.5658 | 0 | 0 | 0 | 5/8/20:00
5 | 8 | 1900-01-20 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 128.8333 | 16.9707 | 86.148 | -75 | 3.623 | 297.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8/21:00
5 | 8 | 1900-01-21 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 128.875 | 16.9824 | 86.148 | -75 | 3.6251 | 312.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8/22:00
5 | 8 | 1900-01-22 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 128.9167 | 16.994 | 86.148 | -75 | 3.6273 | 327.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8/23:00
5 | 8 | 1900-01-23 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 128.9583 | 17.0056 | 86.148 | -75 | 3.6294 | 342.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8/24:00
5 | 9 | 1899-12-31 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 129 | 17.0172 | 86.148 | -75 | 3.6315 | -2.9441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/9/1:00
5 | 9 | 1900-01-01 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 129.0417 | 17.0288 | 86.148 | -75 | 3.6335 | 12.0564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/9/2:00
5 | 9 | 1900-01-02 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 129.0833 | 17.0403 | 86.148 | -75 | 3.6356 | 27.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/9/3:00
5 | 9 | 1900-01-03 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 129.125 | 17.0519 | 86.148 | -75 | 3.6376 | 42.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/9/4:00
5 | 9 | 1900-01-04 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 129.1667 | 17.0635 | 86.148 | -75 | 3.6397 | 57.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/9/5:00
5 | 9 | 1900-01-05 | 3.9 | 7 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 7 | 0 | 0 | 39.791 | 129.2083 | 17.075 | 86.148 | -75 | 3.6417 | 72.0584 | 0 | 7 | 2.2189 | 2.2189 | 0 | 0 | 0 | 5/9/6:00
5 | 9 | 1900-01-06 | 4.4 | 51 | 201 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 51 | 0 | 0 | 39.791 | 129.25 | 17.0866 | 86.148 | -75 | 3.6437 | 87.0589 | 45.3705 | 96.3705 | 30.5478 | 30.5478 | 0 | 0 | 0 | 5/9/7:00
5 | 9 | 1900-01-07 | 7.2 | 93 | 491 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 93 | 0 | 0 | 39.791 | 129.2917 | 17.0981 | 86.148 | -75 | 3.6456 | 102.0594 | 17.0485 | 110.0485 | 34.8835 | 34.8835 | 0 | 0 | 0 | 5/9/8:00
5 | 9 | 1900-01-08 | 10.6 | 131 | 650 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 131 | 0 | 0 | 39.791 | 129.3333 | 17.1096 | 86.148 | -75 | 3.6476 | 117.0599 | -94.7696 | 36.2304 | 11.4844 | 11.4844 | 0 | 0 | 0 | 5/9/9:00
5 | 9 | 1900-01-09 | 12.8 | 160 | 741 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 160 | 0 | 0 | 39.791 | 129.375 | 17.1211 | 86.148 | -75 | 3.6495 | 132.0604 | -224.9166 | -64.9166 | -20.5774 | 0 | -20.5774 | 55.04 | -20.5774 | 5/9/10:00
5 | 9 | 1900-01-10 | 14.4 | 180 | 796 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 180 | 0 | 0 | 39.791 | 129.4167 | 17.1326 | 86.148 | -75 | 3.6515 | 147.0609 | -340.464 | -160.464 | -50.8643 | 0 | -50.8643 | 57.92 | -50.8643 | 5/9/11:00
5 | 9 | 1900-01-11 | 15 | 192 | 827 | 59 | 0 | 1 | 0 | 59 | 0 | 192 | 0 | 0 | 39.791 | 129.4583 | 17.1441 | 86.148 | -75 | 3.6534 | 162.0613 | -421.6825 | -229.6825 | -72.8053 | 0 | -72.8053 | 59 | -72.8053 | 5/9/12:00
5 | 9 | 1900-01-12 | 16.1 | 197 | 837 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 197 | 0 | 0 | 39.791 | 129.5 | 17.1556 | 86.148 | -75 | 3.6553 | 177.0618 | -455.7086 | -258.7086 | -82.0061 | 0 | -82.0061 | 60.98 | -82.0061 | 5/9/13:00
5 | 9 | 1900-01-13 | 17.2 | 195 | 829 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 195 | 0 | 0 | 39.791 | 129.5417 | 17.1671 | 86.148 | -75 | 3.6571 | 192.0623 | -438.5763 | -243.5763 | -77.2094 | 0 | -77.2094 | 62.96 | -77.2094 | 5/9/14:00
5 | 9 | 1900-01-14 | 17.2 | 185 | 811 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 185 | 0 | 0 | 39.791 | 129.5833 | 17.1786 | 86.148 | -75 | 3.659 | 207.0627 | -376.8765 | -191.8765 | -60.8215 | 0 | -60.8215 | 62.96 | -60.8215 | 5/9/15:00
5 | 9 | 1900-01-15 | 17.8 | 168 | 767 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 168 | 0 | 0 | 39.791 | 129.625 | 17.1901 | 86.148 | -75 | 3.6608 | 222.0632 | -272.9192 | -104.9192 | -33.2575 | 0 | -33.2575 | 64.04 | -33.2575 | 5/9/16:00
5 | 9 | 1900-01-16 | 18.3 | 143 | 694 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 143 | 0 | 0 | 39.791 | 129.6667 | 17.2015 | 86.148 | -75 | 3.6627 | 237.0637 | -145.6169 | -2.6169 | -0.8295 | 0 | -0.8295 | 64.94 | -0.8295 | 5/9/17:00
5 | 9 | 1900-01-17 | 18.3 | 108 | 566 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 108 | 0 | 0 | 39.791 | 129.7083 | 17.213 | 86.148 | -75 | 3.6645 | 252.0641 | -20.7379 | 87.2621 | 27.6606 | 0 | 27.6606 | 64.94 | 27.6606 | 5/9/18:00
5 | 9 | 1900-01-18 | 17.8 | 67 | 332 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 67 | 0 | 0 | 39.791 | 129.75 | 17.2244 | 86.148 | -75 | 3.6663 | 267.0646 | 50.4393 | 117.4393 | 37.2262 | 0 | 37.2262 | 64.04 | 37.2262 | 5/9/19:00
5 | 9 | 1900-01-19 | 14.4 | 20 | 14 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 20 | 0 | 0 | 39.791 | 129.7917 | 17.2359 | 86.148 | -75 | 3.668 | 282.065 | 4.8024 | 24.8024 | 7.8619 | 0 | 7.8619 | 57.92 | 7.8619 | 5/9/20:00
5 | 9 | 1900-01-20 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 129.8333 | 17.2473 | 86.148 | -75 | 3.6698 | 297.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/9/21:00
5 | 9 | 1900-01-21 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 129.875 | 17.2587 | 86.148 | -75 | 3.6715 | 312.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/9/22:00
5 | 9 | 1900-01-22 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 129.9167 | 17.2701 | 86.148 | -75 | 3.6732 | 327.0663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/9/23:00
5 | 9 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 129.9583 | 17.2815 | 86.148 | -75 | 3.6749 | 342.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/9/24:00
5 | 10 | 1899-12-31 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 130 | 17.2929 | 86.148 | -75 | 3.6766 | -2.9328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/10/1:00
5 | 10 | 1900-01-01 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 130.0417 | 17.3043 | 86.148 | -75 | 3.6783 | 12.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/10/2:00
5 | 10 | 1900-01-02 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 130.0833 | 17.3157 | 86.148 | -75 | 3.6799 | 27.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/10/3:00
5 | 10 | 1900-01-03 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 130.125 | 17.327 | 86.148 | -75 | 3.6816 | 42.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/10/4:00
5 | 10 | 1900-01-04 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 130.1667 | 17.3384 | 86.148 | -75 | 3.6832 | 57.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/10/5:00
5 | 10 | 1900-01-05 | 5.6 | 9 | 7 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 9 | 0 | 0 | 39.791 | 130.2083 | 17.3497 | 86.148 | -75 | 3.6848 | 72.0692 | 2.9165 | 11.9165 | 3.7773 | 3.7773 | 0 | 0 | 0 | 5/10/6:00
5 | 10 | 1900-01-06 | 7.2 | 64 | 34 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 64 | 0 | 0 | 39.791 | 130.25 | 17.3611 | 86.148 | -75 | 3.6864 | 87.0696 | 7.7677 | 71.7677 | 22.7491 | 22.7491 | 0 | 0 | 0 | 5/10/7:00
5 | 10 | 1900-01-07 | 10.6 | 134 | 78 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 134 | 0 | 0 | 39.791 | 130.2917 | 17.3724 | 86.148 | -75 | 3.688 | 102.07 | 2.944 | 136.944 | 43.4089 | 43.4089 | 0 | 0 | 0 | 5/10/8:00
5 | 10 | 1900-01-08 | 13.9 | 214 | 248 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 214 | 0 | 0 | 39.791 | 130.3333 | 17.3837 | 86.148 | -75 | 3.6895 | 117.0704 | -35.3397 | 178.6603 | 56.6322 | 0 | 56.6322 | 57.02 | 56.6322 | 5/10/9:00
5 | 10 | 1900-01-09 | 17.2 | 365 | 214 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 365 | 0 | 0 | 39.791 | 130.375 | 17.395 | 86.148 | -75 | 3.691 | 132.0708 | -64.1953 | 300.8047 | 95.3498 | 0 | 95.3498 | 62.96 | 95.3498 | 5/10/10:00
5 | 10 | 1900-01-10 | 18.9 | 322 | 386 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 322 | 0 | 0 | 39.791 | 130.4167 | 17.4064 | 86.148 | -75 | 3.6926 | 147.0711 | -163.647 | 158.353 | 50.1951 | 0 | 50.1951 | 66.02 | 50.1951 | 5/10/11:00
5 | 10 | 1900-01-11 | 19.4 | 354 | 134 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 354 | 0 | 0 | 39.791 | 130.4583 | 17.4176 | 86.148 | -75 | 3.694 | 162.0715 | -67.8014 | 286.1986 | 90.72 | 0 | 90.72 | 66.92 | 90.72 | 5/10/12:00
5 | 10 | 1900-01-12 | 19.4 | 314 | 4 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 314 | 0 | 0 | 39.791 | 130.5 | 17.4289 | 86.148 | -75 | 3.6955 | 177.0719 | -2.1618 | 311.8382 | 98.8473 | 0 | 98.8473 | 66.92 | 98.8473 | 5/10/13:00
5 | 10 | 1900-01-13 | 18.9 | 378 | 1 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 378 | 0 | 0 | 39.791 | 130.5417 | 17.4402 | 86.148 | -75 | 3.697 | 192.0722 | -0.52504 | 377.475 | 119.653 | 0 | 119.653 | 66.02 | 119.653 | 5/10/14:00
5 | 10 | 1900-01-14 | 20.6 | 393 | 120 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 393 | 0 | 0 | 39.791 | 130.5833 | 17.4515 | 86.148 | -75 | 3.6984 | 207.0726 | -55.2922 | 337.7078 | 107.0475 | 0 | 107.0475 | 69.08 | 107.0475 | 5/10/15:00
5 | 10 | 1900-01-15 | 20.6 | 326 | 116 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 326 | 0 | 0 | 39.791 | 130.625 | 17.4628 | 86.148 | -75 | 3.6999 | 222.073 | -40.8351 | 285.1649 | 90.3923 | 0 | 90.3923 | 69.08 | 90.3923 | 5/10/16:00
5 | 10 | 1900-01-16 | 20.6 | 256 | 278 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 256 | 0 | 0 | 39.791 | 130.6667 | 17.474 | 86.148 | -75 | 3.7013 | 237.0733 | -57.3295 | 198.6705 | 62.9751 | 0 | 62.9751 | 69.08 | 62.9751 | 5/10/17:00
5 | 10 | 1900-01-17 | 21.1 | 187 | 116 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 187 | 0 | 0 | 39.791 | 130.7083 | 17.4853 | 86.148 | -75 | 3.7027 | 252.0737 | -3.861 | 183.139 | 58.0519 | 0 | 58.0519 | 69.98 | 58.0519 | 5/10/18:00
5 | 10 | 1900-01-18 | 21.7 | 67 | 6 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 67 | 0 | 0 | 39.791 | 130.75 | 17.4965 | 86.148 | -75 | 3.7041 | 267.074 | 0.93002 | 67.93 | 21.5326 | 0 | 21.5326 | 71.06 | 21.5326 | 5/10/19:00
5 | 10 | 1900-01-19 | 20.6 | 10 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 10 | 0 | 0 | 39.791 | 130.7917 | 17.5077 | 86.148 | -75 | 3.7054 | 282.0744 | 0 | 10 | 3.1698 | 0 | 3.1698 | 69.08 | 3.1698 | 5/10/20:00
5 | 10 | 1900-01-20 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 130.8333 | 17.519 | 86.148 | -75 | 3.7068 | 297.0747 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/10/21:00
5 | 10 | 1900-01-21 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 130.875 | 17.5302 | 86.148 | -75 | 3.7081 | 312.075 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 5/10/22:00
5 | 10 | 1900-01-22 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 130.9167 | 17.5414 | 86.148 | -75 | 3.7094 | 327.0754 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 5/10/23:00
5 | 10 | 1900-01-23 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 130.9583 | 17.5526 | 86.148 | -75 | 3.7107 | 342.0757 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 5/10/24:00
5 | 11 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 131 | 17.5637 | 86.148 | -75 | 3.712 | -2.924 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 5/11/1:00
5 | 11 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 131.0417 | 17.5749 | 86.148 | -75 | 3.7133 | 12.0763 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/11/2:00
5 | 11 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 131.0833 | 17.5861 | 86.148 | -75 | 3.7145 | 27.0766 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/11/3:00
5 | 11 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 131.125 | 17.5973 | 86.148 | -75 | 3.7157 | 42.0769 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/11/4:00
5 | 11 | 1900-01-04 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 131.1667 | 17.6084 | 86.148 | -75 | 3.7169 | 57.0772 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 5/11/5:00
5 | 11 | 1900-01-05 | 16.7 | 4 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 4 | 0 | 0 | 39.791 | 131.2083 | 17.6196 | 86.148 | -75 | 3.7181 | 72.0775 | 0 | 4 | 1.2679 | 0 | 1.2679 | 62.06 | 1.2679 | 5/11/6:00
5 | 11 | 1900-01-06 | 17.2 | 60 | 80 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 60 | 0 | 0 | 39.791 | 131.25 | 17.6307 | 86.148 | -75 | 3.7193 | 87.0778 | 18.4938 | 78.4938 | 24.8812 | 0 | 24.8812 | 62.96 | 24.8812 | 5/11/7:00
5 | 11 | 1900-01-07 | 19.4 | 125 | 306 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 125 | 0 | 0 | 39.791 | 131.2917 | 17.6418 | 86.148 | -75 | 3.7205 | 102.0781 | 12.4663 | 137.4663 | 43.5744 | 0 | 43.5744 | 66.92 | 43.5744 | 5/11/8:00
5 | 11 | 1900-01-08 | 22.2 | 266 | 208 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 266 | 0 | 0 | 39.791 | 131.3333 | 17.6529 | 86.148 | -75 | 3.7216 | 117.0784 | -28.9594 | 237.0406 | 75.1377 | 0 | 75.1377 | 71.96 | 75.1377 | 5/11/9:00
5 | 11 | 1900-01-09 | 21.7 | 308 | 5 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 308 | 0 | 0 | 39.791 | 131.375 | 17.664 | 86.148 | -75 | 3.7227 | 132.0787 | -1.4823 | 306.5177 | 97.1608 | 0 | 97.1608 | 71.06 | 97.1608 | 5/11/10:00
5 | 11 | 1900-01-10 | 21.7 | 424 | 1 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 424 | 0 | 0 | 39.791 | 131.4167 | 17.6751 | 86.148 | -75 | 3.7238 | 147.079 | -0.42024 | 423.5798 | 134.2674 | 0 | 134.2674 | 71.06 | 134.2674 | 5/11/11:00
5 | 11 | 1900-01-11 | 22.2 | 427 | 4 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 427 | 0 | 0 | 39.791 | 131.4583 | 17.6862 | 86.148 | -75 | 3.7249 | 162.0792 | -2.0085 | 424.9915 | 134.7149 | 0 | 134.7149 | 71.96 | 134.7149 | 5/11/12:00
5 | 11 | 1900-01-12 | 22.8 | 386 | 1 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 386 | 0 | 0 | 39.791 | 131.5 | 17.6973 | 86.148 | -75 | 3.726 | 177.0795 | -0.53652 | 385.4635 | 122.1852 | 0 | 122.1852 | 73.04 | 122.1852 | 5/11/13:00
5 | 11 | 1900-01-13 | 25 | 443 | 283 | 77 | 0 | 1 | 0 | 77 | 0 | 443 | 0 | 0 | 39.791 | 131.5417 | 17.7084 | 86.148 | -75 | 3.7271 | 192.0798 | -147.4715 | 295.5285 | 93.6774 | 0 | 93.6774 | 77 | 93.6774 | 5/11/14:00
5 | 11 | 1900-01-14 | 25.6 | 402 | 283 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 402 | 0 | 0 | 39.791 | 131.5833 | 17.7195 | 86.148 | -75 | 3.7281 | 207.08 | -129.3042 | 272.6958 | 86.4398 | 0 | 86.4398 | 78.08 | 86.4398 | 5/11/15:00
5 | 11 | 1900-01-15 | 26.1 | 332 | 184 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 332 | 0 | 0 | 39.791 | 131.625 | 17.7305 | 86.148 | -75 | 3.7291 | 222.0803 | -64.0886 | 267.9114 | 84.9232 | 0 | 84.9232 | 78.98 | 84.9232 | 5/11/16:00
5 | 11 | 1900-01-16 | 26.1 | 266 | 61 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 266 | 0 | 0 | 39.791 | 131.6667 | 17.7416 | 86.148 | -75 | 3.7301 | 237.0805 | -12.365 | 253.635 | 80.3979 | 0 | 80.3979 | 78.98 | 80.3979 | 5/11/17:00
5 | 11 | 1900-01-17 | 25 | 135 | 4 | 77 | 0 | 1 | 0 | 77 | 0 | 135 | 0 | 0 | 39.791 | 131.7083 | 17.7526 | 86.148 | -75 | 3.7311 | 252.0808 | -0.12007 | 134.8799 | 42.7546 | 0 | 42.7546 | 77 | 42.7546 | 5/11/18:00
5 | 11 | 1900-01-18 | 22.8 | 25 | 2 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 25 | 0 | 0 | 39.791 | 131.75 | 17.7636 | 86.148 | -75 | 3.7321 | 267.081 | 0.31598 | 25.316 | 8.0247 | 0 | 8.0247 | 73.04 | 8.0247 | 5/11/19:00
5 | 11 | 1900-01-19 | 21.1 | 10 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 10 | 0 | 0 | 39.791 | 131.7917 | 17.7746 | 86.148 | -75 | 3.7331 | 282.0813 | 0 | 10 | 3.1698 | 0 | 3.1698 | 69.98 | 3.1698 | 5/11/20:00
5 | 11 | 1900-01-20 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 131.8333 | 17.7857 | 86.148 | -75 | 3.734 | 297.0815 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 5/11/21:00
5 | 11 | 1900-01-21 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 131.875 | 17.7967 | 86.148 | -75 | 3.7349 | 312.0817 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 5/11/22:00
5 | 11 | 1900-01-22 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 131.9167 | 17.8077 | 86.148 | -75 | 3.7358 | 327.082 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 5/11/23:00
5 | 11 | 1900-01-23 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 131.9583 | 17.8186 | 86.148 | -75 | 3.7367 | 342.0822 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 5/11/24:00
5 | 12 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 132 | 17.8296 | 86.148 | -75 | 3.7376 | -2.9176 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 5/12/1:00
5 | 12 | 1900-01-01 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 132.0417 | 17.8406 | 86.148 | -75 | 3.7384 | 12.0826 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/12/2:00
5 | 12 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 132.0833 | 17.8516 | 86.148 | -75 | 3.7393 | 27.0828 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/12/3:00
5 | 12 | 1900-01-03 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 132.125 | 17.8625 | 86.148 | -75 | 3.7401 | 42.083 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/12/4:00
5 | 12 | 1900-01-04 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 132.1667 | 17.8734 | 86.148 | -75 | 3.7409 | 57.0832 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/12/5:00
5 | 12 | 1900-01-05 | 17.8 | 7 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 7 | 0 | 0 | 39.791 | 132.2083 | 17.8844 | 86.148 | -75 | 3.7417 | 72.0834 | 0 | 7 | 2.2189 | 0 | 2.2189 | 64.04 | 2.2189 | 5/12/6:00
5 | 12 | 1900-01-06 | 16.1 | 49 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 49 | 0 | 0 | 39.791 | 132.25 | 17.8953 | 86.148 | -75 | 3.7425 | 87.0836 | 0 | 49 | 15.5321 | 0 | 15.5321 | 60.98 | 15.5321 | 5/12/7:00
5 | 12 | 1900-01-07 | 15.6 | 86 | 1 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 86 | 0 | 0 | 39.791 | 132.2917 | 17.9062 | 86.148 | -75 | 3.7432 | 102.0838 | 0.043707 | 86.0437 | 27.2744 | 0 | 27.2744 | 60.08 | 27.2744 | 5/12/8:00
5 | 12 | 1900-01-08 | 15 | 129 | 1 | 59 | 0 | 1 | 0 | 59 | 0 | 129 | 0 | 0 | 39.791 | 132.3333 | 17.9171 | 86.148 | -75 | 3.7439 | 117.084 | -0.13599 | 128.864 | 40.8476 | 0 | 40.8476 | 59 | 40.8476 | 5/12/9:00
5 | 12 | 1900-01-09 | 15.6 | 218 | 27 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 218 | 0 | 0 | 39.791 | 132.375 | 17.928 | 86.148 | -75 | 3.7447 | 132.0842 | -7.9104 | 210.0896 | 66.5947 | 0 | 66.5947 | 60.08 | 66.5947 | 5/12/10:00
5 | 12 | 1900-01-10 | 19.4 | 425 | 109 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 425 | 0 | 0 | 39.791 | 132.4167 | 17.9389 | 86.148 | -75 | 3.7454 | 147.0843 | -45.405 | 379.595 | 120.325 | 0 | 120.325 | 66.92 | 120.325 | 5/12/11:00
5 | 12 | 1900-01-11 | 22.2 | 398 | 227 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 398 | 0 | 0 | 39.791 | 132.4583 | 17.9498 | 86.148 | -75 | 3.7461 | 162.0845 | -113.1154 | 284.8846 | 90.3034 | 0 | 90.3034 | 71.96 | 90.3034 | 5/12/12:00
5 | 12 | 1900-01-12 | 22.8 | 456 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 456 | 0 | 0 | 39.791 | 132.5 | 17.9607 | 86.148 | -75 | 3.7467 | 177.0847 | 0 | 456 | 144.544 | 0 | 144.544 | 73.04 | 144.544 | 5/12/13:00
5 | 12 | 1900-01-13 | 23.3 | 438 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 438 | 0 | 0 | 39.791 | 132.5417 | 17.9715 | 86.148 | -75 | 3.7474 | 192.0848 | 0 | 438 | 138.8384 | 0 | 138.8384 | 73.94 | 138.8384 | 5/12/14:00
5 | 12 | 1900-01-14 | 23.3 | 149 | 23 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 149 | 0 | 0 | 39.791 | 132.5833 | 17.9824 | 86.148 | -75 | 3.748 | 207.085 | -10.4217 | 138.5783 | 43.9269 | 0 | 43.9269 | 73.94 | 43.9269 | 5/12/15:00
5 | 12 | 1900-01-15 | 20 | 203 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 203 | 0 | 0 | 39.791 | 132.625 | 17.9932 | 86.148 | -75 | 3.7486 | 222.0852 | 0 | 203 | 64.3475 | 0 | 64.3475 | 68 | 64.3475 | 5/12/16:00
5 | 12 | 1900-01-16 | 20 | 159 | 1 | 68 | 0 | 1 | 0 | 68 | 0 | 159 | 0 | 0 | 39.791 | 132.6667 | 18.0041 | 86.148 | -75 | 3.7492 | 237.0853 | -0.19928 | 158.8007 | 50.3371 | 0 | 50.3371 | 68 | 50.3371 | 5/12/17:00
5 | 12 | 1900-01-17 | 19.4 | 101 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 101 | 0 | 0 | 39.791 | 132.7083 | 18.0149 | 86.148 | -75 | 3.7498 | 252.0855 | 0 | 101 | 32.0152 | 0 | 32.0152 | 66.92 | 32.0152 | 5/12/18:00
5 | 12 | 1900-01-18 | 18.9 | 33 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 33 | 0 | 0 | 39.791 | 132.75 | 18.0257 | 86.148 | -75 | 3.7504 | 267.0856 | 0 | 33 | 10.4604 | 0 | 10.4604 | 66.02 | 10.4604 | 5/12/19:00
5 | 12 | 1900-01-19 | 18.9 | 24 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 24 | 0 | 0 | 39.791 | 132.7917 | 18.0365 | 86.148 | -75 | 3.7509 | 282.0857 | 0 | 24 | 7.6076 | 0 | 7.6076 | 66.02 | 7.6076 | 5/12/20:00
5 | 12 | 1900-01-20 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 132.8333 | 18.0473 | 86.148 | -75 | 3.7515 | 297.0859 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/12/21:00
5 | 12 | 1900-01-21 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 132.875 | 18.0581 | 86.148 | -75 | 3.752 | 312.086 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/12/22:00
5 | 12 | 1900-01-22 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 132.9167 | 18.0689 | 86.148 | -75 | 3.7525 | 327.0861 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/12/23:00
5 | 12 | 1900-01-23 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 132.9583 | 18.0797 | 86.148 | -75 | 3.753 | 342.0862 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 5/12/24:00
5 | 13 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 133 | 18.0904 | 86.148 | -75 | 3.7534 | -2.9136 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 5/13/1:00
5 | 13 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 133.0417 | 18.1012 | 86.148 | -75 | 3.7539 | 12.0865 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/13/2:00
5 | 13 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 133.0833 | 18.1119 | 86.148 | -75 | 3.7543 | 27.0866 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/13/3:00
5 | 13 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 133.125 | 18.1227 | 86.148 | -75 | 3.7547 | 42.0867 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/13/4:00
5 | 13 | 1900-01-04 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 133.1667 | 18.1334 | 86.148 | -75 | 3.7551 | 57.0868 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/13/5:00
5 | 13 | 1900-01-05 | 18.3 | 6 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 6 | 0 | 0 | 39.791 | 133.2083 | 18.1441 | 86.148 | -75 | 3.7555 | 72.0869 | 0.42388 | 6.4239 | 2.0363 | 0 | 2.0363 | 64.94 | 2.0363 | 5/13/6:00
5 | 13 | 1900-01-06 | 18.9 | 53 | 6 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 53 | 0 | 0 | 39.791 | 133.25 | 18.1548 | 86.148 | -75 | 3.7559 | 87.087 | 1.4191 | 54.4191 | 17.2499 | 0 | 17.2499 | 66.02 | 17.2499 | 5/13/7:00
5 | 13 | 1900-01-07 | 20 | 121 | 325 | 68 | 0 | 1 | 0 | 68 | 0 | 121 | 0 | 0 | 39.791 | 133.2917 | 18.1655 | 86.148 | -75 | 3.7562 | 102.0871 | 15.1601 | 136.1601 | 43.1604 | 0 | 43.1604 | 68 | 43.1604 | 5/13/8:00
5 | 13 | 1900-01-08 | 21.1 | 175 | 485 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 175 | 0 | 0 | 39.791 | 133.3333 | 18.1762 | 86.148 | -75 | 3.7566 | 117.0871 | -64.3997 | 110.6003 | 35.0584 | 0 | 35.0584 | 69.98 | 35.0584 | 5/13/9:00
5 | 13 | 1900-01-09 | 22.2 | 172 | 682 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 172 | 0 | 0 | 39.791 | 133.375 | 18.1869 | 86.148 | -75 | 3.7569 | 132.0872 | -197.4646 | -25.4646 | -8.0718 | 0 | -8.0718 | 71.96 | -8.0718 | 5/13/10:00
5 | 13 | 1900-01-10 | 23.9 | 168 | 750 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 168 | 0 | 0 | 39.791 | 133.4167 | 18.1976 | 86.148 | -75 | 3.7572 | 147.0873 | -309.6977 | -141.6977 | -44.9157 | 0 | -44.9157 | 75.02 | -44.9157 | 5/13/11:00
5 | 13 | 1900-01-11 | 25 | 193 | 812 | 77 | 0 | 1 | 0 | 77 | 0 | 193 | 0 | 0 | 39.791 | 133.4583 | 18.2082 | 86.148 | -75 | 3.7575 | 162.0874 | -401.574 | -208.574 | -66.1143 | 0 | -66.1143 | 77 | -66.1143 | 5/13/12:00
5 | 13 | 1900-01-12 | 26.7 | 168 | 799 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 168 | 0 | 0 | 39.791 | 133.5 | 18.2189 | 86.148 | -75 | 3.7577 | 177.0874 | -422.5351 | -254.5351 | -80.6832 | 0 | -80.6832 | 80.06 | -80.6832 | 5/13/13:00
5 | 13 | 1900-01-13 | 27.8 | 418 | 439 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 418 | 0 | 0 | 39.791 | 133.5417 | 18.2295 | 86.148 | -75 | 3.758 | 192.0875 | -225.3976 | 192.6024 | 61.0516 | 0 | 61.0516 | 82.04 | 61.0516 | 5/13/14:00
5 | 13 | 1900-01-14 | 27.2 | 313 | 483 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 313 | 0 | 0 | 39.791 | 133.5833 | 18.2402 | 86.148 | -75 | 3.7582 | 207.0876 | -217.065 | 95.935 | 30.4097 | 0 | 30.4097 | 80.96 | 30.4097 | 5/13/15:00
5 | 13 | 1900-01-15 | 26.7 | 190 | 689 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 190 | 0 | 0 | 39.791 | 133.625 | 18.2508 | 86.148 | -75 | 3.7584 | 222.0876 | -235.0303 | -45.0303 | -14.2738 | 0 | -14.2738 | 80.06 | -14.2738 | 5/13/16:00
5 | 13 | 1900-01-16 | 25.6 | 223 | 402 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 223 | 0 | 0 | 39.791 | 133.6667 | 18.2614 | 86.148 | -75 | 3.7586 | 237.0877 | -78.7662 | 144.2338 | 45.7196 | 0 | 45.7196 | 78.08 | 45.7196 | 5/13/17:00
5 | 13 | 1900-01-17 | 25 | 106 | 561 | 77 | 0 | 1 | 0 | 77 | 0 | 106 | 0 | 0 | 39.791 | 133.7083 | 18.272 | 86.148 | -75 | 3.7588 | 252.0877 | -13.3259 | 92.6741 | 29.3761 | 0 | 29.3761 | 77 | 29.3761 | 5/13/18:00
5 | 13 | 1900-01-18 | 19.4 | 66 | 364 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 66 | 0 | 0 | 39.791 | 133.75 | 18.2826 | 86.148 | -75 | 3.759 | 267.0877 | 59.5866 | 125.5866 | 39.8088 | 0 | 39.8088 | 66.92 | 39.8088 | 5/13/19:00
5 | 13 | 1900-01-19 | 16.1 | 23 | 45 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 23 | 0 | 0 | 39.791 | 133.7917 | 18.2932 | 86.148 | -75 | 3.7591 | 282.0878 | 15.9145 | 38.9145 | 12.3352 | 0 | 12.3352 | 60.98 | 12.3352 | 5/13/20:00
5 | 13 | 1900-01-20 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 133.8333 | 18.3038 | 86.148 | -75 | 3.7593 | 297.0878 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/13/21:00
5 | 13 | 1900-01-21 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 133.875 | 18.3144 | 86.148 | -75 | 3.7594 | 312.0878 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/13/22:00
5 | 13 | 1900-01-22 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 133.9167 | 18.325 | 86.148 | -75 | 3.7595 | 327.0879 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/13/23:00
5 | 13 | 1900-01-23 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 133.9583 | 18.3355 | 86.148 | -75 | 3.7596 | 342.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/13/24:00
5 | 14 | 1899-12-31 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 134 | 18.3461 | 86.148 | -75 | 3.7596 | -2.9121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/14/1:00
5 | 14 | 1900-01-01 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 134.0417 | 18.3566 | 86.148 | -75 | 3.7597 | 12.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/14/2:00
5 | 14 | 1900-01-02 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 134.0833 | 18.3671 | 86.148 | -75 | 3.7597 | 27.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/14/3:00
5 | 14 | 1900-01-03 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 134.125 | 18.3777 | 86.148 | -75 | 3.7597 | 42.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/14/4:00
5 | 14 | 1900-01-04 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 134.1667 | 18.3882 | 86.148 | -75 | 3.7597 | 57.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/14/5:00
5 | 14 | 1900-01-05 | 9.4 | 10 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 10 | 0 | 0 | 39.791 | 134.2083 | 18.3987 | 86.148 | -75 | 3.7597 | 72.0879 | 0.42624 | 10.4262 | 3.3049 | 3.3049 | 0 | 0 | 0 | 5/14/6:00
5 | 14 | 1900-01-06 | 8.9 | 62 | 40 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 62 | 0 | 0 | 39.791 | 134.25 | 18.4092 | 86.148 | -75 | 3.7597 | 87.0879 | 9.5659 | 71.5659 | 22.6851 | 22.6851 | 0 | 0 | 0 | 5/14/7:00
5 | 14 | 1900-01-07 | 9.4 | 151 | 18 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 151 | 0 | 0 | 39.791 | 134.2917 | 18.4196 | 86.148 | -75 | 3.7596 | 102.0879 | 0.89199 | 151.892 | 48.1471 | 48.1471 | 0 | 0 | 0 | 5/14/8:00
5 | 14 | 1900-01-08 | 10.6 | 254 | 65 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 254 | 0 | 0 | 39.791 | 134.3333 | 18.4301 | 86.148 | -75 | 3.7595 | 117.0879 | -8.4248 | 245.5752 | 77.8431 | 77.8431 | 0 | 0 | 0 | 5/14/9:00
5 | 14 | 1900-01-09 | 12.8 | 212 | 593 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 212 | 0 | 0 | 39.791 | 134.375 | 18.4406 | 86.148 | -75 | 3.7595 | 132.0879 | -169.6792 | 42.3208 | 13.4149 | 0 | 13.4149 | 55.04 | 13.4149 | 5/14/10:00
5 | 14 | 1900-01-10 | 13.9 | 329 | 352 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 329 | 0 | 0 | 39.791 | 134.4167 | 18.451 | 86.148 | -75 | 3.7594 | 147.0878 | -144.091 | 184.909 | 58.6129 | 0 | 58.6129 | 57.02 | 58.6129 | 5/14/11:00
5 | 14 | 1900-01-11 | 14.4 | 392 | 576 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 392 | 0 | 0 | 39.791 | 134.4583 | 18.4615 | 86.148 | -75 | 3.7592 | 162.0878 | -282.7293 | 109.2707 | 34.6369 | 0 | 34.6369 | 57.92 | 34.6369 | 5/14/12:00
5 | 14 | 1900-01-12 | 16.1 | 250 | 722 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 250 | 0 | 0 | 39.791 | 134.5 | 18.4719 | 86.148 | -75 | 3.7591 | 177.0878 | -379.1084 | -129.1084 | -40.9251 | 0 | -40.9251 | 60.98 | -40.9251 | 5/14/13:00
5 | 14 | 1900-01-13 | 16.7 | 288 | 667 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 288 | 0 | 0 | 39.791 | 134.5417 | 18.4823 | 86.148 | -75 | 3.759 | 192.0877 | -339.9762 | -51.9762 | -16.4756 | 0 | -16.4756 | 62.06 | -16.4756 | 5/14/14:00
5 | 14 | 1900-01-14 | 17.8 | 246 | 556 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 246 | 0 | 0 | 39.791 | 134.5833 | 18.4928 | 86.148 | -75 | 3.7588 | 207.0877 | -247.8543 | -1.8543 | -0.58779 | 0 | -0.58779 | 64.04 | -0.58779 | 5/14/15:00
5 | 14 | 1900-01-15 | 17.2 | 333 | 37 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 333 | 0 | 0 | 39.791 | 134.625 | 18.5032 | 86.148 | -75 | 3.7586 | 222.0877 | -12.4931 | 320.5069 | 101.5951 | 0 | 101.5951 | 62.96 | 101.5951 | 5/14/16:00
5 | 14 | 1900-01-16 | 17.8 | 184 | 450 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 184 | 0 | 0 | 39.791 | 134.6667 | 18.5136 | 86.148 | -75 | 3.7584 | 237.0876 | -86.7079 | 97.2921 | 30.8399 | 0 | 30.8399 | 64.04 | 30.8399 | 5/14/17:00
5 | 14 | 1900-01-17 | 16.7 | 157 | 319 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 157 | 0 | 0 | 39.791 | 134.7083 | 18.524 | 86.148 | -75 | 3.7582 | 252.0875 | -6.6217 | 150.3783 | 47.6673 | 0 | 47.6673 | 62.06 | 47.6673 | 5/14/18:00
5 | 14 | 1900-01-18 | 17.2 | 77 | 264 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 77 | 0 | 0 | 39.791 | 134.75 | 18.5344 | 86.148 | -75 | 3.758 | 267.0875 | 43.9343 | 120.9343 | 38.3341 | 0 | 38.3341 | 62.96 | 38.3341 | 5/14/19:00
5 | 14 | 1900-01-19 | 14.4 | 26 | 25 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 26 | 0 | 0 | 39.791 | 134.7917 | 18.5447 | 86.148 | -75 | 3.7577 | 282.0874 | 8.9023 | 34.9023 | 11.0634 | 0 | 11.0634 | 57.92 | 11.0634 | 5/14/20:00
5 | 14 | 1900-01-20 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 134.8333 | 18.5551 | 86.148 | -75 | 3.7574 | 297.0874 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/14/21:00
5 | 14 | 1900-01-21 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 134.875 | 18.5654 | 86.148 | -75 | 3.7572 | 312.0873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/14/22:00
5 | 14 | 1900-01-22 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 134.9167 | 18.5758 | 86.148 | -75 | 3.7569 | 327.0872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/14/23:00
5 | 14 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 134.9583 | 18.5861 | 86.148 | -75 | 3.7565 | 342.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/14/24:00
5 | 15 | 1899-12-31 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 135 | 18.5964 | 86.148 | -75 | 3.7562 | -2.9129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/15/1:00
5 | 15 | 1900-01-01 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 135.0417 | 18.6068 | 86.148 | -75 | 3.7559 | 12.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/15/2:00
5 | 15 | 1900-01-02 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 135.0833 | 18.6171 | 86.148 | -75 | 3.7555 | 27.0869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/15/3:00
5 | 15 | 1900-01-03 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 135.125 | 18.6274 | 86.148 | -75 | 3.7551 | 42.0868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/15/4:00
5 | 15 | 1900-01-04 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 135.1667 | 18.6377 | 86.148 | -75 | 3.7547 | 57.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/15/5:00
5 | 15 | 1900-01-05 | 7.2 | 10 | 28 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 10 | 0 | 0 | 39.791 | 135.2083 | 18.6479 | 86.148 | -75 | 3.7543 | 72.0866 | 12 | 22 | 6.9736 | 6.9736 | 0 | 0 | 0 | 5/15/6:00
5 | 15 | 1900-01-06 | 7.8 | 59 | 183 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 59 | 0 | 0 | 39.791 | 135.25 | 18.6582 | 86.148 | -75 | 3.7539 | 87.0865 | 44.2403 | 103.2403 | 32.7254 | 32.7254 | 0 | 0 | 0 | 5/15/7:00
5 | 15 | 1900-01-07 | 11.7 | 105 | 454 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 105 | 0 | 0 | 39.791 | 135.2917 | 18.6685 | 86.148 | -75 | 3.7534 | 102.0864 | 23.8039 | 128.8039 | 40.8286 | 40.8286 | 0 | 0 | 0 | 5/15/8:00
5 | 15 | 1900-01-08 | 14.4 | 168 | 553 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 168 | 0 | 0 | 39.791 | 135.3333 | 18.6787 | 86.148 | -75 | 3.7529 | 117.0862 | -69.9421 | 98.0579 | 31.0826 | 0 | 31.0826 | 57.92 | 31.0826 | 5/15/9:00
5 | 15 | 1900-01-09 | 16.1 | 179 | 699 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 179 | 0 | 0 | 39.791 | 135.375 | 18.689 | 86.148 | -75 | 3.7525 | 132.0861 | -197.663 | -18.663 | -5.9158 | 0 | -5.9158 | 60.98 | -5.9158 | 5/15/10:00
5 | 15 | 1900-01-10 | 18.3 | 238 | 683 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 238 | 0 | 0 | 39.791 | 135.4167 | 18.6992 | 86.148 | -75 | 3.752 | 147.086 | -277.1745 | -39.1745 | -12.4176 | 0 | -12.4176 | 64.94 | -12.4176 | 5/15/11:00
5 | 15 | 1900-01-11 | 19.4 | 255 | 718 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 255 | 0 | 0 | 39.791 | 135.4583 | 18.7094 | 86.148 | -75 | 3.7514 | 162.0859 | -349.8156 | -94.8156 | -30.0549 | 0 | -30.0549 | 66.92 | -30.0549 | 5/15/12:00
5 | 15 | 1900-01-12 | 20 | 365 | 566 | 68 | 0 | 1 | 0 | 68 | 0 | 365 | 0 | 0 | 39.791 | 135.5 | 18.7196 | 86.148 | -75 | 3.7509 | 177.0857 | -295.1119 | 69.8881 | 22.1533 | 0 | 22.1533 | 68 | 22.1533 | 5/15/13:00
5 | 15 | 1900-01-13 | 20.6 | 366 | 503 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 366 | 0 | 0 | 39.791 | 135.5417 | 18.7298 | 86.148 | -75 | 3.7504 | 192.0856 | -254.5481 | 111.4519 | 35.3283 | 0 | 35.3283 | 69.08 | 35.3283 | 5/15/14:00
5 | 15 | 1900-01-14 | 20.6 | 387 | 450 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 387 | 0 | 0 | 39.791 | 135.5833 | 18.74 | 86.148 | -75 | 3.7498 | 207.0855 | -199.0054 | 187.9946 | 59.591 | 0 | 59.591 | 69.08 | 59.591 | 5/15/15:00
5 | 15 | 1900-01-15 | 21.7 | 294 | 514 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 294 | 0 | 0 | 39.791 | 135.625 | 18.7502 | 86.148 | -75 | 3.7492 | 222.0853 | -171.815 | 122.185 | 38.7305 | 0 | 38.7305 | 71.06 | 38.7305 | 5/15/16:00
5 | 15 | 1900-01-16 | 22.2 | 215 | 458 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 215 | 0 | 0 | 39.791 | 135.6667 | 18.7604 | 86.148 | -75 | 3.7486 | 237.0852 | -86.8016 | 128.1984 | 40.6366 | 0 | 40.6366 | 71.96 | 40.6366 | 5/15/17:00
5 | 15 | 1900-01-17 | 21.1 | 183 | 204 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 183 | 0 | 0 | 39.791 | 135.7083 | 18.7706 | 86.148 | -75 | 3.748 | 252.085 | -3.6421 | 179.3579 | 56.8533 | 0 | 56.8533 | 69.98 | 56.8533 | 5/15/18:00
5 | 15 | 1900-01-18 | 20 | 111 | 81 | 68 | 0 | 1 | 0 | 68 | 0 | 111 | 0 | 0 | 39.791 | 135.75 | 18.7807 | 86.148 | -75 | 3.7474 | 267.0848 | 13.6927 | 124.6927 | 39.5254 | 0 | 39.5254 | 68 | 39.5254 | 5/15/19:00
5 | 15 | 1900-01-19 | 17.8 | 23 | 95 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 23 | 0 | 0 | 39.791 | 135.7917 | 18.7909 | 86.148 | -75 | 3.7467 | 282.0847 | 34.052 | 57.052 | 18.0845 | 0 | 18.0845 | 64.04 | 18.0845 | 5/15/20:00
5 | 15 | 1900-01-20 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 135.8333 | 18.801 | 86.148 | -75 | 3.7461 | 297.0845 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/15/21:00
5 | 15 | 1900-01-21 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 135.875 | 18.8111 | 86.148 | -75 | 3.7454 | 312.0843 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/15/22:00
5 | 15 | 1900-01-22 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 135.9167 | 18.8213 | 86.148 | -75 | 3.7447 | 327.0842 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/15/23:00
5 | 15 | 1900-01-23 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 135.9583 | 18.8314 | 86.148 | -75 | 3.744 | 342.084 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/15/24:00
5 | 16 | 1899-12-31 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 136 | 18.8415 | 86.148 | -75 | 3.7433 | -2.9162 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 5/16/1:00
5 | 16 | 1900-01-01 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 136.0417 | 18.8516 | 86.148 | -75 | 3.7425 | 12.0836 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/16/2:00
5 | 16 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 136.0833 | 18.8616 | 86.148 | -75 | 3.7417 | 27.0834 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/16/3:00
5 | 16 | 1900-01-03 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 136.125 | 18.8717 | 86.148 | -75 | 3.741 | 42.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/16/4:00
5 | 16 | 1900-01-04 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 136.1667 | 18.8818 | 86.148 | -75 | 3.7402 | 57.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/16/5:00
5 | 16 | 1900-01-05 | 11.7 | 8 | 7 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 8 | 0 | 0 | 39.791 | 136.2083 | 18.8918 | 86.148 | -75 | 3.7394 | 72.0828 | 3.0161 | 11.0161 | 3.4919 | 3.4919 | 0 | 0 | 0 | 5/16/6:00
5 | 16 | 1900-01-06 | 11.7 | 69 | 166 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 69 | 0 | 0 | 39.791 | 136.25 | 18.9019 | 86.148 | -75 | 3.7385 | 87.0826 | 40.5575 | 109.5575 | 34.7278 | 34.7278 | 0 | 0 | 0 | 5/16/7:00
5 | 16 | 1900-01-07 | 13.3 | 125 | 314 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 125 | 0 | 0 | 39.791 | 136.2917 | 18.9119 | 86.148 | -75 | 3.7377 | 102.0824 | 17.3563 | 142.3563 | 45.1245 | 0 | 45.1245 | 55.94 | 45.1245 | 5/16/8:00
5 | 16 | 1900-01-08 | 15 | 236 | 163 | 59 | 0 | 1 | 0 | 59 | 0 | 236 | 0 | 0 | 39.791 | 136.3333 | 18.9219 | 86.148 | -75 | 3.7368 | 117.0822 | -20.1112 | 215.8888 | 68.433 | 0 | 68.433 | 59 | 68.433 | 5/16/9:00
5 | 16 | 1900-01-09 | 16.7 | 266 | 100 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 266 | 0 | 0 | 39.791 | 136.375 | 18.932 | 86.148 | -75 | 3.736 | 132.082 | -27.9467 | 238.0533 | 75.4587 | 0 | 75.4587 | 62.06 | 75.4587 | 5/16/10:00
5 | 16 | 1900-01-10 | 17.8 | 291 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 291 | 0 | 0 | 39.791 | 136.4167 | 18.942 | 86.148 | -75 | 3.7351 | 147.0818 | 0 | 291 | 92.2419 | 0 | 92.2419 | 64.04 | 92.2419 | 5/16/11:00
5 | 16 | 1900-01-11 | 18.3 | 277 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 277 | 0 | 0 | 39.791 | 136.4583 | 18.952 | 86.148 | -75 | 3.7342 | 162.0815 | 0 | 277 | 87.8042 | 0 | 87.8042 | 64.94 | 87.8042 | 5/16/12:00
5 | 16 | 1900-01-12 | 16.7 | 197 | 2 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 197 | 0 | 0 | 39.791 | 136.5 | 18.962 | 86.148 | -75 | 3.7332 | 177.0813 | -1.0356 | 195.9644 | 62.1173 | 0 | 62.1173 | 62.06 | 62.1173 | 5/16/13:00
5 | 16 | 1900-01-13 | 16.7 | 196 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 196 | 0 | 0 | 39.791 | 136.5417 | 18.9719 | 86.148 | -75 | 3.7323 | 192.0811 | 0 | 196 | 62.1286 | 0 | 62.1286 | 62.06 | 62.1286 | 5/16/14:00
5 | 16 | 1900-01-14 | 15.6 | 234 | 21 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 234 | 0 | 0 | 39.791 | 136.5833 | 18.9819 | 86.148 | -75 | 3.7313 | 207.0808 | -9.2142 | 224.7858 | 71.2532 | 0 | 71.2532 | 60.08 | 71.2532 | 5/16/15:00
5 | 16 | 1900-01-15 | 14.4 | 159 | 3 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 159 | 0 | 0 | 39.791 | 136.625 | 18.9919 | 86.148 | -75 | 3.7304 | 222.0806 | -0.99294 | 158.0071 | 50.0855 | 0 | 50.0855 | 57.92 | 50.0855 | 5/16/16:00
5 | 16 | 1900-01-16 | 13.9 | 158 | 6 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 158 | 0 | 0 | 39.791 | 136.6667 | 19.0018 | 86.148 | -75 | 3.7294 | 237.0803 | -1.1187 | 156.8813 | 49.7286 | 0 | 49.7286 | 57.02 | 49.7286 | 5/16/17:00
5 | 16 | 1900-01-17 | 13.3 | 94 | 3 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 94 | 0 | 0 | 39.791 | 136.7083 | 19.0117 | 86.148 | -75 | 3.7284 | 252.0801 | -0.045124 | 93.9549 | 29.7821 | 0 | 29.7821 | 55.94 | 29.7821 | 5/16/18:00
5 | 16 | 1900-01-18 | 13.3 | 55 | 1 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 55 | 0 | 0 | 39.791 | 136.75 | 19.0217 | 86.148 | -75 | 3.7274 | 267.0798 | 0.17158 | 55.1716 | 17.4884 | 0 | 17.4884 | 55.94 | 17.4884 | 5/16/19:00
5 | 16 | 1900-01-19 | 13.3 | 15 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 15 | 0 | 0 | 39.791 | 136.7917 | 19.0316 | 86.148 | -75 | 3.7263 | 282.0796 | 0 | 15 | 4.7547 | 0 | 4.7547 | 55.94 | 4.7547 | 5/16/20:00
5 | 16 | 1900-01-20 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 136.8333 | 19.0415 | 86.148 | -75 | 3.7253 | 297.0793 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/16/21:00
5 | 16 | 1900-01-21 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 136.875 | 19.0514 | 86.148 | -75 | 3.7242 | 312.079 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/16/22:00
5 | 16 | 1900-01-22 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 136.9167 | 19.0613 | 86.148 | -75 | 3.7231 | 327.0788 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 5/16/23:00
5 | 16 | 1900-01-23 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 136.9583 | 19.0712 | 86.148 | -75 | 3.722 | 342.0785 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 5/16/24:00
5 | 17 | 1899-12-31 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 137 | 19.0811 | 86.148 | -75 | 3.7209 | -2.9218 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/17/1:00
5 | 17 | 1900-01-01 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 137.0417 | 19.0909 | 86.148 | -75 | 3.7197 | 12.0779 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/17/2:00
5 | 17 | 1900-01-02 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 137.0833 | 19.1008 | 86.148 | -75 | 3.7186 | 27.0776 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/17/3:00
5 | 17 | 1900-01-03 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 137.125 | 19.1106 | 86.148 | -75 | 3.7174 | 42.0774 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/17/4:00
5 | 17 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 137.1667 | 19.1205 | 86.148 | -75 | 3.7162 | 57.0771 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/17/5:00
5 | 17 | 1900-01-05 | 16.7 | 9 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 9 | 0 | 0 | 39.791 | 137.2083 | 19.1303 | 86.148 | -75 | 3.715 | 72.0768 | 0 | 9 | 2.8528 | 0 | 2.8528 | 62.06 | 2.8528 | 5/17/6:00
5 | 17 | 1900-01-06 | 16.7 | 56 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 56 | 0 | 0 | 39.791 | 137.25 | 19.1401 | 86.148 | -75 | 3.7138 | 87.0765 | 0 | 56 | 17.751 | 0 | 17.751 | 62.06 | 17.751 | 5/17/7:00
5 | 17 | 1900-01-07 | 16.7 | 133 | 1 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 133 | 0 | 0 | 39.791 | 137.2917 | 19.1499 | 86.148 | -75 | 3.7126 | 102.0761 | 0.058083 | 133.0581 | 42.1771 | 0 | 42.1771 | 62.06 | 42.1771 | 5/17/8:00
5 | 17 | 1900-01-08 | 17.2 | 239 | 1 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 239 | 0 | 0 | 39.791 | 137.3333 | 19.1597 | 86.148 | -75 | 3.7113 | 117.0758 | -0.12033 | 238.8797 | 75.7207 | 0 | 75.7207 | 62.96 | 75.7207 | 5/17/9:00
5 | 17 | 1900-01-09 | 17.2 | 200 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 200 | 0 | 0 | 39.791 | 137.375 | 19.1695 | 86.148 | -75 | 3.7101 | 132.0755 | 0 | 200 | 63.3965 | 0 | 63.3965 | 62.96 | 63.3965 | 5/17/10:00
5 | 17 | 1900-01-10 | 17.2 | 228 | 1 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 228 | 0 | 0 | 39.791 | 137.4167 | 19.1793 | 86.148 | -75 | 3.7088 | 147.0752 | -0.39892 | 227.6011 | 72.1456 | 0 | 72.1456 | 62.96 | 72.1456 | 5/17/11:00
5 | 17 | 1900-01-11 | 17.2 | 248 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 248 | 0 | 0 | 39.791 | 137.4583 | 19.189 | 86.148 | -75 | 3.7075 | 162.0749 | 0 | 248 | 78.6117 | 0 | 78.6117 | 62.96 | 78.6117 | 5/17/12:00
5 | 17 | 1900-01-12 | 17.2 | 254 | 1 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 254 | 0 | 0 | 39.791 | 137.5 | 19.1988 | 86.148 | -75 | 3.7062 | 177.0745 | -0.51425 | 253.4858 | 80.3506 | 0 | 80.3506 | 62.96 | 80.3506 | 5/17/13:00
5 | 17 | 1900-01-13 | 17.2 | 274 | 1 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 274 | 0 | 0 | 39.791 | 137.5417 | 19.2085 | 86.148 | -75 | 3.7049 | 192.0742 | -0.49899 | 273.501 | 86.695 | 0 | 86.695 | 62.96 | 86.695 | 5/17/14:00
5 | 17 | 1900-01-14 | 17.2 | 250 | 1 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 250 | 0 | 0 | 39.791 | 137.5833 | 19.2183 | 86.148 | -75 | 3.7035 | 207.0739 | -0.43539 | 249.5646 | 79.1076 | 0 | 79.1076 | 62.96 | 79.1076 | 5/17/15:00
5 | 17 | 1900-01-15 | 17.8 | 138 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 138 | 0 | 0 | 39.791 | 137.625 | 19.228 | 86.148 | -75 | 3.7022 | 222.0735 | 0 | 138 | 43.7436 | 0 | 43.7436 | 64.04 | 43.7436 | 5/17/16:00
5 | 17 | 1900-01-16 | 17.8 | 109 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 109 | 0 | 0 | 39.791 | 137.6667 | 19.2377 | 86.148 | -75 | 3.7008 | 237.0732 | 0 | 109 | 34.5511 | 0 | 34.5511 | 64.04 | 34.5511 | 5/17/17:00
5 | 17 | 1900-01-17 | 17.8 | 65 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 65 | 0 | 0 | 39.791 | 137.7083 | 19.2474 | 86.148 | -75 | 3.6994 | 252.0728 | 0 | 65 | 20.6039 | 0 | 20.6039 | 64.04 | 20.6039 | 5/17/18:00
5 | 17 | 1900-01-18 | 17.2 | 22 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 22 | 0 | 0 | 39.791 | 137.75 | 19.2571 | 86.148 | -75 | 3.698 | 267.0725 | 0 | 22 | 6.9736 | 0 | 6.9736 | 62.96 | 6.9736 | 5/17/19:00
5 | 17 | 1900-01-19 | 17.2 | 26 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 26 | 0 | 0 | 39.791 | 137.7917 | 19.2668 | 86.148 | -75 | 3.6965 | 282.0721 | 0 | 26 | 8.2415 | 0 | 8.2415 | 62.96 | 8.2415 | 5/17/20:00
5 | 17 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 137.8333 | 19.2765 | 86.148 | -75 | 3.6951 | 297.0718 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/17/21:00
5 | 17 | 1900-01-21 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 137.875 | 19.2862 | 86.148 | -75 | 3.6937 | 312.0714 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/17/22:00
5 | 17 | 1900-01-22 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 137.9167 | 19.2958 | 86.148 | -75 | 3.6922 | 327.071 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/17/23:00
5 | 17 | 1900-01-23 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 137.9583 | 19.3055 | 86.148 | -75 | 3.6907 | 342.0707 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/17/24:00
5 | 18 | 1899-12-31 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 138 | 19.3151 | 86.148 | -75 | 3.6892 | -2.9297 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/18/1:00
5 | 18 | 1900-01-01 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 138.0417 | 19.3247 | 86.148 | -75 | 3.6877 | 12.0699 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/18/2:00
5 | 18 | 1900-01-02 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 138.0833 | 19.3344 | 86.148 | -75 | 3.6861 | 27.0695 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/18/3:00
5 | 18 | 1900-01-03 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 138.125 | 19.344 | 86.148 | -75 | 3.6846 | 42.0691 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/18/4:00
5 | 18 | 1900-01-04 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 138.1667 | 19.3536 | 86.148 | -75 | 3.683 | 57.0688 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/18/5:00
5 | 18 | 1900-01-05 | 17.2 | 12 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 12 | 0 | 0 | 39.791 | 138.2083 | 19.3632 | 86.148 | -75 | 3.6814 | 72.0684 | 0 | 12 | 3.8038 | 0 | 3.8038 | 62.96 | 3.8038 | 5/18/6:00
5 | 18 | 1900-01-06 | 17.2 | 64 | 1 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 64 | 0 | 0 | 39.791 | 138.25 | 19.3727 | 86.148 | -75 | 3.6798 | 87.068 | 0.24937 | 64.2494 | 20.3659 | 0 | 20.3659 | 62.96 | 20.3659 | 5/18/7:00
5 | 18 | 1900-01-07 | 18.3 | 145 | 34 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 145 | 0 | 0 | 39.791 | 138.2917 | 19.3823 | 86.148 | -75 | 3.6782 | 102.0675 | 2.0691 | 147.0691 | 46.6183 | 0 | 46.6183 | 64.94 | 46.6183 | 5/18/8:00
5 | 18 | 1900-01-08 | 18.3 | 271 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 271 | 0 | 0 | 39.791 | 138.3333 | 19.3919 | 86.148 | -75 | 3.6766 | 117.0671 | -0.11731 | 270.8827 | 85.8651 | 0 | 85.8651 | 64.94 | 85.8651 | 5/18/9:00
5 | 18 | 1900-01-09 | 19.4 | 298 | 152 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 298 | 0 | 0 | 39.791 | 138.375 | 19.4014 | 86.148 | -75 | 3.6749 | 132.0667 | -41.4938 | 256.5062 | 81.308 | 0 | 81.308 | 66.92 | 81.308 | 5/18/10:00
5 | 18 | 1900-01-10 | 20 | 270 | 213 | 68 | 0 | 1 | 0 | 68 | 0 | 270 | 0 | 0 | 39.791 | 138.4167 | 19.411 | 86.148 | -75 | 3.6733 | 147.0663 | -84.2528 | 185.7472 | 58.8786 | 0 | 58.8786 | 68 | 58.8786 | 5/18/11:00
5 | 18 | 1900-01-11 | 21.1 | 408 | 278 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 408 | 0 | 0 | 39.791 | 138.4583 | 19.4205 | 86.148 | -75 | 3.6716 | 162.0659 | -132.5114 | 275.4886 | 87.3251 | 0 | 87.3251 | 69.98 | 87.3251 | 5/18/12:00
5 | 18 | 1900-01-12 | 21.1 | 341 | 68 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 341 | 0 | 0 | 39.791 | 138.5 | 19.43 | 86.148 | -75 | 3.6699 | 177.0655 | -34.7329 | 306.2671 | 97.0813 | 0 | 97.0813 | 69.98 | 97.0813 | 5/18/13:00
5 | 18 | 1900-01-13 | 21.1 | 337 | 24 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 337 | 0 | 0 | 39.791 | 138.5417 | 19.4395 | 86.148 | -75 | 3.6682 | 192.065 | -11.8939 | 325.1061 | 103.053 | 0 | 103.053 | 69.98 | 103.053 | 5/18/14:00
5 | 18 | 1900-01-14 | 22.2 | 385 | 70 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 385 | 0 | 0 | 39.791 | 138.5833 | 19.449 | 86.148 | -75 | 3.6664 | 207.0646 | -30.2471 | 354.7529 | 112.4505 | 0 | 112.4505 | 71.96 | 112.4505 | 5/18/15:00
5 | 18 | 1900-01-15 | 21.1 | 356 | 1 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 356 | 0 | 0 | 39.791 | 138.625 | 19.4585 | 86.148 | -75 | 3.6647 | 222.0642 | -0.32467 | 355.6753 | 112.7429 | 0 | 112.7429 | 69.98 | 112.7429 | 5/18/16:00
5 | 18 | 1900-01-16 | 18.3 | 178 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 178 | 0 | 0 | 39.791 | 138.6667 | 19.468 | 86.148 | -75 | 3.6629 | 237.0637 | -0.18059 | 177.8194 | 56.3656 | 0 | 56.3656 | 64.94 | 56.3656 | 5/18/17:00
5 | 18 | 1900-01-17 | 18.3 | 99 | 10 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 99 | 0 | 0 | 39.791 | 138.7083 | 19.4775 | 86.148 | -75 | 3.6612 | 252.0633 | -0.096986 | 98.903 | 31.3505 | 0 | 31.3505 | 64.94 | 31.3505 | 5/18/18:00
5 | 18 | 1900-01-18 | 18.3 | 53 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 53 | 0 | 0 | 39.791 | 138.75 | 19.487 | 86.148 | -75 | 3.6594 | 267.0628 | 0 | 53 | 16.8001 | 0 | 16.8001 | 64.94 | 16.8001 | 5/18/19:00
5 | 18 | 1900-01-19 | 17.2 | 26 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 26 | 0 | 0 | 39.791 | 138.7917 | 19.4964 | 86.148 | -75 | 3.6576 | 282.0624 | 0 | 26 | 8.2415 | 0 | 8.2415 | 62.96 | 8.2415 | 5/18/20:00
5 | 18 | 1900-01-20 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 138.8333 | 19.5059 | 86.148 | -75 | 3.6557 | 297.0619 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/18/21:00
5 | 18 | 1900-01-21 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 138.875 | 19.5153 | 86.148 | -75 | 3.6539 | 312.0615 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/18/22:00
5 | 18 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 138.9167 | 19.5247 | 86.148 | -75 | 3.652 | 327.061 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/18/23:00
5 | 18 | 1900-01-23 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 138.9583 | 19.5341 | 86.148 | -75 | 3.6502 | 342.0605 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/18/24:00
5 | 19 | 1899-12-31 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 139 | 19.5435 | 86.148 | -75 | 3.6483 | -2.9399 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/19/1:00
5 | 19 | 1900-01-01 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 139.0417 | 19.5529 | 86.148 | -75 | 3.6464 | 12.0596 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/19/2:00
5 | 19 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 139.0833 | 19.5623 | 86.148 | -75 | 3.6445 | 27.0591 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/19/3:00
5 | 19 | 1900-01-03 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 139.125 | 19.5717 | 86.148 | -75 | 3.6425 | 42.0586 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/19/4:00
5 | 19 | 1900-01-04 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 139.1667 | 19.581 | 86.148 | -75 | 3.6406 | 57.0581 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/19/5:00
5 | 19 | 1900-01-05 | 15 | 12 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 12 | 0 | 0 | 39.791 | 139.2083 | 19.5904 | 86.148 | -75 | 3.6386 | 72.0577 | 0 | 12 | 3.8038 | 0 | 3.8038 | 59 | 3.8038 | 5/19/6:00
5 | 19 | 1900-01-06 | 15.6 | 92 | 78 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 92 | 0 | 0 | 39.791 | 139.25 | 19.5997 | 86.148 | -75 | 3.6366 | 87.0572 | 19.644 | 111.644 | 35.3892 | 0 | 35.3892 | 60.08 | 35.3892 | 5/19/7:00
5 | 19 | 1900-01-07 | 16.1 | 142 | 168 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 142 | 0 | 0 | 39.791 | 139.2917 | 19.6091 | 86.148 | -75 | 3.6346 | 102.0567 | 10.6831 | 152.6831 | 48.3979 | 0 | 48.3979 | 60.98 | 48.3979 | 5/19/8:00
5 | 19 | 1900-01-08 | 17.2 | 212 | 320 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 212 | 0 | 0 | 39.791 | 139.3333 | 19.6184 | 86.148 | -75 | 3.6326 | 117.0562 | -36.5894 | 175.4106 | 55.6021 | 0 | 55.6021 | 62.96 | 55.6021 | 5/19/9:00
5 | 19 | 1900-01-09 | 18.9 | 349 | 243 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 349 | 0 | 0 | 39.791 | 139.375 | 19.6277 | 86.148 | -75 | 3.6306 | 132.0556 | -65.5662 | 283.4338 | 89.8436 | 0 | 89.8436 | 66.02 | 89.8436 | 5/19/10:00
5 | 19 | 1900-01-10 | 19.4 | 334 | 108 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 334 | 0 | 0 | 39.791 | 139.4167 | 19.637 | 86.148 | -75 | 3.6286 | 147.0551 | -42.3626 | 291.6374 | 92.444 | 0 | 92.444 | 66.92 | 92.444 | 5/19/11:00
5 | 19 | 1900-01-11 | 20.6 | 419 | 107 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 419 | 0 | 0 | 39.791 | 139.4583 | 19.6463 | 86.148 | -75 | 3.6265 | 162.0546 | -50.6405 | 368.3595 | 116.7635 | 0 | 116.7635 | 69.08 | 116.7635 | 5/19/12:00
5 | 19 | 1900-01-12 | 20.6 | 289 | 124 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 289 | 0 | 0 | 39.791 | 139.5 | 19.6556 | 86.148 | -75 | 3.6244 | 177.0541 | -62.9157 | 226.0843 | 71.6648 | 0 | 71.6648 | 69.08 | 71.6648 | 5/19/13:00
5 | 19 | 1900-01-13 | 20.6 | 413 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 413 | 0 | 0 | 39.791 | 139.5417 | 19.6649 | 86.148 | -75 | 3.6223 | 192.0536 | 0 | 413 | 130.9138 | 0 | 130.9138 | 69.08 | 130.9138 | 5/19/14:00
5 | 19 | 1900-01-14 | 20 | 313 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 313 | 0 | 0 | 39.791 | 139.5833 | 19.6741 | 86.148 | -75 | 3.6202 | 207.0531 | 0 | 313 | 99.2155 | 0 | 99.2155 | 68 | 99.2155 | 5/19/15:00
5 | 19 | 1900-01-15 | 20 | 313 | 42 | 68 | 0 | 1 | 0 | 68 | 0 | 313 | 0 | 0 | 39.791 | 139.625 | 19.6834 | 86.148 | -75 | 3.6181 | 222.0525 | -13.5092 | 299.4908 | 94.9333 | 0 | 94.9333 | 68 | 94.9333 | 5/19/16:00
5 | 19 | 1900-01-16 | 20 | 247 | 29 | 68 | 0 | 1 | 0 | 68 | 0 | 247 | 0 | 0 | 39.791 | 139.6667 | 19.6926 | 86.148 | -75 | 3.616 | 237.052 | -5.1564 | 241.8436 | 76.6602 | 0 | 76.6602 | 68 | 76.6602 | 5/19/17:00
5 | 19 | 1900-01-17 | 20 | 183 | 60 | 68 | 0 | 1 | 0 | 68 | 0 | 183 | 0 | 0 | 39.791 | 139.7083 | 19.7019 | 86.148 | -75 | 3.6138 | 252.0515 | -0.43012 | 182.5699 | 57.8715 | 0 | 57.8715 | 68 | 57.8715 | 5/19/18:00
5 | 19 | 1900-01-18 | 19.4 | 119 | 87 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 119 | 0 | 0 | 39.791 | 139.75 | 19.7111 | 86.148 | -75 | 3.6116 | 267.0509 | 15.5415 | 134.5415 | 42.6473 | 0 | 42.6473 | 66.92 | 42.6473 | 5/19/19:00
5 | 19 | 1900-01-19 | 18.3 | 27 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 27 | 0 | 0 | 39.791 | 139.7917 | 19.7203 | 86.148 | -75 | 3.6095 | 282.0504 | 0 | 27 | 8.5585 | 0 | 8.5585 | 64.94 | 8.5585 | 5/19/20:00
5 | 19 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 139.8333 | 19.7295 | 86.148 | -75 | 3.6073 | 297.0498 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/19/21:00
5 | 19 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 139.875 | 19.7387 | 86.148 | -75 | 3.6051 | 312.0493 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/19/22:00
5 | 19 | 1900-01-22 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 139.9167 | 19.7479 | 86.148 | -75 | 3.6028 | 327.0487 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/19/23:00
5 | 19 | 1900-01-23 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 139.9583 | 19.7571 | 86.148 | -75 | 3.6006 | 342.0481 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/19/24:00
5 | 20 | 1899-12-31 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 140 | 19.7662 | 86.148 | -75 | 3.5983 | -2.9524 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/20/1:00
5 | 20 | 1900-01-01 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 140.0417 | 19.7754 | 86.148 | -75 | 3.596 | 12.047 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/20/2:00
5 | 20 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 140.0833 | 19.7845 | 86.148 | -75 | 3.5937 | 27.0464 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/20/3:00
5 | 20 | 1900-01-03 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 140.125 | 19.7937 | 86.148 | -75 | 3.5914 | 42.0459 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/20/4:00
5 | 20 | 1900-01-04 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 140.1667 | 19.8028 | 86.148 | -75 | 3.5891 | 57.0453 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/20/5:00
5 | 20 | 1900-01-05 | 15.6 | 8 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 8 | 0 | 0 | 39.791 | 140.2083 | 19.8119 | 86.148 | -75 | 3.5868 | 72.0447 | 0 | 8 | 2.5359 | 0 | 2.5359 | 60.08 | 2.5359 | 5/20/6:00
5 | 20 | 1900-01-06 | 15.6 | 57 | 60 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 57 | 0 | 0 | 39.791 | 140.25 | 19.821 | 86.148 | -75 | 3.5844 | 87.0441 | 15.2571 | 72.2571 | 22.9042 | 0 | 22.9042 | 60.08 | 22.9042 | 5/20/7:00
5 | 20 | 1900-01-07 | 16.1 | 84 | 23 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 84 | 0 | 0 | 39.791 | 140.2917 | 19.8301 | 86.148 | -75 | 3.5821 | 102.0435 | 1.5246 | 85.5246 | 27.1098 | 0 | 27.1098 | 60.98 | 27.1098 | 5/20/8:00
5 | 20 | 1900-01-08 | 16.1 | 176 | 12 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 176 | 0 | 0 | 39.791 | 140.3333 | 19.8392 | 86.148 | -75 | 3.5797 | 117.0429 | -1.337 | 174.663 | 55.3651 | 0 | 55.3651 | 60.98 | 55.3651 | 5/20/9:00
5 | 20 | 1900-01-09 | 17.8 | 305 | 9 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 305 | 0 | 0 | 39.791 | 140.375 | 19.8483 | 86.148 | -75 | 3.5773 | 132.0423 | -2.4004 | 302.5996 | 95.9188 | 0 | 95.9188 | 64.04 | 95.9188 | 5/20/10:00
5 | 20 | 1900-01-10 | 18.9 | 329 | 344 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 329 | 0 | 0 | 39.791 | 140.4167 | 19.8573 | 86.148 | -75 | 3.5748 | 147.0417 | -133.816 | 195.184 | 61.8699 | 0 | 61.8699 | 66.02 | 61.8699 | 5/20/11:00
5 | 20 | 1900-01-11 | 20.6 | 351 | 349 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 351 | 0 | 0 | 39.791 | 140.4583 | 19.8664 | 86.148 | -75 | 3.5724 | 162.0411 | -164.0162 | 186.9838 | 59.2706 | 0 | 59.2706 | 69.08 | 59.2706 | 5/20/12:00
5 | 20 | 1900-01-12 | 21.7 | 350 | 336 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 350 | 0 | 0 | 39.791 | 140.5 | 19.8754 | 86.148 | -75 | 3.57 | 177.0405 | -169.3674 | 180.6326 | 57.2574 | 0 | 57.2574 | 71.06 | 57.2574 | 5/20/13:00
5 | 20 | 1900-01-13 | 22.2 | 391 | 168 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 391 | 0 | 0 | 39.791 | 140.5417 | 19.8845 | 86.148 | -75 | 3.5675 | 192.0399 | -82.1524 | 308.8476 | 97.8993 | 0 | 97.8993 | 71.96 | 97.8993 | 5/20/14:00
5 | 20 | 1900-01-14 | 21.7 | 371 | 245 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 371 | 0 | 0 | 39.791 | 140.5833 | 19.8935 | 86.148 | -75 | 3.565 | 207.0393 | -104.3174 | 266.6826 | 84.5337 | 0 | 84.5337 | 71.06 | 84.5337 | 5/20/15:00
5 | 20 | 1900-01-15 | 23.3 | 213 | 515 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 213 | 0 | 0 | 39.791 | 140.625 | 19.9025 | 86.148 | -75 | 3.5625 | 222.0386 | -164.1428 | 48.8572 | 15.4869 | 0 | 15.4869 | 73.94 | 15.4869 | 5/20/16:00
5 | 20 | 1900-01-16 | 21.7 | 288 | 146 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 288 | 0 | 0 | 39.791 | 140.6667 | 19.9115 | 86.148 | -75 | 3.56 | 237.038 | -25.5664 | 262.4336 | 83.1869 | 0 | 83.1869 | 71.06 | 83.1869 | 5/20/17:00
5 | 20 | 1900-01-17 | 22.2 | 174 | 61 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 174 | 0 | 0 | 39.791 | 140.7083 | 19.9205 | 86.148 | -75 | 3.5575 | 252.0374 | -0.28877 | 173.7112 | 55.0634 | 0 | 55.0634 | 71.96 | 55.0634 | 5/20/18:00
5 | 20 | 1900-01-18 | 20.6 | 85 | 122 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 85 | 0 | 0 | 39.791 | 140.75 | 19.9295 | 86.148 | -75 | 3.555 | 267.0367 | 22.0583 | 107.0583 | 33.9356 | 0 | 33.9356 | 69.08 | 33.9356 | 5/20/19:00
5 | 20 | 1900-01-19 | 18.9 | 26 | 15 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 26 | 0 | 0 | 39.791 | 140.7917 | 19.9385 | 86.148 | -75 | 3.5524 | 282.0361 | 5.533 | 31.533 | 9.9954 | 0 | 9.9954 | 66.02 | 9.9954 | 5/20/20:00
5 | 20 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 140.8333 | 19.9474 | 86.148 | -75 | 3.5498 | 297.0355 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/20/21:00
5 | 20 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 140.875 | 19.9564 | 86.148 | -75 | 3.5473 | 312.0348 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/20/22:00
5 | 20 | 1900-01-22 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 140.9167 | 19.9653 | 86.148 | -75 | 3.5447 | 327.0342 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/20/23:00
5 | 20 | 1900-01-23 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 140.9583 | 19.9742 | 86.148 | -75 | 3.542 | 342.0335 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/20/24:00
5 | 21 | 1899-12-31 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 141 | 19.9832 | 86.148 | -75 | 3.5394 | -2.9671 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 5/21/1:00
5 | 21 | 1900-01-01 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 141.0417 | 19.9921 | 86.148 | -75 | 3.5368 | 12.0322 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/21/2:00
5 | 21 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 141.0833 | 20.001 | 86.148 | -75 | 3.5341 | 27.0315 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/21/3:00
5 | 21 | 1900-01-03 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 141.125 | 20.0099 | 86.148 | -75 | 3.5314 | 42.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/21/4:00
5 | 21 | 1900-01-04 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 141.1667 | 20.0187 | 86.148 | -75 | 3.5287 | 57.0302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/21/5:00
5 | 21 | 1900-01-05 | 11.1 | 8 | 1 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 8 | 0 | 0 | 39.791 | 141.2083 | 20.0276 | 86.148 | -75 | 3.526 | 72.0295 | 0.44191 | 8.4419 | 2.6759 | 2.6759 | 0 | 0 | 0 | 5/21/6:00
5 | 21 | 1900-01-06 | 11.7 | 43 | 32 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 43 | 0 | 0 | 39.791 | 141.25 | 20.0365 | 86.148 | -75 | 3.5233 | 87.0288 | 8.2141 | 51.2141 | 16.234 | 16.234 | 0 | 0 | 0 | 5/21/7:00
5 | 21 | 1900-01-07 | 14.4 | 125 | 354 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 125 | 0 | 0 | 39.791 | 141.2917 | 20.0453 | 86.148 | -75 | 3.5206 | 102.0281 | 24.4046 | 149.4046 | 47.3587 | 0 | 47.3587 | 57.92 | 47.3587 | 5/21/8:00
5 | 21 | 1900-01-08 | 17.2 | 171 | 585 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 171 | 0 | 0 | 39.791 | 141.3333 | 20.0542 | 86.148 | -75 | 3.5178 | 117.0275 | -63.4954 | 107.5046 | 34.0771 | 0 | 34.0771 | 62.96 | 34.0771 | 5/21/9:00
5 | 21 | 1900-01-09 | 19.4 | 208 | 670 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 208 | 0 | 0 | 39.791 | 141.375 | 20.063 | 86.148 | -75 | 3.5151 | 132.0268 | -176.6448 | 31.3552 | 9.939 | 0 | 9.939 | 66.92 | 9.939 | 5/21/10:00
5 | 21 | 1900-01-10 | 21.1 | 209 | 724 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 209 | 0 | 0 | 39.791 | 141.4167 | 20.0718 | 86.148 | -75 | 3.5123 | 147.0261 | -279.3316 | -70.3316 | -22.2939 | 0 | -22.2939 | 69.98 | -22.2939 | 5/21/11:00
5 | 21 | 1900-01-11 | 23.3 | 366 | 394 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 366 | 0 | 0 | 39.791 | 141.4583 | 20.0806 | 86.148 | -75 | 3.5095 | 162.0254 | -183.8864 | 182.1136 | 57.7268 | 0 | 57.7268 | 73.94 | 57.7268 | 5/21/12:00
5 | 21 | 1900-01-12 | 23.3 | 474 | 221 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 474 | 0 | 0 | 39.791 | 141.5 | 20.0894 | 86.148 | -75 | 3.5067 | 177.0247 | -110.6842 | 363.3158 | 115.1648 | 0 | 115.1648 | 73.94 | 115.1648 | 5/21/13:00
5 | 21 | 1900-01-13 | 23.3 | 412 | 102 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 412 | 0 | 0 | 39.791 | 141.5417 | 20.0982 | 86.148 | -75 | 3.5038 | 192.024 | -49.5559 | 362.4441 | 114.8884 | 0 | 114.8884 | 73.94 | 114.8884 | 5/21/14:00
5 | 21 | 1900-01-14 | 24.4 | 386 | 240 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 386 | 0 | 0 | 39.791 | 141.5833 | 20.107 | 86.148 | -75 | 3.501 | 207.0233 | -101.4633 | 284.5367 | 90.1932 | 0 | 90.1932 | 75.92 | 90.1932 | 5/21/15:00
5 | 21 | 1900-01-15 | 25 | 289 | 475 | 77 | 0 | 1 | 0 | 77 | 0 | 289 | 0 | 0 | 39.791 | 141.625 | 20.1158 | 86.148 | -75 | 3.4981 | 222.0225 | -150.05 | 138.95 | 44.0447 | 0 | 44.0447 | 77 | 44.0447 | 5/21/16:00
5 | 21 | 1900-01-16 | 23.9 | 249 | 70 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 249 | 0 | 0 | 39.791 | 141.6667 | 20.1245 | 86.148 | -75 | 3.4953 | 237.0218 | -12.0761 | 236.9239 | 75.1007 | 0 | 75.1007 | 75.02 | 75.1007 | 5/21/17:00
5 | 21 | 1900-01-17 | 23.9 | 202 | 74 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 202 | 0 | 0 | 39.791 | 141.7083 | 20.1333 | 86.148 | -75 | 3.4924 | 252.0211 | -0.17721 | 201.8228 | 63.9743 | 0 | 63.9743 | 75.02 | 63.9743 | 5/21/18:00
5 | 21 | 1900-01-18 | 23.3 | 101 | 14 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 101 | 0 | 0 | 39.791 | 141.75 | 20.142 | 86.148 | -75 | 3.4895 | 267.0204 | 2.5603 | 103.5603 | 32.8268 | 0 | 32.8268 | 73.94 | 32.8268 | 5/21/19:00
5 | 21 | 1900-01-19 | 21.1 | 27 | 17 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 27 | 0 | 0 | 39.791 | 141.7917 | 20.1507 | 86.148 | -75 | 3.4866 | 282.0196 | 6.3017 | 33.3017 | 10.5561 | 0 | 10.5561 | 69.98 | 10.5561 | 5/21/20:00
5 | 21 | 1900-01-20 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 141.8333 | 20.1594 | 86.148 | -75 | 3.4836 | 297.0189 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 5/21/21:00
5 | 21 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 141.875 | 20.1681 | 86.148 | -75 | 3.4807 | 312.0182 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/21/22:00
5 | 21 | 1900-01-22 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 141.9167 | 20.1768 | 86.148 | -75 | 3.4777 | 327.0174 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/21/23:00
5 | 21 | 1900-01-23 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 141.9583 | 20.1855 | 86.148 | -75 | 3.4747 | 342.0167 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/21/24:00
5 | 22 | 1899-12-31 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 142 | 20.1942 | 86.148 | -75 | 3.4718 | -2.9841 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/22/1:00
5 | 22 | 1900-01-01 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 142.0417 | 20.2029 | 86.148 | -75 | 3.4687 | 12.0152 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/22/2:00
5 | 22 | 1900-01-02 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 142.0833 | 20.2115 | 86.148 | -75 | 3.4657 | 27.0144 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/22/3:00
5 | 22 | 1900-01-03 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 142.125 | 20.2202 | 86.148 | -75 | 3.4627 | 42.0137 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/22/4:00
5 | 22 | 1900-01-04 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 142.1667 | 20.2288 | 86.148 | -75 | 3.4596 | 57.0129 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/22/5:00
5 | 22 | 1900-01-05 | 13.9 | 13 | 77 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 13 | 0 | 0 | 39.791 | 142.2083 | 20.2374 | 86.148 | -75 | 3.4566 | 72.0121 | 34.1895 | 47.1895 | 14.9582 | 0 | 14.9582 | 57.02 | 14.9582 | 5/22/6:00
5 | 22 | 1900-01-06 | 14.4 | 44 | 399 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 44 | 0 | 0 | 39.791 | 142.25 | 20.246 | 86.148 | -75 | 3.4535 | 87.0114 | 103.3634 | 147.3634 | 46.7116 | 0 | 46.7116 | 57.92 | 46.7116 | 5/22/7:00
5 | 22 | 1900-01-07 | 17.8 | 155 | 241 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 155 | 0 | 0 | 39.791 | 142.2917 | 20.2546 | 86.148 | -75 | 3.4504 | 102.0106 | 17.244 | 172.244 | 54.5983 | 0 | 54.5983 | 64.04 | 54.5983 | 5/22/8:00
5 | 22 | 1900-01-08 | 20.6 | 200 | 423 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 200 | 0 | 0 | 39.791 | 142.3333 | 20.2632 | 86.148 | -75 | 3.4473 | 117.0098 | -44.7155 | 155.2845 | 49.2225 | 0 | 49.2225 | 69.08 | 49.2225 | 5/22/9:00
5 | 22 | 1900-01-09 | 22.8 | 329 | 386 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 329 | 0 | 0 | 39.791 | 142.375 | 20.2718 | 86.148 | -75 | 3.4442 | 132.009 | -100.61 | 228.39 | 72.3956 | 0 | 72.3956 | 73.04 | 72.3956 | 5/22/10:00
5 | 22 | 1900-01-10 | 25 | 354 | 465 | 77 | 0 | 1 | 0 | 77 | 0 | 354 | 0 | 0 | 39.791 | 142.4167 | 20.2804 | 86.148 | -75 | 3.441 | 147.0083 | -177.9551 | 176.0449 | 55.8031 | 0 | 55.8031 | 77 | 55.8031 | 5/22/11:00
5 | 22 | 1900-01-11 | 25.6 | 412 | 381 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 412 | 0 | 0 | 39.791 | 142.4583 | 20.2889 | 86.148 | -75 | 3.4379 | 162.0075 | -176.6112 | 235.3888 | 74.6142 | 0 | 74.6142 | 78.08 | 74.6142 | 5/22/12:00
5 | 22 | 1900-01-12 | 25.6 | 320 | 530 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 320 | 0 | 0 | 39.791 | 142.5 | 20.2975 | 86.148 | -75 | 3.4347 | 177.0067 | -263.7698 | 56.2302 | 17.824 | 0 | 17.824 | 78.08 | 17.824 | 5/22/13:00
5 | 22 | 1900-01-13 | 26.7 | 279 | 518 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 279 | 0 | 0 | 39.791 | 142.5417 | 20.306 | 86.148 | -75 | 3.4315 | 192.0059 | -250.0749 | 28.9251 | 9.1688 | 0 | 9.1688 | 80.06 | 9.1688 | 5/22/14:00
5 | 22 | 1900-01-14 | 26.7 | 284 | 497 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 284 | 0 | 0 | 39.791 | 142.5833 | 20.3145 | 86.148 | -75 | 3.4283 | 207.0051 | -208.6581 | 75.3419 | 23.8821 | 0 | 23.8821 | 80.06 | 23.8821 | 5/22/15:00
5 | 22 | 1900-01-15 | 27.2 | 287 | 434 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 287 | 0 | 0 | 39.791 | 142.625 | 20.3231 | 86.148 | -75 | 3.4251 | 222.0043 | -135.9121 | 151.0879 | 47.8922 | 0 | 47.8922 | 80.96 | 47.8922 | 5/22/16:00
5 | 22 | 1900-01-16 | 26.7 | 259 | 203 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 259 | 0 | 0 | 39.791 | 142.6667 | 20.3316 | 86.148 | -75 | 3.4219 | 237.0035 | -34.5134 | 224.4866 | 71.1583 | 0 | 71.1583 | 80.06 | 71.1583 | 5/22/17:00
5 | 22 | 1900-01-17 | 26.1 | 111 | 604 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 111 | 0 | 0 | 39.791 | 142.7083 | 20.3401 | 86.148 | -75 | 3.4186 | 252.0027 | -0.091661 | 110.9083 | 35.156 | 0 | 35.156 | 78.98 | 35.156 | 5/22/18:00
5 | 22 | 1900-01-18 | 25 | 63 | 457 | 77 | 0 | 1 | 0 | 77 | 0 | 63 | 0 | 0 | 39.791 | 142.75 | 20.3486 | 86.148 | -75 | 3.4154 | 267.0018 | 84.482 | 147.482 | 46.7492 | 0 | 46.7492 | 77 | 46.7492 | 5/22/19:00
5 | 22 | 1900-01-19 | 24.4 | 27 | 2 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 27 | 0 | 0 | 39.791 | 142.7917 | 20.357 | 86.148 | -75 | 3.4121 | 282.001 | 0.74485 | 27.7448 | 8.7946 | 0 | 8.7946 | 75.92 | 8.7946 | 5/22/20:00
5 | 22 | 1900-01-20 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 142.8333 | 20.3655 | 86.148 | -75 | 3.4088 | 297.0002 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 5/22/21:00
5 | 22 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 142.875 | 20.374 | 86.148 | -75 | 3.4055 | 311.9994 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 5/22/22:00
5 | 22 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 142.9167 | 20.3824 | 86.148 | -75 | 3.4022 | 326.9985 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 5/22/23:00
5 | 22 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 142.9583 | 20.3908 | 86.148 | -75 | 3.3988 | 341.9977 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 5/22/24:00
5 | 23 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 143 | 20.3993 | 86.148 | -75 | 3.3955 | -3.0031 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 5/23/1:00
5 | 23 | 1900-01-01 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 143.0417 | 20.4077 | 86.148 | -75 | 3.3921 | 11.996 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/23/2:00
5 | 23 | 1900-01-02 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 143.0833 | 20.4161 | 86.148 | -75 | 3.3887 | 26.9952 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 5/23/3:00
5 | 23 | 1900-01-03 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 143.125 | 20.4245 | 86.148 | -75 | 3.3854 | 41.9943 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/23/4:00
5 | 23 | 1900-01-04 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 143.1667 | 20.4328 | 86.148 | -75 | 3.382 | 56.9935 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/23/5:00
5 | 23 | 1900-01-05 | 18.9 | 6 | 1 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 6 | 0 | 0 | 39.791 | 143.2083 | 20.4412 | 86.148 | -75 | 3.3785 | 71.9926 | 0.44609 | 6.4461 | 2.0433 | 0 | 2.0433 | 66.02 | 2.0433 | 5/23/6:00
5 | 23 | 1900-01-06 | 18.9 | 40 | 3 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 40 | 0 | 0 | 39.791 | 143.25 | 20.4496 | 86.148 | -75 | 3.3751 | 86.9918 | 0.78415 | 40.7842 | 12.9279 | 0 | 12.9279 | 66.02 | 12.9279 | 5/23/7:00
5 | 23 | 1900-01-07 | 18.3 | 68 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 68 | 0 | 0 | 39.791 | 143.2917 | 20.4579 | 86.148 | -75 | 3.3716 | 101.9909 | 0.07412 | 68.0741 | 21.5783 | 0 | 21.5783 | 64.94 | 21.5783 | 5/23/8:00
5 | 23 | 1900-01-08 | 18.9 | 293 | 7 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 293 | 0 | 0 | 39.791 | 143.3333 | 20.4663 | 86.148 | -75 | 3.3682 | 116.99 | -0.72053 | 292.2795 | 92.6475 | 0 | 92.6475 | 66.02 | 92.6475 | 5/23/9:00
5 | 23 | 1900-01-09 | 19.4 | 170 | 4 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 170 | 0 | 0 | 39.791 | 143.375 | 20.4746 | 86.148 | -75 | 3.3647 | 131.9892 | -1.0308 | 168.9692 | 53.5603 | 0 | 53.5603 | 66.92 | 53.5603 | 5/23/10:00
5 | 23 | 1900-01-10 | 20.6 | 378 | 7 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 378 | 0 | 0 | 39.791 | 143.4167 | 20.4829 | 86.148 | -75 | 3.3612 | 146.9883 | -2.6575 | 375.3425 | 118.977 | 0 | 118.977 | 69.08 | 118.977 | 5/23/11:00
5 | 23 | 1900-01-11 | 21.1 | 360 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 360 | 0 | 0 | 39.791 | 143.4583 | 20.4912 | 86.148 | -75 | 3.3577 | 161.9874 | 0 | 360 | 114.1137 | 0 | 114.1137 | 69.98 | 114.1137 | 5/23/12:00
5 | 23 | 1900-01-12 | 21.7 | 479 | 72 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 479 | 0 | 0 | 39.791 | 143.5 | 20.4995 | 86.148 | -75 | 3.3542 | 176.9865 | -35.6117 | 443.3883 | 140.5463 | 0 | 140.5463 | 71.06 | 140.5463 | 5/23/13:00
5 | 23 | 1900-01-13 | 24.4 | 327 | 586 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 327 | 0 | 0 | 39.791 | 143.5417 | 20.5078 | 86.148 | -75 | 3.3506 | 191.9857 | -281.1553 | 45.8447 | 14.532 | 0 | 14.532 | 75.92 | 14.532 | 5/23/14:00
5 | 23 | 1900-01-14 | 25 | 416 | 248 | 77 | 0 | 1 | 0 | 77 | 0 | 416 | 0 | 0 | 39.791 | 143.5833 | 20.5161 | 86.148 | -75 | 3.3471 | 206.9848 | -103.4162 | 312.5838 | 99.0836 | 0 | 99.0836 | 77 | 99.0836 | 5/23/15:00
5 | 23 | 1900-01-15 | 25 | 398 | 167 | 77 | 0 | 1 | 0 | 77 | 0 | 398 | 0 | 0 | 39.791 | 143.625 | 20.5244 | 86.148 | -75 | 3.3435 | 221.9839 | -51.8578 | 346.1422 | 109.721 | 0 | 109.721 | 77 | 109.721 | 5/23/16:00
5 | 23 | 1900-01-16 | 25.6 | 275 | 283 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 275 | 0 | 0 | 39.791 | 143.6667 | 20.5326 | 86.148 | -75 | 3.34 | 236.983 | -47.4352 | 227.5648 | 72.1341 | 0 | 72.1341 | 78.08 | 72.1341 | 5/23/17:00
5 | 23 | 1900-01-17 | 25 | 201 | 187 | 77 | 0 | 1 | 0 | 77 | 0 | 201 | 0 | 0 | 39.791 | 143.7083 | 20.5409 | 86.148 | -75 | 3.3364 | 251.9821 | 0.37303 | 201.373 | 63.8317 | 0 | 63.8317 | 77 | 63.8317 | 5/23/18:00
5 | 23 | 1900-01-18 | 23.9 | 68 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 68 | 0 | 0 | 39.791 | 143.75 | 20.5491 | 86.148 | -75 | 3.3328 | 266.9812 | 0 | 68 | 21.5548 | 0 | 21.5548 | 75.02 | 21.5548 | 5/23/19:00
5 | 23 | 1900-01-19 | 17.8 | 23 | 1 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 23 | 0 | 0 | 39.791 | 143.7917 | 20.5573 | 86.148 | -75 | 3.3291 | 281.9803 | 0.37407 | 23.3741 | 7.4092 | 0 | 7.4092 | 64.04 | 7.4092 | 5/23/20:00
5 | 23 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 143.8333 | 20.5655 | 86.148 | -75 | 3.3255 | 296.9794 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/23/21:00
5 | 23 | 1900-01-21 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 143.875 | 20.5737 | 86.148 | -75 | 3.3218 | 311.9785 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/23/22:00
5 | 23 | 1900-01-22 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 143.9167 | 20.5819 | 86.148 | -75 | 3.3182 | 326.9775 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 5/23/23:00
5 | 23 | 1900-01-23 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 143.9583 | 20.5901 | 86.148 | -75 | 3.3145 | 341.9766 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/23/24:00
5 | 24 | 1899-12-31 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 144 | 20.5983 | 86.148 | -75 | 3.3108 | -3.0243 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/24/1:00
5 | 24 | 1900-01-01 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 144.0417 | 20.6064 | 86.148 | -75 | 3.3071 | 11.9748 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/24/2:00
5 | 24 | 1900-01-02 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 144.0833 | 20.6146 | 86.148 | -75 | 3.3034 | 26.9738 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/24/3:00
5 | 24 | 1900-01-03 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 144.125 | 20.6227 | 86.148 | -75 | 3.2996 | 41.9729 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/24/4:00
5 | 24 | 1900-01-04 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 144.1667 | 20.6309 | 86.148 | -75 | 3.2959 | 56.972 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/24/5:00
5 | 24 | 1900-01-05 | 15 | 6 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 6 | 0 | 0 | 39.791 | 144.2083 | 20.639 | 86.148 | -75 | 3.2921 | 71.971 | 0 | 6 | 1.9019 | 0 | 1.9019 | 59 | 1.9019 | 5/24/6:00
5 | 24 | 1900-01-06 | 15.6 | 71 | 3 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 71 | 0 | 0 | 39.791 | 144.25 | 20.6471 | 86.148 | -75 | 3.2883 | 86.9701 | 0.79102 | 71.791 | 22.7565 | 0 | 22.7565 | 60.08 | 22.7565 | 5/24/7:00
5 | 24 | 1900-01-07 | 16.7 | 146 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 146 | 0 | 0 | 39.791 | 144.2917 | 20.6552 | 86.148 | -75 | 3.2845 | 101.9691 | 0 | 146 | 46.2795 | 0 | 46.2795 | 62.06 | 46.2795 | 5/24/8:00
5 | 24 | 1900-01-08 | 17.8 | 257 | 2 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 257 | 0 | 0 | 39.791 | 144.3333 | 20.6633 | 86.148 | -75 | 3.2807 | 116.9682 | -0.20041 | 256.7996 | 81.401 | 0 | 81.401 | 64.04 | 81.401 | 5/24/9:00
5 | 24 | 1900-01-09 | 18.3 | 325 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 325 | 0 | 0 | 39.791 | 144.375 | 20.6713 | 86.148 | -75 | 3.2769 | 131.9672 | -0.25482 | 324.7452 | 102.9385 | 0 | 102.9385 | 64.94 | 102.9385 | 5/24/10:00
5 | 24 | 1900-01-10 | 17.8 | 238 | 1 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 238 | 0 | 0 | 39.791 | 144.4167 | 20.6794 | 86.148 | -75 | 3.2731 | 146.9663 | -0.37667 | 237.6233 | 75.3224 | 0 | 75.3224 | 64.04 | 75.3224 | 5/24/11:00
5 | 24 | 1900-01-11 | 17.8 | 248 | 1 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 248 | 0 | 0 | 39.791 | 144.4583 | 20.6874 | 86.148 | -75 | 3.2692 | 161.9653 | -0.45743 | 247.5426 | 78.4667 | 0 | 78.4667 | 64.04 | 78.4667 | 5/24/12:00
5 | 24 | 1900-01-12 | 20 | 419 | 203 | 68 | 0 | 1 | 0 | 68 | 0 | 419 | 0 | 0 | 39.791 | 144.5 | 20.6955 | 86.148 | -75 | 3.2654 | 176.9643 | -99.7989 | 319.2011 | 101.1812 | 0 | 101.1812 | 68 | 101.1812 | 5/24/13:00
5 | 24 | 1900-01-13 | 21.1 | 357 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 357 | 0 | 0 | 39.791 | 144.5417 | 20.7035 | 86.148 | -75 | 3.2615 | 191.9634 | 0 | 357 | 113.1628 | 0 | 113.1628 | 69.98 | 113.1628 | 5/24/14:00
5 | 24 | 1900-01-14 | 21.7 | 309 | 374 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 309 | 0 | 0 | 39.791 | 144.5833 | 20.7115 | 86.148 | -75 | 3.2576 | 206.9624 | -154.9342 | 154.0658 | 48.8362 | 0 | 48.8362 | 71.06 | 48.8362 | 5/24/15:00
5 | 24 | 1900-01-15 | 23.3 | 157 | 671 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 157 | 0 | 0 | 39.791 | 144.625 | 20.7196 | 86.148 | -75 | 3.2537 | 221.9614 | -206.6602 | -49.6602 | -15.7414 | 0 | -15.7414 | 73.94 | -15.7414 | 5/24/16:00
5 | 24 | 1900-01-16 | 23.9 | 344 | 188 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 344 | 0 | 0 | 39.791 | 144.6667 | 20.7276 | 86.148 | -75 | 3.2498 | 236.9604 | -31.0788 | 312.9212 | 99.1906 | 0 | 99.1906 | 75.02 | 99.1906 | 5/24/17:00
5 | 24 | 1900-01-17 | 22.8 | 202 | 120 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 202 | 0 | 0 | 39.791 | 144.7083 | 20.7355 | 86.148 | -75 | 3.2458 | 251.9595 | 0.48534 | 202.4853 | 64.1843 | 0 | 64.1843 | 73.04 | 64.1843 | 5/24/18:00
5 | 24 | 1900-01-18 | 22.2 | 121 | 135 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 121 | 0 | 0 | 39.791 | 144.75 | 20.7435 | 86.148 | -75 | 3.2419 | 266.9585 | 25.4539 | 146.4539 | 46.4233 | 0 | 46.4233 | 71.96 | 46.4233 | 5/24/19:00
5 | 24 | 1900-01-19 | 20.6 | 36 | 20 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 36 | 0 | 0 | 39.791 | 144.7917 | 20.7515 | 86.148 | -75 | 3.2379 | 281.9575 | 7.5126 | 43.5126 | 13.7927 | 0 | 13.7927 | 69.08 | 13.7927 | 5/24/20:00
5 | 24 | 1900-01-20 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 144.8333 | 20.7594 | 86.148 | -75 | 3.2339 | 296.9565 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/24/21:00
5 | 24 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 144.875 | 20.7674 | 86.148 | -75 | 3.2299 | 311.9555 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/24/22:00
5 | 24 | 1900-01-22 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 144.9167 | 20.7753 | 86.148 | -75 | 3.2259 | 326.9545 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 5/24/23:00
5 | 24 | 1900-01-23 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 144.9583 | 20.7832 | 86.148 | -75 | 3.2219 | 341.9535 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/24/24:00
5 | 25 | 1899-12-31 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 145 | 20.7912 | 86.148 | -75 | 3.2179 | -3.0475 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/25/1:00
5 | 25 | 1900-01-01 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 145.0417 | 20.7991 | 86.148 | -75 | 3.2138 | 11.9515 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 5/25/2:00
5 | 25 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 145.0833 | 20.807 | 86.148 | -75 | 3.2098 | 26.9504 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/25/3:00
5 | 25 | 1900-01-03 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 145.125 | 20.8148 | 86.148 | -75 | 3.2057 | 41.9494 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/25/4:00
5 | 25 | 1900-01-04 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 145.1667 | 20.8227 | 86.148 | -75 | 3.2016 | 56.9484 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/25/5:00
5 | 25 | 1900-01-05 | 15 | 14 | 2 | 59 | 0 | 1 | 0 | 59 | 0 | 14 | 0 | 0 | 39.791 | 145.2083 | 20.8306 | 86.148 | -75 | 3.1975 | 71.9474 | 0.90027 | 14.9003 | 4.7231 | 0 | 4.7231 | 59 | 4.7231 | 5/25/6:00
5 | 25 | 1900-01-06 | 15.6 | 60 | 136 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 60 | 0 | 0 | 39.791 | 145.25 | 20.8384 | 86.148 | -75 | 3.1934 | 86.9463 | 36.1652 | 96.1652 | 30.4827 | 0 | 30.4827 | 60.08 | 30.4827 | 5/25/7:00
5 | 25 | 1900-01-07 | 18.3 | 125 | 374 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 125 | 0 | 0 | 39.791 | 145.2917 | 20.8463 | 86.148 | -75 | 3.1893 | 101.9453 | 29.5908 | 154.5908 | 49.0026 | 0 | 49.0026 | 64.94 | 49.0026 | 5/25/8:00
5 | 25 | 1900-01-08 | 21.1 | 176 | 522 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 176 | 0 | 0 | 39.791 | 145.3333 | 20.8541 | 86.148 | -75 | 3.1851 | 116.9443 | -50.9133 | 125.0867 | 39.6503 | 0 | 39.6503 | 69.98 | 39.6503 | 5/25/9:00
5 | 25 | 1900-01-09 | 23.9 | 215 | 602 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 215 | 0 | 0 | 39.791 | 145.375 | 20.8619 | 86.148 | -75 | 3.181 | 131.9432 | -151.7057 | 63.2943 | 20.0632 | 0 | 20.0632 | 75.02 | 20.0632 | 5/25/10:00
5 | 25 | 1900-01-10 | 26.1 | 242 | 667 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 242 | 0 | 0 | 39.791 | 145.4167 | 20.8697 | 86.148 | -75 | 3.1768 | 146.9422 | -249.2949 | -7.2949 | -2.3124 | 0 | -2.3124 | 78.98 | -2.3124 | 5/25/11:00
5 | 25 | 1900-01-11 | 27.2 | 252 | 668 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 252 | 0 | 0 | 39.791 | 145.4583 | 20.8775 | 86.148 | -75 | 3.1726 | 161.9411 | -303.6029 | -51.6029 | -16.3572 | 0 | -16.3572 | 80.96 | -16.3572 | 5/25/12:00
5 | 25 | 1900-01-12 | 28.3 | 278 | 666 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 278 | 0 | 0 | 39.791 | 145.5 | 20.8853 | 86.148 | -75 | 3.1684 | 176.9401 | -325.4874 | -47.4874 | -15.0527 | 0 | -15.0527 | 82.94 | -15.0527 | 5/25/13:00
5 | 25 | 1900-01-13 | 28.3 | 262 | 698 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 262 | 0 | 0 | 39.791 | 145.5417 | 20.8931 | 86.148 | -75 | 3.1642 | 191.939 | -330.9194 | -68.9194 | -21.8462 | 0 | -21.8462 | 82.94 | -21.8462 | 5/25/14:00
5 | 25 | 1900-01-14 | 29.4 | 250 | 684 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 250 | 0 | 0 | 39.791 | 145.5833 | 20.9008 | 86.148 | -75 | 3.16 | 206.938 | -281.5489 | -31.5489 | -10.0004 | 0 | -10.0004 | 84.92 | -10.0004 | 5/25/15:00
5 | 25 | 1900-01-15 | 29.4 | 227 | 643 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 227 | 0 | 0 | 39.791 | 145.625 | 20.9086 | 86.148 | -75 | 3.1557 | 221.9369 | -196.4687 | 30.5313 | 9.6779 | 0 | 9.6779 | 84.92 | 9.6779 | 5/25/16:00
5 | 25 | 1900-01-16 | 29.4 | 193 | 566 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 193 | 0 | 0 | 39.791 | 145.6667 | 20.9163 | 86.148 | -75 | 3.1515 | 236.9359 | -92.32 | 100.68 | 31.9138 | 0 | 31.9138 | 84.92 | 31.9138 | 5/25/17:00
5 | 25 | 1900-01-17 | 28.9 | 146 | 440 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 146 | 0 | 0 | 39.791 | 145.7083 | 20.924 | 86.148 | -75 | 3.1472 | 251.9348 | 2.6388 | 148.6388 | 47.1159 | 0 | 47.1159 | 84.02 | 47.1159 | 5/25/18:00
5 | 25 | 1900-01-18 | 27.2 | 91 | 244 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 91 | 0 | 0 | 39.791 | 145.75 | 20.9318 | 86.148 | -75 | 3.1429 | 266.9337 | 46.4211 | 137.4211 | 43.5601 | 0 | 43.5601 | 80.96 | 43.5601 | 5/25/19:00
5 | 25 | 1900-01-19 | 26.1 | 30 | 20 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 30 | 0 | 0 | 39.791 | 145.7917 | 20.9395 | 86.148 | -75 | 3.1386 | 281.9327 | 7.542 | 37.542 | 11.9002 | 0 | 11.9002 | 78.98 | 11.9002 | 5/25/20:00
5 | 25 | 1900-01-20 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 145.8333 | 20.9472 | 86.148 | -75 | 3.1343 | 296.9316 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 5/25/21:00
5 | 25 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 145.875 | 20.9548 | 86.148 | -75 | 3.13 | 311.9305 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 5/25/22:00
5 | 25 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 145.9167 | 20.9625 | 86.148 | -75 | 3.1256 | 326.9294 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 5/25/23:00
5 | 25 | 1900-01-23 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 145.9583 | 20.9702 | 86.148 | -75 | 3.1213 | 341.9283 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 5/25/24:00
5 | 26 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 146 | 20.9778 | 86.148 | -75 | 3.1169 | -3.0728 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 5/26/1:00
5 | 26 | 1900-01-01 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 146.0417 | 20.9855 | 86.148 | -75 | 3.1126 | 11.9261 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/26/2:00
5 | 26 | 1900-01-02 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 146.0833 | 20.9931 | 86.148 | -75 | 3.1082 | 26.925 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/26/3:00
5 | 26 | 1900-01-03 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 146.125 | 21.0007 | 86.148 | -75 | 3.1038 | 41.9239 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/26/4:00
5 | 26 | 1900-01-04 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 146.1667 | 21.0083 | 86.148 | -75 | 3.0993 | 56.9228 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/26/5:00
5 | 26 | 1900-01-05 | 12.2 | 15 | 14 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 15 | 0 | 0 | 39.791 | 146.2083 | 21.0159 | 86.148 | -75 | 3.0949 | 71.9217 | 6.3294 | 21.3294 | 6.761 | 6.761 | 0 | 0 | 0 | 5/26/6:00
5 | 26 | 1900-01-06 | 12.8 | 58 | 283 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 58 | 0 | 0 | 39.791 | 146.25 | 21.0235 | 86.148 | -75 | 3.0905 | 86.9206 | 75.8798 | 133.8798 | 42.4376 | 0 | 42.4376 | 55.04 | 42.4376 | 5/26/7:00
5 | 26 | 1900-01-07 | 13.9 | 97 | 531 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 97 | 0 | 0 | 39.791 | 146.2917 | 21.0311 | 86.148 | -75 | 3.086 | 101.9195 | 43.3018 | 140.3018 | 44.4732 | 0 | 44.4732 | 57.02 | 44.4732 | 5/26/8:00
5 | 26 | 1900-01-08 | 15.6 | 131 | 669 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 131 | 0 | 0 | 39.791 | 146.3333 | 21.0387 | 86.148 | -75 | 3.0815 | 116.9184 | -63.5011 | 67.4989 | 21.396 | 0 | 21.396 | 60.08 | 21.396 | 5/26/9:00
5 | 26 | 1900-01-09 | 18.3 | 158 | 745 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 158 | 0 | 0 | 39.791 | 146.375 | 21.0462 | 86.148 | -75 | 3.0771 | 131.9173 | -185.6892 | -27.6892 | -8.777 | 0 | -8.777 | 64.94 | -8.777 | 5/26/10:00
5 | 26 | 1900-01-10 | 20.6 | 183 | 786 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 183 | 0 | 0 | 39.791 | 146.4167 | 21.0538 | 86.148 | -75 | 3.0726 | 146.9161 | -291.5411 | -108.5411 | -34.4056 | 0 | -34.4056 | 69.08 | -34.4056 | 5/26/11:00
5 | 26 | 1900-01-11 | 22.2 | 200 | 796 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 200 | 0 | 0 | 39.791 | 146.4583 | 21.0613 | 86.148 | -75 | 3.068 | 161.915 | -359.5039 | -159.5039 | -50.5599 | 0 | -50.5599 | 71.96 | -50.5599 | 5/26/12:00
5 | 26 | 1900-01-12 | 23.3 | 192 | 828 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 192 | 0 | 0 | 39.791 | 146.5 | 21.0688 | 86.148 | -75 | 3.0635 | 176.9139 | -402.3318 | -210.3318 | -66.6715 | 0 | -66.6715 | 73.94 | -66.6715 | 5/26/13:00
5 | 26 | 1900-01-13 | 25 | 190 | 827 | 77 | 0 | 1 | 0 | 77 | 0 | 190 | 0 | 0 | 39.791 | 146.5417 | 21.0763 | 86.148 | -75 | 3.059 | 191.9127 | -389.841 | -199.841 | -63.3461 | 0 | -63.3461 | 77 | -63.3461 | 5/26/14:00
5 | 26 | 1900-01-14 | 25.6 | 181 | 807 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 181 | 0 | 0 | 39.791 | 146.5833 | 21.0838 | 86.148 | -75 | 3.0544 | 206.9116 | -330.126 | -149.126 | -47.2704 | 0 | -47.2704 | 78.08 | -47.2704 | 5/26/15:00
5 | 26 | 1900-01-15 | 25.6 | 166 | 769 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 166 | 0 | 0 | 39.791 | 146.625 | 21.0913 | 86.148 | -75 | 3.0499 | 221.9105 | -233.1701 | -67.1701 | -21.2918 | 0 | -21.2918 | 78.08 | -21.2918 | 5/26/16:00
5 | 26 | 1900-01-16 | 25.6 | 143 | 703 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 143 | 0 | 0 | 39.791 | 146.6667 | 21.0988 | 86.148 | -75 | 3.0453 | 236.9093 | -113.1873 | 29.8127 | 9.4501 | 0 | 9.4501 | 78.08 | 9.4501 | 5/26/17:00
5 | 26 | 1900-01-17 | 24.4 | 111 | 595 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 111 | 0 | 0 | 39.791 | 146.7083 | 21.1063 | 86.148 | -75 | 3.0407 | 251.9082 | 4.6722 | 115.6722 | 36.6661 | 0 | 36.6661 | 75.92 | 36.6661 | 5/26/18:00
5 | 26 | 1900-01-18 | 22.8 | 74 | 397 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 74 | 0 | 0 | 39.791 | 146.75 | 21.1137 | 86.148 | -75 | 3.0361 | 266.907 | 76.1689 | 150.1689 | 47.6009 | 0 | 47.6009 | 73.04 | 47.6009 | 5/26/19:00
5 | 26 | 1900-01-19 | 21.1 | 27 | 33 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 27 | 0 | 0 | 39.791 | 146.7917 | 21.1212 | 86.148 | -75 | 3.0315 | 281.9059 | 12.49 | 39.49 | 12.5177 | 0 | 12.5177 | 69.98 | 12.5177 | 5/26/20:00
5 | 26 | 1900-01-20 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 146.8333 | 21.1286 | 86.148 | -75 | 3.0268 | 296.9047 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/26/21:00
5 | 26 | 1900-01-21 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 146.875 | 21.136 | 86.148 | -75 | 3.0222 | 311.9035 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/26/22:00
5 | 26 | 1900-01-22 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 146.9167 | 21.1434 | 86.148 | -75 | 3.0175 | 326.9024 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/26/23:00
5 | 26 | 1900-01-23 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 146.9583 | 21.1508 | 86.148 | -75 | 3.0129 | 341.9012 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 5/26/24:00
5 | 27 | 1899-12-31 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 147 | 21.1582 | 86.148 | -75 | 3.0082 | -3.1 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 5/27/1:00
5 | 27 | 1900-01-01 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 147.0417 | 21.1656 | 86.148 | -75 | 3.0035 | 11.8989 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 5/27/2:00
5 | 27 | 1900-01-02 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 147.0833 | 21.173 | 86.148 | -75 | 2.9988 | 26.8977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/27/3:00
5 | 27 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 147.125 | 21.1803 | 86.148 | -75 | 2.994 | 41.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/27/4:00
5 | 27 | 1900-01-04 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 147.1667 | 21.1877 | 86.148 | -75 | 2.9893 | 56.8953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/27/5:00
5 | 27 | 1900-01-05 | 10 | 12 | 1 | 50 | 1 | 0 | 50 | 0 | 0 | 12 | 0 | 0 | 39.791 | 147.2083 | 21.195 | 86.148 | -75 | 2.9845 | 71.8941 | 0.45402 | 12.454 | 3.9477 | 3.9477 | 0 | 0 | 0 | 5/27/6:00
5 | 27 | 1900-01-06 | 12.8 | 80 | 112 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 80 | 0 | 0 | 39.791 | 147.25 | 21.2023 | 86.148 | -75 | 2.9798 | 86.8929 | 30.2723 | 110.2723 | 34.9544 | 0 | 34.9544 | 55.04 | 34.9544 | 5/27/7:00
5 | 27 | 1900-01-07 | 15 | 145 | 343 | 59 | 0 | 1 | 0 | 59 | 0 | 145 | 0 | 0 | 39.791 | 147.2917 | 21.2097 | 86.148 | -75 | 2.975 | 101.8918 | 28.7865 | 173.7865 | 55.0873 | 0 | 55.0873 | 59 | 55.0873 | 5/27/8:00
5 | 27 | 1900-01-08 | 16.7 | 171 | 559 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 171 | 0 | 0 | 39.791 | 147.3333 | 21.217 | 86.148 | -75 | 2.9702 | 116.8906 | -51.6301 | 119.3699 | 37.8382 | 0 | 37.8382 | 62.06 | 37.8382 | 5/27/9:00
5 | 27 | 1900-01-09 | 18.9 | 208 | 656 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 208 | 0 | 0 | 39.791 | 147.375 | 21.2243 | 86.148 | -75 | 2.9654 | 131.8894 | -161.7419 | 46.2581 | 14.663 | 0 | 14.663 | 66.02 | 14.663 | 5/27/10:00
5 | 27 | 1900-01-10 | 21.1 | 233 | 709 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 233 | 0 | 0 | 39.791 | 147.4167 | 21.2315 | 86.148 | -75 | 2.9606 | 146.8881 | -261.0212 | -28.0212 | -8.8822 | 0 | -8.8822 | 69.98 | -8.8822 | 5/27/11:00
5 | 27 | 1900-01-11 | 22.2 | 271 | 721 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 271 | 0 | 0 | 39.791 | 147.4583 | 21.2388 | 86.148 | -75 | 2.9558 | 161.8869 | -323.6307 | -52.6307 | -16.683 | 0 | -16.683 | 71.96 | -16.683 | 5/27/12:00
5 | 27 | 1900-01-12 | 22.8 | 433 | 532 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 433 | 0 | 0 | 39.791 | 147.5 | 21.2461 | 86.148 | -75 | 2.9509 | 176.8857 | -257.0551 | 175.9449 | 55.7715 | 0 | 55.7715 | 73.04 | 55.7715 | 5/27/13:00
5 | 27 | 1900-01-13 | 24.4 | 427 | 468 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 427 | 0 | 0 | 39.791 | 147.5417 | 21.2533 | 86.148 | -75 | 2.9461 | 191.8845 | -219.3904 | 207.6096 | 65.8086 | 0 | 65.8086 | 75.92 | 65.8086 | 5/27/14:00
5 | 27 | 1900-01-14 | 25 | 453 | 388 | 77 | 0 | 1 | 0 | 77 | 0 | 453 | 0 | 0 | 39.791 | 147.5833 | 21.2605 | 86.148 | -75 | 2.9412 | 206.8833 | -157.7742 | 295.2258 | 93.5814 | 0 | 93.5814 | 77 | 93.5814 | 5/27/15:00
5 | 27 | 1900-01-15 | 25.6 | 288 | 567 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 288 | 0 | 0 | 39.791 | 147.625 | 21.2678 | 86.148 | -75 | 2.9363 | 221.8821 | -170.653 | 117.347 | 37.197 | 0 | 37.197 | 78.08 | 37.197 | 5/27/16:00
5 | 27 | 1900-01-16 | 26.1 | 266 | 489 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 266 | 0 | 0 | 39.791 | 147.6667 | 21.275 | 86.148 | -75 | 2.9314 | 236.8809 | -77.7526 | 188.2474 | 59.6711 | 0 | 59.6711 | 78.98 | 59.6711 | 5/27/17:00
5 | 27 | 1900-01-17 | 25.6 | 169 | 448 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 169 | 0 | 0 | 39.791 | 147.7083 | 21.2822 | 86.148 | -75 | 2.9265 | 251.8796 | 4.3053 | 173.3053 | 54.9348 | 0 | 54.9348 | 78.08 | 54.9348 | 5/27/18:00
5 | 27 | 1900-01-18 | 23.3 | 74 | 423 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 74 | 0 | 0 | 39.791 | 147.75 | 21.2894 | 86.148 | -75 | 2.9216 | 266.8784 | 81.7993 | 155.7993 | 49.3857 | 0 | 49.3857 | 73.94 | 49.3857 | 5/27/19:00
5 | 27 | 1900-01-19 | 21.7 | 32 | 17 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 32 | 0 | 0 | 39.791 | 147.7917 | 21.2965 | 86.148 | -75 | 2.9167 | 281.8772 | 6.4564 | 38.4564 | 12.19 | 0 | 12.19 | 71.06 | 12.19 | 5/27/20:00
5 | 27 | 1900-01-20 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 147.8333 | 21.3037 | 86.148 | -75 | 2.9117 | 296.8759 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/27/21:00
5 | 27 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 147.875 | 21.3109 | 86.148 | -75 | 2.9068 | 311.8747 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/27/22:00
5 | 27 | 1900-01-22 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 147.9167 | 21.318 | 86.148 | -75 | 2.9018 | 326.8734 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 5/27/23:00
5 | 27 | 1900-01-23 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 147.9583 | 21.3252 | 86.148 | -75 | 2.8968 | 341.8722 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 5/27/24:00
5 | 28 | 1899-12-31 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 148 | 21.3323 | 86.148 | -75 | 2.8918 | -3.129 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 5/28/1:00
5 | 28 | 1900-01-01 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 148.0417 | 21.3394 | 86.148 | -75 | 2.8868 | 11.8697 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/28/2:00
5 | 28 | 1900-01-02 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 148.0833 | 21.3465 | 86.148 | -75 | 2.8818 | 26.8684 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 5/28/3:00
5 | 28 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 148.125 | 21.3536 | 86.148 | -75 | 2.8767 | 41.8672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/28/4:00
5 | 28 | 1900-01-04 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 148.1667 | 21.3607 | 86.148 | -75 | 2.8717 | 56.8659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/28/5:00
5 | 28 | 1900-01-05 | 12.2 | 19 | 15 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 19 | 0 | 0 | 39.791 | 148.2083 | 21.3677 | 86.148 | -75 | 2.8666 | 71.8647 | 6.8387 | 25.8387 | 8.1904 | 8.1904 | 0 | 0 | 0 | 5/28/6:00
5 | 28 | 1900-01-06 | 12.8 | 80 | 143 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 80 | 0 | 0 | 39.791 | 148.25 | 21.3748 | 86.148 | -75 | 2.8616 | 86.8634 | 38.9541 | 118.9541 | 37.7064 | 0 | 37.7064 | 55.04 | 37.7064 | 5/28/7:00
5 | 28 | 1900-01-07 | 16.7 | 138 | 379 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 138 | 0 | 0 | 39.791 | 148.2917 | 21.3818 | 86.148 | -75 | 2.8565 | 101.8621 | 32.6897 | 170.6897 | 54.1057 | 0 | 54.1057 | 62.06 | 54.1057 | 5/28/8:00
5 | 28 | 1900-01-08 | 20 | 236 | 413 | 68 | 0 | 1 | 0 | 68 | 0 | 236 | 0 | 0 | 39.791 | 148.3333 | 21.3889 | 86.148 | -75 | 2.8514 | 116.8608 | -37.1134 | 198.8866 | 63.0436 | 0 | 63.0436 | 68 | 63.0436 | 5/28/9:00
5 | 28 | 1900-01-09 | 22.8 | 223 | 615 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 223 | 0 | 0 | 39.791 | 148.375 | 21.3959 | 86.148 | -75 | 2.8463 | 131.8596 | -150.0208 | 72.9792 | 23.1331 | 0 | 23.1331 | 73.04 | 23.1331 | 5/28/10:00
5 | 28 | 1900-01-10 | 25 | 240 | 687 | 77 | 0 | 1 | 0 | 77 | 0 | 240 | 0 | 0 | 39.791 | 148.4167 | 21.4029 | 86.148 | -75 | 2.8411 | 146.8583 | -251.0761 | -11.0761 | -3.5109 | 0 | -3.5109 | 77 | -3.5109 | 5/28/11:00
5 | 28 | 1900-01-11 | 25.6 | 250 | 725 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 250 | 0 | 0 | 39.791 | 148.4583 | 21.4099 | 86.148 | -75 | 2.836 | 161.857 | -323.4761 | -73.4761 | -23.2906 | 0 | -23.2906 | 78.08 | -23.2906 | 5/28/12:00
5 | 28 | 1900-01-12 | 26.7 | 256 | 739 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 256 | 0 | 0 | 39.791 | 148.5 | 21.4169 | 86.148 | -75 | 2.8309 | 176.8557 | -355.131 | -99.131 | -31.4228 | 0 | -31.4228 | 80.06 | -31.4228 | 5/28/13:00
5 | 28 | 1900-01-13 | 27.8 | 253 | 731 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 253 | 0 | 0 | 39.791 | 148.5417 | 21.4239 | 86.148 | -75 | 2.8257 | 191.8544 | -340.8442 | -87.8442 | -27.8451 | 0 | -27.8451 | 82.04 | -27.8451 | 5/28/14:00
5 | 28 | 1900-01-14 | 28.3 | 283 | 669 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 283 | 0 | 0 | 39.791 | 148.5833 | 21.4308 | 86.148 | -75 | 2.8205 | 206.8531 | -270.4711 | 12.5289 | 3.9714 | 0 | 3.9714 | 82.94 | 3.9714 | 5/28/15:00
5 | 28 | 1900-01-15 | 28.9 | 276 | 595 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 276 | 0 | 0 | 39.791 | 148.625 | 21.4378 | 86.148 | -75 | 2.8153 | 221.8518 | -177.81 | 98.19 | 31.1245 | 0 | 31.1245 | 84.02 | 31.1245 | 5/28/16:00
5 | 28 | 1900-01-16 | 29.4 | 224 | 549 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 224 | 0 | 0 | 39.791 | 148.6667 | 21.4447 | 86.148 | -75 | 2.8101 | 236.8505 | -86.2485 | 137.7515 | 43.6648 | 0 | 43.6648 | 84.92 | 43.6648 | 5/28/17:00
5 | 28 | 1900-01-17 | 28.9 | 166 | 427 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 166 | 0 | 0 | 39.791 | 148.7083 | 21.4517 | 86.148 | -75 | 2.8049 | 251.8492 | 4.8124 | 170.8124 | 54.1445 | 0 | 54.1445 | 84.02 | 54.1445 | 5/28/18:00
5 | 28 | 1900-01-18 | 26.1 | 123 | 181 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 123 | 0 | 0 | 39.791 | 148.75 | 21.4586 | 86.148 | -75 | 2.7997 | 266.8479 | 35.2596 | 158.2596 | 50.1655 | 0 | 50.1655 | 78.98 | 50.1655 | 5/28/19:00
5 | 28 | 1900-01-19 | 23.3 | 20 | 1 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 20 | 0 | 0 | 39.791 | 148.7917 | 21.4655 | 86.148 | -75 | 2.7945 | 281.8466 | 0.381 | 20.381 | 6.4604 | 0 | 6.4604 | 73.94 | 6.4604 | 5/28/20:00
5 | 28 | 1900-01-20 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 148.8333 | 21.4724 | 86.148 | -75 | 2.7892 | 296.8453 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 5/28/21:00
5 | 28 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 148.875 | 21.4793 | 86.148 | -75 | 2.784 | 311.844 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 5/28/22:00
5 | 28 | 1900-01-22 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 148.9167 | 21.4862 | 86.148 | -75 | 2.7787 | 326.8427 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 5/28/23:00
5 | 28 | 1900-01-23 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 148.9583 | 21.493 | 86.148 | -75 | 2.7734 | 341.8413 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/28/24:00
5 | 29 | 1899-12-31 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 149 | 21.4999 | 86.148 | -75 | 2.7681 | -3.16 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 5/29/1:00
5 | 29 | 1900-01-01 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 149.0417 | 21.5067 | 86.148 | -75 | 2.7628 | 11.8387 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 5/29/2:00
5 | 29 | 1900-01-02 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 149.0833 | 21.5136 | 86.148 | -75 | 2.7575 | 26.8374 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 5/29/3:00
5 | 29 | 1900-01-03 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 149.125 | 21.5204 | 86.148 | -75 | 2.7521 | 41.836 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 5/29/4:00
5 | 29 | 1900-01-04 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 149.1667 | 21.5272 | 86.148 | -75 | 2.7468 | 56.8347 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 5/29/5:00
5 | 29 | 1900-01-05 | 16.7 | 15 | 2 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 15 | 0 | 0 | 39.791 | 149.2083 | 21.534 | 86.148 | -75 | 2.7414 | 71.8334 | 0.91551 | 15.9155 | 5.0449 | 0 | 5.0449 | 62.06 | 5.0449 | 5/29/6:00
5 | 29 | 1900-01-06 | 17.8 | 68 | 149 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 68 | 0 | 0 | 39.791 | 149.25 | 21.5408 | 86.148 | -75 | 2.736 | 86.832 | 40.8973 | 108.8973 | 34.5185 | 0 | 34.5185 | 64.04 | 34.5185 | 5/29/7:00
5 | 29 | 1900-01-07 | 21.1 | 157 | 254 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 157 | 0 | 0 | 39.791 | 149.2917 | 21.5475 | 86.148 | -75 | 2.7307 | 101.8307 | 22.4857 | 179.4857 | 56.8938 | 0 | 56.8938 | 69.98 | 56.8938 | 5/29/8:00
5 | 29 | 1900-01-08 | 23.3 | 255 | 243 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 255 | 0 | 0 | 39.791 | 149.3333 | 21.5543 | 86.148 | -75 | 2.7253 | 116.8293 | -21.2443 | 233.7557 | 74.0965 | 0 | 74.0965 | 73.94 | 74.0965 | 5/29/9:00
5 | 29 | 1900-01-09 | 25.6 | 194 | 348 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 194 | 0 | 0 | 39.791 | 149.375 | 21.5611 | 86.148 | -75 | 2.7199 | 131.828 | -84.0018 | 109.9982 | 34.8675 | 0 | 34.8675 | 78.08 | 34.8675 | 5/29/10:00
5 | 29 | 1900-01-10 | 27.8 | 323 | 388 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 323 | 0 | 0 | 39.791 | 149.4167 | 21.5678 | 86.148 | -75 | 2.7144 | 146.8266 | -140.7893 | 182.2107 | 57.7576 | 0 | 57.7576 | 82.04 | 57.7576 | 5/29/11:00
5 | 29 | 1900-01-11 | 28.9 | 287 | 630 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 287 | 0 | 0 | 39.791 | 149.4583 | 21.5745 | 86.148 | -75 | 2.709 | 161.8253 | -279.4496 | 7.5504 | 2.3934 | 0 | 2.3934 | 84.02 | 2.3934 | 5/29/12:00
5 | 29 | 1900-01-12 | 29.4 | 367 | 507 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 367 | 0 | 0 | 39.791 | 149.5 | 21.5812 | 86.148 | -75 | 2.7036 | 176.8239 | -242.3559 | 124.6441 | 39.51 | 0 | 39.51 | 84.92 | 39.51 | 5/29/13:00
5 | 29 | 1900-01-13 | 30 | 346 | 414 | 86 | 0 | 1 | 0 | 86 | 0 | 346 | 0 | 0 | 39.791 | 149.5417 | 21.588 | 86.148 | -75 | 2.6981 | 191.8225 | -192.0372 | 153.9628 | 48.8035 | 0 | 48.8035 | 86 | 48.8035 | 5/29/14:00
5 | 29 | 1900-01-14 | 30.6 | 297 | 513 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 297 | 0 | 0 | 39.791 | 149.5833 | 21.5947 | 86.148 | -75 | 2.6926 | 206.8212 | -206.2519 | 90.7481 | 28.7656 | 0 | 28.7656 | 87.08 | 28.7656 | 5/29/15:00
5 | 29 | 1900-01-15 | 30 | 330 | 462 | 86 | 0 | 1 | 0 | 86 | 0 | 330 | 0 | 0 | 39.791 | 149.625 | 21.6013 | 86.148 | -75 | 2.6871 | 221.8198 | -137.1253 | 192.8747 | 61.1379 | 0 | 61.1379 | 86 | 61.1379 | 5/29/16:00
5 | 29 | 1900-01-16 | 29.4 | 227 | 465 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 227 | 0 | 0 | 39.791 | 149.6667 | 21.608 | 86.148 | -75 | 2.6817 | 236.8184 | -72.2147 | 154.7853 | 49.0642 | 0 | 49.0642 | 84.92 | 49.0642 | 5/29/17:00
5 | 29 | 1900-01-17 | 28.9 | 185 | 193 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 185 | 0 | 0 | 39.791 | 149.7083 | 21.6147 | 86.148 | -75 | 2.6761 | 251.817 | 2.4767 | 187.4767 | 59.4268 | 0 | 59.4268 | 84.02 | 59.4268 | 5/29/18:00
5 | 29 | 1900-01-18 | 27.8 | 77 | 66 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 77 | 0 | 0 | 39.791 | 149.75 | 21.6213 | 86.148 | -75 | 2.6706 | 266.8157 | 12.9451 | 89.9451 | 28.511 | 0 | 28.511 | 82.04 | 28.511 | 5/29/19:00
5 | 29 | 1900-01-19 | 26.1 | 21 | 10 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 21 | 0 | 0 | 39.791 | 149.7917 | 21.628 | 86.148 | -75 | 2.6651 | 281.8143 | 3.8213 | 24.8213 | 7.8679 | 0 | 7.8679 | 78.98 | 7.8679 | 5/29/20:00
5 | 29 | 1900-01-20 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 149.8333 | 21.6346 | 86.148 | -75 | 2.6596 | 296.8129 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 5/29/21:00
5 | 29 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 149.875 | 21.6412 | 86.148 | -75 | 2.654 | 311.8115 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 5/29/22:00
5 | 29 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 149.9167 | 21.6478 | 86.148 | -75 | 2.6484 | 326.8101 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 5/29/23:00
5 | 29 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 149.9583 | 21.6544 | 86.148 | -75 | 2.6429 | 341.8087 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 5/29/24:00
5 | 30 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 150 | 21.661 | 86.148 | -75 | 2.6373 | -3.1927 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 5/30/1:00
5 | 30 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 150.0417 | 21.6676 | 86.148 | -75 | 2.6317 | 11.8059 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 5/30/2:00
5 | 30 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 150.0833 | 21.6741 | 86.148 | -75 | 2.626 | 26.8045 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/30/3:00
5 | 30 | 1900-01-03 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 150.125 | 21.6807 | 86.148 | -75 | 2.6204 | 41.8031 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/30/4:00
5 | 30 | 1900-01-04 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 150.1667 | 21.6872 | 86.148 | -75 | 2.6148 | 56.8017 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 5/30/5:00
5 | 30 | 1900-01-05 | 19.4 | 8 | 3 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 8 | 0 | 0 | 39.791 | 150.2083 | 21.6937 | 86.148 | -75 | 2.6091 | 71.8003 | 1.3787 | 9.3787 | 2.9729 | 0 | 2.9729 | 66.92 | 2.9729 | 5/30/6:00
5 | 30 | 1900-01-06 | 20 | 69 | 166 | 68 | 0 | 1 | 0 | 68 | 0 | 69 | 0 | 0 | 39.791 | 150.25 | 21.7002 | 86.148 | -75 | 2.6035 | 86.7989 | 45.8995 | 114.8995 | 36.4211 | 0 | 36.4211 | 68 | 36.4211 | 5/30/7:00
5 | 30 | 1900-01-07 | 21.1 | 178 | 32 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 178 | 0 | 0 | 39.791 | 150.2917 | 21.7067 | 86.148 | -75 | 2.5978 | 101.7974 | 2.9039 | 180.9039 | 57.3434 | 0 | 57.3434 | 69.98 | 57.3434 | 5/30/8:00
5 | 30 | 1900-01-08 | 21.7 | 253 | 97 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 253 | 0 | 0 | 39.791 | 150.3333 | 21.7132 | 86.148 | -75 | 2.5921 | 116.796 | -8.2499 | 244.7501 | 77.5815 | 0 | 77.5815 | 71.06 | 77.5815 | 5/30/9:00
5 | 30 | 1900-01-09 | 23.3 | 297 | 486 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 297 | 0 | 0 | 39.791 | 150.375 | 21.7197 | 86.148 | -75 | 2.5864 | 131.7946 | -116.1075 | 180.8925 | 57.3398 | 0 | 57.3398 | 73.94 | 57.3398 | 5/30/10:00
5 | 30 | 1900-01-10 | 25.6 | 450 | 288 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 450 | 0 | 0 | 39.791 | 150.4167 | 21.7262 | 86.148 | -75 | 2.5807 | 146.7932 | -103.7753 | 346.2247 | 109.7472 | 0 | 109.7472 | 78.08 | 109.7472 | 5/30/11:00
5 | 30 | 1900-01-11 | 26.7 | 423 | 81 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 423 | 0 | 0 | 39.791 | 150.4583 | 21.7326 | 86.148 | -75 | 2.575 | 161.7917 | -35.7255 | 387.2745 | 122.7592 | 0 | 122.7592 | 80.06 | 122.7592 | 5/30/12:00
5 | 30 | 1900-01-12 | 27.2 | 328 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 328 | 0 | 0 | 39.791 | 150.5 | 21.7391 | 86.148 | -75 | 2.5693 | 176.7903 | 0 | 328 | 103.9703 | 0 | 103.9703 | 80.96 | 103.9703 | 5/30/13:00
5 | 30 | 1900-01-13 | 26.7 | 486 | 20 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 486 | 0 | 0 | 39.791 | 150.5417 | 21.7455 | 86.148 | -75 | 2.5635 | 191.7889 | -9.2309 | 476.7691 | 151.1275 | 0 | 151.1275 | 80.06 | 151.1275 | 5/30/14:00
5 | 30 | 1900-01-14 | 26.7 | 434 | 216 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 434 | 0 | 0 | 39.791 | 150.5833 | 21.7519 | 86.148 | -75 | 2.5578 | 206.7874 | -86.381 | 347.619 | 110.1891 | 0 | 110.1891 | 80.06 | 110.1891 | 5/30/15:00
5 | 30 | 1900-01-15 | 27.8 | 326 | 398 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 326 | 0 | 0 | 39.791 | 150.625 | 21.7583 | 86.148 | -75 | 2.552 | 221.786 | -117.3619 | 208.6381 | 66.1346 | 0 | 66.1346 | 82.04 | 66.1346 | 5/30/16:00
5 | 30 | 1900-01-16 | 28.3 | 246 | 349 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 246 | 0 | 0 | 39.791 | 150.6667 | 21.7647 | 86.148 | -75 | 2.5462 | 236.7846 | -53.6069 | 192.3931 | 60.9852 | 0 | 60.9852 | 82.94 | 60.9852 | 5/30/17:00
5 | 30 | 1900-01-17 | 27.8 | 145 | 463 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 145 | 0 | 0 | 39.791 | 150.7083 | 21.7711 | 86.148 | -75 | 2.5404 | 251.7831 | 6.6194 | 151.6194 | 48.0607 | 0 | 48.0607 | 82.04 | 48.0607 | 5/30/18:00
5 | 30 | 1900-01-18 | 27.2 | 91 | 272 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 91 | 0 | 0 | 39.791 | 150.75 | 21.7775 | 86.148 | -75 | 2.5346 | 266.7817 | 53.687 | 144.687 | 45.8633 | 0 | 45.8633 | 80.96 | 45.8633 | 5/30/19:00
5 | 30 | 1900-01-19 | 25.6 | 25 | 1 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 25 | 0 | 0 | 39.791 | 150.7917 | 21.7839 | 86.148 | -75 | 2.5288 | 281.7802 | 0.38317 | 25.3832 | 8.046 | 0 | 8.046 | 78.08 | 8.046 | 5/30/20:00
5 | 30 | 1900-01-20 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 150.8333 | 21.7902 | 86.148 | -75 | 2.523 | 296.7787 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 5/30/21:00
5 | 30 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 150.875 | 21.7966 | 86.148 | -75 | 2.5171 | 311.7773 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 5/30/22:00
5 | 30 | 1900-01-22 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 150.9167 | 21.8029 | 86.148 | -75 | 2.5113 | 326.7758 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 5/30/23:00
5 | 30 | 1900-01-23 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 150.9583 | 21.8092 | 86.148 | -75 | 2.5054 | 341.7744 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 5/30/24:00
5 | 31 | 1899-12-31 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 151 | 21.8155 | 86.148 | -75 | 2.4996 | -3.2271 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 5/31/1:00
5 | 31 | 1900-01-01 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 151.0417 | 21.8218 | 86.148 | -75 | 2.4937 | 11.7714 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 5/31/2:00
5 | 31 | 1900-01-02 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 151.0833 | 21.8281 | 86.148 | -75 | 2.4878 | 26.7699 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 5/31/3:00
5 | 31 | 1900-01-03 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 151.125 | 21.8344 | 86.148 | -75 | 2.4819 | 41.7685 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 5/31/4:00
5 | 31 | 1900-01-04 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 151.1667 | 21.8406 | 86.148 | -75 | 2.476 | 56.767 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 5/31/5:00
5 | 31 | 1900-01-05 | 20 | 16 | 22 | 68 | 0 | 1 | 0 | 68 | 0 | 16 | 0 | 0 | 39.791 | 151.2083 | 21.8469 | 86.148 | -75 | 2.47 | 71.7655 | 10.1491 | 26.1491 | 8.2888 | 0 | 8.2888 | 68 | 8.2888 | 5/31/6:00
5 | 31 | 1900-01-06 | 21.1 | 57 | 303 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 57 | 0 | 0 | 39.791 | 151.25 | 21.8531 | 86.148 | -75 | 2.4641 | 86.764 | 84.3792 | 141.3792 | 44.8147 | 0 | 44.8147 | 69.98 | 44.8147 | 5/31/7:00
5 | 31 | 1900-01-07 | 21.7 | 96 | 514 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 96 | 0 | 0 | 39.791 | 151.2917 | 21.8593 | 86.148 | -75 | 2.4581 | 101.7625 | 47.7553 | 143.7553 | 45.5679 | 0 | 45.5679 | 71.06 | 45.5679 | 5/31/8:00
5 | 31 | 1900-01-08 | 23.3 | 192 | 493 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 192 | 0 | 0 | 39.791 | 151.3333 | 21.8656 | 86.148 | -75 | 2.4522 | 116.761 | -40.7908 | 151.2092 | 47.9307 | 0 | 47.9307 | 73.94 | 47.9307 | 5/31/9:00
5 | 31 | 1900-01-09 | 24.4 | 156 | 735 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 156 | 0 | 0 | 39.791 | 151.375 | 21.8718 | 86.148 | -75 | 2.4462 | 131.7596 | -173.8256 | -17.8256 | -5.6504 | 0 | -5.6504 | 75.92 | -5.6504 | 5/31/10:00
5 | 31 | 1900-01-10 | 25.6 | 166 | 791 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 166 | 0 | 0 | 39.791 | 151.4167 | 21.8779 | 86.148 | -75 | 2.4402 | 146.7581 | -283.087 | -117.087 | -37.1145 | 0 | -37.1145 | 78.08 | -37.1145 | 5/31/11:00
5 | 31 | 1900-01-11 | 26.1 | 239 | 704 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 239 | 0 | 0 | 39.791 | 151.4583 | 21.8841 | 86.148 | -75 | 2.4342 | 161.7566 | -308.796 | -69.796 | -22.1241 | 0 | -22.1241 | 78.98 | -22.1241 | 5/31/12:00
5 | 31 | 1900-01-12 | 26.1 | 348 | 344 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 348 | 0 | 0 | 39.791 | 151.5 | 21.8903 | 86.148 | -75 | 2.4282 | 176.7551 | -162.792 | 185.208 | 58.7077 | 0 | 58.7077 | 78.98 | 58.7077 | 5/31/13:00
5 | 31 | 1900-01-13 | 26.7 | 332 | 479 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 332 | 0 | 0 | 39.791 | 151.5417 | 21.8965 | 86.148 | -75 | 2.4222 | 191.7536 | -220.0202 | 111.9798 | 35.4956 | 0 | 35.4956 | 80.06 | 35.4956 | 5/31/14:00
5 | 31 | 1900-01-14 | 27.2 | 217 | 733 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 217 | 0 | 0 | 39.791 | 151.5833 | 21.9026 | 86.148 | -75 | 2.4162 | 206.752 | -291.6442 | -74.6442 | -23.6609 | 0 | -23.6609 | 80.96 | -23.6609 | 5/31/15:00
5 | 31 | 1900-01-15 | 27.8 | 188 | 704 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 188 | 0 | 0 | 39.791 | 151.625 | 21.9087 | 86.148 | -75 | 2.4101 | 221.7505 | -206.3104 | -18.3104 | -5.8041 | 0 | -5.8041 | 82.04 | -5.8041 | 5/31/16:00
5 | 31 | 1900-01-16 | 28.3 | 172 | 633 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 172 | 0 | 0 | 39.791 | 151.6667 | 21.9149 | 86.148 | -75 | 2.4041 | 236.749 | -96.2189 | 75.7811 | 24.0213 | 0 | 24.0213 | 82.94 | 24.0213 | 5/31/17:00
5 | 31 | 1900-01-17 | 27.8 | 152 | 508 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 152 | 0 | 0 | 39.791 | 151.7083 | 21.921 | 86.148 | -75 | 2.398 | 251.7475 | 7.957 | 159.957 | 50.7036 | 0 | 50.7036 | 82.04 | 50.7036 | 5/31/18:00
5 | 31 | 1900-01-18 | 26.7 | 144 | 87 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 144 | 0 | 0 | 39.791 | 151.75 | 21.9271 | 86.148 | -75 | 2.3919 | 266.746 | 17.2719 | 161.2719 | 51.1204 | 0 | 51.1204 | 80.06 | 51.1204 | 5/31/19:00
5 | 31 | 1900-01-19 | 25 | 33 | 11 | 77 | 0 | 1 | 0 | 77 | 0 | 33 | 0 | 0 | 39.791 | 151.7917 | 21.9332 | 86.148 | -75 | 2.3859 | 281.7445 | 4.2255 | 37.2255 | 11.7998 | 0 | 11.7998 | 77 | 11.7998 | 5/31/20:00
5 | 31 | 1900-01-20 | 22.2 | 2 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 2 | 0 | 0 | 39.791 | 151.8333 | 21.9392 | 86.148 | -75 | 2.3798 | 296.7429 | 0 | 2 | 0.63397 | 0 | 0.63397 | 71.96 | 0.63397 | 5/31/21:00
5 | 31 | 1900-01-21 | 21.6 | 0 | 0 | 70.88 | 0 | 1 | 0 | 70.88 | 0 | 0 | 0 | 0 | 39.791 | 151.875 | 21.9453 | 86.148 | -75 | 2.3737 | 311.7414 | 0 | 0 | 0 | 0 | 0 | 70.88 | 0 | 5/31/22:00
5 | 31 | 1900-01-22 | 20.9 | 0 | 0 | 69.62 | 0 | 1 | 0 | 69.62 | 0 | 0 | 0 | 0 | 39.791 | 151.9167 | 21.9513 | 86.148 | -75 | 2.3675 | 326.7399 | 0 | 0 | 0 | 0 | 0 | 69.62 | 0 | 5/31/23:00
5 | 31 | 1900-01-23 | 20.3 | 0 | 0 | 68.54 | 0 | 1 | 0 | 68.54 | 0 | 0 | 0 | 0 | 39.791 | 151.9583 | 21.9574 | 86.148 | -75 | 2.3614 | 341.7384 | 0 | 0 | 0 | 0 | 0 | 68.54 | 0 | 5/31/24:00
6 | 1 | 1899-12-31 | 19.7 | 0 | 0 | 67.46 | 0 | 1 | 0 | 67.46 | 0 | 0 | 0 | 0 | 39.791 | 152 | 21.9634 | 86.148 | -75 | 2.3553 | -3.2632 | 0 | 0 | 0 | 0 | 0 | 67.46 | 0 | 6/1/1:00
6 | 1 | 1900-01-01 | 19.1 | 0 | 0 | 66.38 | 0 | 1 | 0 | 66.38 | 0 | 0 | 0 | 0 | 39.791 | 152.0417 | 21.9694 | 86.148 | -75 | 2.3491 | 11.7353 | 0 | 0 | 0 | 0 | 0 | 66.38 | 0 | 6/1/2:00
6 | 1 | 1900-01-02 | 18.4 | 0 | 0 | 65.12 | 0 | 1 | 0 | 65.12 | 0 | 0 | 0 | 0 | 39.791 | 152.0833 | 21.9754 | 86.148 | -75 | 2.343 | 26.7337 | 0 | 0 | 0 | 0 | 0 | 65.12 | 0 | 6/1/3:00
6 | 1 | 1900-01-03 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 152.125 | 21.9814 | 86.148 | -75 | 2.3368 | 41.7322 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 6/1/4:00
6 | 1 | 1900-01-04 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 152.1667 | 21.9874 | 86.148 | -75 | 2.3306 | 56.7306 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 6/1/5:00
6 | 1 | 1900-01-05 | 18.3 | 14 | 40 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 14 | 0 | 0 | 39.791 | 152.2083 | 21.9934 | 86.148 | -75 | 2.3244 | 71.7291 | 18.5216 | 32.5216 | 10.3088 | 0 | 10.3088 | 64.94 | 10.3088 | 6/1/6:00
6 | 1 | 1900-01-06 | 20 | 48 | 397 | 68 | 0 | 1 | 0 | 68 | 0 | 48 | 0 | 0 | 39.791 | 152.25 | 21.9993 | 86.148 | -75 | 2.3182 | 86.7275 | 111.3212 | 159.3212 | 50.502 | 0 | 50.502 | 68 | 50.502 | 6/1/7:00
6 | 1 | 1900-01-07 | 21.7 | 75 | 610 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 75 | 0 | 0 | 39.791 | 152.2917 | 22.0053 | 86.148 | -75 | 2.312 | 101.726 | 57.9594 | 132.9594 | 42.1458 | 0 | 42.1458 | 71.06 | 42.1458 | 6/1/8:00
6 | 1 | 1900-01-08 | 23.9 | 99 | 726 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 99 | 0 | 0 | 39.791 | 152.3333 | 22.0112 | 86.148 | -75 | 2.3057 | 116.7244 | -58.4398 | 40.5602 | 12.8569 | 0 | 12.8569 | 75.02 | 12.8569 | 6/1/9:00
6 | 1 | 1900-01-09 | 26.1 | 118 | 802 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 118 | 0 | 0 | 39.791 | 152.375 | 22.0171 | 86.148 | -75 | 2.2995 | 131.7229 | -187.8008 | -69.8008 | -22.1256 | 0 | -22.1256 | 78.98 | -22.1256 | 6/1/10:00
6 | 1 | 1900-01-10 | 27.8 | 165 | 758 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 165 | 0 | 0 | 39.791 | 152.4167 | 22.0231 | 86.148 | -75 | 2.2933 | 146.7213 | -269.4862 | -104.4862 | -33.1203 | 0 | -33.1203 | 82.04 | -33.1203 | 6/1/11:00
6 | 1 | 1900-01-11 | 28.3 | 248 | 679 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 248 | 0 | 0 | 39.791 | 152.4583 | 22.029 | 86.148 | -75 | 2.287 | 161.7197 | -296.2457 | -48.2457 | -15.2931 | 0 | -15.2931 | 82.94 | -15.2931 | 6/1/12:00
6 | 1 | 1900-01-12 | 28.9 | 267 | 669 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 267 | 0 | 0 | 39.791 | 152.5 | 22.0349 | 86.148 | -75 | 2.2807 | 176.7182 | -315.089 | -48.089 | -15.2434 | 0 | -15.2434 | 84.02 | -15.2434 | 6/1/13:00
6 | 1 | 1900-01-13 | 30 | 370 | 526 | 86 | 0 | 1 | 0 | 86 | 0 | 370 | 0 | 0 | 39.791 | 152.5417 | 22.0407 | 86.148 | -75 | 2.2744 | 191.7166 | -240.4991 | 129.5009 | 41.0495 | 0 | 41.0495 | 86 | 41.0495 | 6/1/14:00
6 | 1 | 1900-01-14 | 30 | 251 | 599 | 86 | 0 | 1 | 0 | 86 | 0 | 251 | 0 | 0 | 39.791 | 152.5833 | 22.0466 | 86.148 | -75 | 2.2682 | 206.715 | -237.1726 | 13.8274 | 4.383 | 0 | 4.383 | 86 | 4.383 | 6/1/15:00
6 | 1 | 1900-01-15 | 30 | 229 | 581 | 86 | 0 | 1 | 0 | 86 | 0 | 229 | 0 | 0 | 39.791 | 152.625 | 22.0524 | 86.148 | -75 | 2.2618 | 221.7135 | -169.2653 | 59.7347 | 18.9349 | 0 | 18.9349 | 86 | 18.9349 | 6/1/16:00
6 | 1 | 1900-01-16 | 30 | 160 | 748 | 86 | 0 | 1 | 0 | 86 | 0 | 160 | 0 | 0 | 39.791 | 152.6667 | 22.0583 | 86.148 | -75 | 2.2555 | 236.7119 | -112.5815 | 47.4185 | 15.0308 | 0 | 15.0308 | 86 | 15.0308 | 6/1/17:00
6 | 1 | 1900-01-17 | 29.4 | 148 | 463 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 148 | 0 | 0 | 39.791 | 152.7083 | 22.0641 | 86.148 | -75 | 2.2492 | 251.7103 | 7.8396 | 155.8396 | 49.3984 | 0 | 49.3984 | 84.92 | 49.3984 | 6/1/18:00
6 | 1 | 1900-01-18 | 27.8 | 65 | 492 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 65 | 0 | 0 | 39.791 | 152.75 | 22.0699 | 86.148 | -75 | 2.2429 | 266.7087 | 98.1964 | 163.1964 | 51.7304 | 0 | 51.7304 | 82.04 | 51.7304 | 6/1/19:00
6 | 1 | 1900-01-19 | 25.6 | 35 | 65 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 35 | 0 | 0 | 39.791 | 152.7917 | 22.0757 | 86.148 | -75 | 2.2365 | 281.7071 | 25.0257 | 60.0257 | 19.0271 | 0 | 19.0271 | 78.08 | 19.0271 | 6/1/20:00
6 | 1 | 1900-01-20 | 24.4 | 1 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 1 | 0 | 0 | 39.791 | 152.8333 | 22.0815 | 86.148 | -75 | 2.2302 | 296.7055 | 0 | 1 | 0.31698 | 0 | 0.31698 | 75.92 | 0.31698 | 6/1/21:00
6 | 1 | 1900-01-21 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 152.875 | 22.0873 | 86.148 | -75 | 2.2238 | 311.704 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/1/22:00
6 | 1 | 1900-01-22 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 152.9167 | 22.0931 | 86.148 | -75 | 2.2174 | 326.7024 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/1/23:00
6 | 1 | 1900-01-23 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 152.9583 | 22.0989 | 86.148 | -75 | 2.211 | 341.7008 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 6/1/24:00
6 | 2 | 1899-12-31 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 153 | 22.1046 | 86.148 | -75 | 2.2046 | -3.3008 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 6/2/1:00
6 | 2 | 1900-01-01 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 153.0417 | 22.1103 | 86.148 | -75 | 2.1982 | 11.6976 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 6/2/2:00
6 | 2 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 153.0833 | 22.1161 | 86.148 | -75 | 2.1918 | 26.696 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 6/2/3:00
6 | 2 | 1900-01-03 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 153.125 | 22.1218 | 86.148 | -75 | 2.1854 | 41.6943 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/2/4:00
6 | 2 | 1900-01-04 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 153.1667 | 22.1275 | 86.148 | -75 | 2.1789 | 56.6927 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 6/2/5:00
6 | 2 | 1900-01-05 | 13.3 | 13 | 1 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 13 | 0 | 0 | 39.791 | 153.2083 | 22.1332 | 86.148 | -75 | 2.1725 | 71.6911 | 0.46472 | 13.4647 | 4.2681 | 0 | 4.2681 | 55.94 | 4.2681 | 6/2/6:00
6 | 2 | 1900-01-06 | 12.2 | 65 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 65 | 0 | 0 | 39.791 | 153.25 | 22.1389 | 86.148 | -75 | 2.166 | 86.6895 | 0 | 65 | 20.6039 | 20.6039 | 0 | 0 | 0 | 6/2/7:00
6 | 2 | 1900-01-07 | 12.8 | 144 | 334 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 144 | 0 | 0 | 39.791 | 153.2917 | 22.1445 | 86.148 | -75 | 2.1596 | 101.6879 | 32.4189 | 176.4189 | 55.9217 | 0 | 55.9217 | 55.04 | 55.9217 | 6/2/8:00
6 | 2 | 1900-01-08 | 13.3 | 128 | 627 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 128 | 0 | 0 | 39.791 | 153.3333 | 22.1502 | 86.148 | -75 | 2.1531 | 116.6863 | -49.1059 | 78.8941 | 25.0081 | 0 | 25.0081 | 55.94 | 25.0081 | 6/2/9:00
6 | 2 | 1900-01-09 | 15 | 153 | 758 | 59 | 0 | 1 | 0 | 59 | 0 | 153 | 0 | 0 | 39.791 | 153.375 | 22.1558 | 86.148 | -75 | 2.1466 | 131.6846 | -175.7881 | -22.7881 | -7.2234 | 0 | -7.2234 | 59 | -7.2234 | 6/2/10:00
6 | 2 | 1900-01-10 | 16.1 | 171 | 797 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 171 | 0 | 0 | 39.791 | 153.4167 | 22.1614 | 86.148 | -75 | 2.1401 | 146.683 | -281.5368 | -110.5368 | -35.0382 | 0 | -35.0382 | 60.98 | -35.0382 | 6/2/11:00
6 | 2 | 1900-01-11 | 17.2 | 181 | 821 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 181 | 0 | 0 | 39.791 | 153.4583 | 22.1671 | 86.148 | -75 | 2.1336 | 161.6814 | -356.3605 | -175.3605 | -55.5862 | 0 | -55.5862 | 62.96 | -55.5862 | 6/2/12:00
6 | 2 | 1900-01-12 | 18.3 | 186 | 835 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 186 | 0 | 0 | 39.791 | 153.5 | 22.1727 | 86.148 | -75 | 2.127 | 176.6798 | -391.4788 | -205.4788 | -65.1332 | 0 | -65.1332 | 64.94 | -65.1332 | 6/2/13:00
6 | 2 | 1900-01-13 | 20 | 184 | 827 | 68 | 0 | 1 | 0 | 68 | 0 | 184 | 0 | 0 | 39.791 | 153.5417 | 22.1783 | 86.148 | -75 | 2.1205 | 191.6781 | -376.464 | -192.464 | -61.0077 | 0 | -61.0077 | 68 | -61.0077 | 6/2/14:00
6 | 2 | 1900-01-14 | 20 | 176 | 811 | 68 | 0 | 1 | 0 | 68 | 0 | 176 | 0 | 0 | 39.791 | 153.5833 | 22.1839 | 86.148 | -75 | 2.114 | 206.6765 | -319.6339 | -143.6339 | -45.5295 | 0 | -45.5295 | 68 | -45.5295 | 6/2/15:00
6 | 2 | 1900-01-15 | 20.6 | 162 | 775 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 162 | 0 | 0 | 39.791 | 153.625 | 22.1894 | 86.148 | -75 | 2.1074 | 221.6749 | -224.5327 | -62.5327 | -19.8218 | 0 | -19.8218 | 69.08 | -19.8218 | 6/2/16:00
6 | 2 | 1900-01-16 | 21.1 | 140 | 719 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 140 | 0 | 0 | 39.791 | 153.6667 | 22.195 | 86.148 | -75 | 2.1008 | 236.6732 | -107.2158 | 32.7842 | 10.392 | 0 | 10.392 | 69.98 | 10.392 | 6/2/17:00
6 | 2 | 1900-01-17 | 20.6 | 110 | 615 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 110 | 0 | 0 | 39.791 | 153.7083 | 22.2005 | 86.148 | -75 | 2.0943 | 251.6716 | 11.1336 | 121.1336 | 38.3972 | 0 | 38.3972 | 69.08 | 38.3972 | 6/2/18:00
6 | 2 | 1900-01-18 | 19.4 | 74 | 428 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 74 | 0 | 0 | 39.791 | 153.75 | 22.2061 | 86.148 | -75 | 2.0877 | 266.6699 | 85.8368 | 159.8368 | 50.6655 | 0 | 50.6655 | 66.92 | 50.6655 | 6/2/19:00
6 | 2 | 1900-01-19 | 17.8 | 32 | 103 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 32 | 0 | 0 | 39.791 | 153.7917 | 22.2116 | 86.148 | -75 | 2.0811 | 281.6683 | 39.7378 | 71.7378 | 22.7396 | 0 | 22.7396 | 64.04 | 22.7396 | 6/2/20:00
6 | 2 | 1900-01-20 | 16.7 | 1 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 1 | 0 | 0 | 39.791 | 153.8333 | 22.2171 | 86.148 | -75 | 2.0745 | 296.6666 | 0 | 1 | 0.31698 | 0 | 0.31698 | 62.06 | 0.31698 | 6/2/21:00
6 | 2 | 1900-01-21 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 153.875 | 22.2226 | 86.148 | -75 | 2.0679 | 311.665 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/2/22:00
6 | 2 | 1900-01-22 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 153.9167 | 22.2281 | 86.148 | -75 | 2.0612 | 326.6633 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 6/2/23:00
6 | 2 | 1900-01-23 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 153.9583 | 22.2336 | 86.148 | -75 | 2.0546 | 341.6617 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 6/2/24:00
6 | 3 | 1899-12-31 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 154 | 22.239 | 86.148 | -75 | 2.048 | -3.34 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 6/3/1:00
6 | 3 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 154.0417 | 22.2445 | 86.148 | -75 | 2.0413 | 11.6583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/3/2:00
6 | 3 | 1900-01-02 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 154.0833 | 22.2499 | 86.148 | -75 | 2.0346 | 26.6567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/3/3:00
6 | 3 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 154.125 | 22.2554 | 86.148 | -75 | 2.028 | 41.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/3/4:00
6 | 3 | 1900-01-04 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 154.1667 | 22.2608 | 86.148 | -75 | 2.0213 | 56.6533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/3/5:00
6 | 3 | 1900-01-05 | 10 | 16 | 38 | 50 | 1 | 0 | 50 | 0 | 0 | 16 | 0 | 0 | 39.791 | 154.2083 | 22.2662 | 86.148 | -75 | 2.0146 | 71.6516 | 17.7211 | 33.7211 | 10.689 | 10.689 | 0 | 0 | 0 | 6/3/6:00
6 | 3 | 1900-01-06 | 11.7 | 53 | 373 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 53 | 0 | 0 | 39.791 | 154.25 | 22.2716 | 86.148 | -75 | 2.0079 | 86.65 | 105.9714 | 158.9714 | 50.3911 | 50.3911 | 0 | 0 | 0 | 6/3/7:00
6 | 3 | 1900-01-07 | 13.9 | 83 | 608 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 83 | 0 | 0 | 39.791 | 154.2917 | 22.277 | 86.148 | -75 | 2.0012 | 101.6483 | 60.2222 | 143.2222 | 45.3989 | 0 | 45.3989 | 57.02 | 45.3989 | 6/3/8:00
6 | 3 | 1900-01-08 | 16.1 | 111 | 730 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 111 | 0 | 0 | 39.791 | 154.3333 | 22.2823 | 86.148 | -75 | 1.9944 | 116.6466 | -55.6342 | 55.3658 | 17.55 | 0 | 17.55 | 60.98 | 17.55 | 6/3/9:00
6 | 3 | 1900-01-09 | 17.8 | 132 | 799 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 132 | 0 | 0 | 39.791 | 154.375 | 22.2877 | 86.148 | -75 | 1.9877 | 131.6449 | -183.5572 | -51.5572 | -16.3427 | 0 | -16.3427 | 64.04 | -16.3427 | 6/3/10:00
6 | 3 | 1900-01-10 | 18.9 | 147 | 839 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 147 | 0 | 0 | 39.791 | 154.4167 | 22.2931 | 86.148 | -75 | 1.981 | 146.6432 | -294.5358 | -147.5358 | -46.7663 | 0 | -46.7663 | 66.02 | -46.7663 | 6/3/11:00
6 | 3 | 1900-01-11 | 20.6 | 156 | 861 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 156 | 0 | 0 | 39.791 | 154.4583 | 22.2984 | 86.148 | -75 | 1.9742 | 161.6416 | -371.8752 | -215.8752 | -68.4287 | 0 | -68.4287 | 69.08 | -68.4287 | 6/3/12:00
6 | 3 | 1900-01-12 | 21.7 | 156 | 821 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 156 | 0 | 0 | 39.791 | 154.5 | 22.3037 | 86.148 | -75 | 1.9674 | 176.6399 | -383.234 | -227.234 | -72.0292 | 0 | -72.0292 | 71.06 | -72.0292 | 6/3/13:00
6 | 3 | 1900-01-13 | 23.3 | 161 | 814 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 161 | 0 | 0 | 39.791 | 154.5417 | 22.309 | 86.148 | -75 | 1.9607 | 191.6382 | -368.9982 | -207.9982 | -65.9318 | 0 | -65.9318 | 73.94 | -65.9318 | 6/3/14:00
6 | 3 | 1900-01-14 | 23.9 | 159 | 792 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 159 | 0 | 0 | 39.791 | 154.5833 | 22.3143 | 86.148 | -75 | 1.9539 | 206.6365 | -310.785 | -151.785 | -48.1132 | 0 | -48.1132 | 75.02 | -48.1132 | 6/3/15:00
6 | 3 | 1900-01-15 | 25 | 144 | 806 | 77 | 0 | 1 | 0 | 77 | 0 | 144 | 0 | 0 | 39.791 | 154.625 | 22.3196 | 86.148 | -75 | 1.9471 | 221.6348 | -232.2976 | -88.2976 | -27.9888 | 0 | -27.9888 | 77 | -27.9888 | 6/3/16:00
6 | 3 | 1900-01-16 | 25.6 | 125 | 736 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 125 | 0 | 0 | 39.791 | 154.6667 | 22.3249 | 86.148 | -75 | 1.9403 | 236.6331 | -108.8018 | 16.1982 | 5.1345 | 0 | 5.1345 | 78.08 | 5.1345 | 6/3/17:00
6 | 3 | 1900-01-17 | 25 | 96 | 663 | 77 | 0 | 1 | 0 | 77 | 0 | 96 | 0 | 0 | 39.791 | 154.7083 | 22.3301 | 86.148 | -75 | 1.9335 | 251.6314 | 12.7143 | 108.7143 | 34.4605 | 0 | 34.4605 | 77 | 34.4605 | 6/3/18:00
6 | 3 | 1900-01-18 | 23.9 | 66 | 487 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 66 | 0 | 0 | 39.791 | 154.75 | 22.3354 | 86.148 | -75 | 1.9266 | 266.6297 | 98.0963 | 164.0963 | 52.0156 | 0 | 52.0156 | 75.02 | 52.0156 | 6/3/19:00
6 | 3 | 1900-01-19 | 20.6 | 31 | 151 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 31 | 0 | 0 | 39.791 | 154.7917 | 22.3406 | 86.148 | -75 | 1.9198 | 281.628 | 58.3638 | 89.3638 | 28.3268 | 0 | 28.3268 | 69.08 | 28.3268 | 6/3/20:00
6 | 3 | 1900-01-20 | 18.9 | 1 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 1 | 0 | 0 | 39.791 | 154.8333 | 22.3459 | 86.148 | -75 | 1.913 | 296.6262 | 0 | 1 | 0.31698 | 0 | 0.31698 | 66.02 | 0.31698 | 6/3/21:00
6 | 3 | 1900-01-21 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 154.875 | 22.3511 | 86.148 | -75 | 1.9061 | 311.6245 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 6/3/22:00
6 | 3 | 1900-01-22 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 154.9167 | 22.3563 | 86.148 | -75 | 1.8993 | 326.6228 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 6/3/23:00
6 | 3 | 1900-01-23 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 154.9583 | 22.3615 | 86.148 | -75 | 1.8924 | 341.6211 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 6/3/24:00
6 | 4 | 1899-12-31 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 155 | 22.3667 | 86.148 | -75 | 1.8855 | -3.3806 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/4/1:00
6 | 4 | 1900-01-01 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 155.0417 | 22.3718 | 86.148 | -75 | 1.8786 | 11.6177 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 6/4/2:00
6 | 4 | 1900-01-02 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 155.0833 | 22.377 | 86.148 | -75 | 1.8717 | 26.6159 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 6/4/3:00
6 | 4 | 1900-01-03 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 155.125 | 22.3821 | 86.148 | -75 | 1.8648 | 41.6142 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 6/4/4:00
6 | 4 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 155.1667 | 22.3873 | 86.148 | -75 | 1.8579 | 56.6125 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/4/5:00
6 | 4 | 1900-01-05 | 17.2 | 16 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 16 | 0 | 0 | 39.791 | 155.2083 | 22.3924 | 86.148 | -75 | 1.851 | 71.6107 | 0 | 16 | 5.0717 | 0 | 5.0717 | 62.96 | 5.0717 | 6/4/6:00
6 | 4 | 1900-01-06 | 18.3 | 59 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 59 | 0 | 0 | 39.791 | 155.25 | 22.3975 | 86.148 | -75 | 1.844 | 86.609 | 0.28588 | 59.2859 | 18.7926 | 0 | 18.7926 | 64.94 | 18.7926 | 6/4/7:00
6 | 4 | 1900-01-07 | 20 | 165 | 318 | 68 | 0 | 1 | 0 | 68 | 0 | 165 | 0 | 0 | 39.791 | 155.2917 | 22.4026 | 86.148 | -75 | 1.8371 | 101.6073 | 32.11 | 197.11 | 62.4804 | 0 | 62.4804 | 68 | 62.4804 | 6/4/8:00
6 | 4 | 1900-01-08 | 22.2 | 154 | 581 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 154 | 0 | 0 | 39.791 | 155.3333 | 22.4077 | 86.148 | -75 | 1.8301 | 116.6055 | -43.0955 | 110.9045 | 35.1548 | 0 | 35.1548 | 71.96 | 35.1548 | 6/4/9:00
6 | 4 | 1900-01-09 | 23.3 | 222 | 364 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 222 | 0 | 0 | 39.791 | 155.375 | 22.4127 | 86.148 | -75 | 1.8232 | 131.6038 | -82.8598 | 139.1402 | 44.105 | 0 | 44.105 | 73.94 | 44.105 | 6/4/10:00
6 | 4 | 1900-01-10 | 25 | 224 | 714 | 77 | 0 | 1 | 0 | 77 | 0 | 224 | 0 | 0 | 39.791 | 155.4167 | 22.4178 | 86.148 | -75 | 1.8162 | 146.602 | -249.1535 | -25.1535 | -7.9732 | 0 | -7.9732 | 77 | -7.9732 | 6/4/11:00
6 | 4 | 1900-01-11 | 26.7 | 391 | 332 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 391 | 0 | 0 | 39.791 | 155.4583 | 22.4229 | 86.148 | -75 | 1.8092 | 161.6003 | -142.7139 | 248.2861 | 78.7024 | 0 | 78.7024 | 80.06 | 78.7024 | 6/4/12:00
6 | 4 | 1900-01-12 | 27.2 | 443 | 452 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 443 | 0 | 0 | 39.791 | 155.5 | 22.4279 | 86.148 | -75 | 1.8022 | 176.5986 | -210.1093 | 232.8907 | 73.8223 | 0 | 73.8223 | 80.96 | 73.8223 | 6/4/13:00
6 | 4 | 1900-01-13 | 23.9 | 202 | 2 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 202 | 0 | 0 | 39.791 | 155.5417 | 22.4329 | 86.148 | -75 | 1.7952 | 191.5968 | -0.90304 | 201.097 | 63.7442 | 0 | 63.7442 | 75.02 | 63.7442 | 6/4/14:00
6 | 4 | 1900-01-14 | 22.8 | 176 | 1 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 176 | 0 | 0 | 39.791 | 155.5833 | 22.4379 | 86.148 | -75 | 1.7882 | 206.5951 | -0.39079 | 175.6092 | 55.6651 | 0 | 55.6651 | 73.04 | 55.6651 | 6/4/15:00
6 | 4 | 1900-01-15 | 23.9 | 286 | 6 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 286 | 0 | 0 | 39.791 | 155.625 | 22.4429 | 86.148 | -75 | 1.7812 | 221.5933 | -1.7208 | 284.2792 | 90.1115 | 0 | 90.1115 | 75.02 | 90.1115 | 6/4/16:00
6 | 4 | 1900-01-16 | 23.3 | 214 | 4 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 214 | 0 | 0 | 39.791 | 155.6667 | 22.4479 | 86.148 | -75 | 1.7742 | 236.5915 | -0.58657 | 213.4134 | 67.6483 | 0 | 67.6483 | 73.94 | 67.6483 | 6/4/17:00
6 | 4 | 1900-01-17 | 23.3 | 176 | 4 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 176 | 0 | 0 | 39.791 | 155.7083 | 22.4529 | 86.148 | -75 | 1.7671 | 251.5898 | 0.080613 | 176.0806 | 55.8145 | 0 | 55.8145 | 73.94 | 55.8145 | 6/4/18:00
6 | 4 | 1900-01-18 | 23.3 | 79 | 4 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 79 | 0 | 0 | 39.791 | 155.75 | 22.4579 | 86.148 | -75 | 1.7601 | 266.588 | 0.80886 | 79.8089 | 25.298 | 0 | 25.298 | 73.94 | 25.298 | 6/4/19:00
6 | 4 | 1900-01-19 | 22.2 | 38 | 1 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 38 | 0 | 0 | 39.791 | 155.7917 | 22.4628 | 86.148 | -75 | 1.753 | 281.5863 | 0.38714 | 38.3871 | 12.1681 | 0 | 12.1681 | 71.96 | 12.1681 | 6/4/20:00
6 | 4 | 1900-01-20 | 21.7 | 1 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 1 | 0 | 0 | 39.791 | 155.8333 | 22.4678 | 86.148 | -75 | 1.746 | 296.5845 | 0 | 1 | 0.31698 | 0 | 0.31698 | 71.06 | 0.31698 | 6/4/21:00
6 | 4 | 1900-01-21 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 155.875 | 22.4727 | 86.148 | -75 | 1.7389 | 311.5827 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/4/22:00
6 | 4 | 1900-01-22 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 155.9167 | 22.4776 | 86.148 | -75 | 1.7318 | 326.5809 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/4/23:00
6 | 4 | 1900-01-23 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 155.9583 | 22.4825 | 86.148 | -75 | 1.7247 | 341.5792 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/4/24:00
6 | 5 | 1899-12-31 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 156 | 22.4874 | 86.148 | -75 | 1.7176 | -3.4226 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/5/1:00
6 | 5 | 1900-01-01 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 156.0417 | 22.4923 | 86.148 | -75 | 1.7105 | 11.5756 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/5/2:00
6 | 5 | 1900-01-02 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 156.0833 | 22.4972 | 86.148 | -75 | 1.7034 | 26.5738 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/5/3:00
6 | 5 | 1900-01-03 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 156.125 | 22.502 | 86.148 | -75 | 1.6962 | 41.5721 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/5/4:00
6 | 5 | 1900-01-04 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 156.1667 | 22.5069 | 86.148 | -75 | 1.6891 | 56.5703 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/5/5:00
6 | 5 | 1900-01-05 | 21.1 | 18 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 18 | 0 | 0 | 39.791 | 156.2083 | 22.5117 | 86.148 | -75 | 1.682 | 71.5685 | 0 | 18 | 5.7057 | 0 | 5.7057 | 69.98 | 5.7057 | 6/5/6:00
6 | 5 | 1900-01-06 | 21.7 | 76 | 1 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 76 | 0 | 0 | 39.791 | 156.25 | 22.5165 | 86.148 | -75 | 1.6748 | 86.5667 | 0.28759 | 76.2876 | 24.1818 | 0 | 24.1818 | 71.06 | 24.1818 | 6/5/7:00
6 | 5 | 1900-01-07 | 22.2 | 149 | 1 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 149 | 0 | 0 | 39.791 | 156.2917 | 22.5213 | 86.148 | -75 | 1.6676 | 101.5649 | 0.10284 | 149.1028 | 47.263 | 0 | 47.263 | 71.96 | 47.263 | 6/5/8:00
6 | 5 | 1900-01-08 | 22.2 | 248 | 1 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 248 | 0 | 0 | 39.791 | 156.3333 | 22.5261 | 86.148 | -75 | 1.6605 | 116.5631 | -0.07221 | 247.9278 | 78.5888 | 0 | 78.5888 | 71.96 | 78.5888 | 6/5/9:00
6 | 5 | 1900-01-09 | 22.2 | 320 | 1 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 320 | 0 | 0 | 39.791 | 156.375 | 22.5309 | 86.148 | -75 | 1.6533 | 131.5613 | -0.22562 | 319.7744 | 101.3629 | 0 | 101.3629 | 71.96 | 101.3629 | 6/5/10:00
6 | 5 | 1900-01-10 | 22.8 | 427 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 427 | 0 | 0 | 39.791 | 156.4167 | 22.5357 | 86.148 | -75 | 1.6461 | 146.5595 | 0 | 427 | 135.3515 | 0 | 135.3515 | 73.04 | 135.3515 | 6/5/11:00
6 | 5 | 1900-01-11 | 22.2 | 454 | 2 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 454 | 0 | 0 | 39.791 | 156.4583 | 22.5404 | 86.148 | -75 | 1.6389 | 161.5577 | -0.85582 | 453.1442 | 143.6388 | 0 | 143.6388 | 71.96 | 143.6388 | 6/5/12:00
6 | 5 | 1900-01-12 | 25.6 | 445 | 1 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 445 | 0 | 0 | 39.791 | 156.5 | 22.5452 | 86.148 | -75 | 1.6317 | 176.5559 | -0.463 | 444.537 | 140.9105 | 0 | 140.9105 | 78.08 | 140.9105 | 6/5/13:00
6 | 5 | 1900-01-13 | 25.6 | 475 | 2 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 475 | 0 | 0 | 39.791 | 156.5417 | 22.5499 | 86.148 | -75 | 1.6245 | 191.5541 | -0.89966 | 474.1003 | 150.2815 | 0 | 150.2815 | 78.08 | 150.2815 | 6/5/14:00
6 | 5 | 1900-01-14 | 24.4 | 414 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 414 | 0 | 0 | 39.791 | 156.5833 | 22.5546 | 86.148 | -75 | 1.6172 | 206.5523 | 0 | 414 | 131.2308 | 0 | 131.2308 | 75.92 | 131.2308 | 6/5/15:00
6 | 5 | 1900-01-15 | 23.3 | 360 | 1 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 360 | 0 | 0 | 39.791 | 156.625 | 22.5593 | 86.148 | -75 | 1.61 | 221.5505 | -0.28551 | 359.7145 | 114.0232 | 0 | 114.0232 | 73.94 | 114.0232 | 6/5/16:00
6 | 5 | 1900-01-16 | 23.9 | 287 | 1 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 287 | 0 | 0 | 39.791 | 156.6667 | 22.564 | 86.148 | -75 | 1.6028 | 236.5487 | -0.14556 | 286.8544 | 90.9278 | 0 | 90.9278 | 75.02 | 90.9278 | 6/5/17:00
6 | 5 | 1900-01-17 | 24.4 | 189 | 1 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 189 | 0 | 0 | 39.791 | 156.7083 | 22.5687 | 86.148 | -75 | 1.5955 | 251.5469 | 0.021032 | 189.021 | 59.9164 | 0 | 59.9164 | 75.92 | 59.9164 | 6/5/18:00
6 | 5 | 1900-01-18 | 23.9 | 119 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 119 | 0 | 0 | 39.791 | 156.75 | 22.5734 | 86.148 | -75 | 1.5883 | 266.5451 | 0 | 119 | 37.7209 | 0 | 37.7209 | 75.02 | 37.7209 | 6/5/19:00
6 | 5 | 1900-01-19 | 23.3 | 31 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 31 | 0 | 0 | 39.791 | 156.7917 | 22.5781 | 86.148 | -75 | 1.581 | 281.5432 | 0 | 31 | 9.8265 | 0 | 9.8265 | 73.94 | 9.8265 | 6/5/20:00
6 | 5 | 1900-01-20 | 22.8 | 1 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 1 | 0 | 0 | 39.791 | 156.8333 | 22.5827 | 86.148 | -75 | 1.5737 | 296.5414 | 0 | 1 | 0.31698 | 0 | 0.31698 | 73.04 | 0.31698 | 6/5/21:00
6 | 5 | 1900-01-21 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 156.875 | 22.5874 | 86.148 | -75 | 1.5664 | 311.5396 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/5/22:00
6 | 5 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 156.9167 | 22.592 | 86.148 | -75 | 1.5591 | 326.5378 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/5/23:00
6 | 5 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 156.9583 | 22.5966 | 86.148 | -75 | 1.5518 | 341.536 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/5/24:00
6 | 6 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 157 | 22.6012 | 86.148 | -75 | 1.5445 | -3.4659 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/6/1:00
6 | 6 | 1900-01-01 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 157.0417 | 22.6058 | 86.148 | -75 | 1.5372 | 11.5323 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/6/2:00
6 | 6 | 1900-01-02 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 157.0833 | 22.6104 | 86.148 | -75 | 1.5299 | 26.5305 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/6/3:00
6 | 6 | 1900-01-03 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 157.125 | 22.615 | 86.148 | -75 | 1.5225 | 41.5286 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/6/4:00
6 | 6 | 1900-01-04 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 157.1667 | 22.6195 | 86.148 | -75 | 1.5152 | 56.5268 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/6/5:00
6 | 6 | 1900-01-05 | 20.6 | 10 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 10 | 0 | 0 | 39.791 | 157.2083 | 22.624 | 86.148 | -75 | 1.5078 | 71.525 | 0 | 10 | 3.1698 | 0 | 3.1698 | 69.08 | 3.1698 | 6/6/6:00
6 | 6 | 1900-01-06 | 20.6 | 71 | 1 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 71 | 0 | 0 | 39.791 | 157.25 | 22.6286 | 86.148 | -75 | 1.5005 | 86.5231 | 0.28925 | 71.2893 | 22.5974 | 0 | 22.5974 | 69.08 | 22.5974 | 6/6/7:00
6 | 6 | 1900-01-07 | 21.7 | 160 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 160 | 0 | 0 | 39.791 | 157.2917 | 22.6331 | 86.148 | -75 | 1.4931 | 101.5213 | 0 | 160 | 50.7172 | 0 | 50.7172 | 71.06 | 50.7172 | 6/6/8:00
6 | 6 | 1900-01-08 | 22.8 | 277 | 1 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 277 | 0 | 0 | 39.791 | 157.3333 | 22.6376 | 86.148 | -75 | 1.4857 | 116.5194 | -0.07032 | 276.9297 | 87.7819 | 0 | 87.7819 | 73.04 | 87.7819 | 6/6/9:00
6 | 6 | 1900-01-09 | 24.4 | 334 | 1 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 334 | 0 | 0 | 39.791 | 157.375 | 22.6421 | 86.148 | -75 | 1.4784 | 131.5176 | -0.22369 | 333.7763 | 105.8013 | 0 | 105.8013 | 75.92 | 105.8013 | 6/6/10:00
6 | 6 | 1900-01-10 | 23.9 | 238 | 1 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 238 | 0 | 0 | 39.791 | 157.4167 | 22.6466 | 86.148 | -75 | 1.471 | 146.5157 | -0.34502 | 237.655 | 75.3325 | 0 | 75.3325 | 75.02 | 75.3325 | 6/6/11:00
6 | 6 | 1900-01-11 | 23.9 | 441 | 1 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 441 | 0 | 0 | 39.791 | 157.4583 | 22.651 | 86.148 | -75 | 1.4636 | 161.5139 | -0.42606 | 440.5739 | 139.6542 | 0 | 139.6542 | 75.02 | 139.6542 | 6/6/12:00
6 | 6 | 1900-01-12 | 24.4 | 463 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 463 | 0 | 0 | 39.791 | 157.5 | 22.6555 | 86.148 | -75 | 1.4561 | 176.512 | 0 | 463 | 146.7629 | 0 | 146.7629 | 75.92 | 146.7629 | 6/6/13:00
6 | 6 | 1900-01-13 | 24.4 | 450 | 1 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 450 | 0 | 0 | 39.791 | 157.5417 | 22.66 | 86.148 | -75 | 1.4487 | 191.5102 | -0.44825 | 449.5518 | 142.5001 | 0 | 142.5001 | 75.92 | 142.5001 | 6/6/14:00
6 | 6 | 1900-01-14 | 25 | 328 | 130 | 77 | 0 | 1 | 0 | 77 | 0 | 328 | 0 | 0 | 39.791 | 157.5833 | 22.6644 | 86.148 | -75 | 1.4413 | 206.5083 | -50.4266 | 277.5734 | 87.9859 | 0 | 87.9859 | 77 | 87.9859 | 6/6/15:00
6 | 6 | 1900-01-15 | 26.1 | 263 | 415 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 263 | 0 | 0 | 39.791 | 157.625 | 22.6688 | 86.148 | -75 | 1.4339 | 221.5065 | -117.9933 | 145.0067 | 45.9646 | 0 | 45.9646 | 78.98 | 45.9646 | 6/6/16:00
6 | 6 | 1900-01-16 | 26.1 | 255 | 338 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 255 | 0 | 0 | 39.791 | 157.6667 | 22.6732 | 86.148 | -75 | 1.4264 | 236.5046 | -48.8672 | 206.1328 | 65.3405 | 0 | 65.3405 | 78.98 | 65.3405 | 6/6/17:00
6 | 6 | 1900-01-17 | 25.6 | 227 | 247 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 227 | 0 | 0 | 39.791 | 157.7083 | 22.6776 | 86.148 | -75 | 1.419 | 251.5027 | 5.3882 | 232.3882 | 73.663 | 0 | 73.663 | 78.08 | 73.663 | 6/6/18:00
6 | 6 | 1900-01-18 | 25 | 108 | 26 | 77 | 0 | 1 | 0 | 77 | 0 | 108 | 0 | 0 | 39.791 | 157.75 | 22.682 | 86.148 | -75 | 1.4115 | 266.5009 | 5.2915 | 113.2915 | 35.9114 | 0 | 35.9114 | 77 | 35.9114 | 6/6/19:00
6 | 6 | 1900-01-19 | 23.9 | 19 | 2 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 19 | 0 | 0 | 39.791 | 157.7917 | 22.6864 | 86.148 | -75 | 1.404 | 281.499 | 0.77632 | 19.7763 | 6.2687 | 0 | 6.2687 | 75.02 | 6.2687 | 6/6/20:00
6 | 6 | 1900-01-20 | 23.3 | 1 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 1 | 0 | 0 | 39.791 | 157.8333 | 22.6907 | 86.148 | -75 | 1.3966 | 296.4971 | 0 | 1 | 0.31698 | 0 | 0.31698 | 73.94 | 0.31698 | 6/6/21:00
6 | 6 | 1900-01-21 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 157.875 | 22.6951 | 86.148 | -75 | 1.3891 | 311.4953 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/6/22:00
6 | 6 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 157.9167 | 22.6994 | 86.148 | -75 | 1.3816 | 326.4934 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/6/23:00
6 | 6 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 157.9583 | 22.7037 | 86.148 | -75 | 1.3741 | 341.4915 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/6/24:00
6 | 7 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 158 | 22.708 | 86.148 | -75 | 1.3666 | -3.5104 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/7/1:00
6 | 7 | 1900-01-01 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 158.0417 | 22.7123 | 86.148 | -75 | 1.3591 | 11.4878 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/7/2:00
6 | 7 | 1900-01-02 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 158.0833 | 22.7166 | 86.148 | -75 | 1.3516 | 26.4859 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/7/3:00
6 | 7 | 1900-01-03 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 158.125 | 22.7209 | 86.148 | -75 | 1.344 | 41.484 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/7/4:00
6 | 7 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 158.1667 | 22.7252 | 86.148 | -75 | 1.3365 | 56.4821 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/7/5:00
6 | 7 | 1900-01-05 | 21.1 | 14 | 12 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 14 | 0 | 0 | 39.791 | 158.2083 | 22.7294 | 86.148 | -75 | 1.3289 | 71.4802 | 5.6687 | 19.6687 | 6.2346 | 0 | 6.2346 | 69.98 | 6.2346 | 6/7/6:00
6 | 7 | 1900-01-06 | 22.2 | 73 | 7 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 73 | 0 | 0 | 39.791 | 158.25 | 22.7337 | 86.148 | -75 | 1.3214 | 86.4783 | 2.036 | 75.036 | 23.7851 | 0 | 23.7851 | 71.96 | 23.7851 | 6/7/7:00
6 | 7 | 1900-01-07 | 22.8 | 172 | 8 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 172 | 0 | 0 | 39.791 | 158.2917 | 22.7379 | 86.148 | -75 | 1.3138 | 101.4765 | 0.85093 | 172.8509 | 54.7907 | 0 | 54.7907 | 73.04 | 54.7907 | 6/7/8:00
6 | 7 | 1900-01-08 | 22.2 | 277 | 3 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 277 | 0 | 0 | 39.791 | 158.3333 | 22.7421 | 86.148 | -75 | 1.3063 | 116.4746 | -0.20552 | 276.7945 | 87.739 | 0 | 87.739 | 71.96 | 87.739 | 6/7/9:00
6 | 7 | 1900-01-09 | 23.9 | 267 | 7 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 267 | 0 | 0 | 39.791 | 158.375 | 22.7463 | 86.148 | -75 | 1.2987 | 131.4727 | -1.5529 | 265.4471 | 84.1421 | 0 | 84.1421 | 75.02 | 84.1421 | 6/7/10:00
6 | 7 | 1900-01-10 | 25.6 | 360 | 226 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 360 | 0 | 0 | 39.791 | 158.4167 | 22.7505 | 86.148 | -75 | 1.2911 | 146.4708 | -77.5627 | 282.4373 | 89.5277 | 0 | 89.5277 | 78.08 | 89.5277 | 6/7/11:00
6 | 7 | 1900-01-11 | 27.2 | 245 | 641 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 245 | 0 | 0 | 39.791 | 158.4583 | 22.7547 | 86.148 | -75 | 1.2835 | 161.4689 | -271.9778 | -26.9778 | -8.5515 | 0 | -8.5515 | 80.96 | -8.5515 | 6/7/12:00
6 | 7 | 1900-01-12 | 25.6 | 262 | 3 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 262 | 0 | 0 | 39.791 | 158.5 | 22.7588 | 86.148 | -75 | 1.2759 | 176.467 | -1.3789 | 260.6211 | 82.6123 | 0 | 82.6123 | 78.08 | 82.6123 | 6/7/13:00
6 | 7 | 1900-01-13 | 27.2 | 330 | 610 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 330 | 0 | 0 | 39.791 | 158.5417 | 22.763 | 86.148 | -75 | 1.2683 | 191.4651 | -272.5325 | 57.4675 | 18.2162 | 0 | 18.2162 | 80.96 | 18.2162 | 6/7/14:00
6 | 7 | 1900-01-14 | 25.6 | 277 | 182 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 277 | 0 | 0 | 39.791 | 158.5833 | 22.7671 | 86.148 | -75 | 1.2607 | 206.4632 | -70.3632 | 206.6368 | 65.5003 | 0 | 65.5003 | 78.08 | 65.5003 | 6/7/15:00
6 | 7 | 1900-01-15 | 25 | 194 | 168 | 77 | 0 | 1 | 0 | 77 | 0 | 194 | 0 | 0 | 39.791 | 158.625 | 22.7713 | 86.148 | -75 | 1.2531 | 221.4613 | -47.5841 | 146.4159 | 46.4113 | 0 | 46.4113 | 77 | 46.4113 | 6/7/16:00
6 | 7 | 1900-01-16 | 25.6 | 269 | 336 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 269 | 0 | 0 | 39.791 | 158.6667 | 22.7754 | 86.148 | -75 | 1.2454 | 236.4594 | -48.283 | 220.717 | 69.9634 | 0 | 69.9634 | 78.08 | 69.9634 | 6/7/17:00
6 | 7 | 1900-01-17 | 25 | 90 | 24 | 77 | 0 | 1 | 0 | 77 | 0 | 90 | 0 | 0 | 39.791 | 158.7083 | 22.7795 | 86.148 | -75 | 1.2378 | 251.4574 | 0.54001 | 90.54 | 28.6996 | 0 | 28.6996 | 77 | 28.6996 | 6/7/18:00
6 | 7 | 1900-01-18 | 22.2 | 66 | 91 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 66 | 0 | 0 | 39.791 | 158.75 | 22.7836 | 86.148 | -75 | 1.2301 | 266.4555 | 18.5676 | 84.5676 | 26.8064 | 0 | 26.8064 | 71.96 | 26.8064 | 6/7/19:00
6 | 7 | 1900-01-19 | 22.2 | 34 | 11 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 34 | 0 | 0 | 39.791 | 158.7917 | 22.7876 | 86.148 | -75 | 1.2225 | 281.4536 | 4.2741 | 38.2741 | 12.1322 | 0 | 12.1322 | 71.96 | 12.1322 | 6/7/20:00
6 | 7 | 1900-01-20 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 158.8333 | 22.7917 | 86.148 | -75 | 1.2148 | 296.4517 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/7/21:00
6 | 7 | 1900-01-21 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 158.875 | 22.7958 | 86.148 | -75 | 1.2072 | 311.4498 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/7/22:00
6 | 7 | 1900-01-22 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 158.9167 | 22.7998 | 86.148 | -75 | 1.1995 | 326.4479 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/7/23:00
6 | 7 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 158.9583 | 22.8038 | 86.148 | -75 | 1.1918 | 341.446 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/7/24:00
6 | 8 | 1899-12-31 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 159 | 22.8079 | 86.148 | -75 | 1.1841 | -3.556 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/8/1:00
6 | 8 | 1900-01-01 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 159.0417 | 22.8119 | 86.148 | -75 | 1.1764 | 11.4421 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/8/2:00
6 | 8 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 159.0833 | 22.8159 | 86.148 | -75 | 1.1687 | 26.4402 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 6/8/3:00
6 | 8 | 1900-01-03 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 159.125 | 22.8198 | 86.148 | -75 | 1.161 | 41.4383 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 6/8/4:00
6 | 8 | 1900-01-04 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 159.1667 | 22.8238 | 86.148 | -75 | 1.1533 | 56.4363 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 6/8/5:00
6 | 8 | 1900-01-05 | 18.9 | 16 | 16 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 16 | 0 | 0 | 39.791 | 159.2083 | 22.8278 | 86.148 | -75 | 1.1456 | 71.4344 | 7.5804 | 23.5804 | 7.4746 | 0 | 7.4746 | 66.02 | 7.4746 | 6/8/6:00
6 | 8 | 1900-01-06 | 20 | 79 | 183 | 68 | 0 | 1 | 0 | 68 | 0 | 79 | 0 | 0 | 39.791 | 159.25 | 22.8317 | 86.148 | -75 | 1.1378 | 86.4325 | 53.509 | 132.509 | 42.003 | 0 | 42.003 | 68 | 42.003 | 6/8/7:00
6 | 8 | 1900-01-07 | 21.7 | 138 | 3 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 138 | 0 | 0 | 39.791 | 159.2917 | 22.8356 | 86.148 | -75 | 1.1301 | 101.4305 | 0.32409 | 138.3241 | 43.8463 | 0 | 43.8463 | 71.06 | 43.8463 | 6/8/8:00
6 | 8 | 1900-01-08 | 24.4 | 169 | 525 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 169 | 0 | 0 | 39.791 | 159.3333 | 22.8396 | 86.148 | -75 | 1.1223 | 116.4286 | -35.0527 | 133.9473 | 42.4589 | 0 | 42.4589 | 75.92 | 42.4589 | 6/8/9:00
6 | 8 | 1900-01-09 | 26.1 | 228 | 606 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 228 | 0 | 0 | 39.791 | 159.375 | 22.8435 | 86.148 | -75 | 1.1146 | 131.4266 | -133.3692 | 94.6308 | 29.9963 | 0 | 29.9963 | 78.98 | 29.9963 | 6/8/10:00
6 | 8 | 1900-01-10 | 27.8 | 225 | 716 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 225 | 0 | 0 | 39.791 | 159.4167 | 22.8474 | 86.148 | -75 | 1.1068 | 146.4247 | -244.4897 | -19.4897 | -6.1779 | 0 | -6.1779 | 82.04 | -6.1779 | 6/8/11:00
6 | 8 | 1900-01-11 | 28.3 | 413 | 347 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 413 | 0 | 0 | 39.791 | 159.4583 | 22.8512 | 86.148 | -75 | 1.0991 | 161.4228 | -146.6598 | 266.3402 | 84.4252 | 0 | 84.4252 | 82.94 | 84.4252 | 6/8/12:00
6 | 8 | 1900-01-12 | 28.3 | 252 | 498 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 252 | 0 | 0 | 39.791 | 159.5 | 22.8551 | 86.148 | -75 | 1.0913 | 176.4208 | -228.1358 | 23.8642 | 7.5645 | 0 | 7.5645 | 82.94 | 7.5645 | 6/8/13:00
6 | 8 | 1900-01-13 | 29.4 | 323 | 550 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 323 | 0 | 0 | 39.791 | 159.5417 | 22.859 | 86.148 | -75 | 1.0835 | 191.4189 | -244.9758 | 78.0242 | 24.7323 | 0 | 24.7323 | 84.92 | 24.7323 | 6/8/14:00
6 | 8 | 1900-01-14 | 28.3 | 254 | 678 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 254 | 0 | 0 | 39.791 | 159.5833 | 22.8628 | 86.148 | -75 | 1.0757 | 206.4169 | -261.3248 | -7.3248 | -2.3218 | 0 | -2.3218 | 82.94 | -2.3218 | 6/8/15:00
6 | 8 | 1900-01-15 | 30 | 209 | 777 | 86 | 0 | 1 | 0 | 86 | 0 | 209 | 0 | 0 | 39.791 | 159.625 | 22.8666 | 86.148 | -75 | 1.0679 | 221.415 | -219.3184 | -10.3184 | -3.2707 | 0 | -3.2707 | 86 | -3.2707 | 6/8/16:00
6 | 8 | 1900-01-16 | 30 | 191 | 545 | 86 | 0 | 1 | 0 | 86 | 0 | 191 | 0 | 0 | 39.791 | 159.6667 | 22.8705 | 86.148 | -75 | 1.0601 | 236.413 | -77.8936 | 113.1064 | 35.8528 | 0 | 35.8528 | 86 | 35.8528 | 6/8/17:00
6 | 8 | 1900-01-17 | 28.9 | 175 | 378 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 175 | 0 | 0 | 39.791 | 159.7083 | 22.8743 | 86.148 | -75 | 1.0523 | 251.4111 | 8.7281 | 183.7281 | 58.2386 | 0 | 58.2386 | 84.02 | 58.2386 | 6/8/18:00
6 | 8 | 1900-01-18 | 27.8 | 94 | 261 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 94 | 0 | 0 | 39.791 | 159.75 | 22.8781 | 86.148 | -75 | 1.0445 | 266.4091 | 53.3667 | 147.3667 | 46.7127 | 0 | 46.7127 | 82.04 | 46.7127 | 6/8/19:00
6 | 8 | 1900-01-19 | 26.7 | 35 | 104 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 35 | 0 | 0 | 39.791 | 159.7917 | 22.8819 | 86.148 | -75 | 1.0367 | 281.4072 | 40.4415 | 75.4415 | 23.9136 | 0 | 23.9136 | 80.06 | 23.9136 | 6/8/20:00
6 | 8 | 1900-01-20 | 25 | 0 | 1 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 159.8333 | 22.8856 | 86.148 | -75 | 1.0288 | 296.4052 | 0.5637 | 0.5637 | 0.17868 | 0 | 0.17868 | 77 | 0.17868 | 6/8/21:00
6 | 8 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 159.875 | 22.8894 | 86.148 | -75 | 1.021 | 311.4032 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/8/22:00
6 | 8 | 1900-01-22 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 159.9167 | 22.8931 | 86.148 | -75 | 1.0131 | 326.4013 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/8/23:00
6 | 8 | 1900-01-23 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 159.9583 | 22.8969 | 86.148 | -75 | 1.0053 | 341.3993 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/8/24:00
6 | 9 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 160 | 22.9006 | 86.148 | -75 | 0.99743 | -3.6026 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/9/1:00
6 | 9 | 1900-01-01 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 160.0417 | 22.9043 | 86.148 | -75 | 0.98957 | 11.3954 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/9/2:00
6 | 9 | 1900-01-02 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 160.0833 | 22.908 | 86.148 | -75 | 0.98169 | 26.3934 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/9/3:00
6 | 9 | 1900-01-03 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 160.125 | 22.9117 | 86.148 | -75 | 0.97382 | 41.3915 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/9/4:00
6 | 9 | 1900-01-04 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 160.1667 | 22.9154 | 86.148 | -75 | 0.96593 | 56.3895 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/9/5:00
6 | 9 | 1900-01-05 | 20.6 | 16 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 16 | 0 | 0 | 39.791 | 160.2083 | 22.919 | 86.148 | -75 | 0.95804 | 71.3875 | 0 | 16 | 5.0717 | 0 | 5.0717 | 69.08 | 5.0717 | 6/9/6:00
6 | 9 | 1900-01-06 | 22.2 | 73 | 64 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 73 | 0 | 0 | 39.791 | 160.25 | 22.9227 | 86.148 | -75 | 0.95014 | 86.3855 | 18.8086 | 91.8086 | 29.1017 | 0 | 29.1017 | 71.96 | 29.1017 | 6/9/7:00
6 | 9 | 1900-01-07 | 22.2 | 129 | 7 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 129 | 0 | 0 | 39.791 | 160.2917 | 22.9263 | 86.148 | -75 | 0.94223 | 101.3836 | 0.76738 | 129.7674 | 41.134 | 0 | 41.134 | 71.96 | 41.134 | 6/9/8:00
6 | 9 | 1900-01-08 | 23.3 | 194 | 9 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 194 | 0 | 0 | 39.791 | 160.3333 | 22.9299 | 86.148 | -75 | 0.93432 | 116.3816 | -0.58597 | 193.414 | 61.3089 | 0 | 61.3089 | 73.94 | 61.3089 | 6/9/9:00
6 | 9 | 1900-01-09 | 23.3 | 281 | 1 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 281 | 0 | 0 | 39.791 | 160.375 | 22.9335 | 86.148 | -75 | 0.9264 | 131.3796 | -0.21841 | 280.7816 | 89.0029 | 0 | 89.0029 | 73.94 | 89.0029 | 6/9/10:00
6 | 9 | 1900-01-10 | 23.9 | 388 | 1 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 388 | 0 | 0 | 39.791 | 160.4167 | 22.9371 | 86.148 | -75 | 0.91848 | 146.3776 | -0.33983 | 387.6602 | 122.8815 | 0 | 122.8815 | 75.02 | 122.8815 | 6/9/11:00
6 | 9 | 1900-01-11 | 23.9 | 374 | 6 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 374 | 0 | 0 | 39.791 | 160.4583 | 22.9407 | 86.148 | -75 | 0.91055 | 161.3756 | -2.5266 | 371.4734 | 117.7506 | 0 | 117.7506 | 75.02 | 117.7506 | 6/9/12:00
6 | 9 | 1900-01-12 | 25 | 418 | 4 | 77 | 0 | 1 | 0 | 77 | 0 | 418 | 0 | 0 | 39.791 | 160.5 | 22.9443 | 86.148 | -75 | 0.90261 | 176.3737 | -1.8267 | 416.1733 | 131.9197 | 0 | 131.9197 | 77 | 131.9197 | 6/9/13:00
6 | 9 | 1900-01-13 | 25 | 410 | 5 | 77 | 0 | 1 | 0 | 77 | 0 | 410 | 0 | 0 | 39.791 | 160.5417 | 22.9479 | 86.148 | -75 | 0.89467 | 191.3717 | -2.2208 | 407.7792 | 129.2589 | 0 | 129.2589 | 77 | 129.2589 | 6/9/14:00
6 | 9 | 1900-01-14 | 26.1 | 403 | 4 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 403 | 0 | 0 | 39.791 | 160.5833 | 22.9514 | 86.148 | -75 | 0.88671 | 206.3697 | -1.5375 | 401.4625 | 127.2566 | 0 | 127.2566 | 78.98 | 127.2566 | 6/9/15:00
6 | 9 | 1900-01-15 | 26.7 | 377 | 2 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 377 | 0 | 0 | 39.791 | 160.625 | 22.9549 | 86.148 | -75 | 0.87876 | 221.3677 | -0.56279 | 376.4372 | 119.324 | 0 | 119.324 | 80.06 | 119.324 | 6/9/16:00
6 | 9 | 1900-01-16 | 26.7 | 285 | 377 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 285 | 0 | 0 | 39.791 | 160.6667 | 22.9585 | 86.148 | -75 | 0.87079 | 236.3657 | -53.6287 | 231.3713 | 73.3407 | 0 | 73.3407 | 80.06 | 73.3407 | 6/9/17:00
6 | 9 | 1900-01-17 | 26.7 | 171 | 42 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 171 | 0 | 0 | 39.791 | 160.7083 | 22.962 | 86.148 | -75 | 0.86282 | 251.3637 | 0.99053 | 171.9905 | 54.518 | 0 | 54.518 | 80.06 | 54.518 | 6/9/18:00
6 | 9 | 1900-01-18 | 25.6 | 98 | 328 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 98 | 0 | 0 | 39.791 | 160.75 | 22.9655 | 86.148 | -75 | 0.85485 | 266.3617 | 67.1789 | 165.1789 | 52.3588 | 0 | 52.3588 | 78.08 | 52.3588 | 6/9/19:00
6 | 9 | 1900-01-19 | 25 | 38 | 138 | 77 | 0 | 1 | 0 | 77 | 0 | 38 | 0 | 0 | 39.791 | 160.7917 | 22.969 | 86.148 | -75 | 0.84686 | 281.3597 | 53.6947 | 91.6947 | 29.0656 | 0 | 29.0656 | 77 | 29.0656 | 6/9/20:00
6 | 9 | 1900-01-20 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 160.8333 | 22.9724 | 86.148 | -75 | 0.83888 | 296.3577 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/9/21:00
6 | 9 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 160.875 | 22.9759 | 86.148 | -75 | 0.83088 | 311.3557 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/9/22:00
6 | 9 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 160.9167 | 22.9793 | 86.148 | -75 | 0.82288 | 326.3537 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/9/23:00
6 | 9 | 1900-01-23 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 160.9583 | 22.9828 | 86.148 | -75 | 0.81487 | 341.3517 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/9/24:00
6 | 10 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 161 | 22.9862 | 86.148 | -75 | 0.80686 | -3.6503 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/10/1:00
6 | 10 | 1900-01-01 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 161.0417 | 22.9896 | 86.148 | -75 | 0.79884 | 11.3477 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/10/2:00
6 | 10 | 1900-01-02 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 161.0833 | 22.993 | 86.148 | -75 | 0.79081 | 26.3457 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/10/3:00
6 | 10 | 1900-01-03 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 161.125 | 22.9964 | 86.148 | -75 | 0.78278 | 41.3437 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/10/4:00
6 | 10 | 1900-01-04 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 161.1667 | 22.9998 | 86.148 | -75 | 0.77474 | 56.3417 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/10/5:00
6 | 10 | 1900-01-05 | 21.1 | 16 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 16 | 0 | 0 | 39.791 | 161.2083 | 23.0031 | 86.148 | -75 | 0.7667 | 71.3397 | 0 | 16 | 5.0717 | 0 | 5.0717 | 69.98 | 5.0717 | 6/10/6:00
6 | 10 | 1900-01-06 | 21.7 | 23 | 5 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 23 | 0 | 0 | 39.791 | 161.25 | 23.0065 | 86.148 | -75 | 0.75865 | 86.3377 | 1.4765 | 24.4765 | 7.7586 | 0 | 7.7586 | 71.06 | 7.7586 | 6/10/7:00
6 | 10 | 1900-01-07 | 21.7 | 69 | 6 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 69 | 0 | 0 | 39.791 | 161.2917 | 23.0098 | 86.148 | -75 | 0.75059 | 101.3356 | 0.6669 | 69.6669 | 22.0832 | 0 | 22.0832 | 71.06 | 22.0832 | 6/10/8:00
6 | 10 | 1900-01-08 | 22.8 | 197 | 4 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 197 | 0 | 0 | 39.791 | 161.3333 | 23.0132 | 86.148 | -75 | 0.74253 | 116.3336 | -0.25411 | 196.7459 | 62.365 | 0 | 62.365 | 73.04 | 62.365 | 6/10/9:00
6 | 10 | 1900-01-09 | 25 | 398 | 127 | 77 | 0 | 1 | 0 | 77 | 0 | 398 | 0 | 0 | 39.791 | 161.375 | 23.0165 | 86.148 | -75 | 0.73446 | 131.3316 | -27.5365 | 370.4635 | 117.4304 | 0 | 117.4304 | 77 | 117.4304 | 6/10/10:00
6 | 10 | 1900-01-10 | 25.6 | 304 | 146 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 304 | 0 | 0 | 39.791 | 161.4167 | 23.0198 | 86.148 | -75 | 0.72638 | 146.3296 | -49.3906 | 254.6094 | 80.7067 | 0 | 80.7067 | 78.08 | 80.7067 | 6/10/11:00
6 | 10 | 1900-01-11 | 26.7 | 488 | 85 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 488 | 0 | 0 | 39.791 | 161.4583 | 23.0231 | 86.148 | -75 | 0.7183 | 161.3276 | -35.6708 | 452.3292 | 143.3804 | 0 | 143.3804 | 80.06 | 143.3804 | 6/10/12:00
6 | 10 | 1900-01-12 | 25.6 | 355 | 84 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 355 | 0 | 0 | 39.791 | 161.5 | 23.0263 | 86.148 | -75 | 0.71022 | 176.3256 | -38.2515 | 316.7485 | 100.4037 | 0 | 100.4037 | 78.08 | 100.4037 | 6/10/13:00
6 | 10 | 1900-01-13 | 26.1 | 461 | 102 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 461 | 0 | 0 | 39.791 | 161.5417 | 23.0296 | 86.148 | -75 | 0.70212 | 191.3235 | -45.1873 | 415.8127 | 131.8054 | 0 | 131.8054 | 78.98 | 131.8054 | 6/10/14:00
6 | 10 | 1900-01-14 | 28.3 | 433 | 73 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 433 | 0 | 0 | 39.791 | 161.5833 | 23.0329 | 86.148 | -75 | 0.69403 | 206.3215 | -27.9891 | 405.0109 | 128.3814 | 0 | 128.3814 | 82.94 | 128.3814 | 6/10/15:00
6 | 10 | 1900-01-15 | 28.9 | 332 | 447 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 332 | 0 | 0 | 39.791 | 161.625 | 23.0361 | 86.148 | -75 | 0.68592 | 221.3195 | -125.4436 | 206.5564 | 65.4748 | 0 | 65.4748 | 84.02 | 65.4748 | 6/10/16:00
6 | 10 | 1900-01-16 | 28.9 | 280 | 409 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 280 | 0 | 0 | 39.791 | 161.6667 | 23.0393 | 86.148 | -75 | 0.67781 | 236.3175 | -57.9474 | 222.0526 | 70.3868 | 0 | 70.3868 | 84.02 | 70.3868 | 6/10/17:00
6 | 10 | 1900-01-17 | 28.3 | 171 | 378 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 171 | 0 | 0 | 39.791 | 161.7083 | 23.0425 | 86.148 | -75 | 0.6697 | 251.3154 | 9.0655 | 180.0655 | 57.0776 | 0 | 57.0776 | 82.94 | 57.0776 | 6/10/18:00
6 | 10 | 1900-01-18 | 27.2 | 101 | 257 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 101 | 0 | 0 | 39.791 | 161.75 | 23.0457 | 86.148 | -75 | 0.66158 | 266.3134 | 52.7031 | 153.7031 | 48.7212 | 0 | 48.7212 | 80.96 | 48.7212 | 6/10/19:00
6 | 10 | 1900-01-19 | 26.7 | 38 | 21 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 38 | 0 | 0 | 39.791 | 161.7917 | 23.0489 | 86.148 | -75 | 0.65345 | 281.3114 | 8.1742 | 46.1742 | 14.6364 | 0 | 14.6364 | 80.06 | 14.6364 | 6/10/20:00
6 | 10 | 1900-01-20 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 161.8333 | 23.0521 | 86.148 | -75 | 0.64532 | 296.3093 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 6/10/21:00
6 | 10 | 1900-01-21 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 161.875 | 23.0553 | 86.148 | -75 | 0.63718 | 311.3073 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 6/10/22:00
6 | 10 | 1900-01-22 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 161.9167 | 23.0584 | 86.148 | -75 | 0.62904 | 326.3053 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 6/10/23:00
6 | 10 | 1900-01-23 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 161.9583 | 23.0616 | 86.148 | -75 | 0.62089 | 341.3032 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/10/24:00
6 | 11 | 1899-12-31 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 162 | 23.0647 | 86.148 | -75 | 0.61273 | -3.6988 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/11/1:00
6 | 11 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 162.0417 | 23.0678 | 86.148 | -75 | 0.60457 | 11.2991 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/11/2:00
6 | 11 | 1900-01-02 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 162.0833 | 23.0709 | 86.148 | -75 | 0.5964 | 26.2971 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/11/3:00
6 | 11 | 1900-01-03 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 162.125 | 23.074 | 86.148 | -75 | 0.58823 | 41.2951 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/11/4:00
6 | 11 | 1900-01-04 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 162.1667 | 23.0771 | 86.148 | -75 | 0.58005 | 56.293 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/11/5:00
6 | 11 | 1900-01-05 | 22.8 | 17 | 8 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 17 | 0 | 0 | 39.791 | 162.2083 | 23.0801 | 86.148 | -75 | 0.57187 | 71.291 | 3.821 | 20.821 | 6.5999 | 0 | 6.5999 | 73.04 | 6.5999 | 6/11/6:00
6 | 11 | 1900-01-06 | 23.3 | 71 | 3 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 71 | 0 | 0 | 39.791 | 162.25 | 23.0832 | 86.148 | -75 | 0.56368 | 86.2889 | 0.89001 | 71.89 | 22.7879 | 0 | 22.7879 | 73.94 | 22.7879 | 6/11/7:00
6 | 11 | 1900-01-07 | 22.8 | 106 | 10 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 106 | 0 | 0 | 39.791 | 162.2917 | 23.0862 | 86.148 | -75 | 0.55549 | 101.2869 | 1.126 | 107.126 | 33.9571 | 0 | 33.9571 | 73.04 | 33.9571 | 6/11/8:00
6 | 11 | 1900-01-08 | 22.8 | 189 | 7 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 189 | 0 | 0 | 39.791 | 162.3333 | 23.0892 | 86.148 | -75 | 0.54729 | 116.2848 | -0.4342 | 188.5658 | 59.7721 | 0 | 59.7721 | 73.04 | 59.7721 | 6/11/9:00
6 | 11 | 1900-01-09 | 23.3 | 329 | 9 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 329 | 0 | 0 | 39.791 | 162.375 | 23.0923 | 86.148 | -75 | 0.53909 | 131.2828 | -1.938 | 327.062 | 103.673 | 0 | 103.673 | 73.94 | 103.673 | 6/11/10:00
6 | 11 | 1900-01-10 | 23.9 | 402 | 6 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 402 | 0 | 0 | 39.791 | 162.4167 | 23.0953 | 86.148 | -75 | 0.53088 | 146.2807 | -2.0211 | 399.9789 | 126.7863 | 0 | 126.7863 | 75.02 | 126.7863 | 6/11/11:00
6 | 11 | 1900-01-11 | 24.4 | 429 | 7 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 429 | 0 | 0 | 39.791 | 162.4583 | 23.0982 | 86.148 | -75 | 0.52266 | 161.2787 | -2.9282 | 426.0718 | 135.0573 | 0 | 135.0573 | 75.92 | 135.0573 | 6/11/12:00
6 | 11 | 1900-01-12 | 25.6 | 434 | 5 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 434 | 0 | 0 | 39.791 | 162.5 | 23.1012 | 86.148 | -75 | 0.51444 | 176.2766 | -2.2709 | 431.7291 | 136.8506 | 0 | 136.8506 | 78.08 | 136.8506 | 6/11/13:00
6 | 11 | 1900-01-13 | 26.7 | 460 | 77 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 460 | 0 | 0 | 39.791 | 162.5417 | 23.1042 | 86.148 | -75 | 0.50621 | 191.2746 | -34.0325 | 425.9675 | 135.0243 | 0 | 135.0243 | 80.06 | 135.0243 | 6/11/14:00
6 | 11 | 1900-01-14 | 28.3 | 409 | 540 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 409 | 0 | 0 | 39.791 | 162.5833 | 23.1071 | 86.148 | -75 | 0.49798 | 206.2725 | -206.5862 | 202.4138 | 64.1616 | 0 | 64.1616 | 82.94 | 64.1616 | 6/11/15:00
6 | 11 | 1900-01-15 | 28.3 | 343 | 203 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 343 | 0 | 0 | 39.791 | 162.625 | 23.1101 | 86.148 | -75 | 0.48975 | 221.2704 | -56.8362 | 286.1638 | 90.7089 | 0 | 90.7089 | 82.94 | 90.7089 | 6/11/16:00
6 | 11 | 1900-01-16 | 27.8 | 218 | 75 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 218 | 0 | 0 | 39.791 | 162.6667 | 23.113 | 86.148 | -75 | 0.48151 | 236.2684 | -10.5909 | 207.4091 | 65.7451 | 0 | 65.7451 | 82.04 | 65.7451 | 6/11/17:00
6 | 11 | 1900-01-17 | 25.6 | 153 | 41 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 153 | 0 | 0 | 39.791 | 162.7083 | 23.1159 | 86.148 | -75 | 0.47326 | 251.2663 | 0.99575 | 153.9958 | 48.814 | 0 | 48.814 | 78.08 | 48.814 | 6/11/18:00
6 | 11 | 1900-01-18 | 21.7 | 71 | 5 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 71 | 0 | 0 | 39.791 | 162.75 | 23.1188 | 86.148 | -75 | 0.46501 | 266.2643 | 1.0262 | 72.0262 | 22.831 | 0 | 22.831 | 71.06 | 22.831 | 6/11/19:00
6 | 11 | 1900-01-19 | 21.7 | 25 | 2 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 25 | 0 | 0 | 39.791 | 162.7917 | 23.1217 | 86.148 | -75 | 0.45675 | 281.2622 | 0.77865 | 25.7786 | 8.1714 | 0 | 8.1714 | 71.06 | 8.1714 | 6/11/20:00
6 | 11 | 1900-01-20 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 162.8333 | 23.1246 | 86.148 | -75 | 0.44849 | 296.2601 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/11/21:00
6 | 11 | 1900-01-21 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 162.875 | 23.1274 | 86.148 | -75 | 0.44022 | 311.2581 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/11/22:00
6 | 11 | 1900-01-22 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 162.9167 | 23.1303 | 86.148 | -75 | 0.43195 | 326.256 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/11/23:00
6 | 11 | 1900-01-23 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 162.9583 | 23.1331 | 86.148 | -75 | 0.42367 | 341.2539 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/11/24:00
6 | 12 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 163 | 23.136 | 86.148 | -75 | 0.41539 | -3.7482 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/12/1:00
6 | 12 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 163.0417 | 23.1388 | 86.148 | -75 | 0.4071 | 11.2498 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/12/2:00
6 | 12 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 163.0833 | 23.1416 | 86.148 | -75 | 0.39881 | 26.2477 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 6/12/3:00
6 | 12 | 1900-01-03 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 163.125 | 23.1444 | 86.148 | -75 | 0.39051 | 41.2456 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 6/12/4:00
6 | 12 | 1900-01-04 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 163.1667 | 23.1471 | 86.148 | -75 | 0.38221 | 56.2436 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/12/5:00
6 | 12 | 1900-01-05 | 17.8 | 15 | 3 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 15 | 0 | 0 | 39.791 | 163.2083 | 23.1499 | 86.148 | -75 | 0.3739 | 71.2415 | 1.4364 | 16.4364 | 5.2101 | 0 | 5.2101 | 64.04 | 5.2101 | 6/12/6:00
6 | 12 | 1900-01-06 | 17.8 | 66 | 160 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 66 | 0 | 0 | 39.791 | 163.25 | 23.1527 | 86.148 | -75 | 0.36559 | 86.2394 | 47.6752 | 113.6752 | 36.0331 | 0 | 36.0331 | 64.04 | 36.0331 | 6/12/7:00
6 | 12 | 1900-01-07 | 18.3 | 150 | 129 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 150 | 0 | 0 | 39.791 | 163.2917 | 23.1554 | 86.148 | -75 | 0.35728 | 101.2373 | 14.7041 | 164.7041 | 52.2083 | 0 | 52.2083 | 64.94 | 52.2083 | 6/12/8:00
6 | 12 | 1900-01-08 | 18.9 | 223 | 53 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 223 | 0 | 0 | 39.791 | 163.3333 | 23.1581 | 86.148 | -75 | 0.34896 | 116.2352 | -3.2124 | 219.7876 | 69.6688 | 0 | 69.6688 | 66.02 | 69.6688 | 6/12/9:00
6 | 12 | 1900-01-09 | 18.9 | 229 | 7 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 229 | 0 | 0 | 39.791 | 163.375 | 23.1608 | 86.148 | -75 | 0.34063 | 131.2332 | -1.4975 | 227.5025 | 72.1143 | 0 | 72.1143 | 66.02 | 72.1143 | 6/12/10:00
6 | 12 | 1900-01-10 | 18.3 | 258 | 4 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 258 | 0 | 0 | 39.791 | 163.4167 | 23.1635 | 86.148 | -75 | 0.3323 | 146.2311 | -1.342 | 256.658 | 81.3561 | 0 | 81.3561 | 64.94 | 81.3561 | 6/12/11:00
6 | 12 | 1900-01-11 | 18.9 | 380 | 5 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 380 | 0 | 0 | 39.791 | 163.4583 | 23.1662 | 86.148 | -75 | 0.32396 | 161.229 | -2.0854 | 377.9146 | 119.7923 | 0 | 119.7923 | 66.02 | 119.7923 | 6/12/12:00
6 | 12 | 1900-01-12 | 18.3 | 450 | 4 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 450 | 0 | 0 | 39.791 | 163.5 | 23.1689 | 86.148 | -75 | 0.31562 | 176.2269 | -1.8123 | 448.1877 | 142.0677 | 0 | 142.0677 | 64.94 | 142.0677 | 6/12/13:00
6 | 12 | 1900-01-13 | 17.8 | 391 | 3 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 391 | 0 | 0 | 39.791 | 163.5417 | 23.1716 | 86.148 | -75 | 0.30728 | 191.2248 | -1.3232 | 389.6768 | 123.5207 | 0 | 123.5207 | 64.04 | 123.5207 | 6/12/14:00
6 | 12 | 1900-01-14 | 18.9 | 338 | 6 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 338 | 0 | 0 | 39.791 | 163.5833 | 23.1742 | 86.148 | -75 | 0.29893 | 206.2227 | -2.291 | 335.709 | 106.4139 | 0 | 106.4139 | 66.02 | 106.4139 | 6/12/15:00
6 | 12 | 1900-01-15 | 18.3 | 312 | 4 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 312 | 0 | 0 | 39.791 | 163.625 | 23.1768 | 86.148 | -75 | 0.29057 | 221.2206 | -1.1177 | 310.8823 | 98.5442 | 0 | 98.5442 | 64.94 | 98.5442 | 6/12/16:00
6 | 12 | 1900-01-16 | 18.9 | 306 | 2 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 306 | 0 | 0 | 39.791 | 163.6667 | 23.1795 | 86.148 | -75 | 0.28221 | 236.2186 | -0.28169 | 305.7183 | 96.9074 | 0 | 96.9074 | 66.02 | 96.9074 | 6/12/17:00
6 | 12 | 1900-01-17 | 18.3 | 195 | 2 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 195 | 0 | 0 | 39.791 | 163.7083 | 23.1821 | 86.148 | -75 | 0.27385 | 251.2165 | 0.048993 | 195.049 | 61.8271 | 0 | 61.8271 | 64.94 | 61.8271 | 6/12/18:00
6 | 12 | 1900-01-18 | 18.3 | 106 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 106 | 0 | 0 | 39.791 | 163.75 | 23.1847 | 86.148 | -75 | 0.26548 | 266.2144 | 0.20533 | 106.2053 | 33.6652 | 0 | 33.6652 | 64.94 | 33.6652 | 6/12/19:00
6 | 12 | 1900-01-19 | 17.8 | 41 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 41 | 0 | 0 | 39.791 | 163.7917 | 23.1873 | 86.148 | -75 | 0.25711 | 281.2123 | 0 | 41 | 12.9963 | 0 | 12.9963 | 64.04 | 12.9963 | 6/12/20:00
6 | 12 | 1900-01-20 | 17.2 | 2 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 2 | 0 | 0 | 39.791 | 163.8333 | 23.1898 | 86.148 | -75 | 0.24873 | 296.2102 | 0 | 2 | 0.63397 | 0 | 0.63397 | 62.96 | 0.63397 | 6/12/21:00
6 | 12 | 1900-01-21 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 163.875 | 23.1924 | 86.148 | -75 | 0.24035 | 311.2081 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 6/12/22:00
6 | 12 | 1900-01-22 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 163.9167 | 23.195 | 86.148 | -75 | 0.23196 | 326.206 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 6/12/23:00
6 | 12 | 1900-01-23 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 163.9583 | 23.1975 | 86.148 | -75 | 0.22357 | 341.2039 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 6/12/24:00
6 | 13 | 1899-12-31 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 164 | 23.2 | 86.148 | -75 | 0.21518 | -3.7982 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/13/1:00
6 | 13 | 1900-01-01 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 164.0417 | 23.2025 | 86.148 | -75 | 0.20678 | 11.1997 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/13/2:00
6 | 13 | 1900-01-02 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 164.0833 | 23.205 | 86.148 | -75 | 0.19838 | 26.1976 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/13/3:00
6 | 13 | 1900-01-03 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 164.125 | 23.2075 | 86.148 | -75 | 0.18997 | 41.1955 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/13/4:00
6 | 13 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 164.1667 | 23.21 | 86.148 | -75 | 0.18156 | 56.1934 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/13/5:00
6 | 13 | 1900-01-05 | 16.7 | 19 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 19 | 0 | 0 | 39.791 | 164.2083 | 23.2125 | 86.148 | -75 | 0.17314 | 71.1913 | 0 | 19 | 6.0227 | 0 | 6.0227 | 62.06 | 6.0227 | 6/13/6:00
6 | 13 | 1900-01-06 | 16.7 | 66 | 254 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 66 | 0 | 0 | 39.791 | 164.25 | 23.2149 | 86.148 | -75 | 0.16472 | 86.1892 | 75.9981 | 141.9981 | 45.0109 | 0 | 45.0109 | 62.06 | 45.0109 | 6/13/7:00
6 | 13 | 1900-01-07 | 18.3 | 93 | 548 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 93 | 0 | 0 | 39.791 | 164.2917 | 23.2173 | 86.148 | -75 | 0.15629 | 101.1871 | 63.1805 | 156.1805 | 49.5065 | 0 | 49.5065 | 64.94 | 49.5065 | 6/13/8:00
6 | 13 | 1900-01-08 | 18.9 | 131 | 637 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 131 | 0 | 0 | 39.791 | 164.3333 | 23.2198 | 86.148 | -75 | 0.14786 | 116.185 | -37.7609 | 93.2391 | 29.5552 | 0 | 29.5552 | 66.02 | 29.5552 | 6/13/9:00
6 | 13 | 1900-01-09 | 21.1 | 237 | 328 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 237 | 0 | 0 | 39.791 | 164.375 | 23.2222 | 86.148 | -75 | 0.13943 | 131.1829 | -69.7382 | 167.2618 | 53.0191 | 0 | 53.0191 | 69.98 | 53.0191 | 6/13/10:00
6 | 13 | 1900-01-10 | 21.7 | 329 | 610 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 329 | 0 | 0 | 39.791 | 164.4167 | 23.2246 | 86.148 | -75 | 0.13099 | 146.1807 | -203.9054 | 125.0946 | 39.6528 | 0 | 39.6528 | 71.06 | 39.6528 | 6/13/11:00
6 | 13 | 1900-01-11 | 22.8 | 348 | 399 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 348 | 0 | 0 | 39.791 | 164.4583 | 23.227 | 86.148 | -75 | 0.12255 | 161.1786 | -165.966 | 182.034 | 57.7016 | 0 | 57.7016 | 73.04 | 57.7016 | 6/13/12:00
6 | 13 | 1900-01-12 | 23.9 | 355 | 523 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 355 | 0 | 0 | 39.791 | 164.5 | 23.2293 | 86.148 | -75 | 0.11411 | 176.1765 | -236.4497 | 118.5503 | 37.5784 | 0 | 37.5784 | 75.02 | 37.5784 | 6/13/13:00
6 | 13 | 1900-01-13 | 25 | 263 | 514 | 77 | 0 | 1 | 0 | 77 | 0 | 263 | 0 | 0 | 39.791 | 164.5417 | 23.2317 | 86.148 | -75 | 0.10566 | 191.1744 | -226.2892 | 36.7108 | 11.6367 | 0 | 11.6367 | 77 | 11.6367 | 6/13/14:00
6 | 13 | 1900-01-14 | 25.6 | 238 | 734 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 238 | 0 | 0 | 39.791 | 164.5833 | 23.234 | 86.148 | -75 | 0.097203 | 206.1723 | -279.8073 | -41.8073 | -13.2522 | 0 | -13.2522 | 78.08 | -13.2522 | 6/13/15:00
6 | 13 | 1900-01-15 | 26.1 | 280 | 599 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 280 | 0 | 0 | 39.791 | 164.625 | 23.2364 | 86.148 | -75 | 0.088745 | 221.1702 | -167.1195 | 112.8805 | 35.7812 | 0 | 35.7812 | 78.98 | 35.7812 | 6/13/16:00
6 | 13 | 1900-01-16 | 26.1 | 233 | 347 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 233 | 0 | 0 | 39.791 | 164.6667 | 23.2387 | 86.148 | -75 | 0.080283 | 236.1681 | -48.7814 | 184.2186 | 58.3941 | 0 | 58.3941 | 78.98 | 58.3941 | 6/13/17:00
6 | 13 | 1900-01-17 | 26.7 | 144 | 516 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 144 | 0 | 0 | 39.791 | 164.7083 | 23.241 | 86.148 | -75 | 0.071817 | 251.166 | 12.7 | 156.7 | 49.6712 | 0 | 49.6712 | 80.06 | 49.6712 | 6/13/18:00
6 | 13 | 1900-01-18 | 25.6 | 75 | 448 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 75 | 0 | 0 | 39.791 | 164.75 | 23.2433 | 86.148 | -75 | 0.063347 | 266.1638 | 91.9868 | 166.9868 | 52.9319 | 0 | 52.9319 | 78.08 | 52.9319 | 6/13/19:00
6 | 13 | 1900-01-19 | 23.3 | 37 | 143 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 37 | 0 | 0 | 39.791 | 164.7917 | 23.2456 | 86.148 | -75 | 0.054874 | 281.1617 | 55.6634 | 92.6634 | 29.3727 | 0 | 29.3727 | 73.94 | 29.3727 | 6/13/20:00
6 | 13 | 1900-01-20 | 21.7 | 0 | 1 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 164.8333 | 23.2479 | 86.148 | -75 | 0.046396 | 296.1596 | 0.56386 | 0.56386 | 0.17874 | 0 | 0.17874 | 71.06 | 0.17874 | 6/13/21:00
6 | 13 | 1900-01-21 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 164.875 | 23.2501 | 86.148 | -75 | 0.037914 | 311.1575 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/13/22:00
6 | 13 | 1900-01-22 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 164.9167 | 23.2524 | 86.148 | -75 | 0.029429 | 326.1554 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/13/23:00
6 | 13 | 1900-01-23 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 164.9583 | 23.2546 | 86.148 | -75 | 0.02094 | 341.1532 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/13/24:00
6 | 14 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 165 | 23.2568 | 86.148 | -75 | 0.012447 | -3.8489 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/14/1:00
6 | 14 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 165.0417 | 23.259 | 86.148 | -75 | 0.00395 | 11.149 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/14/2:00
6 | 14 | 1900-01-02 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 165.0833 | 23.2612 | 86.148 | -75 | -0.0045505 | 26.1469 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 6/14/3:00
6 | 14 | 1900-01-03 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 165.125 | 23.2634 | 86.148 | -75 | -0.013055 | 41.1447 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 6/14/4:00
6 | 14 | 1900-01-04 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 165.1667 | 23.2656 | 86.148 | -75 | -0.021563 | 56.1426 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 6/14/5:00
6 | 14 | 1900-01-05 | 17.8 | 11 | 4 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 11 | 0 | 0 | 39.791 | 165.2083 | 23.2678 | 86.148 | -75 | -0.030074 | 71.1405 | 1.924 | 12.924 | 4.0967 | 0 | 4.0967 | 64.04 | 4.0967 | 6/14/6:00
6 | 14 | 1900-01-06 | 18.3 | 53 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 53 | 0 | 0 | 39.791 | 165.25 | 23.2699 | 86.148 | -75 | -0.038589 | 86.1384 | 0.30038 | 53.3004 | 16.8953 | 0 | 16.8953 | 64.94 | 16.8953 | 6/14/7:00
6 | 14 | 1900-01-07 | 20 | 142 | 151 | 68 | 0 | 1 | 0 | 68 | 0 | 142 | 0 | 0 | 39.791 | 165.2917 | 23.272 | 86.148 | -75 | -0.047108 | 101.1362 | 17.5953 | 159.5953 | 50.5889 | 0 | 50.5889 | 68 | 50.5889 | 6/14/8:00
6 | 14 | 1900-01-08 | 21.1 | 161 | 572 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 161 | 0 | 0 | 39.791 | 165.3333 | 23.2742 | 86.148 | -75 | -0.055631 | 116.1341 | -33.194 | 127.806 | 40.5123 | 0 | 40.5123 | 69.98 | 40.5123 | 6/14/9:00
6 | 14 | 1900-01-09 | 23.3 | 309 | 239 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 309 | 0 | 0 | 39.791 | 165.375 | 23.2763 | 86.148 | -75 | -0.064157 | 131.132 | -50.5248 | 258.4752 | 81.9321 | 0 | 81.9321 | 73.94 | 81.9321 | 6/14/10:00
6 | 14 | 1900-01-10 | 25 | 306 | 521 | 77 | 0 | 1 | 0 | 77 | 0 | 306 | 0 | 0 | 39.791 | 165.4167 | 23.2784 | 86.148 | -75 | -0.072686 | 146.1298 | -173.5624 | 132.4376 | 41.9804 | 0 | 41.9804 | 77 | 41.9804 | 6/14/11:00
6 | 14 | 1900-01-11 | 26.1 | 312 | 498 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 312 | 0 | 0 | 39.791 | 165.4583 | 23.2804 | 86.148 | -75 | -0.081219 | 161.1277 | -206.6378 | 105.3622 | 33.398 | 0 | 33.398 | 78.98 | 33.398 | 6/14/12:00
6 | 14 | 1900-01-12 | 27.2 | 300 | 639 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 300 | 0 | 0 | 39.791 | 165.5 | 23.2825 | 86.148 | -75 | -0.089756 | 176.1256 | -288.3384 | 11.6616 | 3.6965 | 0 | 3.6965 | 80.96 | 3.6965 | 6/14/13:00
6 | 14 | 1900-01-13 | 27.8 | 434 | 65 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 434 | 0 | 0 | 39.791 | 165.5417 | 23.2846 | 86.148 | -75 | -0.098296 | 191.1234 | -28.5711 | 405.4289 | 128.5139 | 0 | 128.5139 | 82.04 | 128.5139 | 6/14/14:00
6 | 14 | 1900-01-14 | 27.2 | 428 | 344 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 428 | 0 | 0 | 39.791 | 165.5833 | 23.2866 | 86.148 | -75 | -0.10684 | 206.1213 | -130.9596 | 297.0404 | 94.1566 | 0 | 94.1566 | 80.96 | 94.1566 | 6/14/15:00
6 | 14 | 1900-01-15 | 27.2 | 305 | 247 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 305 | 0 | 0 | 39.791 | 165.625 | 23.2887 | 86.148 | -75 | -0.11539 | 221.1192 | -68.8306 | 236.1694 | 74.8616 | 0 | 74.8616 | 80.96 | 74.8616 | 6/14/16:00
6 | 14 | 1900-01-16 | 27.2 | 253 | 56 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 253 | 0 | 0 | 39.791 | 165.6667 | 23.2907 | 86.148 | -75 | -0.12394 | 236.117 | -7.8633 | 245.1367 | 77.7041 | 0 | 77.7041 | 80.96 | 77.7041 | 6/14/17:00
6 | 14 | 1900-01-17 | 27.2 | 161 | 422 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 161 | 0 | 0 | 39.791 | 165.7083 | 23.2927 | 86.148 | -75 | -0.13249 | 251.1149 | 10.3962 | 171.3962 | 54.3296 | 0 | 54.3296 | 80.96 | 54.3296 | 6/14/18:00
6 | 14 | 1900-01-18 | 26.7 | 89 | 193 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 89 | 0 | 0 | 39.791 | 165.75 | 23.2947 | 86.148 | -75 | -0.14105 | 266.1127 | 39.6123 | 128.6123 | 40.7678 | 0 | 40.7678 | 80.06 | 40.7678 | 6/14/19:00
6 | 14 | 1900-01-19 | 24.4 | 41 | 90 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 41 | 0 | 0 | 39.791 | 165.7917 | 23.2967 | 86.148 | -75 | -0.14961 | 281.1106 | 35.0198 | 76.0198 | 24.0969 | 0 | 24.0969 | 75.92 | 24.0969 | 6/14/20:00
6 | 14 | 1900-01-20 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 165.8333 | 23.2986 | 86.148 | -75 | -0.15817 | 296.1085 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/14/21:00
6 | 14 | 1900-01-21 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 165.875 | 23.3006 | 86.148 | -75 | -0.16674 | 311.1063 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/14/22:00
6 | 14 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 165.9167 | 23.3025 | 86.148 | -75 | -0.17531 | 326.1042 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/14/23:00
6 | 14 | 1900-01-23 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 165.9583 | 23.3045 | 86.148 | -75 | -0.18388 | 341.102 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/14/24:00
6 | 15 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 166 | 23.3064 | 86.148 | -75 | -0.19246 | -3.9001 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/15/1:00
6 | 15 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 166.0417 | 23.3083 | 86.148 | -75 | -0.20104 | 11.0977 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/15/2:00
6 | 15 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 166.0833 | 23.3102 | 86.148 | -75 | -0.20962 | 26.0956 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 6/15/3:00
6 | 15 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 166.125 | 23.3121 | 86.148 | -75 | -0.2182 | 41.0934 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/15/4:00
6 | 15 | 1900-01-04 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 166.1667 | 23.3139 | 86.148 | -75 | -0.22679 | 56.0913 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 6/15/5:00
6 | 15 | 1900-01-05 | 18.3 | 15 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 15 | 0 | 0 | 39.791 | 166.2083 | 23.3158 | 86.148 | -75 | -0.23539 | 71.0892 | 0.482 | 15.482 | 4.9075 | 0 | 4.9075 | 64.94 | 4.9075 | 6/15/6:00
6 | 15 | 1900-01-06 | 19.4 | 80 | 34 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 80 | 0 | 0 | 39.791 | 166.25 | 23.3176 | 86.148 | -75 | -0.24398 | 86.087 | 10.2503 | 90.2503 | 28.6078 | 0 | 28.6078 | 66.92 | 28.6078 | 6/15/7:00
6 | 15 | 1900-01-07 | 21.7 | 133 | 80 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 133 | 0 | 0 | 39.791 | 166.2917 | 23.3194 | 86.148 | -75 | -0.25258 | 101.0849 | 9.4145 | 142.4145 | 45.1429 | 0 | 45.1429 | 71.06 | 45.1429 | 6/15/8:00
6 | 15 | 1900-01-08 | 22.8 | 222 | 14 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 222 | 0 | 0 | 39.791 | 166.3333 | 23.3213 | 86.148 | -75 | -0.26118 | 116.0827 | -0.79618 | 221.2038 | 70.1177 | 0 | 70.1177 | 73.04 | 70.1177 | 6/15/9:00
6 | 15 | 1900-01-09 | 23.9 | 222 | 4 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 222 | 0 | 0 | 39.791 | 166.375 | 23.3231 | 86.148 | -75 | -0.26978 | 131.0806 | -0.84112 | 221.1589 | 70.1035 | 0 | 70.1035 | 75.02 | 70.1035 | 6/15/10:00
6 | 15 | 1900-01-10 | 24.4 | 264 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 264 | 0 | 0 | 39.791 | 166.4167 | 23.3249 | 86.148 | -75 | -0.27839 | 146.0784 | 0 | 264 | 83.6834 | 0 | 83.6834 | 75.92 | 83.6834 | 6/15/11:00
6 | 15 | 1900-01-11 | 25 | 346 | 4 | 77 | 0 | 1 | 0 | 77 | 0 | 346 | 0 | 0 | 39.791 | 166.4583 | 23.3266 | 86.148 | -75 | -0.287 | 161.0763 | -1.6561 | 344.3439 | 109.151 | 0 | 109.151 | 77 | 109.151 | 6/15/12:00
6 | 15 | 1900-01-12 | 26.7 | 390 | 213 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 390 | 0 | 0 | 39.791 | 166.5 | 23.3284 | 86.148 | -75 | -0.29561 | 176.0741 | -95.9516 | 294.0484 | 93.2082 | 0 | 93.2082 | 80.06 | 93.2082 | 6/15/13:00
6 | 15 | 1900-01-13 | 26.1 | 386 | 364 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 386 | 0 | 0 | 39.791 | 166.5417 | 23.3302 | 86.148 | -75 | -0.30423 | 191.0719 | -159.786 | 226.214 | 71.7059 | 0 | 71.7059 | 78.98 | 71.7059 | 6/15/14:00
6 | 15 | 1900-01-14 | 27.2 | 373 | 101 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 373 | 0 | 0 | 39.791 | 166.5833 | 23.3319 | 86.148 | -75 | -0.31285 | 206.0698 | -38.4098 | 334.5902 | 106.0592 | 0 | 106.0592 | 80.96 | 106.0592 | 6/15/15:00
6 | 15 | 1900-01-15 | 26.7 | 412 | 69 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 412 | 0 | 0 | 39.791 | 166.625 | 23.3336 | 86.148 | -75 | -0.32147 | 221.0676 | -19.2125 | 392.7875 | 124.5068 | 0 | 124.5068 | 80.06 | 124.5068 | 6/15/16:00
6 | 15 | 1900-01-16 | 27.2 | 257 | 149 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 257 | 0 | 0 | 39.791 | 166.6667 | 23.3353 | 86.148 | -75 | -0.33009 | 236.0655 | -20.9125 | 236.0875 | 74.8356 | 0 | 74.8356 | 80.96 | 74.8356 | 6/15/17:00
6 | 15 | 1900-01-17 | 27.2 | 232 | 123 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 232 | 0 | 0 | 39.791 | 166.7083 | 23.337 | 86.148 | -75 | -0.33872 | 251.0633 | 3.0217 | 235.0217 | 74.4978 | 0 | 74.4978 | 80.96 | 74.4978 | 6/15/18:00
6 | 15 | 1900-01-18 | 26.7 | 113 | 184 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 113 | 0 | 0 | 39.791 | 166.75 | 23.3387 | 86.148 | -75 | -0.34735 | 266.0612 | 37.7346 | 150.7346 | 47.7802 | 0 | 47.7802 | 80.06 | 47.7802 | 6/15/19:00
6 | 15 | 1900-01-19 | 24.4 | 41 | 18 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 41 | 0 | 0 | 39.791 | 166.7917 | 23.3404 | 86.148 | -75 | -0.35598 | 281.059 | 7 | 48 | 15.2152 | 0 | 15.2152 | 75.92 | 15.2152 | 6/15/20:00
6 | 15 | 1900-01-20 | 23.3 | 2 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 2 | 0 | 0 | 39.791 | 166.8333 | 23.3421 | 86.148 | -75 | -0.36461 | 296.0568 | 0 | 2 | 0.63397 | 0 | 0.63397 | 73.94 | 0.63397 | 6/15/21:00
6 | 15 | 1900-01-21 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 166.875 | 23.3437 | 86.148 | -75 | -0.37325 | 311.0547 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/15/22:00
6 | 15 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 166.9167 | 23.3454 | 86.148 | -75 | -0.38189 | 326.0525 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/15/23:00
6 | 15 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 166.9583 | 23.347 | 86.148 | -75 | -0.39053 | 341.0504 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/15/24:00
6 | 16 | 1899-12-31 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 167 | 23.3486 | 86.148 | -75 | -0.39918 | -3.9518 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/16/1:00
6 | 16 | 1900-01-01 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 167.0417 | 23.3502 | 86.148 | -75 | -0.40782 | 11.046 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/16/2:00
6 | 16 | 1900-01-02 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 167.0833 | 23.3518 | 86.148 | -75 | -0.41647 | 26.0439 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/16/3:00
6 | 16 | 1900-01-03 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 167.125 | 23.3534 | 86.148 | -75 | -0.42513 | 41.0417 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/16/4:00
6 | 16 | 1900-01-04 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 167.1667 | 23.3549 | 86.148 | -75 | -0.43378 | 56.0396 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/16/5:00
6 | 16 | 1900-01-05 | 20 | 17 | 28 | 68 | 0 | 1 | 0 | 68 | 0 | 17 | 0 | 0 | 39.791 | 167.2083 | 23.3565 | 86.148 | -75 | -0.44244 | 71.0374 | 13.5226 | 30.5226 | 9.6751 | 0 | 9.6751 | 68 | 9.6751 | 6/16/6:00
6 | 16 | 1900-01-06 | 21.7 | 56 | 295 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 56 | 0 | 0 | 39.791 | 167.25 | 23.358 | 86.148 | -75 | -0.4511 | 86.0352 | 89.2417 | 145.2417 | 46.0391 | 0 | 46.0391 | 71.06 | 46.0391 | 6/16/7:00
6 | 16 | 1900-01-07 | 23.9 | 91 | 546 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 91 | 0 | 0 | 39.791 | 167.2917 | 23.3596 | 86.148 | -75 | -0.45976 | 101.0331 | 64.8423 | 155.8423 | 49.3993 | 0 | 49.3993 | 75.02 | 49.3993 | 6/16/8:00
6 | 16 | 1900-01-08 | 25.6 | 171 | 596 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 171 | 0 | 0 | 39.791 | 167.3333 | 23.3611 | 86.148 | -75 | -0.46843 | 116.0309 | -33.2542 | 137.7458 | 43.663 | 0 | 43.663 | 78.08 | 43.663 | 6/16/9:00
6 | 16 | 1900-01-09 | 26.7 | 324 | 319 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 324 | 0 | 0 | 39.791 | 167.375 | 23.3626 | 86.148 | -75 | -0.47709 | 131.0287 | -66.7527 | 257.2473 | 81.5429 | 0 | 81.5429 | 80.06 | 81.5429 | 6/16/10:00
6 | 16 | 1900-01-10 | 27.8 | 308 | 514 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 308 | 0 | 0 | 39.791 | 167.4167 | 23.3641 | 86.148 | -75 | -0.48576 | 146.0266 | -170.2199 | 137.7801 | 43.6739 | 0 | 43.6739 | 82.04 | 43.6739 | 6/16/11:00
6 | 16 | 1900-01-11 | 28.9 | 362 | 491 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 362 | 0 | 0 | 39.791 | 167.4583 | 23.3655 | 86.148 | -75 | -0.49443 | 161.0244 | -202.8924 | 159.1076 | 50.4343 | 0 | 50.4343 | 84.02 | 50.4343 | 6/16/12:00
6 | 16 | 1900-01-12 | 30 | 321 | 636 | 86 | 0 | 1 | 0 | 86 | 0 | 321 | 0 | 0 | 39.791 | 167.5 | 23.367 | 86.148 | -75 | -0.50311 | 176.0222 | -286.0936 | 34.9064 | 11.0647 | 0 | 11.0647 | 86 | 11.0647 | 6/16/13:00
6 | 16 | 1900-01-13 | 30.6 | 479 | 233 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 479 | 0 | 0 | 39.791 | 167.5417 | 23.3684 | 86.148 | -75 | -0.51178 | 191.0201 | -102.1712 | 376.8288 | 119.4482 | 0 | 119.4482 | 87.08 | 119.4482 | 6/16/14:00
6 | 16 | 1900-01-14 | 31.1 | 379 | 368 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 379 | 0 | 0 | 39.791 | 167.5833 | 23.3699 | 86.148 | -75 | -0.52046 | 206.0179 | -139.8418 | 239.1582 | 75.809 | 0 | 75.809 | 87.98 | 75.809 | 6/16/15:00
6 | 16 | 1900-01-15 | 31.1 | 272 | 278 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 272 | 0 | 0 | 39.791 | 167.625 | 23.3713 | 86.148 | -75 | -0.52914 | 221.0157 | -77.3742 | 194.6258 | 61.693 | 0 | 61.693 | 87.98 | 61.693 | 6/16/16:00
6 | 16 | 1900-01-16 | 31.1 | 226 | 154 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 226 | 0 | 0 | 39.791 | 167.6667 | 23.3727 | 86.148 | -75 | -0.53782 | 236.0135 | -21.6199 | 204.3801 | 64.7849 | 0 | 64.7849 | 87.98 | 64.7849 | 6/16/17:00
6 | 16 | 1900-01-17 | 28.9 | 79 | 4 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 79 | 0 | 0 | 39.791 | 167.7083 | 23.3741 | 86.148 | -75 | -0.54651 | 251.0114 | 0.097622 | 79.0976 | 25.0726 | 0 | 25.0726 | 84.02 | 25.0726 | 6/16/18:00
6 | 16 | 1900-01-18 | 22.2 | 45 | 7 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 45 | 0 | 0 | 39.791 | 167.75 | 23.3755 | 86.148 | -75 | -0.55519 | 266.0092 | 1.4338 | 46.4338 | 14.7187 | 0 | 14.7187 | 71.96 | 14.7187 | 6/16/19:00
6 | 16 | 1900-01-19 | 22.2 | 49 | 2 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 49 | 0 | 0 | 39.791 | 167.7917 | 23.3769 | 86.148 | -75 | -0.56388 | 281.007 | 0.7772 | 49.7772 | 15.7785 | 0 | 15.7785 | 71.96 | 15.7785 | 6/16/20:00
6 | 16 | 1900-01-20 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 167.8333 | 23.3782 | 86.148 | -75 | -0.57257 | 296.0049 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/16/21:00
6 | 16 | 1900-01-21 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 167.875 | 23.3796 | 86.148 | -75 | -0.58127 | 311.0027 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/16/22:00
6 | 16 | 1900-01-22 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 167.9167 | 23.3809 | 86.148 | -75 | -0.58996 | 326.0005 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/16/23:00
6 | 16 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 167.9583 | 23.3822 | 86.148 | -75 | -0.59866 | 340.9983 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/16/24:00
6 | 17 | 1899-12-31 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 168 | 23.3835 | 86.148 | -75 | -0.60736 | -4.0038 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/17/1:00
6 | 17 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 168.0417 | 23.3848 | 86.148 | -75 | -0.61606 | 10.994 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/17/2:00
6 | 17 | 1900-01-02 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 168.0833 | 23.3861 | 86.148 | -75 | -0.62476 | 25.9918 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 6/17/3:00
6 | 17 | 1900-01-03 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 168.125 | 23.3874 | 86.148 | -75 | -0.63346 | 40.9896 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 6/17/4:00
6 | 17 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 168.1667 | 23.3886 | 86.148 | -75 | -0.64217 | 55.9875 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/17/5:00
6 | 17 | 1900-01-05 | 18.9 | 16 | 51 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 16 | 0 | 0 | 39.791 | 168.2083 | 23.3899 | 86.148 | -75 | -0.65088 | 70.9853 | 24.676 | 40.676 | 12.8936 | 0 | 12.8936 | 66.02 | 12.8936 | 6/17/6:00
6 | 17 | 1900-01-06 | 17.2 | 51 | 392 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 51 | 0 | 0 | 39.791 | 168.25 | 23.3911 | 86.148 | -75 | -0.65959 | 85.9831 | 118.9647 | 169.9647 | 53.8758 | 0 | 53.8758 | 62.96 | 53.8758 | 6/17/7:00
6 | 17 | 1900-01-07 | 18.3 | 79 | 608 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 79 | 0 | 0 | 39.791 | 168.2917 | 23.3923 | 86.148 | -75 | -0.6683 | 100.9809 | 72.813 | 151.813 | 48.1221 | 0 | 48.1221 | 64.94 | 48.1221 | 6/17/8:00
6 | 17 | 1900-01-08 | 18.9 | 104 | 730 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 104 | 0 | 0 | 39.791 | 168.3333 | 23.3935 | 86.148 | -75 | -0.67701 | 115.9787 | -40.0112 | 63.9888 | 20.2833 | 0 | 20.2833 | 66.02 | 20.2833 | 6/17/9:00
6 | 17 | 1900-01-09 | 20 | 124 | 803 | 68 | 0 | 1 | 0 | 68 | 0 | 124 | 0 | 0 | 39.791 | 168.375 | 23.3947 | 86.148 | -75 | -0.68573 | 130.9766 | -167.2884 | -43.2884 | -13.7217 | 0 | -13.7217 | 68 | -13.7217 | 6/17/10:00
6 | 17 | 1900-01-10 | 20.6 | 144 | 838 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 144 | 0 | 0 | 39.791 | 168.4167 | 23.3959 | 86.148 | -75 | -0.69444 | 145.9744 | -276.8254 | -132.8254 | -42.1033 | 0 | -42.1033 | 69.08 | -42.1033 | 6/17/11:00
6 | 17 | 1900-01-11 | 21.1 | 154 | 860 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 154 | 0 | 0 | 39.791 | 168.4583 | 23.3971 | 86.148 | -75 | -0.70316 | 160.9722 | -354.7768 | -200.7768 | -63.6427 | 0 | -63.6427 | 69.98 | -63.6427 | 6/17/12:00
6 | 17 | 1900-01-12 | 21.7 | 170 | 864 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 170 | 0 | 0 | 39.791 | 168.5 | 23.3982 | 86.148 | -75 | -0.71188 | 175.97 | -388.1964 | -218.1964 | -69.1645 | 0 | -69.1645 | 71.06 | -69.1645 | 6/17/13:00
6 | 17 | 1900-01-13 | 22.2 | 150 | 805 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 150 | 0 | 0 | 39.791 | 168.5417 | 23.3994 | 86.148 | -75 | -0.7206 | 190.9678 | -352.7078 | -202.7078 | -64.2548 | 0 | -64.2548 | 71.96 | -64.2548 | 6/17/14:00
6 | 17 | 1900-01-14 | 22.8 | 147 | 815 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 147 | 0 | 0 | 39.791 | 168.5833 | 23.4005 | 86.148 | -75 | -0.72932 | 205.9657 | -309.5581 | -162.5581 | -51.5281 | 0 | -51.5281 | 73.04 | -51.5281 | 6/17/15:00
6 | 17 | 1900-01-15 | 23.3 | 143 | 758 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 143 | 0 | 0 | 39.791 | 168.625 | 23.4016 | 86.148 | -75 | -0.73805 | 220.9635 | -210.9614 | -67.9614 | -21.5426 | 0 | -21.5426 | 73.94 | -21.5426 | 6/17/16:00
6 | 17 | 1900-01-16 | 23.3 | 174 | 553 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 174 | 0 | 0 | 39.791 | 168.6667 | 23.4027 | 86.148 | -75 | -0.74677 | 235.9613 | -77.7099 | 96.2901 | 30.5223 | 0 | 30.5223 | 73.94 | 30.5223 | 6/17/17:00
6 | 17 | 1900-01-17 | 22.8 | 119 | 605 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 119 | 0 | 0 | 39.791 | 168.7083 | 23.4038 | 86.148 | -75 | -0.7555 | 250.9591 | 14.6131 | 133.6131 | 42.353 | 0 | 42.353 | 73.04 | 42.353 | 6/17/18:00
6 | 17 | 1900-01-18 | 22.2 | 78 | 440 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 78 | 0 | 0 | 39.791 | 168.75 | 23.4049 | 86.148 | -75 | -0.76423 | 265.9569 | 89.9811 | 167.9811 | 53.2471 | 0 | 53.2471 | 71.96 | 53.2471 | 6/17/19:00
6 | 17 | 1900-01-19 | 20.6 | 35 | 219 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 35 | 0 | 0 | 39.791 | 168.7917 | 23.406 | 86.148 | -75 | -0.77296 | 280.9548 | 85.0235 | 120.0235 | 38.0454 | 0 | 38.0454 | 69.08 | 38.0454 | 6/17/20:00
6 | 17 | 1900-01-20 | 18.9 | 2 | 3 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 2 | 0 | 0 | 39.791 | 168.8333 | 23.407 | 86.148 | -75 | -0.78169 | 295.9526 | 1.6885 | 3.6885 | 1.1692 | 0 | 1.1692 | 66.02 | 1.1692 | 6/17/21:00
6 | 17 | 1900-01-21 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 168.875 | 23.4081 | 86.148 | -75 | -0.79043 | 310.9504 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 6/17/22:00
6 | 17 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 168.9167 | 23.4091 | 86.148 | -75 | -0.79916 | 325.9482 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 6/17/23:00
6 | 17 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 168.9583 | 23.4101 | 86.148 | -75 | -0.8079 | 340.946 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 6/17/24:00
6 | 18 | 1899-12-31 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 169 | 23.4111 | 86.148 | -75 | -0.81663 | -4.0562 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 6/18/1:00
6 | 18 | 1900-01-01 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 169.0417 | 23.4121 | 86.148 | -75 | -0.82537 | 10.9417 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 6/18/2:00
6 | 18 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 169.0833 | 23.4131 | 86.148 | -75 | -0.83411 | 25.9395 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 6/18/3:00
6 | 18 | 1900-01-03 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 169.125 | 23.4141 | 86.148 | -75 | -0.84285 | 40.9373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/18/4:00
6 | 18 | 1900-01-04 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 169.1667 | 23.415 | 86.148 | -75 | -0.85159 | 55.9351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/18/5:00
6 | 18 | 1900-01-05 | 11.7 | 14 | 10 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 14 | 0 | 0 | 39.791 | 169.2083 | 23.4159 | 86.148 | -75 | -0.86034 | 70.9329 | 4.8467 | 18.8467 | 5.9741 | 5.9741 | 0 | 0 | 0 | 6/18/6:00
6 | 18 | 1900-01-06 | 14.4 | 81 | 166 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 81 | 0 | 0 | 39.791 | 169.25 | 23.4169 | 86.148 | -75 | -0.86908 | 85.9307 | 50.5269 | 131.5269 | 41.6917 | 0 | 41.6917 | 57.92 | 41.6917 | 6/18/7:00
6 | 18 | 1900-01-07 | 16.7 | 156 | 374 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 156 | 0 | 0 | 39.791 | 169.2917 | 23.4178 | 86.148 | -75 | -0.87783 | 100.9285 | 45.1335 | 201.1335 | 63.7558 | 0 | 63.7558 | 62.06 | 63.7558 | 6/18/8:00
6 | 18 | 1900-01-08 | 18.9 | 204 | 516 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 204 | 0 | 0 | 39.791 | 169.3333 | 23.4187 | 86.148 | -75 | -0.88657 | 115.9264 | -27.8195 | 176.1805 | 55.8461 | 0 | 55.8461 | 66.02 | 55.8461 | 6/18/9:00
6 | 18 | 1900-01-09 | 20 | 306 | 426 | 68 | 0 | 1 | 0 | 68 | 0 | 306 | 0 | 0 | 39.791 | 169.375 | 23.4196 | 86.148 | -75 | -0.89532 | 130.9242 | -88.3954 | 217.6046 | 68.9769 | 0 | 68.9769 | 68 | 68.9769 | 6/18/10:00
6 | 18 | 1900-01-10 | 21.7 | 318 | 482 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 318 | 0 | 0 | 39.791 | 169.4167 | 23.4204 | 86.148 | -75 | -0.90407 | 145.922 | -158.8767 | 159.1233 | 50.4393 | 0 | 50.4393 | 71.06 | 50.4393 | 6/18/11:00
6 | 18 | 1900-01-11 | 22.8 | 427 | 391 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 427 | 0 | 0 | 39.791 | 169.4583 | 23.4213 | 86.148 | -75 | -0.91282 | 160.9198 | -161.0726 | 265.9274 | 84.2944 | 0 | 84.2944 | 73.04 | 84.2944 | 6/18/12:00
6 | 18 | 1900-01-12 | 23.9 | 416 | 361 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 416 | 0 | 0 | 39.791 | 169.5 | 23.4222 | 86.148 | -75 | -0.92157 | 175.9176 | -162.047 | 253.953 | 80.4987 | 0 | 80.4987 | 75.02 | 80.4987 | 6/18/13:00
6 | 18 | 1900-01-13 | 24.4 | 402 | 352 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 402 | 0 | 0 | 39.791 | 169.5417 | 23.423 | 86.148 | -75 | -0.93032 | 190.9154 | -154.142 | 247.858 | 78.5667 | 0 | 78.5667 | 75.92 | 78.5667 | 6/18/14:00
6 | 18 | 1900-01-14 | 24.4 | 329 | 500 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 329 | 0 | 0 | 39.791 | 169.5833 | 23.4238 | 86.148 | -75 | -0.93908 | 205.9132 | -189.8788 | 139.1212 | 44.099 | 0 | 44.099 | 75.92 | 44.099 | 6/18/15:00
6 | 18 | 1900-01-15 | 25.6 | 281 | 574 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 281 | 0 | 0 | 39.791 | 169.625 | 23.4246 | 86.148 | -75 | -0.94783 | 220.911 | -159.8061 | 121.1939 | 38.4163 | 0 | 38.4163 | 78.08 | 38.4163 | 6/18/16:00
6 | 18 | 1900-01-16 | 25.6 | 277 | 504 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 277 | 0 | 0 | 39.791 | 169.6667 | 23.4254 | 86.148 | -75 | -0.95658 | 235.9089 | -70.9424 | 206.0576 | 65.3167 | 0 | 65.3167 | 78.08 | 65.3167 | 6/18/17:00
6 | 18 | 1900-01-17 | 25 | 191 | 377 | 77 | 0 | 1 | 0 | 77 | 0 | 191 | 0 | 0 | 39.791 | 169.7083 | 23.4262 | 86.148 | -75 | -0.96534 | 250.9067 | 8.9772 | 199.9772 | 63.3893 | 0 | 63.3893 | 77 | 63.3893 | 6/18/18:00
6 | 18 | 1900-01-18 | 23.9 | 122 | 268 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 122 | 0 | 0 | 39.791 | 169.75 | 23.427 | 86.148 | -75 | -0.9741 | 265.9045 | 54.6969 | 176.6969 | 56.0098 | 0 | 56.0098 | 75.02 | 56.0098 | 6/18/19:00
6 | 18 | 1900-01-19 | 22.8 | 42 | 40 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 42 | 0 | 0 | 39.791 | 169.7917 | 23.4278 | 86.148 | -75 | -0.98285 | 280.9023 | 15.5121 | 57.5121 | 18.2303 | 0 | 18.2303 | 73.04 | 18.2303 | 6/18/20:00
6 | 18 | 1900-01-20 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 169.8333 | 23.4285 | 86.148 | -75 | -0.99161 | 295.9001 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/18/21:00
6 | 18 | 1900-01-21 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 169.875 | 23.4292 | 86.148 | -75 | -1.0004 | 310.8979 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/18/22:00
6 | 18 | 1900-01-22 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 169.9167 | 23.43 | 86.148 | -75 | -1.0091 | 325.8957 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 6/18/23:00
6 | 18 | 1900-01-23 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 169.9583 | 23.4307 | 86.148 | -75 | -1.0179 | 340.8935 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 6/18/24:00
6 | 19 | 1899-12-31 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 170 | 23.4314 | 86.148 | -75 | -1.0266 | -4.1087 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 6/19/1:00
6 | 19 | 1900-01-01 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 170.0417 | 23.432 | 86.148 | -75 | -1.0354 | 10.8891 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 6/19/2:00
6 | 19 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 170.0833 | 23.4327 | 86.148 | -75 | -1.0442 | 25.887 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 6/19/3:00
6 | 19 | 1900-01-03 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 170.125 | 23.4334 | 86.148 | -75 | -1.0529 | 40.8848 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 6/19/4:00
6 | 19 | 1900-01-04 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 170.1667 | 23.434 | 86.148 | -75 | -1.0617 | 55.8826 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 6/19/5:00
6 | 19 | 1900-01-05 | 14.4 | 18 | 53 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 18 | 0 | 0 | 39.791 | 170.2083 | 23.4347 | 86.148 | -75 | -1.0705 | 70.8804 | 25.7285 | 43.7285 | 13.8612 | 0 | 13.8612 | 57.92 | 13.8612 | 6/19/6:00
6 | 19 | 1900-01-06 | 16.7 | 75 | 249 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 75 | 0 | 0 | 39.791 | 170.25 | 23.4353 | 86.148 | -75 | -1.0792 | 85.8782 | 75.9961 | 150.9961 | 47.8631 | 0 | 47.8631 | 62.06 | 47.8631 | 6/19/7:00
6 | 19 | 1900-01-07 | 19.4 | 131 | 448 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 131 | 0 | 0 | 39.791 | 170.2917 | 23.4359 | 86.148 | -75 | -1.088 | 100.876 | 54.4393 | 185.4393 | 58.781 | 0 | 58.781 | 66.92 | 58.781 | 6/19/8:00
6 | 19 | 1900-01-08 | 22.2 | 105 | 723 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 105 | 0 | 0 | 39.791 | 170.3333 | 23.4365 | 86.148 | -75 | -1.0968 | 115.8738 | -38.3974 | 66.6026 | 21.1119 | 0 | 21.1119 | 71.96 | 21.1119 | 6/19/9:00
6 | 19 | 1900-01-09 | 24.4 | 126 | 787 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 126 | 0 | 0 | 39.791 | 170.375 | 23.4371 | 86.148 | -75 | -1.1055 | 130.8716 | -162.7295 | -36.7295 | -11.6426 | 0 | -11.6426 | 75.92 | -11.6426 | 6/19/10:00
6 | 19 | 1900-01-10 | 25.6 | 144 | 788 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 144 | 0 | 0 | 39.791 | 170.4167 | 23.4376 | 86.148 | -75 | -1.1143 | 145.8694 | -259.2561 | -115.2561 | -36.5342 | 0 | -36.5342 | 78.08 | -36.5342 | 6/19/11:00
6 | 19 | 1900-01-11 | 26.7 | 135 | 815 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 135 | 0 | 0 | 39.791 | 170.4583 | 23.4382 | 86.148 | -75 | -1.1231 | 160.8672 | -335.3568 | -200.3568 | -63.5096 | 0 | -63.5096 | 80.06 | -63.5096 | 6/19/12:00
6 | 19 | 1900-01-12 | 27.8 | 198 | 778 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 198 | 0 | 0 | 39.791 | 170.5 | 23.4387 | 86.148 | -75 | -1.1318 | 175.865 | -348.9947 | -150.9947 | -47.8627 | 0 | -47.8627 | 82.04 | -47.8627 | 6/19/13:00
6 | 19 | 1900-01-13 | 28.9 | 247 | 667 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 247 | 0 | 0 | 39.791 | 170.5417 | 23.4393 | 86.148 | -75 | -1.1406 | 190.8629 | -291.9951 | -44.9951 | -14.2627 | 0 | -14.2627 | 84.02 | -14.2627 | 6/19/14:00
6 | 19 | 1900-01-14 | 28.9 | 162 | 826 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 162 | 0 | 0 | 39.791 | 170.5833 | 23.4398 | 86.148 | -75 | -1.1494 | 205.8607 | -313.7148 | -151.7148 | -48.0909 | 0 | -48.0909 | 84.02 | -48.0909 | 6/19/15:00
6 | 19 | 1900-01-15 | 29.4 | 153 | 750 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 153 | 0 | 0 | 39.791 | 170.625 | 23.4403 | 86.148 | -75 | -1.1581 | 220.8585 | -208.9559 | -55.9559 | -17.737 | 0 | -17.737 | 84.92 | -17.737 | 6/19/16:00
6 | 19 | 1900-01-16 | 30 | 177 | 572 | 86 | 0 | 1 | 0 | 86 | 0 | 177 | 0 | 0 | 39.791 | 170.6667 | 23.4408 | 86.148 | -75 | -1.1669 | 235.8563 | -80.7042 | 96.2958 | 30.5241 | 0 | 30.5241 | 86 | 30.5241 | 6/19/17:00
6 | 19 | 1900-01-17 | 29.4 | 108 | 612 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 108 | 0 | 0 | 39.791 | 170.7083 | 23.4412 | 86.148 | -75 | -1.1757 | 250.8541 | 14.3092 | 122.3092 | 38.7699 | 0 | 38.7699 | 84.92 | 38.7699 | 6/19/18:00
6 | 19 | 1900-01-18 | 28.3 | 90 | 407 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 90 | 0 | 0 | 39.791 | 170.75 | 23.4417 | 86.148 | -75 | -1.1844 | 265.8519 | 82.8669 | 172.8669 | 54.7958 | 0 | 54.7958 | 82.94 | 54.7958 | 6/19/19:00
6 | 19 | 1900-01-19 | 25.6 | 42 | 135 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 42 | 0 | 0 | 39.791 | 170.7917 | 23.4422 | 86.148 | -75 | -1.1932 | 280.8497 | 52.2855 | 94.2855 | 29.8869 | 0 | 29.8869 | 78.08 | 29.8869 | 6/19/20:00
6 | 19 | 1900-01-20 | 23.3 | 1 | 3 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 1 | 0 | 0 | 39.791 | 170.8333 | 23.4426 | 86.148 | -75 | -1.202 | 295.8475 | 1.6859 | 2.6859 | 0.85137 | 0 | 0.85137 | 73.94 | 0.85137 | 6/19/21:00
6 | 19 | 1900-01-21 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 170.875 | 23.443 | 86.148 | -75 | -1.2107 | 310.8453 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/19/22:00
6 | 19 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 170.9167 | 23.4435 | 86.148 | -75 | -1.2195 | 325.8431 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/19/23:00
6 | 19 | 1900-01-23 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 170.9583 | 23.4439 | 86.148 | -75 | -1.2283 | 340.8409 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/19/24:00
6 | 20 | 1899-12-31 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 171 | 23.4442 | 86.148 | -75 | -1.237 | -4.1613 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/20/1:00
6 | 20 | 1900-01-01 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 171.0417 | 23.4446 | 86.148 | -75 | -1.2458 | 10.8365 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/20/2:00
6 | 20 | 1900-01-02 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 171.0833 | 23.445 | 86.148 | -75 | -1.2546 | 25.8344 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/20/3:00
6 | 20 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 171.125 | 23.4453 | 86.148 | -75 | -1.2633 | 40.8322 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/20/4:00
6 | 20 | 1900-01-04 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 171.1667 | 23.4457 | 86.148 | -75 | -1.2721 | 55.83 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/20/5:00
6 | 20 | 1900-01-05 | 20.6 | 18 | 33 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 18 | 0 | 0 | 39.791 | 171.2083 | 23.446 | 86.148 | -75 | -1.2809 | 70.8278 | 16.043 | 34.043 | 10.791 | 0 | 10.791 | 69.08 | 10.791 | 6/20/6:00
6 | 20 | 1900-01-06 | 22.8 | 73 | 199 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 73 | 0 | 0 | 39.791 | 171.25 | 23.4463 | 86.148 | -75 | -1.2897 | 85.8256 | 60.886 | 133.886 | 42.4395 | 0 | 42.4395 | 73.04 | 42.4395 | 6/20/7:00
6 | 20 | 1900-01-07 | 24.4 | 103 | 480 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 103 | 0 | 0 | 39.791 | 171.2917 | 23.4466 | 86.148 | -75 | -1.2984 | 100.8234 | 58.691 | 161.691 | 51.2532 | 0 | 51.2532 | 75.92 | 51.2532 | 6/20/8:00
6 | 20 | 1900-01-08 | 27.2 | 132 | 610 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 132 | 0 | 0 | 39.791 | 171.3333 | 23.4469 | 86.148 | -75 | -1.3072 | 115.8212 | -31.9608 | 100.0392 | 31.7107 | 0 | 31.7107 | 80.96 | 31.7107 | 6/20/9:00
6 | 20 | 1900-01-09 | 28.9 | 135 | 716 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 135 | 0 | 0 | 39.791 | 171.375 | 23.4472 | 86.148 | -75 | -1.316 | 130.819 | -147.5985 | -12.5985 | -3.9935 | 0 | -3.9935 | 84.02 | -3.9935 | 6/20/10:00
6 | 20 | 1900-01-10 | 30.6 | 156 | 754 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 156 | 0 | 0 | 39.791 | 171.4167 | 23.4474 | 86.148 | -75 | -1.3247 | 145.8168 | -247.6874 | -91.6874 | -29.0633 | 0 | -29.0633 | 87.08 | -29.0633 | 6/20/11:00
6 | 20 | 1900-01-11 | 31.1 | 232 | 645 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 232 | 0 | 0 | 39.791 | 171.4583 | 23.4477 | 86.148 | -75 | -1.3335 | 160.8146 | -265.1742 | -33.1742 | -10.5157 | 0 | -10.5157 | 87.98 | -10.5157 | 6/20/12:00
6 | 20 | 1900-01-12 | 31.1 | 230 | 665 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 230 | 0 | 0 | 39.791 | 171.5 | 23.4479 | 86.148 | -75 | -1.3423 | 175.8124 | -298.1787 | -68.1787 | -21.6115 | 0 | -21.6115 | 87.98 | -21.6115 | 6/20/13:00
6 | 20 | 1900-01-13 | 31.7 | 232 | 545 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 232 | 0 | 0 | 39.791 | 171.5417 | 23.4482 | 86.148 | -75 | -1.351 | 190.8102 | -238.5779 | -6.5779 | -2.0851 | 0 | -2.0851 | 89.06 | -2.0851 | 6/20/14:00
6 | 20 | 1900-01-14 | 31.7 | 192 | 716 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 192 | 0 | 0 | 39.791 | 171.5833 | 23.4484 | 86.148 | -75 | -1.3598 | 205.8081 | -272.0462 | -80.0462 | -25.3732 | 0 | -25.3732 | 89.06 | -25.3732 | 6/20/15:00
6 | 20 | 1900-01-15 | 31.7 | 127 | 768 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 127 | 0 | 0 | 39.791 | 171.625 | 23.4486 | 86.148 | -75 | -1.3686 | 220.8059 | -214.205 | -87.205 | -27.6425 | 0 | -27.6425 | 89.06 | -27.6425 | 6/20/16:00
6 | 20 | 1900-01-16 | 31.1 | 194 | 491 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 194 | 0 | 0 | 39.791 | 171.6667 | 23.4487 | 86.148 | -75 | -1.3773 | 235.8037 | -69.4869 | 124.5131 | 39.4685 | 0 | 39.4685 | 87.98 | 39.4685 | 6/20/17:00
6 | 20 | 1900-01-17 | 31.1 | 91 | 678 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 91 | 0 | 0 | 39.791 | 171.7083 | 23.4489 | 86.148 | -75 | -1.3861 | 250.8015 | 15.5003 | 106.5003 | 33.7587 | 0 | 33.7587 | 87.98 | 33.7587 | 6/20/18:00
6 | 20 | 1900-01-18 | 30 | 65 | 528 | 86 | 0 | 1 | 0 | 86 | 0 | 65 | 0 | 0 | 39.791 | 171.75 | 23.4491 | 86.148 | -75 | -1.3949 | 265.7993 | 107.2035 | 172.2035 | 54.5855 | 0 | 54.5855 | 86 | 54.5855 | 6/20/19:00
6 | 20 | 1900-01-19 | 28.3 | 35 | 226 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 35 | 0 | 0 | 39.791 | 171.7917 | 23.4492 | 86.148 | -75 | -1.4036 | 280.7971 | 87.4009 | 122.4009 | 38.7989 | 0 | 38.7989 | 82.94 | 38.7989 | 6/20/20:00
6 | 20 | 1900-01-20 | 26.7 | 3 | 4 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 3 | 0 | 0 | 39.791 | 171.8333 | 23.4494 | 86.148 | -75 | -1.4124 | 295.7949 | 2.2457 | 5.2457 | 1.6628 | 0 | 1.6628 | 80.06 | 1.6628 | 6/20/21:00
6 | 20 | 1900-01-21 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 171.875 | 23.4495 | 86.148 | -75 | -1.4212 | 310.7927 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 6/20/22:00
6 | 20 | 1900-01-22 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 171.9167 | 23.4496 | 86.148 | -75 | -1.4299 | 325.7905 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/20/23:00
6 | 20 | 1900-01-23 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 171.9583 | 23.4497 | 86.148 | -75 | -1.4387 | 340.7883 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/20/24:00
6 | 21 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 172 | 23.4498 | 86.148 | -75 | -1.4474 | -4.2139 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/21/1:00
6 | 21 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 172.0417 | 23.4498 | 86.148 | -75 | -1.4562 | 10.7839 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/21/2:00
6 | 21 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 172.0833 | 23.4499 | 86.148 | -75 | -1.465 | 25.7818 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/21/3:00
6 | 21 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 172.125 | 23.4499 | 86.148 | -75 | -1.4737 | 40.7796 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/21/4:00
6 | 21 | 1900-01-04 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 172.1667 | 23.45 | 86.148 | -75 | -1.4825 | 55.7774 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 6/21/5:00
6 | 21 | 1900-01-05 | 17.8 | 19 | 5 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 19 | 0 | 0 | 39.791 | 172.2083 | 23.45 | 86.148 | -75 | -1.4912 | 70.7752 | 2.434 | 21.434 | 6.7942 | 0 | 6.7942 | 64.04 | 6.7942 | 6/21/6:00
6 | 21 | 1900-01-06 | 18.9 | 85 | 120 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 85 | 0 | 0 | 39.791 | 172.25 | 23.45 | 86.148 | -75 | -1.5 | 85.773 | 36.7969 | 121.7969 | 38.6075 | 0 | 38.6075 | 66.02 | 38.6075 | 6/21/7:00
6 | 21 | 1900-01-07 | 21.1 | 157 | 314 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 157 | 0 | 0 | 39.791 | 172.2917 | 23.45 | 86.148 | -75 | -1.5088 | 100.7708 | 38.6052 | 195.6052 | 62.0034 | 0 | 62.0034 | 69.98 | 62.0034 | 6/21/8:00
6 | 21 | 1900-01-08 | 22.2 | 209 | 457 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 209 | 0 | 0 | 39.791 | 172.3333 | 23.45 | 86.148 | -75 | -1.5175 | 115.7686 | -23.6606 | 185.3394 | 58.7494 | 0 | 58.7494 | 71.96 | 58.7494 | 6/21/9:00
6 | 21 | 1900-01-09 | 24.4 | 234 | 546 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 234 | 0 | 0 | 39.791 | 172.375 | 23.4499 | 86.148 | -75 | -1.5263 | 130.7664 | -112.2661 | 121.7339 | 38.5875 | 0 | 38.5875 | 75.92 | 38.5875 | 6/21/10:00
6 | 21 | 1900-01-10 | 26.7 | 230 | 628 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 230 | 0 | 0 | 39.791 | 172.4167 | 23.4499 | 86.148 | -75 | -1.535 | 145.7642 | -206.0457 | 23.9543 | 7.5931 | 0 | 7.5931 | 80.06 | 7.5931 | 6/21/11:00
6 | 21 | 1900-01-11 | 28.3 | 216 | 753 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 216 | 0 | 0 | 39.791 | 172.4583 | 23.4498 | 86.148 | -75 | -1.5438 | 160.7621 | -309.3905 | -93.3905 | -29.6032 | 0 | -29.6032 | 82.94 | -29.6032 | 6/21/12:00
6 | 21 | 1900-01-12 | 30 | 215 | 771 | 86 | 0 | 1 | 0 | 86 | 0 | 215 | 0 | 0 | 39.791 | 172.5 | 23.4498 | 86.148 | -75 | -1.5525 | 175.7599 | -345.6492 | -130.6492 | -41.4135 | 0 | -41.4135 | 86 | -41.4135 | 6/21/13:00
6 | 21 | 1900-01-13 | 31.1 | 214 | 768 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 214 | 0 | 0 | 39.791 | 172.5417 | 23.4497 | 86.148 | -75 | -1.5613 | 190.7577 | -336.2725 | -122.2725 | -38.7583 | 0 | -38.7583 | 87.98 | -38.7583 | 6/21/14:00
6 | 21 | 1900-01-14 | 32.2 | 199 | 699 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 199 | 0 | 0 | 39.791 | 172.5833 | 23.4496 | 86.148 | -75 | -1.57 | 205.7555 | -265.7707 | -66.7707 | -21.1651 | 0 | -21.1651 | 89.96 | -21.1651 | 6/21/15:00
6 | 21 | 1900-01-15 | 32.8 | 194 | 657 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 194 | 0 | 0 | 39.791 | 172.625 | 23.4495 | 86.148 | -75 | -1.5788 | 220.7533 | -183.5145 | 10.4855 | 3.3237 | 0 | 3.3237 | 91.04 | 3.3237 | 6/21/16:00
6 | 21 | 1900-01-16 | 32.8 | 236 | 317 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 236 | 0 | 0 | 39.791 | 172.6667 | 23.4494 | 86.148 | -75 | -1.5875 | 235.7511 | -45.0291 | 190.9709 | 60.5344 | 0 | 60.5344 | 91.04 | 60.5344 | 6/21/17:00
6 | 21 | 1900-01-17 | 31.7 | 131 | 517 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 131 | 0 | 0 | 39.791 | 172.7083 | 23.4492 | 86.148 | -75 | -1.5963 | 250.7489 | 11.5058 | 142.5058 | 45.1719 | 0 | 45.1719 | 89.06 | 45.1719 | 6/21/18:00
6 | 21 | 1900-01-18 | 30.6 | 88 | 369 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 88 | 0 | 0 | 39.791 | 172.75 | 23.4491 | 86.148 | -75 | -1.605 | 265.7467 | 74.6828 | 162.6828 | 51.5676 | 0 | 51.5676 | 87.08 | 51.5676 | 6/21/19:00
6 | 21 | 1900-01-19 | 28.3 | 42 | 103 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 42 | 0 | 0 | 39.791 | 172.7917 | 23.4489 | 86.148 | -75 | -1.6138 | 280.7446 | 39.7674 | 81.7674 | 25.9189 | 0 | 25.9189 | 82.94 | 25.9189 | 6/21/20:00
6 | 21 | 1900-01-20 | 26.1 | 1 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 1 | 0 | 0 | 39.791 | 172.8333 | 23.4487 | 86.148 | -75 | -1.6225 | 295.7424 | 0 | 1 | 0.31698 | 0 | 0.31698 | 78.98 | 0.31698 | 6/21/21:00
6 | 21 | 1900-01-21 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 172.875 | 23.4486 | 86.148 | -75 | -1.6313 | 310.7402 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 6/21/22:00
6 | 21 | 1900-01-22 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 172.9167 | 23.4484 | 86.148 | -75 | -1.64 | 325.738 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 6/21/23:00
6 | 21 | 1900-01-23 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 172.9583 | 23.4482 | 86.148 | -75 | -1.6487 | 340.7358 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 6/21/24:00
6 | 22 | 1899-12-31 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 173 | 23.4479 | 86.148 | -75 | -1.6575 | -4.2664 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/22/1:00
6 | 22 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 173.0417 | 23.4477 | 86.148 | -75 | -1.6662 | 10.7314 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/22/2:00
6 | 22 | 1900-01-02 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 173.0833 | 23.4474 | 86.148 | -75 | -1.675 | 25.7293 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/22/3:00
6 | 22 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 173.125 | 23.4472 | 86.148 | -75 | -1.6837 | 40.7271 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/22/4:00
6 | 22 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 173.1667 | 23.4469 | 86.148 | -75 | -1.6924 | 55.7249 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/22/5:00
6 | 22 | 1900-01-05 | 21.1 | 18 | 13 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 18 | 0 | 0 | 39.791 | 173.2083 | 23.4466 | 86.148 | -75 | -1.7012 | 70.7227 | 6.3359 | 24.3359 | 7.7141 | 0 | 7.7141 | 69.98 | 7.7141 | 6/22/6:00
6 | 22 | 1900-01-06 | 23.3 | 62 | 259 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 62 | 0 | 0 | 39.791 | 173.25 | 23.4463 | 86.148 | -75 | -1.7099 | 85.7205 | 79.5774 | 141.5774 | 44.8776 | 0 | 44.8776 | 73.94 | 44.8776 | 6/22/7:00
6 | 22 | 1900-01-07 | 25.6 | 103 | 483 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 103 | 0 | 0 | 39.791 | 173.2917 | 23.446 | 86.148 | -75 | -1.7186 | 100.7183 | 59.6678 | 162.6678 | 51.5628 | 0 | 51.5628 | 78.08 | 51.5628 | 6/22/8:00
6 | 22 | 1900-01-08 | 27.2 | 139 | 617 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 139 | 0 | 0 | 39.791 | 173.3333 | 23.4457 | 86.148 | -75 | -1.7274 | 115.7162 | -31.6189 | 107.3811 | 34.0379 | 0 | 34.0379 | 80.96 | 34.0379 | 6/22/9:00
6 | 22 | 1900-01-09 | 29.4 | 172 | 678 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 172 | 0 | 0 | 39.791 | 173.375 | 23.4453 | 86.148 | -75 | -1.7361 | 130.714 | -139.1186 | 32.8814 | 10.4228 | 0 | 10.4228 | 84.92 | 10.4228 | 6/22/10:00
6 | 22 | 1900-01-10 | 30 | 178 | 697 | 86 | 0 | 1 | 0 | 86 | 0 | 178 | 0 | 0 | 39.791 | 173.4167 | 23.445 | 86.148 | -75 | -1.7448 | 145.7118 | -228.4814 | -50.4814 | -16.0017 | 0 | -16.0017 | 86 | -16.0017 | 6/22/11:00
6 | 22 | 1900-01-11 | 31.7 | 273 | 704 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 273 | 0 | 0 | 39.791 | 173.4583 | 23.4446 | 86.148 | -75 | -1.7535 | 160.7096 | -289.1638 | -16.1638 | -5.1236 | 0 | -5.1236 | 89.06 | -5.1236 | 6/22/12:00
6 | 22 | 1900-01-12 | 30.6 | 405 | 477 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 405 | 0 | 0 | 39.791 | 173.5 | 23.4442 | 86.148 | -75 | -1.7623 | 175.7074 | -213.8634 | 191.1366 | 60.587 | 0 | 60.587 | 87.08 | 60.587 | 6/22/13:00
6 | 22 | 1900-01-13 | 32.2 | 264 | 641 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 264 | 0 | 0 | 39.791 | 173.5417 | 23.4439 | 86.148 | -75 | -1.771 | 190.7053 | -280.7998 | -16.7998 | -5.3253 | 0 | -5.3253 | 89.96 | -5.3253 | 6/22/14:00
6 | 22 | 1900-01-14 | 32.8 | 385 | 372 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 385 | 0 | 0 | 39.791 | 173.5833 | 23.4435 | 86.148 | -75 | -1.7797 | 205.7031 | -141.5787 | 243.4213 | 77.1603 | 0 | 77.1603 | 91.04 | 77.1603 | 6/22/15:00
6 | 22 | 1900-01-15 | 32.8 | 393 | 316 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 393 | 0 | 0 | 39.791 | 173.625 | 23.443 | 86.148 | -75 | -1.7884 | 220.7009 | -88.4278 | 304.5722 | 96.5441 | 0 | 96.5441 | 91.04 | 96.5441 | 6/22/16:00
6 | 22 | 1900-01-16 | 32.2 | 186 | 634 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 186 | 0 | 0 | 39.791 | 173.6667 | 23.4426 | 86.148 | -75 | -1.7971 | 235.6987 | -90.4527 | 95.5473 | 30.2868 | 0 | 30.2868 | 89.96 | 30.2868 | 6/22/17:00
6 | 22 | 1900-01-17 | 31.1 | 173 | 342 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 173 | 0 | 0 | 39.791 | 173.7083 | 23.4422 | 86.148 | -75 | -1.8059 | 250.6965 | 7.3741 | 180.3741 | 57.1754 | 0 | 57.1754 | 87.98 | 57.1754 | 6/22/18:00
6 | 22 | 1900-01-18 | 24.4 | 60 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 60 | 0 | 0 | 39.791 | 173.75 | 23.4417 | 86.148 | -75 | -1.8146 | 265.6944 | 0 | 60 | 19.019 | 0 | 19.019 | 75.92 | 19.019 | 6/22/19:00
6 | 22 | 1900-01-19 | 23.3 | 30 | 1 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 30 | 0 | 0 | 39.791 | 173.7917 | 23.4412 | 86.148 | -75 | -1.8233 | 280.6922 | 0.38539 | 30.3854 | 9.6316 | 0 | 9.6316 | 73.94 | 9.6316 | 6/22/20:00
6 | 22 | 1900-01-20 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 173.8333 | 23.4408 | 86.148 | -75 | -1.832 | 295.69 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/22/21:00
6 | 22 | 1900-01-21 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 173.875 | 23.4403 | 86.148 | -75 | -1.8407 | 310.6878 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/22/22:00
6 | 22 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 173.9167 | 23.4398 | 86.148 | -75 | -1.8494 | 325.6856 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/22/23:00
6 | 22 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 173.9583 | 23.4393 | 86.148 | -75 | -1.8581 | 340.6835 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/22/24:00
6 | 23 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 174 | 23.4387 | 86.148 | -75 | -1.8668 | -4.3187 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/23/1:00
6 | 23 | 1900-01-01 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 174.0417 | 23.4382 | 86.148 | -75 | -1.8755 | 10.6791 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/23/2:00
6 | 23 | 1900-01-02 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 174.0833 | 23.4376 | 86.148 | -75 | -1.8842 | 25.6769 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/23/3:00
6 | 23 | 1900-01-03 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 174.125 | 23.4371 | 86.148 | -75 | -1.8929 | 40.6748 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/23/4:00
6 | 23 | 1900-01-04 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 174.1667 | 23.4365 | 86.148 | -75 | -1.9016 | 55.6726 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/23/5:00
6 | 23 | 1900-01-05 | 20 | 17 | 5 | 68 | 0 | 1 | 0 | 68 | 0 | 17 | 0 | 0 | 39.791 | 174.2083 | 23.4359 | 86.148 | -75 | -1.9103 | 70.6704 | 2.4395 | 19.4395 | 6.162 | 0 | 6.162 | 68 | 6.162 | 6/23/6:00
6 | 23 | 1900-01-06 | 22.2 | 83 | 77 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 83 | 0 | 0 | 39.791 | 174.25 | 23.4353 | 86.148 | -75 | -1.919 | 85.6683 | 23.6992 | 106.6992 | 33.8218 | 0 | 33.8218 | 71.96 | 33.8218 | 6/23/7:00
6 | 23 | 1900-01-07 | 23.3 | 143 | 385 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 143 | 0 | 0 | 39.791 | 174.2917 | 23.4347 | 86.148 | -75 | -1.9277 | 100.6661 | 47.7554 | 190.7554 | 60.4661 | 0 | 60.4661 | 73.94 | 60.4661 | 6/23/8:00
6 | 23 | 1900-01-08 | 25 | 216 | 407 | 77 | 0 | 1 | 0 | 77 | 0 | 216 | 0 | 0 | 39.791 | 174.3333 | 23.434 | 86.148 | -75 | -1.9364 | 115.6639 | -20.681 | 195.319 | 61.9127 | 0 | 61.9127 | 77 | 61.9127 | 6/23/9:00
6 | 23 | 1900-01-09 | 26.7 | 219 | 588 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 219 | 0 | 0 | 39.791 | 174.375 | 23.4334 | 86.148 | -75 | -1.9451 | 130.6617 | -120.4615 | 98.5385 | 31.235 | 0 | 31.235 | 80.06 | 31.235 | 6/23/10:00
6 | 23 | 1900-01-10 | 27.2 | 299 | 539 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 299 | 0 | 0 | 39.791 | 174.4167 | 23.4327 | 86.148 | -75 | -1.9537 | 145.6596 | -176.5896 | 122.4104 | 38.802 | 0 | 38.802 | 80.96 | 38.802 | 6/23/11:00
6 | 23 | 1900-01-11 | 27.2 | 369 | 240 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 369 | 0 | 0 | 39.791 | 174.4583 | 23.432 | 86.148 | -75 | -1.9624 | 160.6574 | -98.5737 | 270.4263 | 85.7204 | 0 | 85.7204 | 80.96 | 85.7204 | 6/23/12:00
6 | 23 | 1900-01-12 | 27.2 | 327 | 576 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 327 | 0 | 0 | 39.791 | 174.5 | 23.4314 | 86.148 | -75 | -1.9711 | 175.6552 | -258.3378 | 68.6622 | 21.7647 | 0 | 21.7647 | 80.96 | 21.7647 | 6/23/13:00
6 | 23 | 1900-01-13 | 27.8 | 274 | 669 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 274 | 0 | 0 | 39.791 | 174.5417 | 23.4307 | 86.148 | -75 | -1.9798 | 190.6531 | -293.282 | -19.282 | -6.1121 | 0 | -6.1121 | 82.04 | -6.1121 | 6/23/14:00
6 | 23 | 1900-01-14 | 27.8 | 382 | 328 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 382 | 0 | 0 | 39.791 | 174.5833 | 23.43 | 86.148 | -75 | -1.9885 | 205.6509 | -124.9908 | 257.0092 | 81.4674 | 0 | 81.4674 | 82.04 | 81.4674 | 6/23/15:00
6 | 23 | 1900-01-15 | 28.3 | 338 | 296 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 338 | 0 | 0 | 39.791 | 174.625 | 23.4292 | 86.148 | -75 | -1.9971 | 220.6487 | -83.0133 | 254.9867 | 80.8263 | 0 | 80.8263 | 82.94 | 80.8263 | 6/23/16:00
6 | 23 | 1900-01-16 | 28.9 | 252 | 327 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 252 | 0 | 0 | 39.791 | 174.6667 | 23.4285 | 86.148 | -75 | -2.0058 | 235.6466 | -46.8875 | 205.1125 | 65.0171 | 0 | 65.0171 | 84.02 | 65.0171 | 6/23/17:00
6 | 23 | 1900-01-17 | 27.8 | 189 | 238 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 189 | 0 | 0 | 39.791 | 174.7083 | 23.4278 | 86.148 | -75 | -2.0145 | 250.6444 | 4.9464 | 193.9464 | 61.4776 | 0 | 61.4776 | 82.04 | 61.4776 | 6/23/18:00
6 | 23 | 1900-01-18 | 26.7 | 129 | 37 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 129 | 0 | 0 | 39.791 | 174.75 | 23.427 | 86.148 | -75 | -2.0231 | 265.6422 | 7.4324 | 136.4324 | 43.2467 | 0 | 43.2467 | 80.06 | 43.2467 | 6/23/19:00
6 | 23 | 1900-01-19 | 25 | 32 | 6 | 77 | 0 | 1 | 0 | 77 | 0 | 32 | 0 | 0 | 39.791 | 174.7917 | 23.4262 | 86.148 | -75 | -2.0318 | 280.6401 | 2.3077 | 34.3077 | 10.8749 | 0 | 10.8749 | 77 | 10.8749 | 6/23/20:00
6 | 23 | 1900-01-20 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 174.8333 | 23.4254 | 86.148 | -75 | -2.0404 | 295.6379 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/23/21:00
6 | 23 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 174.875 | 23.4246 | 86.148 | -75 | -2.0491 | 310.6357 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/23/22:00
6 | 23 | 1900-01-22 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 174.9167 | 23.4238 | 86.148 | -75 | -2.0578 | 325.6336 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/23/23:00
6 | 23 | 1900-01-23 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 174.9583 | 23.423 | 86.148 | -75 | -2.0664 | 340.6314 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/23/24:00
6 | 24 | 1899-12-31 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 175 | 23.4222 | 86.148 | -75 | -2.0751 | -4.3708 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/24/1:00
6 | 24 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 175.0417 | 23.4213 | 86.148 | -75 | -2.0837 | 10.6271 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/24/2:00
6 | 24 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 175.0833 | 23.4204 | 86.148 | -75 | -2.0924 | 25.6249 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 6/24/3:00
6 | 24 | 1900-01-03 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 175.125 | 23.4196 | 86.148 | -75 | -2.101 | 40.6227 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 6/24/4:00
6 | 24 | 1900-01-04 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 175.1667 | 23.4187 | 86.148 | -75 | -2.1096 | 55.6206 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 6/24/5:00
6 | 24 | 1900-01-05 | 17.8 | 17 | 10 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 17 | 0 | 0 | 39.791 | 175.2083 | 23.4178 | 86.148 | -75 | -2.1183 | 70.6184 | 4.8834 | 21.8834 | 6.9367 | 0 | 6.9367 | 64.04 | 6.9367 | 6/24/6:00
6 | 24 | 1900-01-06 | 19.4 | 64 | 235 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 64 | 0 | 0 | 39.791 | 175.25 | 23.4169 | 86.148 | -75 | -2.1269 | 85.6163 | 72.4359 | 136.4359 | 43.2478 | 0 | 43.2478 | 66.92 | 43.2478 | 6/24/7:00
6 | 24 | 1900-01-07 | 20 | 108 | 470 | 68 | 0 | 1 | 0 | 68 | 0 | 108 | 0 | 0 | 39.791 | 175.2917 | 23.4159 | 86.148 | -75 | -2.1356 | 100.6141 | 58.4954 | 166.4954 | 52.7761 | 0 | 52.7761 | 68 | 52.7761 | 6/24/8:00
6 | 24 | 1900-01-08 | 21.1 | 147 | 610 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 147 | 0 | 0 | 39.791 | 175.3333 | 23.415 | 86.148 | -75 | -2.1442 | 115.612 | -30.7902 | 116.2098 | 36.8365 | 0 | 36.8365 | 69.98 | 36.8365 | 6/24/9:00
6 | 24 | 1900-01-09 | 22.2 | 177 | 688 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 177 | 0 | 0 | 39.791 | 175.375 | 23.4141 | 86.148 | -75 | -2.1528 | 130.6098 | -140.7969 | 36.2031 | 11.4757 | 0 | 11.4757 | 71.96 | 11.4757 | 6/24/10:00
6 | 24 | 1900-01-10 | 22.8 | 241 | 648 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 241 | 0 | 0 | 39.791 | 175.4167 | 23.4131 | 86.148 | -75 | -2.1614 | 145.6076 | -212.2532 | 28.7468 | 9.1122 | 0 | 9.1122 | 73.04 | 9.1122 | 6/24/11:00
6 | 24 | 1900-01-11 | 23.3 | 281 | 497 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 281 | 0 | 0 | 39.791 | 175.4583 | 23.4121 | 86.148 | -75 | -2.1701 | 160.6055 | -204.1758 | 76.8242 | 24.3519 | 0 | 24.3519 | 73.94 | 24.3519 | 6/24/12:00
6 | 24 | 1900-01-12 | 23.9 | 375 | 484 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 375 | 0 | 0 | 39.791 | 175.5 | 23.4111 | 86.148 | -75 | -2.1787 | 175.6033 | -217.2044 | 157.7956 | 50.0184 | 0 | 50.0184 | 75.02 | 50.0184 | 6/24/13:00
6 | 24 | 1900-01-13 | 23.9 | 256 | 692 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 256 | 0 | 0 | 39.791 | 175.5417 | 23.4101 | 86.148 | -75 | -2.1873 | 190.6012 | -303.6666 | -47.6666 | -15.1095 | 0 | -15.1095 | 75.02 | -15.1095 | 6/24/14:00
6 | 24 | 1900-01-14 | 23.3 | 206 | 718 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 206 | 0 | 0 | 39.791 | 175.5833 | 23.4091 | 86.148 | -75 | -2.1959 | 205.599 | -274.0314 | -68.0314 | -21.5648 | 0 | -21.5648 | 73.94 | -21.5648 | 6/24/15:00
6 | 24 | 1900-01-15 | 23.3 | 190 | 727 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 190 | 0 | 0 | 39.791 | 175.625 | 23.4081 | 86.148 | -75 | -2.2045 | 220.5969 | -204.4094 | -14.4094 | -4.5675 | 0 | -4.5675 | 73.94 | -4.5675 | 6/24/16:00
6 | 24 | 1900-01-16 | 22.8 | 165 | 667 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 165 | 0 | 0 | 39.791 | 175.6667 | 23.407 | 86.148 | -75 | -2.2131 | 235.5947 | -96.1801 | 68.8199 | 21.8147 | 0 | 21.8147 | 73.04 | 21.8147 | 6/24/17:00
6 | 24 | 1900-01-17 | 22.2 | 134 | 558 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 134 | 0 | 0 | 39.791 | 175.7083 | 23.406 | 86.148 | -75 | -2.2217 | 250.5926 | 11.1153 | 145.1153 | 45.999 | 0 | 45.999 | 71.96 | 45.999 | 6/24/18:00
6 | 24 | 1900-01-18 | 20.6 | 92 | 379 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 92 | 0 | 0 | 39.791 | 175.75 | 23.4049 | 86.148 | -75 | -2.2303 | 265.5904 | 75.8014 | 167.8014 | 53.1901 | 0 | 53.1901 | 69.08 | 53.1901 | 6/24/19:00
6 | 24 | 1900-01-19 | 18.3 | 42 | 108 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 42 | 0 | 0 | 39.791 | 175.7917 | 23.4038 | 86.148 | -75 | -2.2389 | 280.5883 | 41.4487 | 83.4487 | 26.4518 | 0 | 26.4518 | 64.94 | 26.4518 | 6/24/20:00
6 | 24 | 1900-01-20 | 16.1 | 3 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 3 | 0 | 0 | 39.791 | 175.8333 | 23.4027 | 86.148 | -75 | -2.2475 | 295.5861 | 0 | 3 | 0.95095 | 0 | 0.95095 | 60.98 | 0.95095 | 6/24/21:00
6 | 24 | 1900-01-21 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 175.875 | 23.4016 | 86.148 | -75 | -2.2561 | 310.584 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 6/24/22:00
6 | 24 | 1900-01-22 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 175.9167 | 23.4005 | 86.148 | -75 | -2.2647 | 325.5818 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 6/24/23:00
6 | 24 | 1900-01-23 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 175.9583 | 23.3994 | 86.148 | -75 | -2.2733 | 340.5797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/24/24:00
6 | 25 | 1899-12-31 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 176 | 23.3982 | 86.148 | -75 | -2.2819 | -4.4225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/25/1:00
6 | 25 | 1900-01-01 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 176.0417 | 23.3971 | 86.148 | -75 | -2.2905 | 10.5754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/25/2:00
6 | 25 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 176.0833 | 23.3959 | 86.148 | -75 | -2.299 | 25.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/25/3:00
6 | 25 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 176.125 | 23.3947 | 86.148 | -75 | -2.3076 | 40.5711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/25/4:00
6 | 25 | 1900-01-04 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 176.1667 | 23.3935 | 86.148 | -75 | -2.3162 | 55.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6/25/5:00
6 | 25 | 1900-01-05 | 9.4 | 15 | 91 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 15 | 0 | 0 | 39.791 | 176.2083 | 23.3923 | 86.148 | -75 | -2.3247 | 70.5668 | 44.4741 | 59.4741 | 18.8523 | 18.8523 | 0 | 0 | 0 | 6/25/6:00
6 | 25 | 1900-01-06 | 11.7 | 42 | 472 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 42 | 0 | 0 | 39.791 | 176.25 | 23.3911 | 86.148 | -75 | -2.3333 | 85.5647 | 145.6676 | 187.6676 | 59.4873 | 59.4873 | 0 | 0 | 0 | 6/25/7:00
6 | 25 | 1900-01-07 | 15 | 65 | 682 | 59 | 0 | 1 | 0 | 59 | 0 | 65 | 0 | 0 | 39.791 | 176.2917 | 23.3899 | 86.148 | -75 | -2.3419 | 100.5625 | 85.1066 | 150.1066 | 47.5812 | 0 | 47.5812 | 59 | 47.5812 | 6/25/8:00
6 | 25 | 1900-01-08 | 16.7 | 86 | 786 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 86 | 0 | 0 | 39.791 | 176.3333 | 23.3886 | 86.148 | -75 | -2.3504 | 115.5604 | -39.4841 | 46.5159 | 14.7447 | 0 | 14.7447 | 62.06 | 14.7447 | 6/25/9:00
6 | 25 | 1900-01-09 | 18.3 | 185 | 690 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 185 | 0 | 0 | 39.791 | 176.375 | 23.3874 | 86.148 | -75 | -2.359 | 130.5583 | -141.1262 | 43.8738 | 13.9072 | 0 | 13.9072 | 64.94 | 13.9072 | 6/25/10:00
6 | 25 | 1900-01-10 | 20.6 | 219 | 699 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 219 | 0 | 0 | 39.791 | 176.4167 | 23.3861 | 86.148 | -75 | -2.3675 | 145.5561 | -228.984 | -9.984 | -3.1647 | 0 | -3.1647 | 69.08 | -3.1647 | 6/25/11:00
6 | 25 | 1900-01-11 | 21.1 | 234 | 743 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 234 | 0 | 0 | 39.791 | 176.4583 | 23.3848 | 86.148 | -75 | -2.3761 | 160.554 | -305.3896 | -71.3896 | -22.6293 | 0 | -22.6293 | 69.98 | -22.6293 | 6/25/12:00
6 | 25 | 1900-01-12 | 22.8 | 293 | 669 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 293 | 0 | 0 | 39.791 | 176.5 | 23.3835 | 86.148 | -75 | -2.3846 | 175.5518 | -300.4813 | -7.4813 | -2.3714 | 0 | -2.3714 | 73.04 | -2.3714 | 6/25/13:00
6 | 25 | 1900-01-13 | 23.9 | 285 | 646 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 285 | 0 | 0 | 39.791 | 176.5417 | 23.3822 | 86.148 | -75 | -2.3932 | 190.5497 | -283.8348 | 1.1652 | 0.36933 | 0 | 0.36933 | 75.02 | 0.36933 | 6/25/14:00
6 | 25 | 1900-01-14 | 24.4 | 290 | 665 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 290 | 0 | 0 | 39.791 | 176.5833 | 23.3809 | 86.148 | -75 | -2.4017 | 205.5476 | -254.2676 | 35.7324 | 11.3266 | 0 | 11.3266 | 75.92 | 11.3266 | 6/25/15:00
6 | 25 | 1900-01-15 | 25 | 237 | 673 | 77 | 0 | 1 | 0 | 77 | 0 | 237 | 0 | 0 | 39.791 | 176.625 | 23.3796 | 86.148 | -75 | -2.4102 | 220.5454 | -189.7777 | 47.2223 | 14.9687 | 0 | 14.9687 | 77 | 14.9687 | 6/25/16:00
6 | 25 | 1900-01-16 | 25 | 174 | 634 | 77 | 0 | 1 | 0 | 77 | 0 | 174 | 0 | 0 | 39.791 | 176.6667 | 23.3782 | 86.148 | -75 | -2.4188 | 235.5433 | -91.9947 | 82.0053 | 25.9942 | 0 | 25.9942 | 77 | 25.9942 | 6/25/17:00
6 | 25 | 1900-01-17 | 25.6 | 143 | 547 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 143 | 0 | 0 | 39.791 | 176.7083 | 23.3769 | 86.148 | -75 | -2.4273 | 250.5412 | 10.3784 | 153.3784 | 48.6183 | 0 | 48.6183 | 78.08 | 48.6183 | 6/25/18:00
6 | 25 | 1900-01-18 | 24.4 | 122 | 297 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 122 | 0 | 0 | 39.791 | 176.75 | 23.3755 | 86.148 | -75 | -2.4358 | 265.539 | 59.1207 | 181.1207 | 57.4121 | 0 | 57.4121 | 75.92 | 57.4121 | 6/25/19:00
6 | 25 | 1900-01-19 | 22.8 | 45 | 177 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 45 | 0 | 0 | 39.791 | 176.7917 | 23.3741 | 86.148 | -75 | -2.4443 | 280.5369 | 67.771 | 112.771 | 35.7464 | 0 | 35.7464 | 73.04 | 35.7464 | 6/25/20:00
6 | 25 | 1900-01-20 | 20.6 | 2 | 11 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 2 | 0 | 0 | 39.791 | 176.8333 | 23.3727 | 86.148 | -75 | -2.4528 | 295.5348 | 6.1372 | 8.1372 | 2.5794 | 0 | 2.5794 | 69.08 | 2.5794 | 6/25/21:00
6 | 25 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 176.875 | 23.3713 | 86.148 | -75 | -2.4614 | 310.5327 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 6/25/22:00
6 | 25 | 1900-01-22 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 176.9167 | 23.3699 | 86.148 | -75 | -2.4699 | 325.5305 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 6/25/23:00
6 | 25 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 176.9583 | 23.3684 | 86.148 | -75 | -2.4784 | 340.5284 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 6/25/24:00
6 | 26 | 1899-12-31 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 177 | 23.367 | 86.148 | -75 | -2.4869 | -4.4737 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 6/26/1:00
6 | 26 | 1900-01-01 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 177.0417 | 23.3655 | 86.148 | -75 | -2.4954 | 10.5242 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 6/26/2:00
6 | 26 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 177.0833 | 23.3641 | 86.148 | -75 | -2.5039 | 25.522 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 6/26/3:00
6 | 26 | 1900-01-03 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 177.125 | 23.3626 | 86.148 | -75 | -2.5124 | 40.5199 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 6/26/4:00
6 | 26 | 1900-01-04 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 177.1667 | 23.3611 | 86.148 | -75 | -2.5208 | 55.5178 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 6/26/5:00
6 | 26 | 1900-01-05 | 13.9 | 21 | 16 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 21 | 0 | 0 | 39.791 | 177.2083 | 23.3596 | 86.148 | -75 | -2.5293 | 70.5157 | 7.8247 | 28.8247 | 9.1369 | 0 | 9.1369 | 57.02 | 9.1369 | 6/26/6:00
6 | 26 | 1900-01-06 | 17.2 | 58 | 152 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 58 | 0 | 0 | 39.791 | 177.25 | 23.358 | 86.148 | -75 | -2.5378 | 85.5136 | 46.9558 | 104.9558 | 33.2691 | 0 | 33.2691 | 62.96 | 33.2691 | 6/26/7:00
6 | 26 | 1900-01-07 | 19.4 | 115 | 482 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 115 | 0 | 0 | 39.791 | 177.2917 | 23.3565 | 86.148 | -75 | -2.5463 | 100.5114 | 60.266 | 175.266 | 55.5563 | 0 | 55.5563 | 66.92 | 55.5563 | 6/26/8:00
6 | 26 | 1900-01-08 | 22.8 | 143 | 588 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 143 | 0 | 0 | 39.791 | 177.3333 | 23.3549 | 86.148 | -75 | -2.5547 | 115.5093 | -29.4528 | 113.5472 | 35.9925 | 0 | 35.9925 | 73.04 | 35.9925 | 6/26/9:00
6 | 26 | 1900-01-09 | 23.9 | 181 | 675 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 181 | 0 | 0 | 39.791 | 177.375 | 23.3534 | 86.148 | -75 | -2.5632 | 130.5072 | -138.0505 | 42.9495 | 13.6142 | 0 | 13.6142 | 75.02 | 13.6142 | 6/26/10:00
6 | 26 | 1900-01-10 | 26.1 | 174 | 761 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 174 | 0 | 0 | 39.791 | 177.4167 | 23.3518 | 86.148 | -75 | -2.5717 | 145.5051 | -249.406 | -75.406 | -23.9024 | 0 | -23.9024 | 78.98 | -23.9024 | 6/26/11:00
6 | 26 | 1900-01-11 | 27.2 | 257 | 422 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 257 | 0 | 0 | 39.791 | 177.4583 | 23.3502 | 86.148 | -75 | -2.5801 | 160.503 | -173.5862 | 83.4138 | 26.4407 | 0 | 26.4407 | 80.96 | 26.4407 | 6/26/12:00
6 | 26 | 1900-01-12 | 27.8 | 272 | 675 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 272 | 0 | 0 | 39.791 | 177.5 | 23.3486 | 86.148 | -75 | -2.5886 | 175.5009 | -303.5098 | -31.5098 | -9.9881 | 0 | -9.9881 | 82.04 | -9.9881 | 6/26/13:00
6 | 26 | 1900-01-13 | 28.9 | 202 | 772 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 202 | 0 | 0 | 39.791 | 177.5417 | 23.347 | 86.148 | -75 | -2.597 | 190.4987 | -339.7054 | -137.7054 | -43.6502 | 0 | -43.6502 | 84.02 | -43.6502 | 6/26/14:00
6 | 26 | 1900-01-14 | 27.2 | 214 | 770 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 214 | 0 | 0 | 39.791 | 177.5833 | 23.3454 | 86.148 | -75 | -2.6055 | 205.4966 | -295.035 | -81.035 | -25.6867 | 0 | -25.6867 | 80.96 | -25.6867 | 6/26/15:00
6 | 26 | 1900-01-15 | 28.3 | 242 | 539 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 242 | 0 | 0 | 39.791 | 177.625 | 23.3437 | 86.148 | -75 | -2.6139 | 220.4945 | -152.487 | 89.513 | 28.374 | 0 | 28.374 | 82.94 | 28.374 | 6/26/16:00
6 | 26 | 1900-01-16 | 28.9 | 225 | 409 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 225 | 0 | 0 | 39.791 | 177.6667 | 23.3421 | 86.148 | -75 | -2.6224 | 235.4924 | -59.7541 | 165.2459 | 52.3801 | 0 | 52.3801 | 84.02 | 52.3801 | 6/26/17:00
6 | 26 | 1900-01-17 | 27.8 | 118 | 553 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 118 | 0 | 0 | 39.791 | 177.7083 | 23.3404 | 86.148 | -75 | -2.6308 | 250.4903 | 9.9232 | 127.9232 | 40.5494 | 0 | 40.5494 | 82.04 | 40.5494 | 6/26/18:00
6 | 26 | 1900-01-18 | 27.2 | 117 | 315 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 117 | 0 | 0 | 39.791 | 177.75 | 23.3387 | 86.148 | -75 | -2.6392 | 265.4882 | 62.3836 | 179.3836 | 56.8615 | 0 | 56.8615 | 80.96 | 56.8615 | 6/26/19:00
6 | 26 | 1900-01-19 | 26.1 | 51 | 70 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 51 | 0 | 0 | 39.791 | 177.7917 | 23.337 | 86.148 | -75 | -2.6476 | 280.4861 | 26.7349 | 77.7349 | 24.6406 | 0 | 24.6406 | 78.98 | 24.6406 | 6/26/20:00
6 | 26 | 1900-01-20 | 24.4 | 4 | 1 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 4 | 0 | 0 | 39.791 | 177.8333 | 23.3353 | 86.148 | -75 | -2.6561 | 295.484 | 0.55707 | 4.5571 | 1.4445 | 0 | 1.4445 | 75.92 | 1.4445 | 6/26/21:00
6 | 26 | 1900-01-21 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 177.875 | 23.3336 | 86.148 | -75 | -2.6645 | 310.4819 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/26/22:00
6 | 26 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 177.9167 | 23.3319 | 86.148 | -75 | -2.6729 | 325.4798 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/26/23:00
6 | 26 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 177.9583 | 23.3302 | 86.148 | -75 | -2.6813 | 340.4777 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/26/24:00
6 | 27 | 1899-12-31 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 178 | 23.3284 | 86.148 | -75 | -2.6897 | -4.5244 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/27/1:00
6 | 27 | 1900-01-01 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 178.0417 | 23.3266 | 86.148 | -75 | -2.6981 | 10.4735 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/27/2:00
6 | 27 | 1900-01-02 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 178.0833 | 23.3249 | 86.148 | -75 | -2.7065 | 25.4714 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/27/3:00
6 | 27 | 1900-01-03 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 178.125 | 23.3231 | 86.148 | -75 | -2.7149 | 40.4693 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/27/4:00
6 | 27 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 178.1667 | 23.3213 | 86.148 | -75 | -2.7233 | 55.4672 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/27/5:00
6 | 27 | 1900-01-05 | 21.7 | 18 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 18 | 0 | 0 | 39.791 | 178.2083 | 23.3194 | 86.148 | -75 | -2.7317 | 70.4651 | 0 | 18 | 5.7057 | 0 | 5.7057 | 71.06 | 5.7057 | 6/27/6:00
6 | 27 | 1900-01-06 | 22.8 | 43 | 15 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 43 | 0 | 0 | 39.791 | 178.25 | 23.3176 | 86.148 | -75 | -2.74 | 85.463 | 4.6371 | 47.6371 | 15.1001 | 0 | 15.1001 | 73.04 | 15.1001 | 6/27/7:00
6 | 27 | 1900-01-07 | 25.6 | 96 | 5 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 96 | 0 | 0 | 39.791 | 178.2917 | 23.3158 | 86.148 | -75 | -2.7484 | 100.4609 | 0.62594 | 96.6259 | 30.6287 | 0 | 30.6287 | 78.08 | 30.6287 | 6/27/8:00
6 | 27 | 1900-01-08 | 27.8 | 228 | 88 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 228 | 0 | 0 | 39.791 | 178.3333 | 23.3139 | 86.148 | -75 | -2.7568 | 115.4588 | -4.4038 | 223.5962 | 70.8761 | 0 | 70.8761 | 82.04 | 70.8761 | 6/27/9:00
6 | 27 | 1900-01-09 | 28.3 | 266 | 555 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 266 | 0 | 0 | 39.791 | 178.375 | 23.3121 | 86.148 | -75 | -2.7651 | 130.4567 | -113.5601 | 152.4399 | 48.3208 | 0 | 48.3208 | 82.94 | 48.3208 | 6/27/10:00
6 | 27 | 1900-01-10 | 30 | 316 | 472 | 86 | 0 | 1 | 0 | 86 | 0 | 316 | 0 | 0 | 39.791 | 178.4167 | 23.3102 | 86.148 | -75 | -2.7735 | 145.4546 | -154.8121 | 161.1879 | 51.0938 | 0 | 51.0938 | 86 | 51.0938 | 6/27/11:00
6 | 27 | 1900-01-11 | 31.1 | 337 | 580 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 337 | 0 | 0 | 39.791 | 178.4583 | 23.3083 | 86.148 | -75 | -2.7818 | 160.4525 | -238.829 | 98.171 | 31.1185 | 0 | 31.1185 | 87.98 | 31.1185 | 6/27/12:00
6 | 27 | 1900-01-12 | 31.7 | 323 | 538 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 323 | 0 | 0 | 39.791 | 178.5 | 23.3064 | 86.148 | -75 | -2.7902 | 175.4505 | -242.2356 | 80.7644 | 25.6009 | 0 | 25.6009 | 89.06 | 25.6009 | 6/27/13:00
6 | 27 | 1900-01-13 | 32.8 | 275 | 579 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 275 | 0 | 0 | 39.791 | 178.5417 | 23.3045 | 86.148 | -75 | -2.7985 | 190.4484 | -255.2256 | 19.7744 | 6.2681 | 0 | 6.2681 | 91.04 | 6.2681 | 6/27/14:00
6 | 27 | 1900-01-14 | 33.3 | 220 | 665 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 220 | 0 | 0 | 39.791 | 178.5833 | 23.3025 | 86.148 | -75 | -2.8069 | 205.4463 | -255.4092 | -35.4092 | -11.2241 | 0 | -11.2241 | 91.94 | -11.2241 | 6/27/15:00
6 | 27 | 1900-01-15 | 33.3 | 241 | 591 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 241 | 0 | 0 | 39.791 | 178.625 | 23.3006 | 86.148 | -75 | -2.8152 | 220.4442 | -167.8005 | 73.1995 | 23.203 | 0 | 23.203 | 91.94 | 23.203 | 6/27/16:00
6 | 27 | 1900-01-16 | 32.8 | 241 | 500 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 241 | 0 | 0 | 39.791 | 178.6667 | 23.2986 | 86.148 | -75 | -2.8235 | 235.4421 | -73.5924 | 167.4076 | 53.0653 | 0 | 53.0653 | 91.04 | 53.0653 | 6/27/17:00
6 | 27 | 1900-01-17 | 32.2 | 187 | 226 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 187 | 0 | 0 | 39.791 | 178.7083 | 23.2967 | 86.148 | -75 | -2.8319 | 250.44 | 3.8046 | 190.8046 | 60.4817 | 0 | 60.4817 | 89.96 | 60.4817 | 6/27/18:00
6 | 27 | 1900-01-18 | 31.1 | 141 | 66 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 141 | 0 | 0 | 39.791 | 178.75 | 23.2947 | 86.148 | -75 | -2.8402 | 265.438 | 12.9991 | 153.9991 | 48.815 | 0 | 48.815 | 87.98 | 48.815 | 6/27/19:00
6 | 27 | 1900-01-19 | 24.4 | 32 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 32 | 0 | 0 | 39.791 | 178.7917 | 23.2927 | 86.148 | -75 | -2.8485 | 280.4359 | 0 | 32 | 10.1434 | 0 | 10.1434 | 75.92 | 10.1434 | 6/27/20:00
6 | 27 | 1900-01-20 | 22.2 | 4 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 4 | 0 | 0 | 39.791 | 178.8333 | 23.2907 | 86.148 | -75 | -2.8568 | 295.4338 | 0 | 4 | 1.2679 | 0 | 1.2679 | 71.96 | 1.2679 | 6/27/21:00
6 | 27 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 178.875 | 23.2887 | 86.148 | -75 | -2.8651 | 310.4317 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/27/22:00
6 | 27 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 178.9167 | 23.2866 | 86.148 | -75 | -2.8734 | 325.4296 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/27/23:00
6 | 27 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 178.9583 | 23.2846 | 86.148 | -75 | -2.8817 | 340.4276 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/27/24:00
6 | 28 | 1899-12-31 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 179 | 23.2825 | 86.148 | -75 | -2.89 | -4.5745 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/28/1:00
6 | 28 | 1900-01-01 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 179.0417 | 23.2804 | 86.148 | -75 | -2.8983 | 10.4234 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/28/2:00
6 | 28 | 1900-01-02 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 179.0833 | 23.2784 | 86.148 | -75 | -2.9066 | 25.4214 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/28/3:00
6 | 28 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 179.125 | 23.2763 | 86.148 | -75 | -2.9149 | 40.4193 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/28/4:00
6 | 28 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 179.1667 | 23.2742 | 86.148 | -75 | -2.9231 | 55.4172 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/28/5:00
6 | 28 | 1900-01-05 | 21.1 | 11 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 11 | 0 | 0 | 39.791 | 179.2083 | 23.272 | 86.148 | -75 | -2.9314 | 70.4152 | 0 | 11 | 3.4868 | 0 | 3.4868 | 69.98 | 3.4868 | 6/28/6:00
6 | 28 | 1900-01-06 | 22.2 | 85 | 158 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 85 | 0 | 0 | 39.791 | 179.25 | 23.2699 | 86.148 | -75 | -2.9397 | 85.4131 | 48.8672 | 133.8672 | 42.4336 | 0 | 42.4336 | 71.96 | 42.4336 | 6/28/7:00
6 | 28 | 1900-01-07 | 22.8 | 59 | 1 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 59 | 0 | 0 | 39.791 | 179.2917 | 23.2678 | 86.148 | -75 | -2.9479 | 100.411 | 0.12525 | 59.1253 | 18.7417 | 0 | 18.7417 | 73.04 | 18.7417 | 6/28/8:00
6 | 28 | 1900-01-08 | 25 | 161 | 2 | 77 | 0 | 1 | 0 | 77 | 0 | 161 | 0 | 0 | 39.791 | 179.3333 | 23.2656 | 86.148 | -75 | -2.9562 | 115.409 | -0.10019 | 160.8998 | 51.0024 | 0 | 51.0024 | 77 | 51.0024 | 6/28/9:00
6 | 28 | 1900-01-09 | 25.6 | 302 | 427 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 302 | 0 | 0 | 39.791 | 179.375 | 23.2634 | 86.148 | -75 | -2.9644 | 130.4069 | -87.4546 | 214.5454 | 68.0071 | 0 | 68.0071 | 78.08 | 68.0071 | 6/28/10:00
6 | 28 | 1900-01-10 | 26.7 | 394 | 242 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 394 | 0 | 0 | 39.791 | 179.4167 | 23.2612 | 86.148 | -75 | -2.9726 | 145.4048 | -79.4629 | 314.5371 | 99.7028 | 0 | 99.7028 | 80.06 | 99.7028 | 6/28/11:00
6 | 28 | 1900-01-11 | 27.2 | 307 | 104 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 307 | 0 | 0 | 39.791 | 179.4583 | 23.259 | 86.148 | -75 | -2.9809 | 160.4028 | -42.8813 | 264.1187 | 83.721 | 0 | 83.721 | 80.96 | 83.721 | 6/28/12:00
6 | 28 | 1900-01-12 | 28.3 | 386 | 315 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 386 | 0 | 0 | 39.791 | 179.5 | 23.2568 | 86.148 | -75 | -2.9891 | 175.4007 | -142.0566 | 243.9434 | 77.3258 | 0 | 77.3258 | 82.94 | 77.3258 | 6/28/13:00
6 | 28 | 1900-01-13 | 29.4 | 289 | 511 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 289 | 0 | 0 | 39.791 | 179.5417 | 23.2546 | 86.148 | -75 | -2.9973 | 190.3987 | -225.7016 | 63.2984 | 20.0645 | 0 | 20.0645 | 84.92 | 20.0645 | 6/28/14:00
6 | 28 | 1900-01-14 | 30 | 367 | 502 | 86 | 0 | 1 | 0 | 86 | 0 | 367 | 0 | 0 | 39.791 | 179.5833 | 23.2524 | 86.148 | -75 | -3.0056 | 205.3966 | -193.3157 | 173.6843 | 55.0549 | 0 | 55.0549 | 86 | 55.0549 | 6/28/15:00
6 | 28 | 1900-01-15 | 30 | 260 | 548 | 86 | 0 | 1 | 0 | 86 | 0 | 260 | 0 | 0 | 39.791 | 179.625 | 23.2501 | 86.148 | -75 | -3.0138 | 220.3946 | -156.2042 | 103.7958 | 32.9015 | 0 | 32.9015 | 86 | 32.9015 | 6/28/16:00
6 | 28 | 1900-01-16 | 30 | 254 | 145 | 86 | 0 | 1 | 0 | 86 | 0 | 254 | 0 | 0 | 39.791 | 179.6667 | 23.2479 | 86.148 | -75 | -3.022 | 235.3925 | -21.5124 | 232.4876 | 73.6945 | 0 | 73.6945 | 86 | 73.6945 | 6/28/17:00
6 | 28 | 1900-01-17 | 29.4 | 199 | 311 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 199 | 0 | 0 | 39.791 | 179.7083 | 23.2456 | 86.148 | -75 | -3.0302 | 250.3905 | 4.8654 | 203.8654 | 64.6218 | 0 | 64.6218 | 84.92 | 64.6218 | 6/28/18:00
6 | 28 | 1900-01-18 | 28.3 | 115 | 332 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 115 | 0 | 0 | 39.791 | 179.75 | 23.2433 | 86.148 | -75 | -3.0384 | 265.3884 | 65.0052 | 180.0052 | 57.0585 | 0 | 57.0585 | 82.94 | 57.0585 | 6/28/19:00
6 | 28 | 1900-01-19 | 26.7 | 41 | 12 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 41 | 0 | 0 | 39.791 | 179.7917 | 23.241 | 86.148 | -75 | -3.0466 | 280.3864 | 4.5579 | 45.5579 | 14.4411 | 0 | 14.4411 | 80.06 | 14.4411 | 6/28/20:00
6 | 28 | 1900-01-20 | 25.6 | 2 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 2 | 0 | 0 | 39.791 | 179.8333 | 23.2387 | 86.148 | -75 | -3.0548 | 295.3843 | 0 | 2 | 0.63397 | 0 | 0.63397 | 78.08 | 0.63397 | 6/28/21:00
6 | 28 | 1900-01-21 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 179.875 | 23.2364 | 86.148 | -75 | -3.0629 | 310.3823 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 6/28/22:00
6 | 28 | 1900-01-22 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 179.9167 | 23.234 | 86.148 | -75 | -3.0711 | 325.3802 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/28/23:00
6 | 28 | 1900-01-23 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 179.9583 | 23.2317 | 86.148 | -75 | -3.0793 | 340.3782 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/28/24:00
6 | 29 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 180 | 23.2293 | 86.148 | -75 | -3.0874 | -4.6239 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 6/29/1:00
6 | 29 | 1900-01-01 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 180.0417 | 23.227 | 86.148 | -75 | -3.0956 | 10.3741 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/29/2:00
6 | 29 | 1900-01-02 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 180.0833 | 23.2246 | 86.148 | -75 | -3.1038 | 25.3721 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/29/3:00
6 | 29 | 1900-01-03 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 180.125 | 23.2222 | 86.148 | -75 | -3.1119 | 40.37 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 6/29/4:00
6 | 29 | 1900-01-04 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 180.1667 | 23.2198 | 86.148 | -75 | -3.1201 | 55.368 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/29/5:00
6 | 29 | 1900-01-05 | 20 | 13 | 2 | 68 | 0 | 1 | 0 | 68 | 0 | 13 | 0 | 0 | 39.791 | 180.2083 | 23.2173 | 86.148 | -75 | -3.1282 | 70.366 | 0.97915 | 13.9791 | 4.4311 | 0 | 4.4311 | 68 | 4.4311 | 6/29/6:00
6 | 29 | 1900-01-06 | 21.7 | 68 | 162 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 68 | 0 | 0 | 39.791 | 180.25 | 23.2149 | 86.148 | -75 | -3.1363 | 85.3639 | 50.1145 | 118.1145 | 37.4402 | 0 | 37.4402 | 71.06 | 37.4402 | 6/29/7:00
6 | 29 | 1900-01-07 | 23.3 | 157 | 232 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 157 | 0 | 0 | 39.791 | 180.2917 | 23.2125 | 86.148 | -75 | -3.1444 | 100.3619 | 29.0531 | 186.0531 | 58.9756 | 0 | 58.9756 | 73.94 | 58.9756 | 6/29/8:00
6 | 29 | 1900-01-08 | 26.1 | 172 | 529 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 172 | 0 | 0 | 39.791 | 180.3333 | 23.21 | 86.148 | -75 | -3.1526 | 115.3599 | -26.5792 | 145.4208 | 46.0959 | 0 | 46.0959 | 78.98 | 46.0959 | 6/29/9:00
6 | 29 | 1900-01-09 | 27.8 | 277 | 545 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 277 | 0 | 0 | 39.791 | 180.375 | 23.2075 | 86.148 | -75 | -3.1607 | 130.3578 | -111.7885 | 165.2115 | 52.3691 | 0 | 52.3691 | 82.04 | 52.3691 | 6/29/10:00
6 | 29 | 1900-01-10 | 27.8 | 279 | 587 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 279 | 0 | 0 | 39.791 | 180.4167 | 23.205 | 86.148 | -75 | -3.1688 | 145.3558 | -193.0277 | 85.9723 | 27.2517 | 0 | 27.2517 | 82.04 | 27.2517 | 6/29/11:00
6 | 29 | 1900-01-11 | 28.9 | 424 | 276 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 424 | 0 | 0 | 39.791 | 180.4583 | 23.2025 | 86.148 | -75 | -3.1769 | 160.3538 | -113.9821 | 310.0179 | 98.2703 | 0 | 98.2703 | 84.02 | 98.2703 | 6/29/12:00
6 | 29 | 1900-01-12 | 28.9 | 421 | 94 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 421 | 0 | 0 | 39.791 | 180.5 | 23.2 | 86.148 | -75 | -3.185 | 175.3518 | -42.4699 | 378.5301 | 119.9874 | 0 | 119.9874 | 84.02 | 119.9874 | 6/29/13:00
6 | 29 | 1900-01-13 | 28.9 | 491 | 7 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 491 | 0 | 0 | 39.791 | 180.5417 | 23.1975 | 86.148 | -75 | -3.1931 | 190.3497 | -3.0987 | 487.9013 | 154.6562 | 0 | 154.6562 | 84.02 | 154.6562 | 6/29/14:00
6 | 29 | 1900-01-14 | 28.9 | 406 | 2 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 406 | 0 | 0 | 39.791 | 180.5833 | 23.195 | 86.148 | -75 | -3.2012 | 205.3477 | -0.77243 | 405.2276 | 128.4501 | 0 | 128.4501 | 84.02 | 128.4501 | 6/29/15:00
6 | 29 | 1900-01-15 | 28.3 | 368 | 399 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 368 | 0 | 0 | 39.791 | 180.625 | 23.1924 | 86.148 | -75 | -3.2092 | 220.3457 | -114.2174 | 253.7826 | 80.4446 | 0 | 80.4446 | 82.94 | 80.4446 | 6/29/16:00
6 | 29 | 1900-01-16 | 28.9 | 295 | 263 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 295 | 0 | 0 | 39.791 | 180.6667 | 23.1898 | 86.148 | -75 | -3.2173 | 235.3437 | -39.3518 | 255.6482 | 81.036 | 0 | 81.036 | 84.02 | 81.036 | 6/29/17:00
6 | 29 | 1900-01-17 | 28.9 | 191 | 292 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 191 | 0 | 0 | 39.791 | 180.7083 | 23.1873 | 86.148 | -75 | -3.2254 | 250.3417 | 4.1977 | 195.1977 | 61.8742 | 0 | 61.8742 | 84.02 | 61.8742 | 6/29/18:00
6 | 29 | 1900-01-18 | 28.9 | 124 | 134 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 124 | 0 | 0 | 39.791 | 180.75 | 23.1847 | 86.148 | -75 | -3.2334 | 265.3396 | 26.0727 | 150.0727 | 47.5704 | 0 | 47.5704 | 84.02 | 47.5704 | 6/29/19:00
6 | 29 | 1900-01-19 | 26.7 | 37 | 66 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 37 | 0 | 0 | 39.791 | 180.7917 | 23.1821 | 86.148 | -75 | -3.2415 | 280.3376 | 24.9933 | 61.9933 | 19.6508 | 0 | 19.6508 | 80.06 | 19.6508 | 6/29/20:00
6 | 29 | 1900-01-20 | 25 | 1 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 1 | 0 | 0 | 39.791 | 180.8333 | 23.1795 | 86.148 | -75 | -3.2495 | 295.3356 | 0 | 1 | 0.31698 | 0 | 0.31698 | 77 | 0.31698 | 6/29/21:00
6 | 29 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 180.875 | 23.1768 | 86.148 | -75 | -3.2576 | 310.3336 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 6/29/22:00
6 | 29 | 1900-01-22 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 180.9167 | 23.1742 | 86.148 | -75 | -3.2656 | 325.3316 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 6/29/23:00
6 | 29 | 1900-01-23 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 180.9583 | 23.1716 | 86.148 | -75 | -3.2736 | 340.3296 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 6/29/24:00
6 | 30 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 181 | 23.1689 | 86.148 | -75 | -3.2817 | -4.6724 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 6/30/1:00
6 | 30 | 1900-01-01 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 181.0417 | 23.1662 | 86.148 | -75 | -3.2897 | 10.3256 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/30/2:00
6 | 30 | 1900-01-02 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 181.0833 | 23.1635 | 86.148 | -75 | -3.2977 | 25.3236 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/30/3:00
6 | 30 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 181.125 | 23.1608 | 86.148 | -75 | -3.3057 | 40.3216 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 6/30/4:00
6 | 30 | 1900-01-04 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 181.1667 | 23.1581 | 86.148 | -75 | -3.3137 | 55.3196 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 6/30/5:00
6 | 30 | 1900-01-05 | 20.6 | 11 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 11 | 0 | 0 | 39.791 | 181.2083 | 23.1554 | 86.148 | -75 | -3.3217 | 70.3176 | 0 | 11 | 3.4868 | 0 | 3.4868 | 69.08 | 3.4868 | 6/30/6:00
6 | 30 | 1900-01-06 | 21.1 | 59 | 3 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 59 | 0 | 0 | 39.791 | 181.25 | 23.1527 | 86.148 | -75 | -3.3297 | 85.3156 | 0.92799 | 59.928 | 18.9961 | 0 | 18.9961 | 69.98 | 18.9961 | 6/30/7:00
6 | 30 | 1900-01-07 | 21.1 | 125 | 1 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 125 | 0 | 0 | 39.791 | 181.2917 | 23.1499 | 86.148 | -75 | -3.3376 | 100.3136 | 0.12511 | 125.1251 | 39.6625 | 0 | 39.6625 | 69.98 | 39.6625 | 6/30/8:00
6 | 30 | 1900-01-08 | 19.4 | 150 | 7 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 150 | 0 | 0 | 39.791 | 181.3333 | 23.1471 | 86.148 | -75 | -3.3456 | 115.3116 | -0.35346 | 149.6465 | 47.4353 | 0 | 47.4353 | 66.92 | 47.4353 | 6/30/9:00
6 | 30 | 1900-01-09 | 20.6 | 274 | 3 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 274 | 0 | 0 | 39.791 | 181.375 | 23.1444 | 86.148 | -75 | -3.3536 | 130.3096 | -0.61658 | 273.3834 | 86.6578 | 0 | 86.6578 | 69.08 | 86.6578 | 6/30/10:00
6 | 30 | 1900-01-10 | 23.3 | 314 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 314 | 0 | 0 | 39.791 | 181.4167 | 23.1416 | 86.148 | -75 | -3.3615 | 145.3076 | 0 | 314 | 99.5325 | 0 | 99.5325 | 73.94 | 99.5325 | 6/30/11:00
6 | 30 | 1900-01-11 | 23.3 | 379 | 4 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 379 | 0 | 0 | 39.791 | 181.4583 | 23.1388 | 86.148 | -75 | -3.3695 | 160.3056 | -1.655 | 377.345 | 119.6118 | 0 | 119.6118 | 73.94 | 119.6118 | 6/30/12:00
6 | 30 | 1900-01-12 | 23.9 | 418 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 418 | 0 | 0 | 39.791 | 181.5 | 23.136 | 86.148 | -75 | -3.3774 | 175.3036 | 0 | 418 | 132.4987 | 0 | 132.4987 | 75.02 | 132.4987 | 6/30/13:00
6 | 30 | 1900-01-13 | 24.4 | 409 | 2 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 409 | 0 | 0 | 39.791 | 181.5417 | 23.1331 | 86.148 | -75 | -3.3854 | 190.3017 | -0.88756 | 408.1124 | 129.3645 | 0 | 129.3645 | 75.92 | 129.3645 | 6/30/14:00
6 | 30 | 1900-01-14 | 25.6 | 433 | 1 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 433 | 0 | 0 | 39.791 | 181.5833 | 23.1303 | 86.148 | -75 | -3.3933 | 205.2997 | -0.38744 | 432.6126 | 137.1306 | 0 | 137.1306 | 78.08 | 137.1306 | 6/30/15:00
6 | 30 | 1900-01-15 | 25 | 360 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 360 | 0 | 0 | 39.791 | 181.625 | 23.1274 | 86.148 | -75 | -3.4012 | 220.2977 | 0 | 360 | 114.1137 | 0 | 114.1137 | 77 | 114.1137 | 6/30/16:00
6 | 30 | 1900-01-16 | 23.9 | 188 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 188 | 0 | 0 | 39.791 | 181.6667 | 23.1246 | 86.148 | -75 | -3.4092 | 235.2957 | 0 | 188 | 59.5927 | 0 | 59.5927 | 75.02 | 59.5927 | 6/30/17:00
6 | 30 | 1900-01-17 | 23.3 | 132 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 132 | 0 | 0 | 39.791 | 181.7083 | 23.1217 | 86.148 | -75 | -3.4171 | 250.2937 | 0 | 132 | 41.8417 | 0 | 41.8417 | 73.94 | 41.8417 | 6/30/18:00
6 | 30 | 1900-01-18 | 22.8 | 105 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 105 | 0 | 0 | 39.791 | 181.75 | 23.1188 | 86.148 | -75 | -3.425 | 265.2918 | 0 | 105 | 33.2832 | 0 | 33.2832 | 73.04 | 33.2832 | 6/30/19:00
6 | 30 | 1900-01-19 | 22.8 | 46 | 19 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 46 | 0 | 0 | 39.791 | 181.7917 | 23.1159 | 86.148 | -75 | -3.4329 | 280.2898 | 7.1723 | 53.1723 | 16.8547 | 0 | 16.8547 | 73.04 | 16.8547 | 6/30/20:00
6 | 30 | 1900-01-20 | 20.6 | 2 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 2 | 0 | 0 | 39.791 | 181.8333 | 23.113 | 86.148 | -75 | -3.4408 | 295.2878 | 0 | 2 | 0.63397 | 0 | 0.63397 | 69.08 | 0.63397 | 6/30/21:00
6 | 30 | 1900-01-21 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 181.875 | 23.1101 | 86.148 | -75 | -3.4487 | 310.2858 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 6/30/22:00
6 | 30 | 1900-01-22 | 19.3 | 0 | 0 | 66.74 | 0 | 1 | 0 | 66.74 | 0 | 0 | 0 | 0 | 39.791 | 181.9167 | 23.1071 | 86.148 | -75 | -3.4565 | 325.2839 | 0 | 0 | 0 | 0 | 0 | 66.74 | 0 | 6/30/23:00
6 | 30 | 1900-01-23 | 18.7 | 0 | 0 | 65.66 | 0 | 1 | 0 | 65.66 | 0 | 0 | 0 | 0 | 39.791 | 181.9583 | 23.1042 | 86.148 | -75 | -3.4644 | 340.2819 | 0 | 0 | 0 | 0 | 0 | 65.66 | 0 | 6/30/24:00
7 | 1 | 1899-12-31 | 18 | 0 | 0 | 64.4 | 0 | 1 | 0 | 64.4 | 0 | 0 | 0 | 0 | 39.791 | 182 | 23.1012 | 86.148 | -75 | -3.4723 | -4.7201 | 0 | 0 | 0 | 0 | 0 | 64.4 | 0 | 7/1/1:00
7 | 1 | 1900-01-01 | 17.4 | 0 | 0 | 63.32 | 0 | 1 | 0 | 63.32 | 0 | 0 | 0 | 0 | 39.791 | 182.0417 | 23.0982 | 86.148 | -75 | -3.4801 | 10.278 | 0 | 0 | 0 | 0 | 0 | 63.32 | 0 | 7/1/2:00
7 | 1 | 1900-01-02 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 182.0833 | 23.0953 | 86.148 | -75 | -3.488 | 25.276 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 7/1/3:00
7 | 1 | 1900-01-03 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 182.125 | 23.0923 | 86.148 | -75 | -3.4958 | 40.274 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 7/1/4:00
7 | 1 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 182.1667 | 23.0892 | 86.148 | -75 | -3.5037 | 55.2721 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 7/1/5:00
7 | 1 | 1900-01-05 | 15 | 9 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 9 | 0 | 0 | 39.791 | 182.2083 | 23.0862 | 86.148 | -75 | -3.5115 | 70.2701 | 0 | 9 | 2.8528 | 0 | 2.8528 | 59 | 2.8528 | 7/1/6:00
7 | 1 | 1900-01-06 | 16.1 | 73 | 98 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 73 | 0 | 0 | 39.791 | 182.25 | 23.0832 | 86.148 | -75 | -3.5193 | 85.2682 | 30.3045 | 103.3045 | 32.7457 | 0 | 32.7457 | 60.98 | 32.7457 | 7/1/7:00
7 | 1 | 1900-01-07 | 18.3 | 149 | 302 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 149 | 0 | 0 | 39.791 | 182.2917 | 23.0801 | 86.148 | -75 | -3.5272 | 100.2662 | 37.7215 | 186.7215 | 59.1874 | 0 | 59.1874 | 64.94 | 59.1874 | 7/1/8:00
7 | 1 | 1900-01-08 | 20 | 262 | 321 | 68 | 0 | 1 | 0 | 68 | 0 | 262 | 0 | 0 | 39.791 | 182.3333 | 23.0771 | 86.148 | -75 | -3.535 | 115.2643 | -16.3207 | 245.6793 | 77.876 | 0 | 77.876 | 68 | 77.876 | 7/1/9:00
7 | 1 | 1900-01-09 | 20.6 | 296 | 467 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 296 | 0 | 0 | 39.791 | 182.375 | 23.074 | 86.148 | -75 | -3.5428 | 130.2623 | -96.2231 | 199.7769 | 63.3258 | 0 | 63.3258 | 69.08 | 63.3258 | 7/1/10:00
7 | 1 | 1900-01-10 | 22.2 | 388 | 434 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 388 | 0 | 0 | 39.791 | 182.4167 | 23.0709 | 86.148 | -75 | -3.5506 | 145.2604 | -143.275 | 244.725 | 77.5736 | 0 | 77.5736 | 71.96 | 77.5736 | 7/1/11:00
7 | 1 | 1900-01-11 | 22.8 | 538 | 326 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 538 | 0 | 0 | 39.791 | 182.4583 | 23.0678 | 86.148 | -75 | -3.5584 | 160.2584 | -135.1709 | 402.8291 | 127.6898 | 0 | 127.6898 | 73.04 | 127.6898 | 7/1/12:00
7 | 1 | 1900-01-12 | 22.8 | 415 | 316 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 415 | 0 | 0 | 39.791 | 182.5 | 23.0647 | 86.148 | -75 | -3.5662 | 175.2565 | -143.4046 | 271.5954 | 86.091 | 0 | 86.091 | 73.04 | 86.091 | 7/1/13:00
7 | 1 | 1900-01-13 | 22.8 | 257 | 200 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 257 | 0 | 0 | 39.791 | 182.5417 | 23.0616 | 86.148 | -75 | -3.5739 | 190.2545 | -88.9978 | 168.0022 | 53.2538 | 0 | 53.2538 | 73.04 | 53.2538 | 7/1/14:00
7 | 1 | 1900-01-14 | 22.8 | 424 | 461 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 424 | 0 | 0 | 39.791 | 182.5833 | 23.0584 | 86.148 | -75 | -3.5817 | 205.2526 | -179.2218 | 244.7782 | 77.5904 | 0 | 77.5904 | 73.04 | 77.5904 | 7/1/15:00
7 | 1 | 1900-01-15 | 22.8 | 319 | 492 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 319 | 0 | 0 | 39.791 | 182.625 | 23.0553 | 86.148 | -75 | -3.5895 | 220.2506 | -142.1768 | 176.8232 | 56.0499 | 0 | 56.0499 | 73.04 | 56.0499 | 7/1/16:00
7 | 1 | 1900-01-16 | 23.9 | 223 | 564 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 223 | 0 | 0 | 39.791 | 182.6667 | 23.0521 | 86.148 | -75 | -3.5972 | 235.2487 | -85.9636 | 137.0364 | 43.4382 | 0 | 43.4382 | 75.02 | 43.4382 | 7/1/17:00
7 | 1 | 1900-01-17 | 23.3 | 204 | 328 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 204 | 0 | 0 | 39.791 | 182.7083 | 23.0489 | 86.148 | -75 | -3.605 | 250.2468 | 3.807 | 207.807 | 65.8712 | 0 | 65.8712 | 73.94 | 65.8712 | 7/1/18:00
7 | 1 | 1900-01-18 | 21.7 | 140 | 127 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 140 | 0 | 0 | 39.791 | 182.75 | 23.0457 | 86.148 | -75 | -3.6127 | 265.2448 | 24.3738 | 164.3738 | 52.1036 | 0 | 52.1036 | 71.06 | 52.1036 | 7/1/19:00
7 | 1 | 1900-01-19 | 19.4 | 47 | 25 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 47 | 0 | 0 | 39.791 | 182.7917 | 23.0425 | 86.148 | -75 | -3.6204 | 280.2429 | 9.4059 | 56.4059 | 17.8797 | 0 | 17.8797 | 66.92 | 17.8797 | 7/1/20:00
7 | 1 | 1900-01-20 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 182.8333 | 23.0393 | 86.148 | -75 | -3.6282 | 295.241 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 7/1/21:00
7 | 1 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 182.875 | 23.0361 | 86.148 | -75 | -3.6359 | 310.239 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 7/1/22:00
7 | 1 | 1900-01-22 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 182.9167 | 23.0329 | 86.148 | -75 | -3.6436 | 325.2371 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 7/1/23:00
7 | 1 | 1900-01-23 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 182.9583 | 23.0296 | 86.148 | -75 | -3.6513 | 340.2352 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 7/1/24:00
7 | 2 | 1899-12-31 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 183 | 23.0263 | 86.148 | -75 | -3.659 | -4.7667 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 7/2/1:00
7 | 2 | 1900-01-01 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 183.0417 | 23.0231 | 86.148 | -75 | -3.6667 | 10.2313 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 7/2/2:00
7 | 2 | 1900-01-02 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 183.0833 | 23.0198 | 86.148 | -75 | -3.6744 | 25.2294 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 7/2/3:00
7 | 2 | 1900-01-03 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 183.125 | 23.0165 | 86.148 | -75 | -3.682 | 40.2275 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 7/2/4:00
7 | 2 | 1900-01-04 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 183.1667 | 23.0132 | 86.148 | -75 | -3.6897 | 55.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7/2/5:00
7 | 2 | 1900-01-05 | 11.7 | 8 | 18 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 8 | 0 | 0 | 39.791 | 183.2083 | 23.0098 | 86.148 | -75 | -3.6974 | 70.2237 | 8.8103 | 16.8103 | 5.3286 | 5.3286 | 0 | 0 | 0 | 7/2/6:00
7 | 2 | 1900-01-06 | 14.4 | 58 | 240 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 58 | 0 | 0 | 39.791 | 183.25 | 23.0065 | 86.148 | -75 | -3.705 | 85.2217 | 74.1709 | 132.1709 | 41.8959 | 0 | 41.8959 | 57.92 | 41.8959 | 7/2/7:00
7 | 2 | 1900-01-07 | 16.1 | 151 | 327 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 151 | 0 | 0 | 39.791 | 183.2917 | 23.0031 | 86.148 | -75 | -3.7127 | 100.2198 | 40.7461 | 191.7461 | 60.7802 | 0 | 60.7802 | 60.98 | 60.7802 | 7/2/8:00
7 | 2 | 1900-01-08 | 17.2 | 338 | 98 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 338 | 0 | 0 | 39.791 | 183.3333 | 22.9998 | 86.148 | -75 | -3.7203 | 115.2179 | -5.0268 | 332.9732 | 105.5467 | 0 | 105.5467 | 62.96 | 105.5467 | 7/2/9:00
7 | 2 | 1900-01-09 | 18.9 | 264 | 538 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 264 | 0 | 0 | 39.791 | 183.375 | 22.9964 | 86.148 | -75 | -3.7279 | 130.216 | -111.1882 | 152.8118 | 48.4387 | 0 | 48.4387 | 66.02 | 48.4387 | 7/2/10:00
7 | 2 | 1900-01-10 | 19.4 | 303 | 528 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 303 | 0 | 0 | 39.791 | 183.4167 | 22.993 | 86.148 | -75 | -3.7356 | 145.2141 | -174.735 | 128.265 | 40.6578 | 0 | 40.6578 | 66.92 | 40.6578 | 7/2/11:00
7 | 2 | 1900-01-11 | 21.1 | 178 | 770 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 178 | 0 | 0 | 39.791 | 183.4583 | 22.9896 | 86.148 | -75 | -3.7432 | 160.2122 | -320.0362 | -142.0362 | -45.023 | 0 | -45.023 | 69.98 | -45.023 | 7/2/12:00
7 | 2 | 1900-01-12 | 21.1 | 215 | 793 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 215 | 0 | 0 | 39.791 | 183.5 | 22.9862 | 86.148 | -75 | -3.7508 | 175.2103 | -360.8003 | -145.8003 | -46.2161 | 0 | -46.2161 | 69.98 | -46.2161 | 7/2/13:00
7 | 2 | 1900-01-13 | 22.2 | 238 | 678 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 238 | 0 | 0 | 39.791 | 183.5417 | 22.9828 | 86.148 | -75 | -3.7584 | 190.2084 | -302.5958 | -64.5958 | -20.4758 | 0 | -20.4758 | 71.96 | -20.4758 | 7/2/14:00
7 | 2 | 1900-01-14 | 22.8 | 211 | 720 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 211 | 0 | 0 | 39.791 | 183.5833 | 22.9793 | 86.148 | -75 | -3.766 | 205.2065 | -280.9424 | -69.9424 | -22.1705 | 0 | -22.1705 | 73.04 | -22.1705 | 7/2/15:00
7 | 2 | 1900-01-15 | 22.8 | 177 | 725 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 177 | 0 | 0 | 39.791 | 183.625 | 22.9759 | 86.148 | -75 | -3.7736 | 220.2046 | -210.5964 | -33.5964 | -10.6495 | 0 | -10.6495 | 73.04 | -10.6495 | 7/2/16:00
7 | 2 | 1900-01-16 | 22.8 | 148 | 596 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 148 | 0 | 0 | 39.791 | 183.6667 | 22.9724 | 86.148 | -75 | -3.7811 | 235.2027 | -91.7489 | 56.2511 | 17.8306 | 0 | 17.8306 | 73.04 | 17.8306 | 7/2/17:00
7 | 2 | 1900-01-17 | 22.2 | 114 | 619 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 114 | 0 | 0 | 39.791 | 183.7083 | 22.969 | 86.148 | -75 | -3.7887 | 250.2008 | 6.2576 | 120.2576 | 38.1196 | 0 | 38.1196 | 71.96 | 38.1196 | 7/2/18:00
7 | 2 | 1900-01-18 | 21.7 | 81 | 408 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 81 | 0 | 0 | 39.791 | 183.75 | 22.9655 | 86.148 | -75 | -3.7963 | 265.1989 | 77.7219 | 158.7219 | 50.3121 | 0 | 50.3121 | 71.06 | 50.3121 | 7/2/19:00
7 | 2 | 1900-01-19 | 18.9 | 44 | 99 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 44 | 0 | 0 | 39.791 | 183.7917 | 22.962 | 86.148 | -75 | -3.8038 | 280.197 | 37.1175 | 81.1175 | 25.7128 | 0 | 25.7128 | 66.02 | 25.7128 | 7/2/20:00
7 | 2 | 1900-01-20 | 18.3 | 0 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 183.8333 | 22.9585 | 86.148 | -75 | -3.8114 | 295.1952 | 0.55083 | 0.55083 | 0.1746 | 0 | 0.1746 | 64.94 | 0.1746 | 7/2/21:00
7 | 2 | 1900-01-21 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 183.875 | 22.9549 | 86.148 | -75 | -3.8189 | 310.1933 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 7/2/22:00
7 | 2 | 1900-01-22 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 183.9167 | 22.9514 | 86.148 | -75 | -3.8264 | 325.1914 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 7/2/23:00
7 | 2 | 1900-01-23 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 183.9583 | 22.9479 | 86.148 | -75 | -3.8339 | 340.1895 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 7/2/24:00
7 | 3 | 1899-12-31 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 184 | 22.9443 | 86.148 | -75 | -3.8415 | -4.8124 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 7/3/1:00
7 | 3 | 1900-01-01 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 184.0417 | 22.9407 | 86.148 | -75 | -3.849 | 10.1858 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 7/3/2:00
7 | 3 | 1900-01-02 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 184.0833 | 22.9371 | 86.148 | -75 | -3.8565 | 25.1839 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 7/3/3:00
7 | 3 | 1900-01-03 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 184.125 | 22.9335 | 86.148 | -75 | -3.8639 | 40.182 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 7/3/4:00
7 | 3 | 1900-01-04 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 184.1667 | 22.9299 | 86.148 | -75 | -3.8714 | 55.1801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7/3/5:00
7 | 3 | 1900-01-05 | 13.3 | 7 | 25 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 7 | 0 | 0 | 39.791 | 184.2083 | 22.9263 | 86.148 | -75 | -3.8789 | 70.1783 | 12.232 | 19.232 | 6.0962 | 0 | 6.0962 | 55.94 | 6.0962 | 7/3/6:00
7 | 3 | 1900-01-06 | 13.9 | 54 | 345 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 54 | 0 | 0 | 39.791 | 184.25 | 22.9227 | 86.148 | -75 | -3.8864 | 85.1764 | 106.5284 | 160.5284 | 50.8847 | 0 | 50.8847 | 57.02 | 50.8847 | 7/3/7:00
7 | 3 | 1900-01-07 | 16.1 | 118 | 205 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 118 | 0 | 0 | 39.791 | 184.2917 | 22.919 | 86.148 | -75 | -3.8938 | 100.1745 | 25.4636 | 143.4636 | 45.4755 | 0 | 45.4755 | 60.98 | 45.4755 | 7/3/8:00
7 | 3 | 1900-01-08 | 19.4 | 115 | 598 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 115 | 0 | 0 | 39.791 | 184.3333 | 22.9154 | 86.148 | -75 | -3.9013 | 115.1727 | -31.0029 | 83.9971 | 26.6256 | 0 | 26.6256 | 66.92 | 26.6256 | 7/3/9:00
7 | 3 | 1900-01-09 | 21.1 | 124 | 719 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 124 | 0 | 0 | 39.791 | 184.375 | 22.9117 | 86.148 | -75 | -3.9087 | 130.1708 | -149.1211 | -25.1211 | -7.9629 | 0 | -7.9629 | 69.98 | -7.9629 | 7/3/10:00
7 | 3 | 1900-01-10 | 22.2 | 173 | 694 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 173 | 0 | 0 | 39.791 | 184.4167 | 22.908 | 86.148 | -75 | -3.9161 | 145.169 | -230.31 | -57.31 | -18.1663 | 0 | -18.1663 | 71.96 | -18.1663 | 7/3/11:00
7 | 3 | 1900-01-11 | 23.3 | 235 | 556 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 235 | 0 | 0 | 39.791 | 184.4583 | 22.9043 | 86.148 | -75 | -3.9236 | 160.1671 | -231.7075 | 3.2925 | 1.0437 | 0 | 1.0437 | 73.94 | 1.0437 | 7/3/12:00
7 | 3 | 1900-01-12 | 23.9 | 265 | 569 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 265 | 0 | 0 | 39.791 | 184.5 | 22.9006 | 86.148 | -75 | -3.931 | 175.1653 | -259.6128 | 5.3872 | 1.7076 | 0 | 1.7076 | 75.02 | 1.7076 | 7/3/13:00
7 | 3 | 1900-01-13 | 25 | 286 | 660 | 77 | 0 | 1 | 0 | 77 | 0 | 286 | 0 | 0 | 39.791 | 184.5417 | 22.8969 | 86.148 | -75 | -3.9384 | 190.1634 | -295.5022 | -9.5022 | -3.012 | 0 | -3.012 | 77 | -3.012 | 7/3/14:00
7 | 3 | 1900-01-14 | 25.6 | 269 | 432 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 269 | 0 | 0 | 39.791 | 184.5833 | 22.8931 | 86.148 | -75 | -3.9458 | 205.1616 | -169.2268 | 99.7732 | 31.6264 | 0 | 31.6264 | 78.08 | 31.6264 | 7/3/15:00
7 | 3 | 1900-01-15 | 25.6 | 269 | 521 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 269 | 0 | 0 | 39.791 | 184.625 | 22.8894 | 86.148 | -75 | -3.9532 | 220.1597 | -152.169 | 116.831 | 37.0334 | 0 | 37.0334 | 78.08 | 37.0334 | 7/3/16:00
7 | 3 | 1900-01-16 | 24.4 | 209 | 354 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 209 | 0 | 0 | 39.791 | 184.6667 | 22.8856 | 86.148 | -75 | -3.9606 | 235.1579 | -55.064 | 153.936 | 48.795 | 0 | 48.795 | 75.92 | 48.795 | 7/3/17:00
7 | 3 | 1900-01-17 | 24.4 | 334 | 62 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 334 | 0 | 0 | 39.791 | 184.7083 | 22.8819 | 86.148 | -75 | -3.9679 | 250.156 | 0.52936 | 334.5294 | 106.04 | 0 | 106.04 | 75.92 | 106.04 | 7/3/18:00
7 | 3 | 1900-01-18 | 23.9 | 142 | 45 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 142 | 0 | 0 | 39.791 | 184.75 | 22.8781 | 86.148 | -75 | -3.9753 | 265.1542 | 8.5053 | 150.5053 | 47.7075 | 0 | 47.7075 | 75.02 | 47.7075 | 7/3/19:00
7 | 3 | 1900-01-19 | 22.8 | 30 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 30 | 0 | 0 | 39.791 | 184.7917 | 22.8743 | 86.148 | -75 | -3.9827 | 280.1523 | 0 | 30 | 9.5095 | 0 | 9.5095 | 73.04 | 9.5095 | 7/3/20:00
7 | 3 | 1900-01-20 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 184.8333 | 22.8705 | 86.148 | -75 | -3.99 | 295.1505 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/3/21:00
7 | 3 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 184.875 | 22.8666 | 86.148 | -75 | -3.9973 | 310.1487 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/3/22:00
7 | 3 | 1900-01-22 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 184.9167 | 22.8628 | 86.148 | -75 | -4.0047 | 325.1468 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/3/23:00
7 | 3 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 184.9583 | 22.859 | 86.148 | -75 | -4.012 | 340.145 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/3/24:00
7 | 4 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 185 | 22.8551 | 86.148 | -75 | -4.0193 | -4.8568 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/4/1:00
7 | 4 | 1900-01-01 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 185.0417 | 22.8512 | 86.148 | -75 | -4.0266 | 10.1413 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/4/2:00
7 | 4 | 1900-01-02 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 185.0833 | 22.8474 | 86.148 | -75 | -4.0339 | 25.1395 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/4/3:00
7 | 4 | 1900-01-03 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 185.125 | 22.8435 | 86.148 | -75 | -4.0412 | 40.1377 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/4/4:00
7 | 4 | 1900-01-04 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 185.1667 | 22.8396 | 86.148 | -75 | -4.0485 | 55.1359 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 7/4/5:00
7 | 4 | 1900-01-05 | 19.4 | 8 | 16 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 8 | 0 | 0 | 39.791 | 185.2083 | 22.8356 | 86.148 | -75 | -4.0558 | 70.1341 | 7.8243 | 15.8243 | 5.016 | 0 | 5.016 | 66.92 | 5.016 | 7/4/6:00
7 | 4 | 1900-01-06 | 20 | 40 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 40 | 0 | 0 | 39.791 | 185.25 | 22.8317 | 86.148 | -75 | -4.063 | 85.1322 | 0 | 40 | 12.6793 | 0 | 12.6793 | 68 | 12.6793 | 7/4/7:00
7 | 4 | 1900-01-07 | 20.6 | 80 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 80 | 0 | 0 | 39.791 | 185.2917 | 22.8278 | 86.148 | -75 | -4.0703 | 100.1304 | 0 | 80 | 25.3586 | 0 | 25.3586 | 69.08 | 25.3586 | 7/4/8:00
7 | 4 | 1900-01-08 | 21.1 | 129 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 129 | 0 | 0 | 39.791 | 185.3333 | 22.8238 | 86.148 | -75 | -4.0775 | 115.1286 | 0 | 129 | 40.8907 | 0 | 40.8907 | 69.98 | 40.8907 | 7/4/9:00
7 | 4 | 1900-01-09 | 21.7 | 173 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 173 | 0 | 0 | 39.791 | 185.375 | 22.8198 | 86.148 | -75 | -4.0848 | 130.1268 | 0 | 173 | 54.838 | 0 | 54.838 | 71.06 | 54.838 | 7/4/10:00
7 | 4 | 1900-01-10 | 22.2 | 207 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 207 | 0 | 0 | 39.791 | 185.4167 | 22.8159 | 86.148 | -75 | -4.092 | 145.125 | 0 | 207 | 65.6154 | 0 | 65.6154 | 71.96 | 65.6154 | 7/4/11:00
7 | 4 | 1900-01-11 | 23.9 | 231 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 231 | 0 | 0 | 39.791 | 185.4583 | 22.8119 | 86.148 | -75 | -4.0992 | 160.1232 | 0 | 231 | 73.223 | 0 | 73.223 | 75.02 | 73.223 | 7/4/12:00
7 | 4 | 1900-01-12 | 23.9 | 241 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 241 | 0 | 0 | 39.791 | 185.5 | 22.8079 | 86.148 | -75 | -4.1064 | 175.1214 | 0 | 241 | 76.3928 | 0 | 76.3928 | 75.02 | 76.3928 | 7/4/13:00
7 | 4 | 1900-01-13 | 23.9 | 285 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 285 | 0 | 0 | 39.791 | 185.5417 | 22.8038 | 86.148 | -75 | -4.1136 | 190.1196 | 0 | 285 | 90.34 | 0 | 90.34 | 75.02 | 90.34 | 7/4/14:00
7 | 4 | 1900-01-14 | 26.1 | 355 | 266 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 355 | 0 | 0 | 39.791 | 185.5833 | 22.7998 | 86.148 | -75 | -4.1208 | 205.1178 | -104.6335 | 250.3665 | 79.3618 | 0 | 79.3618 | 78.98 | 79.3618 | 7/4/15:00
7 | 4 | 1900-01-15 | 26.7 | 235 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 235 | 0 | 0 | 39.791 | 185.625 | 22.7958 | 86.148 | -75 | -4.128 | 220.116 | 0 | 235 | 74.4909 | 0 | 74.4909 | 80.06 | 74.4909 | 7/4/16:00
7 | 4 | 1900-01-16 | 28.3 | 373 | 261 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 373 | 0 | 0 | 39.791 | 185.6667 | 22.7917 | 86.148 | -75 | -4.1352 | 235.1142 | -41.0388 | 331.9612 | 105.2259 | 0 | 105.2259 | 82.94 | 105.2259 | 7/4/17:00
7 | 4 | 1900-01-17 | 28.3 | 106 | 173 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 106 | 0 | 0 | 39.791 | 185.7083 | 22.7876 | 86.148 | -75 | -4.1423 | 250.1124 | 1.1928 | 107.1928 | 33.9782 | 0 | 33.9782 | 82.94 | 33.9782 | 7/4/18:00
7 | 4 | 1900-01-18 | 26.7 | 94 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 94 | 0 | 0 | 39.791 | 185.75 | 22.7836 | 86.148 | -75 | -4.1495 | 265.1106 | 0 | 94 | 29.7964 | 0 | 29.7964 | 80.06 | 29.7964 | 7/4/19:00
7 | 4 | 1900-01-19 | 25.6 | 29 | 39 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 29 | 0 | 0 | 39.791 | 185.7917 | 22.7795 | 86.148 | -75 | -4.1566 | 280.1088 | 14.5135 | 43.5135 | 13.793 | 0 | 13.793 | 78.08 | 13.793 | 7/4/20:00
7 | 4 | 1900-01-20 | 23.9 | 0 | 2 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 185.8333 | 22.7754 | 86.148 | -75 | -4.1638 | 295.1071 | 1.0967 | 1.0967 | 0.34764 | 0 | 0.34764 | 75.02 | 0.34764 | 7/4/21:00
7 | 4 | 1900-01-21 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 185.875 | 22.7713 | 86.148 | -75 | -4.1709 | 310.1053 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/4/22:00
7 | 4 | 1900-01-22 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 185.9167 | 22.7671 | 86.148 | -75 | -4.178 | 325.1035 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/4/23:00
7 | 4 | 1900-01-23 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 185.9583 | 22.763 | 86.148 | -75 | -4.1852 | 340.1017 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/4/24:00
7 | 5 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 186 | 22.7588 | 86.148 | -75 | -4.1923 | -4.9001 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/5/1:00
7 | 5 | 1900-01-01 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 186.0417 | 22.7547 | 86.148 | -75 | -4.1994 | 10.0982 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/5/2:00
7 | 5 | 1900-01-02 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 186.0833 | 22.7505 | 86.148 | -75 | -4.2064 | 25.0964 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/5/3:00
7 | 5 | 1900-01-03 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 186.125 | 22.7463 | 86.148 | -75 | -4.2135 | 40.0946 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/5/4:00
7 | 5 | 1900-01-04 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 186.1667 | 22.7421 | 86.148 | -75 | -4.2206 | 55.0929 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/5/5:00
7 | 5 | 1900-01-05 | 21.1 | 4 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 4 | 0 | 0 | 39.791 | 186.2083 | 22.7379 | 86.148 | -75 | -4.2276 | 70.0911 | 0 | 4 | 1.2679 | 0 | 1.2679 | 69.98 | 1.2679 | 7/5/6:00
7 | 5 | 1900-01-06 | 21.1 | 33 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 33 | 0 | 0 | 39.791 | 186.25 | 22.7337 | 86.148 | -75 | -4.2347 | 85.0893 | 0 | 33 | 10.4604 | 0 | 10.4604 | 69.98 | 10.4604 | 7/5/7:00
7 | 5 | 1900-01-07 | 21.7 | 71 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 71 | 0 | 0 | 39.791 | 186.2917 | 22.7294 | 86.148 | -75 | -4.2417 | 100.0876 | 0 | 71 | 22.5058 | 0 | 22.5058 | 71.06 | 22.5058 | 7/5/8:00
7 | 5 | 1900-01-08 | 21.7 | 120 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 120 | 0 | 0 | 39.791 | 186.3333 | 22.7252 | 86.148 | -75 | -4.2488 | 115.0858 | 0 | 120 | 38.0379 | 0 | 38.0379 | 71.06 | 38.0379 | 7/5/9:00
7 | 5 | 1900-01-09 | 22.2 | 166 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 166 | 0 | 0 | 39.791 | 186.375 | 22.7209 | 86.148 | -75 | -4.2558 | 130.0841 | 0 | 166 | 52.6191 | 0 | 52.6191 | 71.96 | 52.6191 | 7/5/10:00
7 | 5 | 1900-01-10 | 25 | 360 | 89 | 77 | 0 | 1 | 0 | 77 | 0 | 360 | 0 | 0 | 39.791 | 186.4167 | 22.7166 | 86.148 | -75 | -4.2628 | 145.0823 | -29.7289 | 330.2711 | 104.6902 | 0 | 104.6902 | 77 | 104.6902 | 7/5/11:00
7 | 5 | 1900-01-11 | 26.1 | 536 | 301 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 536 | 0 | 0 | 39.791 | 186.4583 | 22.7123 | 86.148 | -75 | -4.2698 | 160.0806 | -126.2066 | 409.7934 | 129.8973 | 0 | 129.8973 | 78.98 | 129.8973 | 7/5/12:00
7 | 5 | 1900-01-12 | 28.3 | 437 | 268 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 437 | 0 | 0 | 39.791 | 186.5 | 22.708 | 86.148 | -75 | -4.2768 | 175.0788 | -123.0523 | 313.9477 | 99.5159 | 0 | 99.5159 | 82.94 | 99.5159 | 7/5/13:00
7 | 5 | 1900-01-13 | 28.3 | 461 | 458 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 461 | 0 | 0 | 39.791 | 186.5417 | 22.7037 | 86.148 | -75 | -4.2838 | 190.0771 | -206.5099 | 254.4901 | 80.6689 | 0 | 80.6689 | 82.94 | 80.6689 | 7/5/14:00
7 | 5 | 1900-01-14 | 28.9 | 272 | 562 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 272 | 0 | 0 | 39.791 | 186.5833 | 22.6994 | 86.148 | -75 | -4.2907 | 205.0753 | -222.0391 | 49.9609 | 15.8367 | 0 | 15.8367 | 84.02 | 15.8367 | 7/5/15:00
7 | 5 | 1900-01-15 | 29.4 | 297 | 367 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 297 | 0 | 0 | 39.791 | 186.625 | 22.6951 | 86.148 | -75 | -4.2977 | 220.0736 | -108.4595 | 188.5405 | 59.764 | 0 | 59.764 | 84.92 | 59.764 | 7/5/16:00
7 | 5 | 1900-01-16 | 28.3 | 209 | 468 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 209 | 0 | 0 | 39.791 | 186.6667 | 22.6907 | 86.148 | -75 | -4.3047 | 235.0718 | -74.415 | 134.585 | 42.6611 | 0 | 42.6611 | 82.94 | 42.6611 | 7/5/17:00
7 | 5 | 1900-01-17 | 27.8 | 205 | 279 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 205 | 0 | 0 | 39.791 | 186.7083 | 22.6864 | 86.148 | -75 | -4.3116 | 250.0701 | 1.4454 | 206.4454 | 65.4396 | 0 | 65.4396 | 82.04 | 65.4396 | 7/5/18:00
7 | 5 | 1900-01-18 | 27.2 | 127 | 84 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 127 | 0 | 0 | 39.791 | 186.75 | 22.682 | 86.148 | -75 | -4.3185 | 265.0684 | 15.6108 | 142.6108 | 45.2051 | 0 | 45.2051 | 80.96 | 45.2051 | 7/5/19:00
7 | 5 | 1900-01-19 | 26.1 | 44 | 13 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 44 | 0 | 0 | 39.791 | 186.7917 | 22.6776 | 86.148 | -75 | -4.3255 | 280.0666 | 4.8187 | 48.8187 | 15.4747 | 0 | 15.4747 | 78.98 | 15.4747 | 7/5/20:00
7 | 5 | 1900-01-20 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 186.8333 | 22.6732 | 86.148 | -75 | -4.3324 | 295.0649 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/5/21:00
7 | 5 | 1900-01-21 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 186.875 | 22.6688 | 86.148 | -75 | -4.3393 | 310.0632 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/5/22:00
7 | 5 | 1900-01-22 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 186.9167 | 22.6644 | 86.148 | -75 | -4.3462 | 325.0615 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/5/23:00
7 | 5 | 1900-01-23 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 186.9583 | 22.66 | 86.148 | -75 | -4.3531 | 340.0597 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/5/24:00
7 | 6 | 1899-12-31 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 187 | 22.6555 | 86.148 | -75 | -4.36 | -4.942 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/6/1:00
7 | 6 | 1900-01-01 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 187.0417 | 22.651 | 86.148 | -75 | -4.3668 | 10.0563 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/6/2:00
7 | 6 | 1900-01-02 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 187.0833 | 22.6466 | 86.148 | -75 | -4.3737 | 25.0546 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/6/3:00
7 | 6 | 1900-01-03 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 187.125 | 22.6421 | 86.148 | -75 | -4.3805 | 40.0529 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/6/4:00
7 | 6 | 1900-01-04 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 187.1667 | 22.6376 | 86.148 | -75 | -4.3874 | 55.0512 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/6/5:00
7 | 6 | 1900-01-05 | 21.1 | 7 | 5 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 7 | 0 | 0 | 39.791 | 187.2083 | 22.6331 | 86.148 | -75 | -4.3942 | 70.0494 | 2.4414 | 9.4414 | 2.9928 | 0 | 2.9928 | 69.98 | 2.9928 | 7/6/6:00
7 | 6 | 1900-01-06 | 21.1 | 71 | 132 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 71 | 0 | 0 | 39.791 | 187.25 | 22.6286 | 86.148 | -75 | -4.401 | 85.0477 | 40.5853 | 111.5853 | 35.3706 | 0 | 35.3706 | 69.98 | 35.3706 | 7/6/7:00
7 | 6 | 1900-01-07 | 21.7 | 87 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 87 | 0 | 0 | 39.791 | 187.2917 | 22.624 | 86.148 | -75 | -4.4078 | 100.046 | 0 | 87 | 27.5775 | 0 | 27.5775 | 71.06 | 27.5775 | 7/6/8:00
7 | 6 | 1900-01-08 | 22.2 | 146 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 146 | 0 | 0 | 39.791 | 187.3333 | 22.6195 | 86.148 | -75 | -4.4146 | 115.0443 | 0 | 146 | 46.2795 | 0 | 46.2795 | 71.96 | 46.2795 | 7/6/9:00
7 | 6 | 1900-01-09 | 22.2 | 200 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 200 | 0 | 0 | 39.791 | 187.375 | 22.615 | 86.148 | -75 | -4.4214 | 130.0426 | 0 | 200 | 63.3965 | 0 | 63.3965 | 71.96 | 63.3965 | 7/6/10:00
7 | 6 | 1900-01-10 | 24.4 | 231 | 685 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 231 | 0 | 0 | 39.791 | 187.4167 | 22.6104 | 86.148 | -75 | -4.4282 | 145.0409 | -229.6702 | 1.3298 | 0.42152 | 0 | 0.42152 | 75.92 | 0.42152 | 7/6/11:00
7 | 6 | 1900-01-11 | 25 | 250 | 365 | 77 | 0 | 1 | 0 | 77 | 0 | 250 | 0 | 0 | 39.791 | 187.4583 | 22.6058 | 86.148 | -75 | -4.435 | 160.0393 | -153.5674 | 96.4326 | 30.5675 | 0 | 30.5675 | 77 | 30.5675 | 7/6/12:00
7 | 6 | 1900-01-12 | 26.1 | 226 | 651 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 226 | 0 | 0 | 39.791 | 187.5 | 22.6012 | 86.148 | -75 | -4.4417 | 175.0376 | -299.9531 | -73.9531 | -23.4418 | 0 | -23.4418 | 78.98 | -23.4418 | 7/6/13:00
7 | 6 | 1900-01-13 | 27.8 | 271 | 618 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 271 | 0 | 0 | 39.791 | 187.5417 | 22.5966 | 86.148 | -75 | -4.4485 | 190.0359 | -279.7272 | -8.7272 | -2.7664 | 0 | -2.7664 | 82.04 | -2.7664 | 7/6/14:00
7 | 6 | 1900-01-14 | 27.8 | 230 | 689 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 230 | 0 | 0 | 39.791 | 187.5833 | 22.592 | 86.148 | -75 | -4.4552 | 205.0342 | -273.4729 | -43.4729 | -13.7801 | 0 | -13.7801 | 82.04 | -13.7801 | 7/6/15:00
7 | 6 | 1900-01-15 | 28.3 | 139 | 732 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 139 | 0 | 0 | 39.791 | 187.625 | 22.5874 | 86.148 | -75 | -4.462 | 220.0325 | -217.6918 | -78.6918 | -24.9439 | 0 | -24.9439 | 82.94 | -24.9439 | 7/6/16:00
7 | 6 | 1900-01-16 | 28.3 | 185 | 608 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 185 | 0 | 0 | 39.791 | 187.6667 | 22.5827 | 86.148 | -75 | -4.4687 | 235.0308 | -97.8 | 87.2 | 27.6409 | 0 | 27.6409 | 82.94 | 27.6409 | 7/6/17:00
7 | 6 | 1900-01-17 | 27.8 | 156 | 422 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 156 | 0 | 0 | 39.791 | 187.7083 | 22.5781 | 86.148 | -75 | -4.4754 | 250.0291 | 1.4335 | 157.4335 | 49.9037 | 0 | 49.9037 | 82.04 | 49.9037 | 7/6/18:00
7 | 6 | 1900-01-18 | 26.7 | 89 | 466 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 89 | 0 | 0 | 39.791 | 187.75 | 22.5734 | 86.148 | -75 | -4.4821 | 265.0275 | 85.8237 | 174.8237 | 55.4161 | 0 | 55.4161 | 80.06 | 55.4161 | 7/6/19:00
7 | 6 | 1900-01-19 | 25 | 51 | 55 | 77 | 0 | 1 | 0 | 77 | 0 | 51 | 0 | 0 | 39.791 | 187.7917 | 22.5687 | 86.148 | -75 | -4.4888 | 280.0258 | 20.3031 | 71.3031 | 22.6018 | 0 | 22.6018 | 77 | 22.6018 | 7/6/20:00
7 | 6 | 1900-01-20 | 23.9 | 0 | 2 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 187.8333 | 22.564 | 86.148 | -75 | -4.4955 | 295.0241 | 1.0914 | 1.0914 | 0.34597 | 0 | 0.34597 | 75.02 | 0.34597 | 7/6/21:00
7 | 6 | 1900-01-21 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 187.875 | 22.5593 | 86.148 | -75 | -4.5021 | 310.0225 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/6/22:00
7 | 6 | 1900-01-22 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 187.9167 | 22.5546 | 86.148 | -75 | -4.5088 | 325.0208 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/6/23:00
7 | 6 | 1900-01-23 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 187.9583 | 22.5499 | 86.148 | -75 | -4.5155 | 340.0191 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 7/6/24:00
7 | 7 | 1899-12-31 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 188 | 22.5452 | 86.148 | -75 | -4.5221 | -4.9825 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 7/7/1:00
7 | 7 | 1900-01-01 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 188.0417 | 22.5404 | 86.148 | -75 | -4.5287 | 10.0158 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 7/7/2:00
7 | 7 | 1900-01-02 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 188.0833 | 22.5357 | 86.148 | -75 | -4.5354 | 25.0142 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 7/7/3:00
7 | 7 | 1900-01-03 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 188.125 | 22.5309 | 86.148 | -75 | -4.542 | 40.0125 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 7/7/4:00
7 | 7 | 1900-01-04 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 188.1667 | 22.5261 | 86.148 | -75 | -4.5486 | 55.0109 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 7/7/5:00
7 | 7 | 1900-01-05 | 16.7 | 6 | 50 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 6 | 0 | 0 | 39.791 | 188.2083 | 22.5213 | 86.148 | -75 | -4.5552 | 70.0092 | 24.3893 | 30.3893 | 9.6329 | 0 | 9.6329 | 62.06 | 9.6329 | 7/7/6:00
7 | 7 | 1900-01-06 | 17.2 | 43 | 402 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 43 | 0 | 0 | 39.791 | 188.25 | 22.5165 | 86.148 | -75 | -4.5617 | 85.0076 | 123.3554 | 166.3554 | 52.7317 | 0 | 52.7317 | 62.96 | 52.7317 | 7/7/7:00
7 | 7 | 1900-01-07 | 19.4 | 69 | 634 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 69 | 0 | 0 | 39.791 | 188.2917 | 22.5117 | 86.148 | -75 | -4.5683 | 100.0059 | 77.1578 | 146.1578 | 46.3295 | 0 | 46.3295 | 66.92 | 46.3295 | 7/7/8:00
7 | 7 | 1900-01-08 | 21.7 | 92 | 752 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 92 | 0 | 0 | 39.791 | 188.3333 | 22.5069 | 86.148 | -75 | -4.5749 | 115.0043 | -41.4079 | 50.5921 | 16.0368 | 0 | 16.0368 | 71.06 | 16.0368 | 7/7/9:00
7 | 7 | 1900-01-09 | 23.3 | 111 | 819 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 111 | 0 | 0 | 39.791 | 188.375 | 22.502 | 86.148 | -75 | -4.5814 | 130.0026 | -173.1332 | -62.1332 | -19.6951 | 0 | -19.6951 | 73.94 | -19.6951 | 7/7/10:00
7 | 7 | 1900-01-10 | 24.4 | 124 | 859 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 124 | 0 | 0 | 39.791 | 188.4167 | 22.4972 | 86.148 | -75 | -4.5879 | 145.001 | -289.1796 | -165.1796 | -52.359 | 0 | -52.359 | 75.92 | -52.359 | 7/7/11:00
7 | 7 | 1900-01-11 | 25.6 | 132 | 881 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 132 | 0 | 0 | 39.791 | 188.4583 | 22.4923 | 86.148 | -75 | -4.5945 | 159.9994 | -372.0317 | -240.0317 | -76.0859 | 0 | -76.0859 | 78.08 | -76.0859 | 7/7/12:00
7 | 7 | 1900-01-12 | 26.7 | 142 | 870 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 142 | 0 | 0 | 39.791 | 188.5 | 22.4874 | 86.148 | -75 | -4.601 | 174.9978 | -402.3504 | -260.3504 | -82.5265 | 0 | -82.5265 | 80.06 | -82.5265 | 7/7/13:00
7 | 7 | 1900-01-13 | 27.2 | 141 | 880 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 141 | 0 | 0 | 39.791 | 188.5417 | 22.4825 | 86.148 | -75 | -4.6075 | 189.9961 | -399.9366 | -258.9366 | -82.0784 | 0 | -82.0784 | 80.96 | -82.0784 | 7/7/14:00
7 | 7 | 1900-01-14 | 27.2 | 135 | 824 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 135 | 0 | 0 | 39.791 | 188.5833 | 22.4776 | 86.148 | -75 | -4.614 | 204.9945 | -328.6389 | -193.6389 | -61.3801 | 0 | -61.3801 | 80.96 | -61.3801 | 7/7/15:00
7 | 7 | 1900-01-15 | 27.8 | 130 | 772 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 130 | 0 | 0 | 39.791 | 188.625 | 22.4727 | 86.148 | -75 | -4.6205 | 219.9929 | -231.093 | -101.093 | -32.0447 | 0 | -32.0447 | 82.04 | -32.0447 | 7/7/16:00
7 | 7 | 1900-01-16 | 27.8 | 194 | 627 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 194 | 0 | 0 | 39.791 | 188.6667 | 22.4678 | 86.148 | -75 | -4.627 | 234.9913 | -102.0642 | 91.9358 | 29.1421 | 0 | 29.1421 | 82.04 | 29.1421 | 7/7/17:00
7 | 7 | 1900-01-17 | 27.2 | 97 | 662 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 97 | 0 | 0 | 39.791 | 188.7083 | 22.4628 | 86.148 | -75 | -4.6334 | 249.9896 | 1.0231 | 98.0231 | 31.0716 | 0 | 31.0716 | 80.96 | 31.0716 | 7/7/18:00
7 | 7 | 1900-01-18 | 26.1 | 65 | 551 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 65 | 0 | 0 | 39.791 | 188.75 | 22.4579 | 86.148 | -75 | -4.6399 | 264.988 | 100.5246 | 165.5246 | 52.4684 | 0 | 52.4684 | 78.98 | 52.4684 | 7/7/19:00
7 | 7 | 1900-01-19 | 23.3 | 45 | 104 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 45 | 0 | 0 | 39.791 | 188.7917 | 22.4529 | 86.148 | -75 | -4.6463 | 279.9864 | 38.2278 | 83.2278 | 26.3818 | 0 | 26.3818 | 73.94 | 26.3818 | 7/7/20:00
7 | 7 | 1900-01-20 | 21.1 | 0 | 4 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 188.8333 | 22.4479 | 86.148 | -75 | -4.6527 | 294.9848 | 2.1773 | 2.1773 | 0.69018 | 0 | 0.69018 | 69.98 | 0.69018 | 7/7/21:00
7 | 7 | 1900-01-21 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 188.875 | 22.4429 | 86.148 | -75 | -4.6592 | 309.9832 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/7/22:00
7 | 7 | 1900-01-22 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 188.9167 | 22.4379 | 86.148 | -75 | -4.6656 | 324.9816 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 7/7/23:00
7 | 7 | 1900-01-23 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 188.9583 | 22.4329 | 86.148 | -75 | -4.672 | 339.98 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/7/24:00
7 | 8 | 1899-12-31 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 189 | 22.4279 | 86.148 | -75 | -4.6784 | -5.0216 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 7/8/1:00
7 | 8 | 1900-01-01 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 189.0417 | 22.4229 | 86.148 | -75 | -4.6848 | 9.9768 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 7/8/2:00
7 | 8 | 1900-01-02 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 189.0833 | 22.4178 | 86.148 | -75 | -4.6911 | 24.9752 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 7/8/3:00
7 | 8 | 1900-01-03 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 189.125 | 22.4127 | 86.148 | -75 | -4.6975 | 39.9736 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 7/8/4:00
7 | 8 | 1900-01-04 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 189.1667 | 22.4077 | 86.148 | -75 | -4.7038 | 54.972 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 7/8/5:00
7 | 8 | 1900-01-05 | 15 | 6 | 12 | 59 | 0 | 1 | 0 | 59 | 0 | 6 | 0 | 0 | 39.791 | 189.2083 | 22.4026 | 86.148 | -75 | -4.7102 | 69.9705 | 5.8466 | 11.8466 | 3.7552 | 0 | 3.7552 | 59 | 3.7552 | 7/8/6:00
7 | 8 | 1900-01-06 | 16.7 | 68 | 201 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 68 | 0 | 0 | 39.791 | 189.25 | 22.3975 | 86.148 | -75 | -4.7165 | 84.9689 | 61.5375 | 129.5375 | 41.0611 | 0 | 41.0611 | 62.06 | 41.0611 | 7/8/7:00
7 | 8 | 1900-01-07 | 18.9 | 160 | 269 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 160 | 0 | 0 | 39.791 | 189.2917 | 22.3924 | 86.148 | -75 | -4.7228 | 99.9673 | 32.5043 | 192.5043 | 61.0205 | 0 | 61.0205 | 66.02 | 61.0205 | 7/8/8:00
7 | 8 | 1900-01-08 | 20 | 228 | 429 | 68 | 0 | 1 | 0 | 68 | 0 | 228 | 0 | 0 | 39.791 | 189.3333 | 22.3873 | 86.148 | -75 | -4.7291 | 114.9657 | -24.077 | 203.923 | 64.64 | 0 | 64.64 | 68 | 64.64 | 7/8/9:00
7 | 8 | 1900-01-09 | 21.7 | 242 | 595 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 242 | 0 | 0 | 39.791 | 189.375 | 22.3821 | 86.148 | -75 | -4.7354 | 129.9641 | -126.534 | 115.466 | 36.6007 | 0 | 36.6007 | 71.06 | 36.6007 | 7/8/10:00
7 | 8 | 1900-01-10 | 23.3 | 183 | 715 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 183 | 0 | 0 | 39.791 | 189.4167 | 22.377 | 86.148 | -75 | -4.7417 | 144.9626 | -241.7542 | -58.7542 | -18.624 | 0 | -18.624 | 73.94 | -18.624 | 7/8/11:00
7 | 8 | 1900-01-11 | 23.9 | 276 | 644 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 276 | 0 | 0 | 39.791 | 189.4583 | 22.3718 | 86.148 | -75 | -4.748 | 159.961 | -273.0196 | 2.9804 | 0.94474 | 0 | 0.94474 | 75.02 | 0.94474 | 7/8/12:00
7 | 8 | 1900-01-12 | 24.4 | 406 | 527 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 406 | 0 | 0 | 39.791 | 189.5 | 22.3667 | 86.148 | -75 | -4.7542 | 174.9594 | -244.682 | 161.318 | 51.135 | 0 | 51.135 | 75.92 | 51.135 | 7/8/13:00
7 | 8 | 1900-01-13 | 25.6 | 390 | 556 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 390 | 0 | 0 | 39.791 | 189.5417 | 22.3615 | 86.148 | -75 | -4.7605 | 189.9579 | -253.7667 | 136.2333 | 43.1836 | 0 | 43.1836 | 78.08 | 43.1836 | 7/8/14:00
7 | 8 | 1900-01-14 | 27.2 | 288 | 613 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 288 | 0 | 0 | 39.791 | 189.5833 | 22.3563 | 86.148 | -75 | -4.7667 | 204.9563 | -245.7202 | 42.2798 | 13.402 | 0 | 13.402 | 80.96 | 13.402 | 7/8/15:00
7 | 8 | 1900-01-15 | 26.7 | 380 | 405 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 380 | 0 | 0 | 39.791 | 189.625 | 22.3511 | 86.148 | -75 | -4.7729 | 219.9548 | -122.0585 | 257.9415 | 81.7629 | 0 | 81.7629 | 80.06 | 81.7629 | 7/8/16:00
7 | 8 | 1900-01-16 | 26.7 | 163 | 635 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 163 | 0 | 0 | 39.791 | 189.6667 | 22.3459 | 86.148 | -75 | -4.7791 | 234.9532 | -104.6381 | 58.3619 | 18.4997 | 0 | 18.4997 | 80.06 | 18.4997 | 7/8/17:00
7 | 8 | 1900-01-17 | 26.7 | 138 | 533 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 138 | 0 | 0 | 39.791 | 189.7083 | 22.3406 | 86.148 | -75 | -4.7854 | 249.9517 | -0.19859 | 137.8014 | 43.6806 | 0 | 43.6806 | 80.06 | 43.6806 | 7/8/18:00
7 | 8 | 1900-01-18 | 26.7 | 103 | 357 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 103 | 0 | 0 | 39.791 | 189.75 | 22.3354 | 86.148 | -75 | -4.7915 | 264.9501 | 64.4929 | 167.4929 | 53.0923 | 0 | 53.0923 | 80.06 | 53.0923 | 7/8/19:00
7 | 8 | 1900-01-19 | 23.3 | 51 | 52 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 51 | 0 | 0 | 39.791 | 189.7917 | 22.3301 | 86.148 | -75 | -4.7977 | 279.9486 | 19.0296 | 70.0296 | 22.1982 | 0 | 22.1982 | 73.94 | 22.1982 | 7/8/20:00
7 | 8 | 1900-01-20 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 189.8333 | 22.3249 | 86.148 | -75 | -4.8039 | 294.947 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/8/21:00
7 | 8 | 1900-01-21 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 189.875 | 22.3196 | 86.148 | -75 | -4.8101 | 309.9455 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/8/22:00
7 | 8 | 1900-01-22 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 189.9167 | 22.3143 | 86.148 | -75 | -4.8162 | 324.9439 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/8/23:00
7 | 8 | 1900-01-23 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 189.9583 | 22.309 | 86.148 | -75 | -4.8224 | 339.9424 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 7/8/24:00
7 | 9 | 1899-12-31 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 190 | 22.3037 | 86.148 | -75 | -4.8285 | -5.0591 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/9/1:00
7 | 9 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 190.0417 | 22.2984 | 86.148 | -75 | -4.8346 | 9.9394 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/9/2:00
7 | 9 | 1900-01-02 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 190.0833 | 22.2931 | 86.148 | -75 | -4.8407 | 24.9378 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 7/9/3:00
7 | 9 | 1900-01-03 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 190.125 | 22.2877 | 86.148 | -75 | -4.8468 | 39.9363 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 7/9/4:00
7 | 9 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 190.1667 | 22.2823 | 86.148 | -75 | -4.8529 | 54.9348 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 7/9/5:00
7 | 9 | 1900-01-05 | 16.1 | 6 | 5 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 6 | 0 | 0 | 39.791 | 190.2083 | 22.277 | 86.148 | -75 | -4.8589 | 69.9333 | 2.4329 | 8.4329 | 2.6731 | 0 | 2.6731 | 60.98 | 2.6731 | 7/9/6:00
7 | 9 | 1900-01-06 | 18.3 | 60 | 201 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 60 | 0 | 0 | 39.791 | 190.25 | 22.2716 | 86.148 | -75 | -4.865 | 84.9317 | 61.3796 | 121.3796 | 38.4752 | 0 | 38.4752 | 64.94 | 38.4752 | 7/9/7:00
7 | 9 | 1900-01-07 | 21.1 | 84 | 475 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 84 | 0 | 0 | 39.791 | 190.2917 | 22.2662 | 86.148 | -75 | -4.8711 | 99.9302 | 56.9392 | 140.9392 | 44.6753 | 0 | 44.6753 | 69.98 | 44.6753 | 7/9/8:00
7 | 9 | 1900-01-08 | 23.3 | 125 | 574 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 125 | 0 | 0 | 39.791 | 190.3333 | 22.2608 | 86.148 | -75 | -4.8771 | 114.9287 | -32.8822 | 92.1178 | 29.1997 | 0 | 29.1997 | 73.94 | 29.1997 | 7/9/9:00
7 | 9 | 1900-01-09 | 25 | 218 | 523 | 77 | 0 | 1 | 0 | 77 | 0 | 218 | 0 | 0 | 39.791 | 190.375 | 22.2554 | 86.148 | -75 | -4.8831 | 129.9272 | -111.9404 | 106.0596 | 33.619 | 0 | 33.619 | 77 | 33.619 | 7/9/10:00
7 | 9 | 1900-01-10 | 26.1 | 191 | 672 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 191 | 0 | 0 | 39.791 | 190.4167 | 22.2499 | 86.148 | -75 | -4.8891 | 144.9257 | -228.2767 | -37.2767 | -11.816 | 0 | -11.816 | 78.98 | -11.816 | 7/9/11:00
7 | 9 | 1900-01-11 | 26.7 | 262 | 602 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 262 | 0 | 0 | 39.791 | 190.4583 | 22.2445 | 86.148 | -75 | -4.8951 | 159.9242 | -256.2784 | 5.7216 | 1.8137 | 0 | 1.8137 | 80.06 | 1.8137 | 7/9/12:00
7 | 9 | 1900-01-12 | 27.8 | 169 | 697 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 169 | 0 | 0 | 39.791 | 190.5 | 22.239 | 86.148 | -75 | -4.9011 | 174.9227 | -324.9538 | -155.9538 | -49.4346 | 0 | -49.4346 | 82.04 | -49.4346 | 7/9/13:00
7 | 9 | 1900-01-13 | 28.9 | 237 | 731 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 237 | 0 | 0 | 39.791 | 190.5417 | 22.2336 | 86.148 | -75 | -4.9071 | 189.9212 | -335.1316 | -98.1316 | -31.106 | 0 | -31.106 | 84.02 | -31.106 | 7/9/14:00
7 | 9 | 1900-01-14 | 30 | 315 | 475 | 86 | 0 | 1 | 0 | 86 | 0 | 315 | 0 | 0 | 39.791 | 190.5833 | 22.2281 | 86.148 | -75 | -4.9131 | 204.9197 | -191.4042 | 123.5958 | 39.1777 | 0 | 39.1777 | 86 | 39.1777 | 7/9/15:00
7 | 9 | 1900-01-15 | 29.4 | 223 | 680 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 223 | 0 | 0 | 39.791 | 190.625 | 22.2226 | 86.148 | -75 | -4.919 | 219.9182 | -206.3792 | 16.6208 | 5.2685 | 0 | 5.2685 | 84.92 | 5.2685 | 7/9/16:00
7 | 9 | 1900-01-16 | 28.3 | 296 | 100 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 296 | 0 | 0 | 39.791 | 190.6667 | 22.2171 | 86.148 | -75 | -4.925 | 234.9168 | -16.6862 | 279.3138 | 88.5376 | 0 | 88.5376 | 82.94 | 88.5376 | 7/9/17:00
7 | 9 | 1900-01-17 | 28.3 | 186 | 109 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 186 | 0 | 0 | 39.791 | 190.7083 | 22.2116 | 86.148 | -75 | -4.9309 | 249.9153 | -0.25677 | 185.7432 | 58.8774 | 0 | 58.8774 | 82.94 | 58.8774 | 7/9/18:00
7 | 9 | 1900-01-18 | 27.2 | 146 | 106 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 146 | 0 | 0 | 39.791 | 190.75 | 22.2061 | 86.148 | -75 | -4.9368 | 264.9138 | 18.9537 | 164.9537 | 52.2874 | 0 | 52.2874 | 80.96 | 52.2874 | 7/9/19:00
7 | 9 | 1900-01-19 | 26.1 | 37 | 5 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 37 | 0 | 0 | 39.791 | 190.7917 | 22.2005 | 86.148 | -75 | -4.9427 | 279.9123 | 1.8214 | 38.8214 | 12.3057 | 0 | 12.3057 | 78.98 | 12.3057 | 7/9/20:00
7 | 9 | 1900-01-20 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 190.8333 | 22.195 | 86.148 | -75 | -4.9486 | 294.9108 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/9/21:00
7 | 9 | 1900-01-21 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 190.875 | 22.1894 | 86.148 | -75 | -4.9545 | 309.9094 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/9/22:00
7 | 9 | 1900-01-22 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 190.9167 | 22.1839 | 86.148 | -75 | -4.9604 | 324.9079 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/9/23:00
7 | 9 | 1900-01-23 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 190.9583 | 22.1783 | 86.148 | -75 | -4.9663 | 339.9064 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/9/24:00
7 | 10 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 191 | 22.1727 | 86.148 | -75 | -4.9721 | -5.095 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/10/1:00
7 | 10 | 1900-01-01 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 191.0417 | 22.1671 | 86.148 | -75 | -4.978 | 9.9035 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/10/2:00
7 | 10 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 191.0833 | 22.1614 | 86.148 | -75 | -4.9838 | 24.9021 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 7/10/3:00
7 | 10 | 1900-01-03 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 191.125 | 22.1558 | 86.148 | -75 | -4.9896 | 39.9006 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 7/10/4:00
7 | 10 | 1900-01-04 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 191.1667 | 22.1502 | 86.148 | -75 | -4.9954 | 54.8991 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/10/5:00
7 | 10 | 1900-01-05 | 18.9 | 7 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 7 | 0 | 0 | 39.791 | 191.2083 | 22.1445 | 86.148 | -75 | -5.0012 | 69.8977 | 0 | 7 | 2.2189 | 0 | 2.2189 | 66.02 | 2.2189 | 7/10/6:00
7 | 10 | 1900-01-06 | 20.6 | 69 | 21 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 69 | 0 | 0 | 39.791 | 191.25 | 22.1389 | 86.148 | -75 | -5.007 | 84.8963 | 6.3944 | 75.3944 | 23.8987 | 0 | 23.8987 | 69.08 | 23.8987 | 7/10/7:00
7 | 10 | 1900-01-07 | 22.2 | 138 | 268 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 138 | 0 | 0 | 39.791 | 191.2917 | 22.1332 | 86.148 | -75 | -5.0128 | 99.8948 | 31.842 | 169.842 | 53.837 | 0 | 53.837 | 71.96 | 53.837 | 7/10/8:00
7 | 10 | 1900-01-08 | 23.3 | 203 | 419 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 203 | 0 | 0 | 39.791 | 191.3333 | 22.1275 | 86.148 | -75 | -5.0185 | 114.8934 | -24.5329 | 178.4671 | 56.571 | 0 | 56.571 | 73.94 | 56.571 | 7/10/9:00
7 | 10 | 1900-01-09 | 25.6 | 288 | 426 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 288 | 0 | 0 | 39.791 | 191.375 | 22.1218 | 86.148 | -75 | -5.0243 | 129.8919 | -91.8093 | 196.1907 | 62.189 | 0 | 62.189 | 78.08 | 62.189 | 7/10/10:00
7 | 10 | 1900-01-10 | 26.7 | 346 | 337 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 346 | 0 | 0 | 39.791 | 191.4167 | 22.1161 | 86.148 | -75 | -5.03 | 144.8905 | -115.0468 | 230.9532 | 73.2081 | 0 | 73.2081 | 80.06 | 73.2081 | 7/10/11:00
7 | 10 | 1900-01-11 | 27.2 | 505 | 359 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 505 | 0 | 0 | 39.791 | 191.4583 | 22.1103 | 86.148 | -75 | -5.0357 | 159.8891 | -153.5037 | 351.4963 | 111.4182 | 0 | 111.4182 | 80.96 | 111.4182 | 7/10/12:00
7 | 10 | 1900-01-12 | 28.3 | 367 | 555 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 367 | 0 | 0 | 39.791 | 191.5 | 22.1046 | 86.148 | -75 | -5.0414 | 174.8876 | -259.8773 | 107.1227 | 33.956 | 0 | 33.956 | 82.94 | 33.956 | 7/10/13:00
7 | 10 | 1900-01-13 | 28.9 | 322 | 631 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 322 | 0 | 0 | 39.791 | 191.5417 | 22.0989 | 86.148 | -75 | -5.0471 | 189.8862 | -290.6362 | 31.3638 | 9.9418 | 0 | 9.9418 | 84.02 | 9.9418 | 7/10/14:00
7 | 10 | 1900-01-14 | 29.4 | 381 | 512 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 381 | 0 | 0 | 39.791 | 191.5833 | 22.0931 | 86.148 | -75 | -5.0528 | 204.8848 | -207.4393 | 173.5607 | 55.0157 | 0 | 55.0157 | 84.92 | 55.0157 | 7/10/15:00
7 | 10 | 1900-01-15 | 28.9 | 357 | 452 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 357 | 0 | 0 | 39.791 | 191.625 | 22.0873 | 86.148 | -75 | -5.0585 | 219.8834 | -138.1769 | 218.8231 | 69.3631 | 0 | 69.3631 | 84.02 | 69.3631 | 7/10/16:00
7 | 10 | 1900-01-16 | 29.4 | 254 | 445 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 254 | 0 | 0 | 39.791 | 191.6667 | 22.0815 | 86.148 | -75 | -5.0641 | 234.882 | -75.2103 | 178.7897 | 56.6732 | 0 | 56.6732 | 84.92 | 56.6732 | 7/10/17:00
7 | 10 | 1900-01-17 | 28.9 | 204 | 292 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 204 | 0 | 0 | 39.791 | 191.7083 | 22.0757 | 86.148 | -75 | -5.0698 | 249.8806 | -1.2854 | 202.7146 | 64.257 | 0 | 64.257 | 84.02 | 64.257 | 7/10/18:00
7 | 10 | 1900-01-18 | 28.3 | 123 | 136 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 123 | 0 | 0 | 39.791 | 191.75 | 22.0699 | 86.148 | -75 | -5.0754 | 264.8791 | 24.0598 | 147.0598 | 46.6154 | 0 | 46.6154 | 82.94 | 46.6154 | 7/10/19:00
7 | 10 | 1900-01-19 | 25.6 | 50 | 5 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 50 | 0 | 0 | 39.791 | 191.7917 | 22.0641 | 86.148 | -75 | -5.0811 | 279.8777 | 1.8128 | 51.8128 | 16.4238 | 0 | 16.4238 | 78.08 | 16.4238 | 7/10/20:00
7 | 10 | 1900-01-20 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 191.8333 | 22.0583 | 86.148 | -75 | -5.0867 | 294.8763 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/10/21:00
7 | 10 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 191.875 | 22.0524 | 86.148 | -75 | -5.0923 | 309.8749 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/10/22:00
7 | 10 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 191.9167 | 22.0466 | 86.148 | -75 | -5.0979 | 324.8735 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/10/23:00
7 | 10 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 191.9583 | 22.0407 | 86.148 | -75 | -5.1034 | 339.8721 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/10/24:00
7 | 11 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 192 | 22.0349 | 86.148 | -75 | -5.109 | -5.1293 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/11/1:00
7 | 11 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 192.0417 | 22.029 | 86.148 | -75 | -5.1146 | 9.8694 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/11/2:00
7 | 11 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 192.0833 | 22.0231 | 86.148 | -75 | -5.1201 | 24.868 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/11/3:00
7 | 11 | 1900-01-03 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 192.125 | 22.0171 | 86.148 | -75 | -5.1256 | 39.8666 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 7/11/4:00
7 | 11 | 1900-01-04 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 192.1667 | 22.0112 | 86.148 | -75 | -5.1311 | 54.8652 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 7/11/5:00
7 | 11 | 1900-01-05 | 17.8 | 6 | 20 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 6 | 0 | 0 | 39.791 | 192.2083 | 22.0053 | 86.148 | -75 | -5.1367 | 69.8638 | 9.7009 | 15.7009 | 4.9769 | 0 | 4.9769 | 64.04 | 4.9769 | 7/11/6:00
7 | 11 | 1900-01-06 | 19.4 | 42 | 345 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 42 | 0 | 0 | 39.791 | 192.25 | 21.9993 | 86.148 | -75 | -5.1421 | 84.8625 | 104.7191 | 146.7191 | 46.5074 | 0 | 46.5074 | 66.92 | 46.5074 | 7/11/7:00
7 | 11 | 1900-01-07 | 22.2 | 65 | 605 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 65 | 0 | 0 | 39.791 | 192.2917 | 21.9934 | 86.148 | -75 | -5.1476 | 99.8611 | 71.1834 | 136.1834 | 43.1677 | 0 | 43.1677 | 71.96 | 43.1677 | 7/11/8:00
7 | 11 | 1900-01-08 | 25 | 215 | 456 | 77 | 0 | 1 | 0 | 77 | 0 | 215 | 0 | 0 | 39.791 | 192.3333 | 21.9874 | 86.148 | -75 | -5.1531 | 114.8597 | -27.3228 | 187.6772 | 59.4904 | 0 | 59.4904 | 77 | 59.4904 | 7/11/9:00
7 | 11 | 1900-01-09 | 26.7 | 156 | 682 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 156 | 0 | 0 | 39.791 | 192.375 | 21.9814 | 86.148 | -75 | -5.1585 | 129.8584 | -148.0627 | 7.9373 | 2.516 | 0 | 2.516 | 80.06 | 2.516 | 7/11/10:00
7 | 11 | 1900-01-10 | 28.9 | 127 | 834 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 127 | 0 | 0 | 39.791 | 192.4167 | 21.9754 | 86.148 | -75 | -5.164 | 144.857 | -286.2127 | -159.2127 | -50.4676 | 0 | -50.4676 | 84.02 | -50.4676 | 7/11/11:00
7 | 11 | 1900-01-11 | 29.4 | 155 | 841 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 155 | 0 | 0 | 39.791 | 192.4583 | 21.9694 | 86.148 | -75 | -5.1694 | 159.8556 | -361.2675 | -206.2675 | -65.3832 | 0 | -65.3832 | 84.92 | -65.3832 | 7/11/12:00
7 | 11 | 1900-01-12 | 30.6 | 122 | 853 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 122 | 0 | 0 | 39.791 | 192.5 | 21.9634 | 86.148 | -75 | -5.1748 | 174.8543 | -401.234 | -279.234 | -88.5123 | 0 | -88.5123 | 87.08 | -88.5123 | 7/11/13:00
7 | 11 | 1900-01-13 | 31.1 | 124 | 887 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 124 | 0 | 0 | 39.791 | 192.5417 | 21.9574 | 86.148 | -75 | -5.1802 | 189.8529 | -410.533 | -286.533 | -90.826 | 0 | -90.826 | 87.98 | -90.826 | 7/11/14:00
7 | 11 | 1900-01-14 | 31.1 | 125 | 861 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 125 | 0 | 0 | 39.791 | 192.5833 | 21.9513 | 86.148 | -75 | -5.1856 | 204.8516 | -350.8085 | -225.8085 | -71.5773 | 0 | -71.5773 | 87.98 | -71.5773 | 7/11/15:00
7 | 11 | 1900-01-15 | 32.2 | 232 | 580 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 232 | 0 | 0 | 39.791 | 192.625 | 21.9453 | 86.148 | -75 | -5.191 | 219.8502 | -178.6307 | 53.3693 | 16.9171 | 0 | 16.9171 | 89.96 | 16.9171 | 7/11/16:00
7 | 11 | 1900-01-16 | 31.7 | 202 | 471 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 202 | 0 | 0 | 39.791 | 192.6667 | 21.9392 | 86.148 | -75 | -5.1964 | 234.8489 | -80.651 | 121.349 | 38.4655 | 0 | 38.4655 | 89.06 | 38.4655 | 7/11/17:00
7 | 11 | 1900-01-17 | 31.1 | 206 | 110 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 206 | 0 | 0 | 39.791 | 192.7083 | 21.9332 | 86.148 | -75 | -5.2017 | 249.8476 | -0.71618 | 205.2838 | 65.0714 | 0 | 65.0714 | 87.98 | 65.0714 | 7/11/18:00
7 | 11 | 1900-01-18 | 30 | 93 | 214 | 86 | 0 | 1 | 0 | 86 | 0 | 93 | 0 | 0 | 39.791 | 192.75 | 21.9271 | 86.148 | -75 | -5.2071 | 264.8462 | 37.4411 | 130.4411 | 41.3476 | 0 | 41.3476 | 86 | 41.3476 | 7/11/19:00
7 | 11 | 1900-01-19 | 28.9 | 34 | 13 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 34 | 0 | 0 | 39.791 | 192.7917 | 21.921 | 86.148 | -75 | -5.2124 | 279.8449 | 4.6905 | 38.6905 | 12.2642 | 0 | 12.2642 | 84.02 | 12.2642 | 7/11/20:00
7 | 11 | 1900-01-20 | 26.7 | 0 | 3 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 192.8333 | 21.9149 | 86.148 | -75 | -5.2177 | 294.8436 | 1.6151 | 1.6151 | 0.51196 | 0 | 0.51196 | 80.06 | 0.51196 | 7/11/21:00
7 | 11 | 1900-01-21 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 192.875 | 21.9087 | 86.148 | -75 | -5.223 | 309.8422 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 7/11/22:00
7 | 11 | 1900-01-22 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 192.9167 | 21.9026 | 86.148 | -75 | -5.2283 | 324.8409 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 7/11/23:00
7 | 11 | 1900-01-23 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 192.9583 | 21.8965 | 86.148 | -75 | -5.2336 | 339.8396 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 7/11/24:00
7 | 12 | 1899-12-31 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 193 | 21.8903 | 86.148 | -75 | -5.2389 | -5.1617 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/12/1:00
7 | 12 | 1900-01-01 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 193.0417 | 21.8841 | 86.148 | -75 | -5.2441 | 9.837 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/12/2:00
7 | 12 | 1900-01-02 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 193.0833 | 21.8779 | 86.148 | -75 | -5.2494 | 24.8357 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/12/3:00
7 | 12 | 1900-01-03 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 193.125 | 21.8718 | 86.148 | -75 | -5.2546 | 39.8344 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/12/4:00
7 | 12 | 1900-01-04 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 193.1667 | 21.8656 | 86.148 | -75 | -5.2598 | 54.833 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/12/5:00
7 | 12 | 1900-01-05 | 21.1 | 5 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 5 | 0 | 0 | 39.791 | 193.2083 | 21.8593 | 86.148 | -75 | -5.265 | 69.8317 | 0 | 5 | 1.5849 | 0 | 1.5849 | 69.98 | 1.5849 | 7/12/6:00
7 | 12 | 1900-01-06 | 22.8 | 63 | 115 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 63 | 0 | 0 | 39.791 | 193.25 | 21.8531 | 86.148 | -75 | -5.2702 | 84.8304 | 34.7853 | 97.7853 | 30.9962 | 0 | 30.9962 | 73.04 | 30.9962 | 7/12/7:00
7 | 12 | 1900-01-07 | 25.6 | 122 | 338 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 122 | 0 | 0 | 39.791 | 193.2917 | 21.8469 | 86.148 | -75 | -5.2754 | 99.8292 | 39.3454 | 161.3454 | 51.1437 | 0 | 51.1437 | 78.08 | 51.1437 | 7/12/8:00
7 | 12 | 1900-01-08 | 27.2 | 179 | 482 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 179 | 0 | 0 | 39.791 | 193.3333 | 21.8406 | 86.148 | -75 | -5.2805 | 114.8279 | -29.5893 | 149.4107 | 47.3606 | 0 | 47.3606 | 80.96 | 47.3606 | 7/12/9:00
7 | 12 | 1900-01-09 | 29.4 | 220 | 570 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 220 | 0 | 0 | 39.791 | 193.375 | 21.8344 | 86.148 | -75 | -5.2857 | 129.8266 | -124.7118 | 95.2882 | 30.2047 | 0 | 30.2047 | 84.92 | 30.2047 | 7/12/10:00
7 | 12 | 1900-01-10 | 30.6 | 257 | 555 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 257 | 0 | 0 | 39.791 | 193.4167 | 21.8281 | 86.148 | -75 | -5.2908 | 144.8253 | -191.5211 | 65.4789 | 20.7557 | 0 | 20.7557 | 87.08 | 20.7557 | 7/12/11:00
7 | 12 | 1900-01-11 | 30.6 | 356 | 362 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 356 | 0 | 0 | 39.791 | 193.4583 | 21.8218 | 86.148 | -75 | -5.296 | 159.824 | -156.2595 | 199.7405 | 63.3142 | 0 | 63.3142 | 87.08 | 63.3142 | 7/12/12:00
7 | 12 | 1900-01-12 | 31.7 | 309 | 598 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 309 | 0 | 0 | 39.791 | 193.5 | 21.8155 | 86.148 | -75 | -5.3011 | 174.8227 | -282.6231 | 26.3769 | 8.361 | 0 | 8.361 | 89.06 | 8.361 | 7/12/13:00
7 | 12 | 1900-01-13 | 32.8 | 283 | 637 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 283 | 0 | 0 | 39.791 | 193.5417 | 21.8092 | 86.148 | -75 | -5.3062 | 189.8215 | -296.3105 | -13.3105 | -4.2192 | 0 | -4.2192 | 91.04 | -4.2192 | 7/12/14:00
7 | 12 | 1900-01-14 | 32.8 | 290 | 608 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 290 | 0 | 0 | 39.791 | 193.5833 | 21.8029 | 86.148 | -75 | -5.3113 | 204.8202 | -249.1701 | 40.8299 | 12.9424 | 0 | 12.9424 | 91.04 | 12.9424 | 7/12/15:00
7 | 12 | 1900-01-15 | 32.8 | 284 | 535 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 284 | 0 | 0 | 39.791 | 193.625 | 21.7966 | 86.148 | -75 | -5.3163 | 219.8189 | -166.0352 | 117.9648 | 37.3928 | 0 | 37.3928 | 91.04 | 37.3928 | 7/12/16:00
7 | 12 | 1900-01-16 | 32.8 | 296 | 393 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 296 | 0 | 0 | 39.791 | 193.6667 | 21.7902 | 86.148 | -75 | -5.3214 | 234.8176 | -68.1953 | 227.8047 | 72.2101 | 0 | 72.2101 | 91.04 | 72.2101 | 7/12/17:00
7 | 12 | 1900-01-17 | 32.2 | 210 | 336 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 210 | 0 | 0 | 39.791 | 193.7083 | 21.7839 | 86.148 | -75 | -5.3265 | 249.8164 | -2.9163 | 207.0837 | 65.6419 | 0 | 65.6419 | 89.96 | 65.6419 | 7/12/18:00
7 | 12 | 1900-01-18 | 31.1 | 124 | 212 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 124 | 0 | 0 | 39.791 | 193.75 | 21.7775 | 86.148 | -75 | -5.3315 | 264.8151 | 36.6665 | 160.6665 | 50.9285 | 0 | 50.9285 | 87.98 | 50.9285 | 7/12/19:00
7 | 12 | 1900-01-19 | 29.4 | 48 | 28 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 48 | 0 | 0 | 39.791 | 193.7917 | 21.7711 | 86.148 | -75 | -5.3365 | 279.8139 | 10.052 | 58.052 | 18.4015 | 0 | 18.4015 | 84.92 | 18.4015 | 7/12/20:00
7 | 12 | 1900-01-20 | 27.8 | 0 | 0 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 0 | 0 | 0 | 39.791 | 193.8333 | 21.7647 | 86.148 | -75 | -5.3415 | 294.8126 | 0 | 0 | 0 | 0 | 0 | 82.04 | 0 | 7/12/21:00
7 | 12 | 1900-01-21 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 193.875 | 21.7583 | 86.148 | -75 | -5.3465 | 309.8114 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 7/12/22:00
7 | 12 | 1900-01-22 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 193.9167 | 21.7519 | 86.148 | -75 | -5.3515 | 324.8101 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 7/12/23:00
7 | 12 | 1900-01-23 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 193.9583 | 21.7455 | 86.148 | -75 | -5.3565 | 339.8089 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 7/12/24:00
7 | 13 | 1899-12-31 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 194 | 21.7391 | 86.148 | -75 | -5.3614 | -5.1924 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/13/1:00
7 | 13 | 1900-01-01 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 194.0417 | 21.7326 | 86.148 | -75 | -5.3664 | 9.8064 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 7/13/2:00
7 | 13 | 1900-01-02 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 194.0833 | 21.7262 | 86.148 | -75 | -5.3713 | 24.8052 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/13/3:00
7 | 13 | 1900-01-03 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 194.125 | 21.7197 | 86.148 | -75 | -5.3762 | 39.8039 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/13/4:00
7 | 13 | 1900-01-04 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 194.1667 | 21.7132 | 86.148 | -75 | -5.3811 | 54.8027 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/13/5:00
7 | 13 | 1900-01-05 | 22.8 | 5 | 31 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 5 | 0 | 0 | 39.791 | 194.2083 | 21.7067 | 86.148 | -75 | -5.386 | 69.8015 | 14.979 | 19.979 | 6.333 | 0 | 6.333 | 73.04 | 6.333 | 7/13/6:00
7 | 13 | 1900-01-06 | 24.4 | 41 | 381 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 41 | 0 | 0 | 39.791 | 194.25 | 21.7002 | 86.148 | -75 | -5.3909 | 84.8003 | 114.8098 | 155.8098 | 49.389 | 0 | 49.389 | 75.92 | 49.389 | 7/13/7:00
7 | 13 | 1900-01-07 | 27.2 | 66 | 617 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 66 | 0 | 0 | 39.791 | 194.2917 | 21.6937 | 86.148 | -75 | -5.3958 | 99.7991 | 70.9903 | 136.9903 | 43.4235 | 0 | 43.4235 | 80.96 | 43.4235 | 7/13/8:00
7 | 13 | 1900-01-08 | 28.9 | 89 | 736 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 89 | 0 | 0 | 39.791 | 194.3333 | 21.6872 | 86.148 | -75 | -5.4006 | 114.7978 | -46.3393 | 42.6607 | 13.5227 | 0 | 13.5227 | 84.02 | 13.5227 | 7/13/9:00
7 | 13 | 1900-01-09 | 30.6 | 108 | 804 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 108 | 0 | 0 | 39.791 | 194.375 | 21.6807 | 86.148 | -75 | -5.4055 | 129.7966 | -177.3543 | -69.3543 | -21.9841 | 0 | -21.9841 | 87.08 | -21.9841 | 7/13/10:00
7 | 13 | 1900-01-10 | 32.2 | 133 | 817 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 133 | 0 | 0 | 39.791 | 194.4167 | 21.6741 | 86.148 | -75 | -5.4103 | 144.7954 | -283.5739 | -150.5739 | -47.7293 | 0 | -47.7293 | 89.96 | -47.7293 | 7/13/11:00
7 | 13 | 1900-01-11 | 32.8 | 159 | 770 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 159 | 0 | 0 | 39.791 | 194.4583 | 21.6676 | 86.148 | -75 | -5.4151 | 159.7942 | -334.0629 | -175.0629 | -55.4919 | 0 | -55.4919 | 91.04 | -55.4919 | 7/13/12:00
7 | 13 | 1900-01-12 | 33.9 | 154 | 800 | 93.02 | 0 | 1 | 0 | 93.02 | 0 | 154 | 0 | 0 | 39.791 | 194.5 | 21.661 | 86.148 | -75 | -5.4199 | 174.793 | -379.9585 | -225.9585 | -71.6249 | 0 | -71.6249 | 93.02 | -71.6249 | 7/13/13:00
7 | 13 | 1900-01-13 | 34.4 | 143 | 752 | 93.92 | 0 | 1 | 0 | 93.92 | 0 | 143 | 0 | 0 | 39.791 | 194.5417 | 21.6544 | 86.148 | -75 | -5.4247 | 189.7918 | -351.6294 | -208.6294 | -66.1319 | 0 | -66.1319 | 93.92 | -66.1319 | 7/13/14:00
7 | 13 | 1900-01-14 | 35 | 164 | 772 | 95 | 0 | 1 | 0 | 95 | 0 | 164 | 0 | 0 | 39.791 | 194.5833 | 21.6478 | 86.148 | -75 | -5.4294 | 204.7906 | -318.2815 | -154.2815 | -48.9045 | 0 | -48.9045 | 95 | -48.9045 | 7/13/15:00
7 | 13 | 1900-01-15 | 35 | 127 | 759 | 95 | 0 | 1 | 0 | 95 | 0 | 127 | 0 | 0 | 39.791 | 194.625 | 21.6412 | 86.148 | -75 | -5.4342 | 219.7894 | -237.4042 | -110.4042 | -34.9962 | 0 | -34.9962 | 95 | -34.9962 | 7/13/16:00
7 | 13 | 1900-01-16 | 34.4 | 103 | 789 | 93.92 | 0 | 1 | 0 | 93.92 | 0 | 103 | 0 | 0 | 39.791 | 194.6667 | 21.6346 | 86.148 | -75 | -5.4389 | 234.7883 | -138.7726 | -35.7726 | -11.3393 | 0 | -11.3393 | 93.92 | -11.3393 | 7/13/17:00
7 | 13 | 1900-01-17 | 34.4 | 82 | 710 | 93.92 | 0 | 1 | 0 | 93.92 | 0 | 82 | 0 | 0 | 39.791 | 194.7083 | 21.628 | 86.148 | -75 | -5.4437 | 249.7871 | -7.7442 | 74.2558 | 23.5378 | 0 | 23.5378 | 93.92 | 23.5378 | 7/13/18:00
7 | 13 | 1900-01-18 | 32.8 | 58 | 565 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 58 | 0 | 0 | 39.791 | 194.75 | 21.6213 | 86.148 | -75 | -5.4484 | 264.7859 | 96.5593 | 154.5593 | 48.9926 | 0 | 48.9926 | 91.04 | 48.9926 | 7/13/19:00
7 | 13 | 1900-01-19 | 31.1 | 32 | 265 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 32 | 0 | 0 | 39.791 | 194.7917 | 21.6147 | 86.148 | -75 | -5.4531 | 279.7847 | 94.6447 | 126.6447 | 40.1442 | 0 | 40.1442 | 87.98 | 40.1442 | 7/13/20:00
7 | 13 | 1900-01-20 | 29.4 | 0 | 7 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 0 | 0 | 0 | 39.791 | 194.8333 | 21.608 | 86.148 | -75 | -5.4578 | 294.7836 | 3.746 | 3.746 | 1.1874 | 0 | 1.1874 | 84.92 | 1.1874 | 7/13/21:00
7 | 13 | 1900-01-21 | 27.8 | 0 | 0 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 0 | 0 | 0 | 39.791 | 194.875 | 21.6013 | 86.148 | -75 | -5.4625 | 309.7824 | 0 | 0 | 0 | 0 | 0 | 82.04 | 0 | 7/13/22:00
7 | 13 | 1900-01-22 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 194.9167 | 21.5947 | 86.148 | -75 | -5.4671 | 324.7812 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 7/13/23:00
7 | 13 | 1900-01-23 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 194.9583 | 21.588 | 86.148 | -75 | -5.4718 | 339.7801 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 7/13/24:00
7 | 14 | 1899-12-31 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 195 | 21.5812 | 86.148 | -75 | -5.4764 | -5.2211 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 7/14/1:00
7 | 14 | 1900-01-01 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 195.0417 | 21.5745 | 86.148 | -75 | -5.4811 | 9.7777 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 7/14/2:00
7 | 14 | 1900-01-02 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 195.0833 | 21.5678 | 86.148 | -75 | -5.4857 | 24.7766 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 7/14/3:00
7 | 14 | 1900-01-03 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 195.125 | 21.5611 | 86.148 | -75 | -5.4903 | 39.7754 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 7/14/4:00
7 | 14 | 1900-01-04 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 195.1667 | 21.5543 | 86.148 | -75 | -5.4948 | 54.7743 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 7/14/5:00
7 | 14 | 1900-01-05 | 24.4 | 4 | 21 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 4 | 0 | 0 | 39.791 | 195.2083 | 21.5475 | 86.148 | -75 | -5.4994 | 69.7731 | 10.125 | 14.125 | 4.4774 | 0 | 4.4774 | 75.92 | 4.4774 | 7/14/6:00
7 | 14 | 1900-01-06 | 25.6 | 45 | 331 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 45 | 0 | 0 | 39.791 | 195.25 | 21.5408 | 86.148 | -75 | -5.504 | 84.772 | 99.3347 | 144.3347 | 45.7516 | 0 | 45.7516 | 78.08 | 45.7516 | 7/14/7:00
7 | 14 | 1900-01-07 | 28.3 | 75 | 580 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 75 | 0 | 0 | 39.791 | 195.2917 | 21.534 | 86.148 | -75 | -5.5085 | 99.7709 | 65.8941 | 140.8941 | 44.661 | 0 | 44.661 | 82.94 | 44.661 | 7/14/8:00
7 | 14 | 1900-01-08 | 30 | 102 | 708 | 86 | 0 | 1 | 0 | 86 | 0 | 102 | 0 | 0 | 39.791 | 195.3333 | 21.5272 | 86.148 | -75 | -5.513 | 114.7697 | -45.7622 | 56.2378 | 17.8264 | 0 | 17.8264 | 86 | 17.8264 | 7/14/9:00
7 | 14 | 1900-01-09 | 31.7 | 123 | 781 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 123 | 0 | 0 | 39.791 | 195.375 | 21.5204 | 86.148 | -75 | -5.5175 | 129.7686 | -173.7666 | -50.7666 | -16.0921 | 0 | -16.0921 | 89.06 | -16.0921 | 7/14/10:00
7 | 14 | 1900-01-10 | 33.3 | 138 | 824 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 138 | 0 | 0 | 39.791 | 195.4167 | 21.5136 | 86.148 | -75 | -5.5221 | 144.7675 | -287.7454 | -149.7454 | -47.4667 | 0 | -47.4667 | 91.94 | -47.4667 | 7/14/11:00
7 | 14 | 1900-01-11 | 33.9 | 209 | 742 | 93.02 | 0 | 1 | 0 | 93.02 | 0 | 209 | 0 | 0 | 39.791 | 195.4583 | 21.5067 | 86.148 | -75 | -5.5265 | 159.7664 | -323.6181 | -114.6181 | -36.3319 | 0 | -36.3319 | 93.02 | -36.3319 | 7/14/12:00
7 | 14 | 1900-01-12 | 35 | 251 | 488 | 95 | 0 | 1 | 0 | 95 | 0 | 251 | 0 | 0 | 39.791 | 195.5 | 21.4999 | 86.148 | -75 | -5.531 | 174.7652 | -232.9621 | 18.0379 | 5.7177 | 0 | 5.7177 | 95 | 5.7177 | 7/14/13:00
7 | 14 | 1900-01-13 | 35 | 345 | 370 | 95 | 0 | 1 | 0 | 95 | 0 | 345 | 0 | 0 | 39.791 | 195.5417 | 21.493 | 86.148 | -75 | -5.5355 | 189.7641 | -173.9412 | 171.0588 | 54.2226 | 0 | 54.2226 | 95 | 54.2226 | 7/14/14:00
7 | 14 | 1900-01-14 | 36.1 | 265 | 502 | 96.98 | 0 | 1 | 0 | 96.98 | 0 | 265 | 0 | 0 | 39.791 | 195.5833 | 21.4862 | 86.148 | -75 | -5.5399 | 204.763 | -208.244 | 56.756 | 17.9907 | 0 | 17.9907 | 96.98 | 17.9907 | 7/14/15:00
7 | 14 | 1900-01-15 | 36.1 | 162 | 763 | 96.98 | 0 | 1 | 0 | 96.98 | 0 | 162 | 0 | 0 | 39.791 | 195.625 | 21.4793 | 86.148 | -75 | -5.5443 | 219.7619 | -240.5744 | -78.5744 | -24.9067 | 0 | -24.9067 | 96.98 | -24.9067 | 7/14/16:00
7 | 14 | 1900-01-16 | 35.6 | 124 | 709 | 96.08 | 0 | 1 | 0 | 96.08 | 0 | 124 | 0 | 0 | 39.791 | 195.6667 | 21.4724 | 86.148 | -75 | -5.5488 | 234.7608 | -126.4216 | -2.4216 | -0.76761 | 0 | -0.76761 | 96.08 | -0.76761 | 7/14/17:00
7 | 14 | 1900-01-17 | 35 | 94 | 674 | 95 | 0 | 1 | 0 | 95 | 0 | 94 | 0 | 0 | 39.791 | 195.7083 | 21.4655 | 86.148 | -75 | -5.5532 | 249.7597 | -8.8915 | 85.1085 | 26.9779 | 0 | 26.9779 | 95 | 26.9779 | 7/14/18:00
7 | 14 | 1900-01-18 | 33.9 | 110 | 338 | 93.02 | 0 | 1 | 0 | 93.02 | 0 | 110 | 0 | 0 | 39.791 | 195.75 | 21.4586 | 86.148 | -75 | -5.5576 | 264.7586 | 57.0539 | 167.0539 | 52.9532 | 0 | 52.9532 | 93.02 | 52.9532 | 7/14/19:00
7 | 14 | 1900-01-19 | 31.7 | 46 | 121 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 46 | 0 | 0 | 39.791 | 195.7917 | 21.4517 | 86.148 | -75 | -5.5619 | 279.7575 | 42.9862 | 88.9862 | 28.2071 | 0 | 28.2071 | 89.06 | 28.2071 | 7/14/20:00
7 | 14 | 1900-01-20 | 30 | 0 | 3 | 86 | 0 | 1 | 0 | 86 | 0 | 0 | 0 | 0 | 39.791 | 195.8333 | 21.4447 | 86.148 | -75 | -5.5663 | 294.7564 | 1.6004 | 1.6004 | 0.50731 | 0 | 0.50731 | 86 | 0.50731 | 7/14/21:00
7 | 14 | 1900-01-21 | 28.3 | 0 | 0 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 0 | 0 | 0 | 39.791 | 195.875 | 21.4378 | 86.148 | -75 | -5.5706 | 309.7553 | 0 | 0 | 0 | 0 | 0 | 82.94 | 0 | 7/14/22:00
7 | 14 | 1900-01-22 | 27.2 | 0 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 0 | 0 | 0 | 39.791 | 195.9167 | 21.4308 | 86.148 | -75 | -5.575 | 324.7543 | 0 | 0 | 0 | 0 | 0 | 80.96 | 0 | 7/14/23:00
7 | 14 | 1900-01-23 | 27.2 | 0 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 0 | 0 | 0 | 39.791 | 195.9583 | 21.4239 | 86.148 | -75 | -5.5793 | 339.7532 | 0 | 0 | 0 | 0 | 0 | 80.96 | 0 | 7/14/24:00
7 | 15 | 1899-12-31 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 196 | 21.4169 | 86.148 | -75 | -5.5836 | -5.2479 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 7/15/1:00
7 | 15 | 1900-01-01 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 196.0417 | 21.4099 | 86.148 | -75 | -5.5879 | 9.751 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 7/15/2:00
7 | 15 | 1900-01-02 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 196.0833 | 21.4029 | 86.148 | -75 | -5.5922 | 24.75 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 7/15/3:00
7 | 15 | 1900-01-03 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 196.125 | 21.3959 | 86.148 | -75 | -5.5964 | 39.7489 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/15/4:00
7 | 15 | 1900-01-04 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 196.1667 | 21.3889 | 86.148 | -75 | -5.6007 | 54.7478 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 7/15/5:00
7 | 15 | 1900-01-05 | 23.9 | 4 | 7 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 4 | 0 | 0 | 39.791 | 196.2083 | 21.3818 | 86.148 | -75 | -5.6049 | 69.7468 | 3.3671 | 7.3671 | 2.3352 | 0 | 2.3352 | 75.02 | 2.3352 | 7/15/6:00
7 | 15 | 1900-01-06 | 26.1 | 50 | 50 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 50 | 0 | 0 | 39.791 | 196.25 | 21.3748 | 86.148 | -75 | -5.6092 | 84.7457 | 14.939 | 64.939 | 20.5845 | 0 | 20.5845 | 78.98 | 20.5845 | 7/15/7:00
7 | 15 | 1900-01-07 | 26.7 | 137 | 124 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 137 | 0 | 0 | 39.791 | 196.2917 | 21.3677 | 86.148 | -75 | -5.6134 | 99.7447 | 13.8962 | 150.8962 | 47.8315 | 0 | 47.8315 | 80.06 | 47.8315 | 7/15/8:00
7 | 15 | 1900-01-08 | 29.4 | 128 | 519 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 128 | 0 | 0 | 39.791 | 196.3333 | 21.3607 | 86.148 | -75 | -5.6176 | 114.7436 | -34.4683 | 93.5317 | 29.6479 | 0 | 29.6479 | 84.92 | 29.6479 | 7/15/9:00
7 | 15 | 1900-01-09 | 32.2 | 197 | 606 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 197 | 0 | 0 | 39.791 | 196.375 | 21.3536 | 86.148 | -75 | -5.6217 | 129.7426 | -136.0467 | 60.9533 | 19.3211 | 0 | 19.3211 | 89.96 | 19.3211 | 7/15/10:00
7 | 15 | 1900-01-10 | 33.3 | 211 | 590 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 211 | 0 | 0 | 39.791 | 196.4167 | 21.3465 | 86.148 | -75 | -5.6259 | 144.7415 | -207.3403 | 3.6597 | 1.1601 | 0 | 1.1601 | 91.94 | 1.1601 | 7/15/11:00
7 | 15 | 1900-01-11 | 34.4 | 310 | 653 | 93.92 | 0 | 1 | 0 | 93.92 | 0 | 310 | 0 | 0 | 39.791 | 196.4583 | 21.3394 | 86.148 | -75 | -5.6301 | 159.7405 | -286.3667 | 23.6333 | 7.4913 | 0 | 7.4913 | 93.92 | 7.4913 | 7/15/12:00
7 | 15 | 1900-01-12 | 33.3 | 595 | 109 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 595 | 0 | 0 | 39.791 | 196.5 | 21.3323 | 86.148 | -75 | -5.6342 | 174.7395 | -52.3104 | 542.6896 | 172.0231 | 0 | 172.0231 | 91.94 | 172.0231 | 7/15/13:00
7 | 15 | 1900-01-13 | 28.9 | 278 | 0 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 278 | 0 | 0 | 39.791 | 196.5417 | 21.3252 | 86.148 | -75 | -5.6383 | 189.7384 | 0 | 278 | 88.1211 | 0 | 88.1211 | 84.02 | 88.1211 | 7/15/14:00
7 | 15 | 1900-01-14 | 27.2 | 414 | 199 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 414 | 0 | 0 | 39.791 | 196.5833 | 21.318 | 86.148 | -75 | -5.6424 | 204.7374 | -83.0743 | 330.9257 | 104.8977 | 0 | 104.8977 | 80.96 | 104.8977 | 7/15/15:00
7 | 15 | 1900-01-15 | 28.9 | 281 | 0 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 281 | 0 | 0 | 39.791 | 196.625 | 21.3109 | 86.148 | -75 | -5.6465 | 219.7364 | 0 | 281 | 89.0721 | 0 | 89.0721 | 84.02 | 89.0721 | 7/15/16:00
7 | 15 | 1900-01-16 | 26.1 | 176 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 176 | 0 | 0 | 39.791 | 196.6667 | 21.3037 | 86.148 | -75 | -5.6506 | 234.7353 | 0 | 176 | 55.7889 | 0 | 55.7889 | 78.98 | 55.7889 | 7/15/17:00
7 | 15 | 1900-01-17 | 25 | 149 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 149 | 0 | 0 | 39.791 | 196.7083 | 21.2965 | 86.148 | -75 | -5.6547 | 249.7343 | 0 | 149 | 47.2304 | 0 | 47.2304 | 77 | 47.2304 | 7/15/18:00
7 | 15 | 1900-01-18 | 25 | 77 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 77 | 0 | 0 | 39.791 | 196.75 | 21.2894 | 86.148 | -75 | -5.6587 | 264.7333 | 0 | 77 | 24.4077 | 0 | 24.4077 | 77 | 24.4077 | 7/15/19:00
7 | 15 | 1900-01-19 | 25 | 44 | 8 | 77 | 0 | 1 | 0 | 77 | 0 | 44 | 0 | 0 | 39.791 | 196.7917 | 21.2822 | 86.148 | -75 | -5.6628 | 279.7323 | 2.8266 | 46.8266 | 14.8432 | 0 | 14.8432 | 77 | 14.8432 | 7/15/20:00
7 | 15 | 1900-01-20 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 196.8333 | 21.275 | 86.148 | -75 | -5.6668 | 294.7313 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/15/21:00
7 | 15 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 196.875 | 21.2678 | 86.148 | -75 | -5.6708 | 309.7303 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/15/22:00
7 | 15 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 196.9167 | 21.2605 | 86.148 | -75 | -5.6748 | 324.7293 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/15/23:00
7 | 15 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 196.9583 | 21.2533 | 86.148 | -75 | -5.6788 | 339.7283 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/15/24:00
7 | 16 | 1899-12-31 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 197 | 21.2461 | 86.148 | -75 | -5.6827 | -5.2727 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/16/1:00
7 | 16 | 1900-01-01 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 197.0417 | 21.2388 | 86.148 | -75 | -5.6867 | 9.7263 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/16/2:00
7 | 16 | 1900-01-02 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 197.0833 | 21.2315 | 86.148 | -75 | -5.6906 | 24.7253 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/16/3:00
7 | 16 | 1900-01-03 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 197.125 | 21.2243 | 86.148 | -75 | -5.6946 | 39.7244 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/16/4:00
7 | 16 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 197.1667 | 21.217 | 86.148 | -75 | -5.6985 | 54.7234 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/16/5:00
7 | 16 | 1900-01-05 | 21.7 | 3 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 3 | 0 | 0 | 39.791 | 197.2083 | 21.2097 | 86.148 | -75 | -5.7024 | 69.7224 | 0 | 3 | 0.95095 | 0 | 0.95095 | 71.06 | 0.95095 | 7/16/6:00
7 | 16 | 1900-01-06 | 22.2 | 54 | 41 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 54 | 0 | 0 | 39.791 | 197.25 | 21.2023 | 86.148 | -75 | -5.7062 | 84.7214 | 12.192 | 66.192 | 20.9817 | 0 | 20.9817 | 71.96 | 20.9817 | 7/16/7:00
7 | 16 | 1900-01-07 | 23.9 | 103 | 401 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 103 | 0 | 0 | 39.791 | 197.2917 | 21.195 | 86.148 | -75 | -5.7101 | 99.7205 | 44.2803 | 147.2803 | 46.6853 | 0 | 46.6853 | 75.02 | 46.6853 | 7/16/8:00
7 | 16 | 1900-01-08 | 25.6 | 194 | 390 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 194 | 0 | 0 | 39.791 | 197.3333 | 21.1877 | 86.148 | -75 | -5.714 | 114.7195 | -26.6338 | 167.3662 | 53.0522 | 0 | 53.0522 | 78.08 | 53.0522 | 7/16/9:00
7 | 16 | 1900-01-09 | 28.3 | 129 | 754 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 129 | 0 | 0 | 39.791 | 197.375 | 21.1803 | 86.148 | -75 | -5.7178 | 129.7186 | -170.8644 | -41.8644 | -13.2703 | 0 | -13.2703 | 82.94 | -13.2703 | 7/16/10:00
7 | 16 | 1900-01-10 | 29.4 | 145 | 799 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 145 | 0 | 0 | 39.791 | 197.4167 | 21.173 | 86.148 | -75 | -5.7216 | 144.7176 | -282.6435 | -137.6435 | -43.6306 | 0 | -43.6306 | 84.92 | -43.6306 | 7/16/11:00
7 | 16 | 1900-01-11 | 31.7 | 155 | 824 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 155 | 0 | 0 | 39.791 | 197.4583 | 21.1656 | 86.148 | -75 | -5.7254 | 159.7166 | -363.4155 | -208.4155 | -66.0641 | 0 | -66.0641 | 89.06 | -66.0641 | 7/16/12:00
7 | 16 | 1900-01-12 | 32.8 | 305 | 568 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 305 | 0 | 0 | 39.791 | 197.5 | 21.1582 | 86.148 | -75 | -5.7292 | 174.7157 | -274.082 | 30.918 | 9.8005 | 0 | 9.8005 | 91.04 | 9.8005 | 7/16/13:00
7 | 16 | 1900-01-13 | 32.8 | 453 | 445 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 453 | 0 | 0 | 39.791 | 197.5417 | 21.1508 | 86.148 | -75 | -5.733 | 189.7148 | -211.5622 | 241.4378 | 76.5316 | 0 | 76.5316 | 91.04 | 76.5316 | 7/16/14:00
7 | 16 | 1900-01-14 | 31.7 | 433 | 111 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 433 | 0 | 0 | 39.791 | 197.5833 | 21.1434 | 86.148 | -75 | -5.7368 | 204.7138 | -46.6388 | 386.3612 | 122.4697 | 0 | 122.4697 | 89.06 | 122.4697 | 7/16/15:00
7 | 16 | 1900-01-15 | 32.2 | 197 | 579 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 197 | 0 | 0 | 39.791 | 197.625 | 21.136 | 86.148 | -75 | -5.7405 | 219.7129 | -185.5988 | 11.4012 | 3.614 | 0 | 3.614 | 89.96 | 3.614 | 7/16/16:00
7 | 16 | 1900-01-16 | 32.8 | 177 | 532 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 177 | 0 | 0 | 39.791 | 197.6667 | 21.1286 | 86.148 | -75 | -5.7442 | 234.7119 | -97.5438 | 79.4562 | 25.1862 | 0 | 25.1862 | 91.04 | 25.1862 | 7/16/17:00
7 | 16 | 1900-01-17 | 27.8 | 139 | 125 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 139 | 0 | 0 | 39.791 | 197.7083 | 21.1212 | 86.148 | -75 | -5.748 | 249.711 | -2.2409 | 136.7591 | 43.3502 | 0 | 43.3502 | 82.04 | 43.3502 | 7/16/18:00
7 | 16 | 1900-01-18 | 30 | 106 | 271 | 86 | 0 | 1 | 0 | 86 | 0 | 106 | 0 | 0 | 39.791 | 197.75 | 21.1137 | 86.148 | -75 | -5.7517 | 264.7101 | 44.5663 | 150.5663 | 47.7269 | 0 | 47.7269 | 86 | 47.7269 | 7/16/19:00
7 | 16 | 1900-01-19 | 27.2 | 41 | 111 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 41 | 0 | 0 | 39.791 | 197.7917 | 21.1063 | 86.148 | -75 | -5.7554 | 279.7092 | 39 | 80 | 25.3586 | 0 | 25.3586 | 80.96 | 25.3586 | 7/16/20:00
7 | 16 | 1900-01-20 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 197.8333 | 21.0988 | 86.148 | -75 | -5.759 | 294.7082 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 7/16/21:00
7 | 16 | 1900-01-21 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 197.875 | 21.0913 | 86.148 | -75 | -5.7627 | 309.7073 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/16/22:00
7 | 16 | 1900-01-22 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 197.9167 | 21.0838 | 86.148 | -75 | -5.7663 | 324.7064 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/16/23:00
7 | 16 | 1900-01-23 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 197.9583 | 21.0763 | 86.148 | -75 | -5.77 | 339.7055 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 7/16/24:00
7 | 17 | 1899-12-31 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 198 | 21.0688 | 86.148 | -75 | -5.7736 | -5.2954 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/17/1:00
7 | 17 | 1900-01-01 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 198.0417 | 21.0613 | 86.148 | -75 | -5.7772 | 9.7037 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/17/2:00
7 | 17 | 1900-01-02 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 198.0833 | 21.0538 | 86.148 | -75 | -5.7808 | 24.7028 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/17/3:00
7 | 17 | 1900-01-03 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 198.125 | 21.0462 | 86.148 | -75 | -5.7843 | 39.7019 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/17/4:00
7 | 17 | 1900-01-04 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 198.1667 | 21.0387 | 86.148 | -75 | -5.7879 | 54.701 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/17/5:00
7 | 17 | 1900-01-05 | 22.8 | 3 | 3 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 3 | 0 | 0 | 39.791 | 198.2083 | 21.0311 | 86.148 | -75 | -5.7914 | 69.7001 | 1.4355 | 4.4355 | 1.406 | 0 | 1.406 | 73.04 | 1.406 | 7/17/6:00
7 | 17 | 1900-01-06 | 23.3 | 57 | 59 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 57 | 0 | 0 | 39.791 | 198.25 | 21.0235 | 86.148 | -75 | -5.795 | 84.6993 | 17.4556 | 74.4556 | 23.6011 | 0 | 23.6011 | 73.94 | 23.6011 | 7/17/7:00
7 | 17 | 1900-01-07 | 25.6 | 56 | 654 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 56 | 0 | 0 | 39.791 | 198.2917 | 21.0159 | 86.148 | -75 | -5.7985 | 99.6984 | 71.0801 | 127.0801 | 40.2822 | 0 | 40.2822 | 78.08 | 40.2822 | 7/17/8:00
7 | 17 | 1900-01-08 | 27.2 | 76 | 766 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 76 | 0 | 0 | 39.791 | 198.3333 | 21.0083 | 86.148 | -75 | -5.802 | 114.6975 | -53.8287 | 22.1713 | 7.0279 | 0 | 7.0279 | 80.96 | 7.0279 | 7/17/9:00
7 | 17 | 1900-01-09 | 28.3 | 178 | 556 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 178 | 0 | 0 | 39.791 | 198.375 | 21.0007 | 86.148 | -75 | -5.8055 | 129.6966 | -127.2268 | 50.7732 | 16.0942 | 0 | 16.0942 | 82.94 | 16.0942 | 7/17/10:00
7 | 17 | 1900-01-10 | 28.9 | 99 | 864 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 99 | 0 | 0 | 39.791 | 198.4167 | 20.9931 | 86.148 | -75 | -5.8089 | 144.6958 | -307.7322 | -208.7322 | -66.1645 | 0 | -66.1645 | 84.02 | -66.1645 | 7/17/11:00
7 | 17 | 1900-01-11 | 29.4 | 243 | 747 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 243 | 0 | 0 | 39.791 | 198.4583 | 20.9855 | 86.148 | -75 | -5.8124 | 159.6949 | -331.3962 | -88.3962 | -28.0201 | 0 | -28.0201 | 84.92 | -28.0201 | 7/17/12:00
7 | 17 | 1900-01-12 | 30.6 | 265 | 534 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 265 | 0 | 0 | 39.791 | 198.5 | 20.9778 | 86.148 | -75 | -5.8158 | 174.694 | -259.1289 | 5.8711 | 1.861 | 0 | 1.861 | 87.08 | 1.861 | 7/17/13:00
7 | 17 | 1900-01-13 | 30.6 | 299 | 497 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 299 | 0 | 0 | 39.791 | 198.5417 | 20.9702 | 86.148 | -75 | -5.8193 | 189.6932 | -237.6692 | 61.3308 | 19.4408 | 0 | 19.4408 | 87.08 | 19.4408 | 7/17/14:00
7 | 17 | 1900-01-14 | 32.2 | 167 | 709 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 167 | 0 | 0 | 39.791 | 198.5833 | 20.9625 | 86.148 | -75 | -5.8227 | 204.6923 | -299.8784 | -132.8784 | -42.1201 | 0 | -42.1201 | 89.96 | -42.1201 | 7/17/15:00
7 | 17 | 1900-01-15 | 31.7 | 204 | 598 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 204 | 0 | 0 | 39.791 | 198.625 | 20.9548 | 86.148 | -75 | -5.8261 | 219.6915 | -193.3225 | 10.6775 | 3.3846 | 0 | 3.3846 | 89.06 | 3.3846 | 7/17/16:00
7 | 17 | 1900-01-16 | 31.7 | 120 | 662 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 120 | 0 | 0 | 39.791 | 198.6667 | 20.9472 | 86.148 | -75 | -5.8294 | 234.6906 | -123.1101 | -3.1101 | -0.98585 | 0 | -0.98585 | 89.06 | -0.98585 | 7/17/17:00
7 | 17 | 1900-01-17 | 31.1 | 132 | 279 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 132 | 0 | 0 | 39.791 | 198.7083 | 20.9395 | 86.148 | -75 | -5.8328 | 249.6898 | -5.6844 | 126.3156 | 40.0398 | 0 | 40.0398 | 87.98 | 40.0398 | 7/17/18:00
7 | 17 | 1900-01-18 | 30 | 75 | 445 | 86 | 0 | 1 | 0 | 86 | 0 | 75 | 0 | 0 | 39.791 | 198.75 | 20.9318 | 86.148 | -75 | -5.8361 | 264.689 | 72.1834 | 147.1834 | 46.6546 | 0 | 46.6546 | 86 | 46.6546 | 7/17/19:00
7 | 17 | 1900-01-19 | 27.8 | 30 | 280 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 30 | 0 | 0 | 39.791 | 198.7917 | 20.924 | 86.148 | -75 | -5.8395 | 279.6881 | 97.8151 | 127.8151 | 40.5152 | 0 | 40.5152 | 82.04 | 40.5152 | 7/17/20:00
7 | 17 | 1900-01-20 | 25.6 | 0 | 9 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 198.8333 | 20.9163 | 86.148 | -75 | -5.8428 | 294.6873 | 4.7543 | 4.7543 | 1.507 | 0 | 1.507 | 78.08 | 1.507 | 7/17/21:00
7 | 17 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 198.875 | 20.9086 | 86.148 | -75 | -5.8461 | 309.6865 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/17/22:00
7 | 17 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 198.9167 | 20.9008 | 86.148 | -75 | -5.8494 | 324.6857 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/17/23:00
7 | 17 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 198.9583 | 20.8931 | 86.148 | -75 | -5.8527 | 339.6848 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/17/24:00
7 | 18 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 199 | 20.8853 | 86.148 | -75 | -5.8559 | -5.316 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/18/1:00
7 | 18 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 199.0417 | 20.8775 | 86.148 | -75 | -5.8592 | 9.6832 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/18/2:00
7 | 18 | 1900-01-02 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 199.0833 | 20.8697 | 86.148 | -75 | -5.8624 | 24.6824 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 7/18/3:00
7 | 18 | 1900-01-03 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 199.125 | 20.8619 | 86.148 | -75 | -5.8656 | 39.6816 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 7/18/4:00
7 | 18 | 1900-01-04 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 199.1667 | 20.8541 | 86.148 | -75 | -5.8688 | 54.6808 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 7/18/5:00
7 | 18 | 1900-01-05 | 16.7 | 3 | 39 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 3 | 0 | 0 | 39.791 | 199.2083 | 20.8463 | 86.148 | -75 | -5.872 | 69.68 | 18.6074 | 21.6074 | 6.8492 | 0 | 6.8492 | 62.06 | 6.8492 | 7/18/6:00
7 | 18 | 1900-01-06 | 18.3 | 39 | 354 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 39 | 0 | 0 | 39.791 | 199.25 | 20.8384 | 86.148 | -75 | -5.8751 | 84.6792 | 104.1675 | 143.1675 | 45.3816 | 0 | 45.3816 | 64.94 | 45.3816 | 7/18/7:00
7 | 18 | 1900-01-07 | 22.2 | 58 | 604 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 58 | 0 | 0 | 39.791 | 199.2917 | 20.8306 | 86.148 | -75 | -5.8783 | 99.6784 | 64.5362 | 122.5362 | 38.8418 | 0 | 38.8418 | 71.96 | 38.8418 | 7/18/8:00
7 | 18 | 1900-01-08 | 24.4 | 107 | 673 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 107 | 0 | 0 | 39.791 | 199.3333 | 20.8227 | 86.148 | -75 | -5.8814 | 114.6776 | -48.6946 | 58.3054 | 18.4818 | 0 | 18.4818 | 75.92 | 18.4818 | 7/18/9:00
7 | 18 | 1900-01-09 | 25.6 | 96 | 781 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 96 | 0 | 0 | 39.791 | 199.375 | 20.8148 | 86.148 | -75 | -5.8846 | 129.6769 | -180.5222 | -84.5222 | -26.7921 | 0 | -26.7921 | 78.08 | -26.7921 | 7/18/10:00
7 | 18 | 1900-01-10 | 27.2 | 110 | 862 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 110 | 0 | 0 | 39.791 | 199.4167 | 20.807 | 86.148 | -75 | -5.8877 | 144.6761 | -309.1979 | -199.1979 | -63.1423 | 0 | -63.1423 | 80.96 | -63.1423 | 7/18/11:00
7 | 18 | 1900-01-11 | 27.2 | 125 | 809 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 125 | 0 | 0 | 39.791 | 199.4583 | 20.7991 | 86.148 | -75 | -5.8908 | 159.6753 | -361.0829 | -236.0829 | -74.8342 | 0 | -74.8342 | 80.96 | -74.8342 | 7/18/12:00
7 | 18 | 1900-01-12 | 28.9 | 290 | 554 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 290 | 0 | 0 | 39.791 | 199.5 | 20.7912 | 86.148 | -75 | -5.8938 | 174.6745 | -270.3931 | 19.6069 | 6.215 | 0 | 6.215 | 84.02 | 6.215 | 7/18/13:00
7 | 18 | 1900-01-13 | 28.9 | 182 | 549 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 182 | 0 | 0 | 39.791 | 199.5417 | 20.7832 | 86.148 | -75 | -5.8969 | 189.6738 | -264.113 | -82.113 | -26.0284 | 0 | -26.0284 | 84.02 | -26.0284 | 7/18/14:00
7 | 18 | 1900-01-14 | 29.4 | 206 | 532 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 206 | 0 | 0 | 39.791 | 199.5833 | 20.7753 | 86.148 | -75 | -5.8999 | 204.673 | -226.5401 | -20.5401 | -6.5109 | 0 | -6.5109 | 84.92 | -6.5109 | 7/18/15:00
7 | 18 | 1900-01-15 | 28.9 | 162 | 800 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 162 | 0 | 0 | 39.791 | 199.625 | 20.7674 | 86.148 | -75 | -5.903 | 219.6723 | -260.865 | -98.865 | -31.3385 | 0 | -31.3385 | 84.02 | -31.3385 | 7/18/16:00
7 | 18 | 1900-01-16 | 28.9 | 156 | 602 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 156 | 0 | 0 | 39.791 | 199.6667 | 20.7594 | 86.148 | -75 | -5.906 | 234.6715 | -113.5614 | 42.4386 | 13.4523 | 0 | 13.4523 | 84.02 | 13.4523 | 7/18/17:00
7 | 18 | 1900-01-17 | 28.9 | 84 | 659 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 84 | 0 | 0 | 39.791 | 199.7083 | 20.7515 | 86.148 | -75 | -5.909 | 249.6708 | -15.0725 | 68.9275 | 21.8488 | 0 | 21.8488 | 84.02 | 21.8488 | 7/18/18:00
7 | 18 | 1900-01-18 | 27.8 | 51 | 602 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 51 | 0 | 0 | 39.791 | 199.75 | 20.7435 | 86.148 | -75 | -5.912 | 264.67 | 96.2749 | 147.2749 | 46.6836 | 0 | 46.6836 | 82.04 | 46.6836 | 7/18/19:00
7 | 18 | 1900-01-19 | 25.6 | 27 | 299 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 27 | 0 | 0 | 39.791 | 199.7917 | 20.7355 | 86.148 | -75 | -5.9149 | 279.6693 | 103.8397 | 130.8397 | 41.4739 | 0 | 41.4739 | 78.08 | 41.4739 | 7/18/20:00
7 | 18 | 1900-01-20 | 24.4 | 0 | 9 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 199.8333 | 20.7276 | 86.148 | -75 | -5.9179 | 294.6685 | 4.738 | 4.738 | 1.5019 | 0 | 1.5019 | 75.92 | 1.5019 | 7/18/21:00
7 | 18 | 1900-01-21 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 199.875 | 20.7196 | 86.148 | -75 | -5.9208 | 309.6678 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/18/22:00
7 | 18 | 1900-01-22 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 199.9167 | 20.7115 | 86.148 | -75 | -5.9237 | 324.6671 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 7/18/23:00
7 | 18 | 1900-01-23 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 199.9583 | 20.7035 | 86.148 | -75 | -5.9266 | 339.6663 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/18/24:00
7 | 19 | 1899-12-31 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 200 | 20.6955 | 86.148 | -75 | -5.9295 | -5.3344 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/19/1:00
7 | 19 | 1900-01-01 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 200.0417 | 20.6874 | 86.148 | -75 | -5.9324 | 9.6649 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 7/19/2:00
7 | 19 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 200.0833 | 20.6794 | 86.148 | -75 | -5.9353 | 24.6642 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/19/3:00
7 | 19 | 1900-01-03 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 200.125 | 20.6713 | 86.148 | -75 | -5.9381 | 39.6635 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 7/19/4:00
7 | 19 | 1900-01-04 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 200.1667 | 20.6633 | 86.148 | -75 | -5.9409 | 54.6628 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 7/19/5:00
7 | 19 | 1900-01-05 | 17.8 | 3 | 12 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 3 | 0 | 0 | 39.791 | 200.2083 | 20.6552 | 86.148 | -75 | -5.9437 | 69.6621 | 5.7077 | 8.7077 | 2.7602 | 0 | 2.7602 | 64.04 | 2.7602 | 7/19/6:00
7 | 19 | 1900-01-06 | 18.3 | 55 | 189 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 55 | 0 | 0 | 39.791 | 200.25 | 20.6471 | 86.148 | -75 | -5.9465 | 84.6614 | 55.2952 | 110.2952 | 34.9616 | 0 | 34.9616 | 64.94 | 34.9616 | 7/19/7:00
7 | 19 | 1900-01-07 | 22.2 | 83 | 492 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 83 | 0 | 0 | 39.791 | 200.2917 | 20.639 | 86.148 | -75 | -5.9493 | 99.6607 | 51.6173 | 134.6173 | 42.6713 | 0 | 42.6713 | 71.96 | 42.6713 | 7/19/8:00
7 | 19 | 1900-01-08 | 26.1 | 117 | 623 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 117 | 0 | 0 | 39.791 | 200.3333 | 20.6309 | 86.148 | -75 | -5.9521 | 114.66 | -46.4369 | 70.5631 | 22.3673 | 0 | 22.3673 | 78.98 | 22.3673 | 7/19/9:00
7 | 19 | 1900-01-09 | 27.8 | 124 | 772 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 124 | 0 | 0 | 39.791 | 200.375 | 20.6227 | 86.148 | -75 | -5.9548 | 129.6593 | -180.3096 | -56.3096 | -17.8492 | 0 | -17.8492 | 82.04 | -17.8492 | 7/19/10:00
7 | 19 | 1900-01-10 | 28.9 | 138 | 815 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 138 | 0 | 0 | 39.791 | 200.4167 | 20.6146 | 86.148 | -75 | -5.9576 | 144.6586 | -294.4805 | -156.4805 | -49.6016 | 0 | -49.6016 | 84.02 | -49.6016 | 7/19/11:00
7 | 19 | 1900-01-11 | 29.4 | 293 | 590 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 293 | 0 | 0 | 39.791 | 200.4583 | 20.6064 | 86.148 | -75 | -5.9603 | 159.6579 | -264.9842 | 28.0158 | 8.8805 | 0 | 8.8805 | 84.92 | 8.8805 | 7/19/12:00
7 | 19 | 1900-01-12 | 30 | 491 | 237 | 86 | 0 | 1 | 0 | 86 | 0 | 491 | 0 | 0 | 39.791 | 200.5 | 20.5983 | 86.148 | -75 | -5.963 | 174.6572 | -116.3622 | 374.6378 | 118.7536 | 0 | 118.7536 | 86 | 118.7536 | 7/19/13:00
7 | 19 | 1900-01-13 | 30.6 | 302 | 425 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 302 | 0 | 0 | 39.791 | 200.5417 | 20.5901 | 86.148 | -75 | -5.9657 | 189.6566 | -205.7156 | 96.2844 | 30.5205 | 0 | 30.5205 | 87.08 | 30.5205 | 7/19/14:00
7 | 19 | 1900-01-14 | 30 | 266 | 506 | 86 | 0 | 1 | 0 | 86 | 0 | 266 | 0 | 0 | 39.791 | 200.5833 | 20.5819 | 86.148 | -75 | -5.9684 | 204.6559 | -216.9577 | 49.0423 | 15.5455 | 0 | 15.5455 | 86 | 15.5455 | 7/19/15:00
7 | 19 | 1900-01-15 | 30.6 | 250 | 618 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 250 | 0 | 0 | 39.791 | 200.625 | 20.5737 | 86.148 | -75 | -5.971 | 219.6552 | -203.2893 | 46.7107 | 14.8065 | 0 | 14.8065 | 87.08 | 14.8065 | 7/19/16:00
7 | 19 | 1900-01-16 | 30.6 | 123 | 707 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 123 | 0 | 0 | 39.791 | 200.6667 | 20.5655 | 86.148 | -75 | -5.9737 | 234.6546 | -135.2992 | -12.2992 | -3.8986 | 0 | -3.8986 | 87.08 | -3.8986 | 7/19/17:00
7 | 19 | 1900-01-17 | 29.4 | 95 | 666 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 95 | 0 | 0 | 39.791 | 200.7083 | 20.5573 | 86.148 | -75 | -5.9763 | 249.6539 | -16.9287 | 78.0713 | 24.7472 | 0 | 24.7472 | 84.92 | 24.7472 | 7/19/18:00
7 | 19 | 1900-01-18 | 28.3 | 66 | 505 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 66 | 0 | 0 | 39.791 | 200.75 | 20.5491 | 86.148 | -75 | -5.9789 | 264.6533 | 79.5871 | 145.5871 | 46.1486 | 0 | 46.1486 | 82.94 | 46.1486 | 7/19/19:00
7 | 19 | 1900-01-19 | 26.7 | 32 | 190 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 32 | 0 | 0 | 39.791 | 200.7917 | 20.5409 | 86.148 | -75 | -5.9815 | 279.6526 | 65.5886 | 97.5886 | 30.9339 | 0 | 30.9339 | 80.06 | 30.9339 | 7/19/20:00
7 | 19 | 1900-01-20 | 25 | 0 | 1 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 200.8333 | 20.5326 | 86.148 | -75 | -5.9841 | 294.652 | 0.52461 | 0.52461 | 0.16629 | 0 | 0.16629 | 77 | 0.16629 | 7/19/21:00
7 | 19 | 1900-01-21 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 200.875 | 20.5244 | 86.148 | -75 | -5.9866 | 309.6513 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/19/22:00
7 | 19 | 1900-01-22 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 200.9167 | 20.5161 | 86.148 | -75 | -5.9892 | 324.6507 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/19/23:00
7 | 19 | 1900-01-23 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 200.9583 | 20.5078 | 86.148 | -75 | -5.9917 | 339.6501 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/19/24:00
7 | 20 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 201 | 20.4995 | 86.148 | -75 | -5.9942 | -5.3506 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/20/1:00
7 | 20 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 201.0417 | 20.4912 | 86.148 | -75 | -5.9967 | 9.6488 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/20/2:00
7 | 20 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 201.0833 | 20.4829 | 86.148 | -75 | -5.9992 | 24.6482 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/20/3:00
7 | 20 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 201.125 | 20.4746 | 86.148 | -75 | -6.0017 | 39.6476 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 7/20/4:00
7 | 20 | 1900-01-04 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 201.1667 | 20.4663 | 86.148 | -75 | -6.0041 | 54.647 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 7/20/5:00
7 | 20 | 1900-01-05 | 18.3 | 3 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 3 | 0 | 0 | 39.791 | 201.2083 | 20.4579 | 86.148 | -75 | -6.0066 | 69.6464 | 0.47409 | 3.4741 | 1.1012 | 0 | 1.1012 | 64.94 | 1.1012 | 7/20/6:00
7 | 20 | 1900-01-06 | 20 | 88 | 1 | 68 | 0 | 1 | 0 | 68 | 0 | 88 | 0 | 0 | 39.791 | 201.25 | 20.4496 | 86.148 | -75 | -6.009 | 84.6458 | 0.29078 | 88.2908 | 27.9866 | 0 | 27.9866 | 68 | 27.9866 | 7/20/7:00
7 | 20 | 1900-01-07 | 21.7 | 101 | 95 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 101 | 0 | 0 | 39.791 | 201.2917 | 20.4412 | 86.148 | -75 | -6.0114 | 99.6452 | 9.7737 | 110.7737 | 35.1133 | 0 | 35.1133 | 71.06 | 35.1133 | 7/20/8:00
7 | 20 | 1900-01-08 | 22.8 | 175 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 175 | 0 | 0 | 39.791 | 201.3333 | 20.4328 | 86.148 | -75 | -6.0138 | 114.6446 | 0 | 175 | 55.4719 | 0 | 55.4719 | 73.04 | 55.4719 | 7/20/9:00
7 | 20 | 1900-01-09 | 26.1 | 157 | 259 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 157 | 0 | 0 | 39.791 | 201.375 | 20.4245 | 86.148 | -75 | -6.0161 | 129.644 | -61.1453 | 95.8547 | 30.3843 | 0 | 30.3843 | 78.98 | 30.3843 | 7/20/10:00
7 | 20 | 1900-01-10 | 27.2 | 345 | 179 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 345 | 0 | 0 | 39.791 | 201.4167 | 20.4161 | 86.148 | -75 | -6.0185 | 144.6434 | -65.1654 | 279.8346 | 88.7027 | 0 | 88.7027 | 80.96 | 88.7027 | 7/20/11:00
7 | 20 | 1900-01-11 | 27.8 | 204 | 112 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 204 | 0 | 0 | 39.791 | 201.4583 | 20.4077 | 86.148 | -75 | -6.0208 | 159.6428 | -50.6256 | 153.3744 | 48.617 | 0 | 48.617 | 82.04 | 48.617 | 7/20/12:00
7 | 20 | 1900-01-12 | 28.9 | 619 | 92 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 619 | 0 | 0 | 39.791 | 201.5 | 20.3993 | 86.148 | -75 | -6.0232 | 174.6422 | -45.4457 | 573.5543 | 181.8067 | 0 | 181.8067 | 84.02 | 181.8067 | 7/20/13:00
7 | 20 | 1900-01-13 | 29.4 | 348 | 0 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 348 | 0 | 0 | 39.791 | 201.5417 | 20.3908 | 86.148 | -75 | -6.0255 | 189.6416 | 0 | 348 | 110.3099 | 0 | 110.3099 | 84.92 | 110.3099 | 7/20/14:00
7 | 20 | 1900-01-14 | 28.3 | 325 | 0 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 325 | 0 | 0 | 39.791 | 201.5833 | 20.3824 | 86.148 | -75 | -6.0278 | 204.6411 | 0 | 325 | 103.0193 | 0 | 103.0193 | 82.94 | 103.0193 | 7/20/15:00
7 | 20 | 1900-01-15 | 26.1 | 283 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 283 | 0 | 0 | 39.791 | 201.625 | 20.374 | 86.148 | -75 | -6.03 | 219.6405 | 0 | 283 | 89.7061 | 0 | 89.7061 | 78.98 | 89.7061 | 7/20/16:00
7 | 20 | 1900-01-16 | 23.9 | 224 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 224 | 0 | 0 | 39.791 | 201.6667 | 20.3655 | 86.148 | -75 | -6.0323 | 234.6399 | 0 | 224 | 71.0041 | 0 | 71.0041 | 75.02 | 71.0041 | 7/20/17:00
7 | 20 | 1900-01-17 | 23.3 | 153 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 153 | 0 | 0 | 39.791 | 201.7083 | 20.357 | 86.148 | -75 | -6.0345 | 249.6394 | 0 | 153 | 48.4983 | 0 | 48.4983 | 73.94 | 48.4983 | 7/20/18:00
7 | 20 | 1900-01-18 | 22.2 | 63 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 63 | 0 | 0 | 39.791 | 201.75 | 20.3486 | 86.148 | -75 | -6.0368 | 264.6388 | 0 | 63 | 19.9699 | 0 | 19.9699 | 71.96 | 19.9699 | 7/20/19:00
7 | 20 | 1900-01-19 | 22.2 | 24 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 24 | 0 | 0 | 39.791 | 201.7917 | 20.3401 | 86.148 | -75 | -6.039 | 279.6383 | 0 | 24 | 7.6076 | 0 | 7.6076 | 71.96 | 7.6076 | 7/20/20:00
7 | 20 | 1900-01-20 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 201.8333 | 20.3316 | 86.148 | -75 | -6.0412 | 294.6377 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/20/21:00
7 | 20 | 1900-01-21 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 201.875 | 20.3231 | 86.148 | -75 | -6.0434 | 309.6372 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/20/22:00
7 | 20 | 1900-01-22 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 201.9167 | 20.3145 | 86.148 | -75 | -6.0455 | 324.6366 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/20/23:00
7 | 20 | 1900-01-23 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 201.9583 | 20.306 | 86.148 | -75 | -6.0477 | 339.6361 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/20/24:00
7 | 21 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 202 | 20.2975 | 86.148 | -75 | -6.0498 | -5.3645 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/21/1:00
7 | 21 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 202.0417 | 20.2889 | 86.148 | -75 | -6.0519 | 9.635 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/21/2:00
7 | 21 | 1900-01-02 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 202.0833 | 20.2804 | 86.148 | -75 | -6.054 | 24.6345 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/21/3:00
7 | 21 | 1900-01-03 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 202.125 | 20.2718 | 86.148 | -75 | -6.0561 | 39.634 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/21/4:00
7 | 21 | 1900-01-04 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 202.1667 | 20.2632 | 86.148 | -75 | -6.0582 | 54.6335 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/21/5:00
7 | 21 | 1900-01-05 | 20.6 | 1 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 1 | 0 | 0 | 39.791 | 202.2083 | 20.2546 | 86.148 | -75 | -6.0602 | 69.6329 | 0 | 1 | 0.31698 | 0 | 0.31698 | 69.08 | 0.31698 | 7/21/6:00
7 | 21 | 1900-01-06 | 21.1 | 32 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 32 | 0 | 0 | 39.791 | 202.25 | 20.246 | 86.148 | -75 | -6.0623 | 84.6324 | 0 | 32 | 10.1434 | 0 | 10.1434 | 69.98 | 10.1434 | 7/21/7:00
7 | 21 | 1900-01-07 | 21.7 | 61 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 61 | 0 | 0 | 39.791 | 202.2917 | 20.2374 | 86.148 | -75 | -6.0643 | 99.6319 | 0 | 61 | 19.3359 | 0 | 19.3359 | 71.06 | 19.3359 | 7/21/8:00
7 | 21 | 1900-01-08 | 22.2 | 111 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 111 | 0 | 0 | 39.791 | 202.3333 | 20.2288 | 86.148 | -75 | -6.0663 | 114.6314 | 0 | 111 | 35.1851 | 0 | 35.1851 | 71.96 | 35.1851 | 7/21/9:00
7 | 21 | 1900-01-09 | 23.9 | 188 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 188 | 0 | 0 | 39.791 | 202.375 | 20.2202 | 86.148 | -75 | -6.0683 | 129.6309 | 0 | 188 | 59.5927 | 0 | 59.5927 | 75.02 | 59.5927 | 7/21/10:00
7 | 21 | 1900-01-10 | 24.4 | 233 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 233 | 0 | 0 | 39.791 | 202.4167 | 20.2115 | 86.148 | -75 | -6.0702 | 144.6304 | 0 | 233 | 73.8569 | 0 | 73.8569 | 75.92 | 73.8569 | 7/21/11:00
7 | 21 | 1900-01-11 | 25.6 | 264 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 264 | 0 | 0 | 39.791 | 202.4583 | 20.2029 | 86.148 | -75 | -6.0722 | 159.63 | 0 | 264 | 83.6834 | 0 | 83.6834 | 78.08 | 83.6834 | 7/21/12:00
7 | 21 | 1900-01-12 | 26.7 | 278 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 278 | 0 | 0 | 39.791 | 202.5 | 20.1942 | 86.148 | -75 | -6.0741 | 174.6295 | 0 | 278 | 88.1211 | 0 | 88.1211 | 80.06 | 88.1211 | 7/21/13:00
7 | 21 | 1900-01-13 | 27.2 | 459 | 122 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 459 | 0 | 0 | 39.791 | 202.5417 | 20.1855 | 86.148 | -75 | -6.076 | 189.629 | -59.8037 | 399.1963 | 126.5382 | 0 | 126.5382 | 80.96 | 126.5382 | 7/21/14:00
7 | 21 | 1900-01-14 | 27.2 | 343 | 358 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 343 | 0 | 0 | 39.791 | 202.5833 | 20.1768 | 86.148 | -75 | -6.0779 | 204.6285 | -155.6852 | 187.3148 | 59.3755 | 0 | 59.3755 | 80.96 | 59.3755 | 7/21/15:00
7 | 21 | 1900-01-15 | 28.9 | 293 | 448 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 293 | 0 | 0 | 39.791 | 202.625 | 20.1681 | 86.148 | -75 | -6.0798 | 219.628 | -150.0219 | 142.9781 | 45.3215 | 0 | 45.3215 | 84.02 | 45.3215 | 7/21/16:00
7 | 21 | 1900-01-16 | 29.4 | 230 | 542 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 230 | 0 | 0 | 39.791 | 202.6667 | 20.1594 | 86.148 | -75 | -6.0817 | 234.6276 | -106.7724 | 123.2276 | 39.061 | 0 | 39.061 | 84.92 | 39.061 | 7/21/17:00
7 | 21 | 1900-01-17 | 28.9 | 193 | 288 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 193 | 0 | 0 | 39.791 | 202.7083 | 20.1507 | 86.148 | -75 | -6.0836 | 249.6271 | -8.8279 | 184.1721 | 58.3793 | 0 | 58.3793 | 84.02 | 58.3793 | 7/21/18:00
7 | 21 | 1900-01-18 | 27.8 | 93 | 292 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 93 | 0 | 0 | 39.791 | 202.75 | 20.142 | 86.148 | -75 | -6.0854 | 264.6266 | 44.6246 | 137.6246 | 43.6246 | 0 | 43.6246 | 82.04 | 43.6246 | 7/21/19:00
7 | 21 | 1900-01-19 | 26.1 | 39 | 41 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 39 | 0 | 0 | 39.791 | 202.7917 | 20.1333 | 86.148 | -75 | -6.0872 | 279.6262 | 13.9779 | 52.9779 | 16.7931 | 0 | 16.7931 | 78.98 | 16.7931 | 7/21/20:00
7 | 21 | 1900-01-20 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 202.8333 | 20.1245 | 86.148 | -75 | -6.089 | 294.6257 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/21/21:00
7 | 21 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 202.875 | 20.1158 | 86.148 | -75 | -6.0908 | 309.6253 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/21/22:00
7 | 21 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 202.9167 | 20.107 | 86.148 | -75 | -6.0926 | 324.6249 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/21/23:00
7 | 21 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 202.9583 | 20.0982 | 86.148 | -75 | -6.0944 | 339.6244 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/21/24:00
7 | 22 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 203 | 20.0894 | 86.148 | -75 | -6.0961 | -5.376 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/22/1:00
7 | 22 | 1900-01-01 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 203.0417 | 20.0806 | 86.148 | -75 | -6.0978 | 9.6235 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/22/2:00
7 | 22 | 1900-01-02 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 203.0833 | 20.0718 | 86.148 | -75 | -6.0995 | 24.6231 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/22/3:00
7 | 22 | 1900-01-03 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 203.125 | 20.063 | 86.148 | -75 | -6.1012 | 39.6227 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/22/4:00
7 | 22 | 1900-01-04 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 203.1667 | 20.0542 | 86.148 | -75 | -6.1029 | 54.6223 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/22/5:00
7 | 22 | 1900-01-05 | 20 | 2 | 22 | 68 | 0 | 1 | 0 | 68 | 0 | 2 | 0 | 0 | 39.791 | 203.2083 | 20.0453 | 86.148 | -75 | -6.1046 | 69.6219 | 10.3558 | 12.3558 | 3.9166 | 0 | 3.9166 | 68 | 3.9166 | 7/22/6:00
7 | 22 | 1900-01-06 | 21.1 | 33 | 410 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 33 | 0 | 0 | 39.791 | 203.25 | 20.0365 | 86.148 | -75 | -6.1062 | 84.6214 | 117.6444 | 150.6444 | 47.7516 | 0 | 47.7516 | 69.98 | 47.7516 | 7/22/7:00
7 | 22 | 1900-01-07 | 23.3 | 64 | 460 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 64 | 0 | 0 | 39.791 | 203.2917 | 20.0276 | 86.148 | -75 | -6.1078 | 99.621 | 45.3211 | 109.3211 | 34.6529 | 0 | 34.6529 | 73.94 | 34.6529 | 7/22/8:00
7 | 22 | 1900-01-08 | 26.1 | 83 | 689 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 83 | 0 | 0 | 39.791 | 203.3333 | 20.0187 | 86.148 | -75 | -6.1094 | 114.6206 | -56.2832 | 26.7168 | 8.4688 | 0 | 8.4688 | 78.98 | 8.4688 | 7/22/9:00
7 | 22 | 1900-01-09 | 28.3 | 160 | 690 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 160 | 0 | 0 | 39.791 | 203.375 | 20.0099 | 86.148 | -75 | -6.111 | 129.6202 | -166.5824 | -6.5824 | -2.0865 | 0 | -2.0865 | 82.94 | -2.0865 | 7/22/10:00
7 | 22 | 1900-01-10 | 30 | 210 | 542 | 86 | 0 | 1 | 0 | 86 | 0 | 210 | 0 | 0 | 39.791 | 203.4167 | 20.001 | 86.148 | -75 | -6.1126 | 144.6198 | -200.432 | 9.568 | 3.0329 | 0 | 3.0329 | 86 | 3.0329 | 7/22/11:00
7 | 22 | 1900-01-11 | 30 | 290 | 677 | 86 | 0 | 1 | 0 | 86 | 0 | 290 | 0 | 0 | 39.791 | 203.4583 | 19.9921 | 86.148 | -75 | -6.1142 | 159.6195 | -310.1156 | -20.1156 | -6.3763 | 0 | -6.3763 | 86 | -6.3763 | 7/22/12:00
7 | 22 | 1900-01-12 | 29.4 | 319 | 145 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 319 | 0 | 0 | 39.791 | 203.5 | 19.9832 | 86.148 | -75 | -6.1157 | 174.6191 | -72.533 | 246.467 | 78.1257 | 0 | 78.1257 | 84.92 | 78.1257 | 7/22/13:00
7 | 22 | 1900-01-13 | 30.6 | 380 | 100 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 380 | 0 | 0 | 39.791 | 203.5417 | 19.9742 | 86.148 | -75 | -6.1172 | 189.6187 | -49.3392 | 330.6608 | 104.8137 | 0 | 104.8137 | 87.08 | 104.8137 | 7/22/14:00
7 | 22 | 1900-01-14 | 30 | 330 | 0 | 86 | 0 | 1 | 0 | 86 | 0 | 330 | 0 | 0 | 39.791 | 203.5833 | 19.9653 | 86.148 | -75 | -6.1187 | 204.6183 | 0 | 330 | 104.6042 | 0 | 104.6042 | 86 | 104.6042 | 7/22/15:00
7 | 22 | 1900-01-15 | 27.2 | 289 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 289 | 0 | 0 | 39.791 | 203.625 | 19.9564 | 86.148 | -75 | -6.1202 | 219.6179 | 0 | 289 | 91.608 | 0 | 91.608 | 80.96 | 91.608 | 7/22/16:00
7 | 22 | 1900-01-16 | 22.2 | 185 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 185 | 0 | 0 | 39.791 | 203.6667 | 19.9474 | 86.148 | -75 | -6.1217 | 234.6176 | 0 | 185 | 58.6418 | 0 | 58.6418 | 71.96 | 58.6418 | 7/22/17:00
7 | 22 | 1900-01-17 | 22.2 | 113 | 644 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 113 | 0 | 0 | 39.791 | 203.7083 | 19.9385 | 86.148 | -75 | -6.1232 | 249.6172 | -21.4688 | 91.5312 | 29.0138 | 0 | 29.0138 | 71.96 | 29.0138 | 7/22/18:00
7 | 22 | 1900-01-18 | 22.2 | 51 | 268 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 51 | 0 | 0 | 39.791 | 203.75 | 19.9295 | 86.148 | -75 | -6.1246 | 264.6168 | 40.3017 | 91.3017 | 28.941 | 0 | 28.941 | 71.96 | 28.941 | 7/22/19:00
7 | 22 | 1900-01-19 | 22.8 | 29 | 80 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 29 | 0 | 0 | 39.791 | 203.7917 | 19.9205 | 86.148 | -75 | -6.1261 | 279.6165 | 27.0988 | 56.0988 | 17.7823 | 0 | 17.7823 | 73.04 | 17.7823 | 7/22/20:00
7 | 22 | 1900-01-20 | 21.7 | 0 | 2 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 203.8333 | 19.9115 | 86.148 | -75 | -6.1275 | 294.6161 | 1.0378 | 1.0378 | 0.32896 | 0 | 0.32896 | 71.06 | 0.32896 | 7/22/21:00
7 | 22 | 1900-01-21 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 203.875 | 19.9025 | 86.148 | -75 | -6.1289 | 309.6158 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/22/22:00
7 | 22 | 1900-01-22 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 203.9167 | 19.8935 | 86.148 | -75 | -6.1302 | 324.6154 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/22/23:00
7 | 22 | 1900-01-23 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 203.9583 | 19.8845 | 86.148 | -75 | -6.1316 | 339.6151 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/22/24:00
7 | 23 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 204 | 19.8754 | 86.148 | -75 | -6.1329 | -5.3852 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/23/1:00
7 | 23 | 1900-01-01 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 204.0417 | 19.8664 | 86.148 | -75 | -6.1343 | 9.6144 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/23/2:00
7 | 23 | 1900-01-02 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 204.0833 | 19.8573 | 86.148 | -75 | -6.1356 | 24.6141 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/23/3:00
7 | 23 | 1900-01-03 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 204.125 | 19.8483 | 86.148 | -75 | -6.1369 | 39.6138 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/23/4:00
7 | 23 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 204.1667 | 19.8392 | 86.148 | -75 | -6.1381 | 54.6135 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/23/5:00
7 | 23 | 1900-01-05 | 21.7 | 1 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 1 | 0 | 0 | 39.791 | 204.2083 | 19.8301 | 86.148 | -75 | -6.1394 | 69.6131 | 0 | 1 | 0.31698 | 0 | 0.31698 | 71.06 | 0.31698 | 7/23/6:00
7 | 23 | 1900-01-06 | 22.2 | 29 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 29 | 0 | 0 | 39.791 | 204.25 | 19.821 | 86.148 | -75 | -6.1407 | 84.6128 | 0 | 29 | 9.1925 | 0 | 9.1925 | 71.96 | 9.1925 | 7/23/7:00
7 | 23 | 1900-01-07 | 22.8 | 59 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 59 | 0 | 0 | 39.791 | 204.2917 | 19.8119 | 86.148 | -75 | -6.1419 | 99.6125 | 0 | 59 | 18.702 | 0 | 18.702 | 73.04 | 18.702 | 7/23/8:00
7 | 23 | 1900-01-08 | 23.9 | 91 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 91 | 0 | 0 | 39.791 | 204.3333 | 19.8028 | 86.148 | -75 | -6.1431 | 114.6122 | 0 | 91 | 28.8454 | 0 | 28.8454 | 75.02 | 28.8454 | 7/23/9:00
7 | 23 | 1900-01-09 | 26.1 | 321 | 71 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 321 | 0 | 0 | 39.791 | 204.375 | 19.7937 | 86.148 | -75 | -6.1443 | 129.6119 | -17.3412 | 303.6588 | 96.2545 | 0 | 96.2545 | 78.98 | 96.2545 | 7/23/10:00
7 | 23 | 1900-01-10 | 26.7 | 382 | 81 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 382 | 0 | 0 | 39.791 | 204.4167 | 19.7845 | 86.148 | -75 | -6.1455 | 144.6116 | -30.1984 | 351.8016 | 111.515 | 0 | 111.515 | 80.06 | 111.515 | 7/23/11:00
7 | 23 | 1900-01-11 | 27.2 | 433 | 61 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 433 | 0 | 0 | 39.791 | 204.4583 | 19.7754 | 86.148 | -75 | -6.1466 | 159.6113 | -28.1356 | 404.8644 | 128.3349 | 0 | 128.3349 | 80.96 | 128.3349 | 7/23/12:00
7 | 23 | 1900-01-12 | 27.8 | 279 | 0 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 279 | 0 | 0 | 39.791 | 204.5 | 19.7662 | 86.148 | -75 | -6.1478 | 174.6111 | 0 | 279 | 88.4381 | 0 | 88.4381 | 82.04 | 88.4381 | 7/23/13:00
7 | 23 | 1900-01-13 | 23.3 | 277 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 277 | 0 | 0 | 39.791 | 204.5417 | 19.7571 | 86.148 | -75 | -6.1489 | 189.6108 | 0 | 277 | 87.8042 | 0 | 87.8042 | 73.94 | 87.8042 | 7/23/14:00
7 | 23 | 1900-01-14 | 23.9 | 288 | 299 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 288 | 0 | 0 | 39.791 | 204.5833 | 19.7479 | 86.148 | -75 | -6.15 | 204.6105 | -131.9362 | 156.0638 | 49.4695 | 0 | 49.4695 | 75.02 | 49.4695 | 7/23/15:00
7 | 23 | 1900-01-15 | 23.3 | 221 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 221 | 0 | 0 | 39.791 | 204.625 | 19.7387 | 86.148 | -75 | -6.1511 | 219.6102 | 0 | 221 | 70.0531 | 0 | 70.0531 | 73.94 | 70.0531 | 7/23/16:00
7 | 23 | 1900-01-16 | 21.1 | 171 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 171 | 0 | 0 | 39.791 | 204.6667 | 19.7295 | 86.148 | -75 | -6.1522 | 234.61 | 0 | 171 | 54.204 | 0 | 54.204 | 69.98 | 54.204 | 7/23/17:00
7 | 23 | 1900-01-17 | 21.7 | 173 | 130 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 173 | 0 | 0 | 39.791 | 204.7083 | 19.7203 | 86.148 | -75 | -6.1532 | 249.6097 | -4.6882 | 168.3118 | 53.3519 | 0 | 53.3519 | 71.06 | 53.3519 | 7/23/18:00
7 | 23 | 1900-01-18 | 22.2 | 92 | 33 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 92 | 0 | 0 | 39.791 | 204.75 | 19.7111 | 86.148 | -75 | -6.1543 | 264.6094 | 4.8806 | 96.8806 | 30.7095 | 0 | 30.7095 | 71.96 | 30.7095 | 7/23/19:00
7 | 23 | 1900-01-19 | 22.2 | 36 | 5 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 36 | 0 | 0 | 39.791 | 204.7917 | 19.7019 | 86.148 | -75 | -6.1553 | 279.6092 | 1.6826 | 37.6826 | 11.9447 | 0 | 11.9447 | 71.96 | 11.9447 | 7/23/20:00
7 | 23 | 1900-01-20 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 204.8333 | 19.6926 | 86.148 | -75 | -6.1563 | 294.6089 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/23/21:00
7 | 23 | 1900-01-21 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 204.875 | 19.6834 | 86.148 | -75 | -6.1573 | 309.6087 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/23/22:00
7 | 23 | 1900-01-22 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 204.9167 | 19.6741 | 86.148 | -75 | -6.1583 | 324.6084 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/23/23:00
7 | 23 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 204.9583 | 19.6649 | 86.148 | -75 | -6.1592 | 339.6082 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/23/24:00
7 | 24 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 205 | 19.6556 | 86.148 | -75 | -6.1602 | -5.392 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/24/1:00
7 | 24 | 1900-01-01 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 205.0417 | 19.6463 | 86.148 | -75 | -6.1611 | 9.6077 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/24/2:00
7 | 24 | 1900-01-02 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 205.0833 | 19.637 | 86.148 | -75 | -6.162 | 24.6075 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/24/3:00
7 | 24 | 1900-01-03 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 205.125 | 19.6277 | 86.148 | -75 | -6.1629 | 39.6073 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/24/4:00
7 | 24 | 1900-01-04 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 205.1667 | 19.6184 | 86.148 | -75 | -6.1638 | 54.6071 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/24/5:00
7 | 24 | 1900-01-05 | 21.1 | 1 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 1 | 0 | 0 | 39.791 | 205.2083 | 19.6091 | 86.148 | -75 | -6.1646 | 69.6068 | 0 | 1 | 0.31698 | 0 | 0.31698 | 69.98 | 0.31698 | 7/24/6:00
7 | 24 | 1900-01-06 | 20.6 | 30 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 30 | 0 | 0 | 39.791 | 205.25 | 19.5997 | 86.148 | -75 | -6.1655 | 84.6066 | 0 | 30 | 9.5095 | 0 | 9.5095 | 69.08 | 9.5095 | 7/24/7:00
7 | 24 | 1900-01-07 | 21.1 | 65 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 65 | 0 | 0 | 39.791 | 205.2917 | 19.5904 | 86.148 | -75 | -6.1663 | 99.6064 | 0 | 65 | 20.6039 | 0 | 20.6039 | 69.98 | 20.6039 | 7/24/8:00
7 | 24 | 1900-01-08 | 21.7 | 97 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 97 | 0 | 0 | 39.791 | 205.3333 | 19.581 | 86.148 | -75 | -6.1671 | 114.6062 | 0 | 97 | 30.7473 | 0 | 30.7473 | 71.06 | 30.7473 | 7/24/9:00
7 | 24 | 1900-01-09 | 22.2 | 132 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 132 | 0 | 0 | 39.791 | 205.375 | 19.5717 | 86.148 | -75 | -6.1679 | 129.606 | 0 | 132 | 41.8417 | 0 | 41.8417 | 71.96 | 41.8417 | 7/24/10:00
7 | 24 | 1900-01-10 | 23.9 | 197 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 197 | 0 | 0 | 39.791 | 205.4167 | 19.5623 | 86.148 | -75 | -6.1686 | 144.6058 | 0 | 197 | 62.4456 | 0 | 62.4456 | 75.02 | 62.4456 | 7/24/11:00
7 | 24 | 1900-01-11 | 25.6 | 280 | 73 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 280 | 0 | 0 | 39.791 | 205.4583 | 19.5529 | 86.148 | -75 | -6.1694 | 159.6056 | -33.9082 | 246.0918 | 78.0068 | 0 | 78.0068 | 78.08 | 78.0068 | 7/24/12:00
7 | 24 | 1900-01-12 | 27.8 | 426 | 342 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 426 | 0 | 0 | 39.791 | 205.5 | 19.5435 | 86.148 | -75 | -6.1701 | 174.6055 | -173.3316 | 252.6684 | 80.0915 | 0 | 80.0915 | 82.04 | 80.0915 | 7/24/13:00
7 | 24 | 1900-01-13 | 28.3 | 463 | 190 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 463 | 0 | 0 | 39.791 | 205.5417 | 19.5341 | 86.148 | -75 | -6.1709 | 189.6053 | -95.0026 | 367.9974 | 116.6488 | 0 | 116.6488 | 82.94 | 116.6488 | 7/24/14:00
7 | 24 | 1900-01-14 | 29.4 | 459 | 213 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 459 | 0 | 0 | 39.791 | 205.5833 | 19.5247 | 86.148 | -75 | -6.1716 | 204.6051 | -94.6889 | 364.3111 | 115.4802 | 0 | 115.4802 | 84.92 | 115.4802 | 7/24/15:00
7 | 24 | 1900-01-15 | 30 | 328 | 479 | 86 | 0 | 1 | 0 | 86 | 0 | 328 | 0 | 0 | 39.791 | 205.625 | 19.5153 | 86.148 | -75 | -6.1722 | 219.6049 | -164.8741 | 163.1259 | 51.7081 | 0 | 51.7081 | 86 | 51.7081 | 7/24/16:00
7 | 24 | 1900-01-16 | 29.4 | 327 | 345 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 327 | 0 | 0 | 39.791 | 205.6667 | 19.5059 | 86.148 | -75 | -6.1729 | 234.6048 | -71.0082 | 255.9918 | 81.1449 | 0 | 81.1449 | 84.92 | 81.1449 | 7/24/17:00
7 | 24 | 1900-01-17 | 28.9 | 216 | 102 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 216 | 0 | 0 | 39.791 | 205.7083 | 19.4964 | 86.148 | -75 | -6.1736 | 249.6046 | -3.9607 | 212.0393 | 67.2128 | 0 | 67.2128 | 84.02 | 67.2128 | 7/24/18:00
7 | 24 | 1900-01-18 | 27.8 | 159 | 38 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 159 | 0 | 0 | 39.791 | 205.75 | 19.487 | 86.148 | -75 | -6.1742 | 264.6044 | 5.5245 | 164.5245 | 52.1514 | 0 | 52.1514 | 82.04 | 52.1514 | 7/24/19:00
7 | 24 | 1900-01-19 | 26.7 | 40 | 3 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 40 | 0 | 0 | 39.791 | 205.7917 | 19.4775 | 86.148 | -75 | -6.1748 | 279.6043 | 1.0028 | 41.0028 | 12.9972 | 0 | 12.9972 | 80.06 | 12.9972 | 7/24/20:00
7 | 24 | 1900-01-20 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 205.8333 | 19.468 | 86.148 | -75 | -6.1754 | 294.6041 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 7/24/21:00
7 | 24 | 1900-01-21 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 205.875 | 19.4585 | 86.148 | -75 | -6.176 | 309.604 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/24/22:00
7 | 24 | 1900-01-22 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 205.9167 | 19.449 | 86.148 | -75 | -6.1766 | 324.6039 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/24/23:00
7 | 24 | 1900-01-23 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 205.9583 | 19.4395 | 86.148 | -75 | -6.1771 | 339.6037 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/24/24:00
7 | 25 | 1899-12-31 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 206 | 19.43 | 86.148 | -75 | -6.1777 | -5.3964 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/25/1:00
7 | 25 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 206.0417 | 19.4205 | 86.148 | -75 | -6.1782 | 9.6035 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/25/2:00
7 | 25 | 1900-01-02 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 206.0833 | 19.411 | 86.148 | -75 | -6.1787 | 24.6033 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/25/3:00
7 | 25 | 1900-01-03 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 206.125 | 19.4014 | 86.148 | -75 | -6.1791 | 39.6032 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/25/4:00
7 | 25 | 1900-01-04 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 206.1667 | 19.3919 | 86.148 | -75 | -6.1796 | 54.6031 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/25/5:00
7 | 25 | 1900-01-05 | 21.7 | 1 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 1 | 0 | 0 | 39.791 | 206.2083 | 19.3823 | 86.148 | -75 | -6.1801 | 69.603 | 0 | 1 | 0.31698 | 0 | 0.31698 | 71.06 | 0.31698 | 7/25/6:00
7 | 25 | 1900-01-06 | 22.2 | 34 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 34 | 0 | 0 | 39.791 | 206.25 | 19.3727 | 86.148 | -75 | -6.1805 | 84.6029 | 0 | 34 | 10.7774 | 0 | 10.7774 | 71.96 | 10.7774 | 7/25/7:00
7 | 25 | 1900-01-07 | 22.8 | 73 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 73 | 0 | 0 | 39.791 | 206.2917 | 19.3632 | 86.148 | -75 | -6.1809 | 99.6028 | 0 | 73 | 23.1397 | 0 | 23.1397 | 73.04 | 23.1397 | 7/25/8:00
7 | 25 | 1900-01-08 | 22.8 | 111 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 111 | 0 | 0 | 39.791 | 206.3333 | 19.3536 | 86.148 | -75 | -6.1813 | 114.6027 | 0 | 111 | 35.1851 | 0 | 35.1851 | 73.04 | 35.1851 | 7/25/9:00
7 | 25 | 1900-01-09 | 22.8 | 158 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 158 | 0 | 0 | 39.791 | 206.375 | 19.344 | 86.148 | -75 | -6.1817 | 129.6026 | 0 | 158 | 50.0832 | 0 | 50.0832 | 73.04 | 50.0832 | 7/25/10:00
7 | 25 | 1900-01-10 | 21.1 | 163 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 163 | 0 | 0 | 39.791 | 206.4167 | 19.3344 | 86.148 | -75 | -6.182 | 144.6025 | 0 | 163 | 51.6682 | 0 | 51.6682 | 69.98 | 51.6682 | 7/25/11:00
7 | 25 | 1900-01-11 | 24.4 | 155 | 69 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 155 | 0 | 0 | 39.791 | 206.4583 | 19.3247 | 86.148 | -75 | -6.1824 | 159.6024 | -32.281 | 122.719 | 38.8998 | 0 | 38.8998 | 75.92 | 38.8998 | 7/25/12:00
7 | 25 | 1900-01-12 | 24.4 | 277 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 277 | 0 | 0 | 39.791 | 206.5 | 19.3151 | 86.148 | -75 | -6.1827 | 174.6023 | 0 | 277 | 87.8042 | 0 | 87.8042 | 75.92 | 87.8042 | 7/25/13:00
7 | 25 | 1900-01-13 | 27.2 | 426 | 288 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 426 | 0 | 0 | 39.791 | 206.5417 | 19.3055 | 86.148 | -75 | -6.183 | 189.6022 | -144.989 | 281.011 | 89.0756 | 0 | 89.0756 | 80.96 | 89.0756 | 7/25/14:00
7 | 25 | 1900-01-14 | 27.2 | 330 | 263 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 330 | 0 | 0 | 39.791 | 206.5833 | 19.2958 | 86.148 | -75 | -6.1833 | 204.6022 | -117.7986 | 212.2014 | 67.2641 | 0 | 67.2641 | 80.96 | 67.2641 | 7/25/15:00
7 | 25 | 1900-01-15 | 28.3 | 243 | 569 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 243 | 0 | 0 | 39.791 | 206.625 | 19.2862 | 86.148 | -75 | -6.1836 | 219.6021 | -197.6866 | 45.3134 | 14.3636 | 0 | 14.3636 | 82.94 | 14.3636 | 7/25/16:00
7 | 25 | 1900-01-16 | 28.9 | 150 | 627 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 150 | 0 | 0 | 39.791 | 206.6667 | 19.2765 | 86.148 | -75 | -6.1838 | 234.602 | -130.9535 | 19.0465 | 6.0374 | 0 | 6.0374 | 84.02 | 6.0374 | 7/25/17:00
7 | 25 | 1900-01-17 | 28.9 | 136 | 511 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 136 | 0 | 0 | 39.791 | 206.7083 | 19.2668 | 86.148 | -75 | -6.1841 | 249.602 | -21.2766 | 114.7234 | 36.3653 | 0 | 36.3653 | 84.02 | 36.3653 | 7/25/18:00
7 | 25 | 1900-01-18 | 28.3 | 94 | 286 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 94 | 0 | 0 | 39.791 | 206.75 | 19.2571 | 86.148 | -75 | -6.1843 | 264.6019 | 40.8501 | 134.8501 | 42.7451 | 0 | 42.7451 | 82.94 | 42.7451 | 7/25/19:00
7 | 25 | 1900-01-19 | 26.1 | 30 | 64 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 30 | 0 | 0 | 39.791 | 206.7917 | 19.2474 | 86.148 | -75 | -6.1845 | 279.6019 | 21.2464 | 51.2464 | 16.2442 | 0 | 16.2442 | 78.98 | 16.2442 | 7/25/20:00
7 | 25 | 1900-01-20 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 206.8333 | 19.2377 | 86.148 | -75 | -6.1847 | 294.6018 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/25/21:00
7 | 25 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 206.875 | 19.228 | 86.148 | -75 | -6.1848 | 309.6018 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/25/22:00
7 | 25 | 1900-01-22 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 206.9167 | 19.2183 | 86.148 | -75 | -6.185 | 324.6018 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/25/23:00
7 | 25 | 1900-01-23 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 206.9583 | 19.2085 | 86.148 | -75 | -6.1851 | 339.6017 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/25/24:00
7 | 26 | 1899-12-31 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 207 | 19.1988 | 86.148 | -75 | -6.1853 | -5.3983 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/26/1:00
7 | 26 | 1900-01-01 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 207.0417 | 19.189 | 86.148 | -75 | -6.1854 | 9.6017 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/26/2:00
7 | 26 | 1900-01-02 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 207.0833 | 19.1793 | 86.148 | -75 | -6.1854 | 24.6016 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/26/3:00
7 | 26 | 1900-01-03 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 207.125 | 19.1695 | 86.148 | -75 | -6.1855 | 39.6016 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/26/4:00
7 | 26 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 207.1667 | 19.1597 | 86.148 | -75 | -6.1855 | 54.6016 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/26/5:00
7 | 26 | 1900-01-05 | 21.7 | 1 | 3 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 1 | 0 | 0 | 39.791 | 207.2083 | 19.1499 | 86.148 | -75 | -6.1856 | 69.6016 | 1.3888 | 2.3888 | 0.75721 | 0 | 0.75721 | 71.06 | 0.75721 | 7/26/6:00
7 | 26 | 1900-01-06 | 22.8 | 38 | 62 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 38 | 0 | 0 | 39.791 | 207.25 | 19.1401 | 86.148 | -75 | -6.1856 | 84.6016 | 17.2442 | 55.2442 | 17.5115 | 0 | 17.5115 | 73.04 | 17.5115 | 7/26/7:00
7 | 26 | 1900-01-07 | 23.9 | 95 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 95 | 0 | 0 | 39.791 | 207.2917 | 19.1303 | 86.148 | -75 | -6.1856 | 99.6016 | 0 | 95 | 30.1133 | 0 | 30.1133 | 75.02 | 30.1133 | 7/26/8:00
7 | 26 | 1900-01-08 | 24.4 | 136 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 136 | 0 | 0 | 39.791 | 207.3333 | 19.1205 | 86.148 | -75 | -6.1856 | 114.6016 | 0 | 136 | 43.1096 | 0 | 43.1096 | 75.92 | 43.1096 | 7/26/9:00
7 | 26 | 1900-01-09 | 25.6 | 258 | 321 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 258 | 0 | 0 | 39.791 | 207.375 | 19.1106 | 86.148 | -75 | -6.1855 | 129.6016 | -81.3033 | 176.6967 | 56.0098 | 0 | 56.0098 | 78.08 | 56.0098 | 7/26/10:00
7 | 26 | 1900-01-10 | 27.2 | 329 | 420 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 329 | 0 | 0 | 39.791 | 207.4167 | 19.1008 | 86.148 | -75 | -6.1855 | 144.6016 | -160.6232 | 168.3768 | 53.3725 | 0 | 53.3725 | 80.96 | 53.3725 | 7/26/11:00
7 | 26 | 1900-01-11 | 28.3 | 173 | 760 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 173 | 0 | 0 | 39.791 | 207.4583 | 19.0909 | 86.148 | -75 | -6.1854 | 159.6016 | -358.165 | -185.165 | -58.6941 | 0 | -58.6941 | 82.94 | -58.6941 | 7/26/12:00
7 | 26 | 1900-01-12 | 28.9 | 256 | 603 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 256 | 0 | 0 | 39.791 | 207.5 | 19.0811 | 86.148 | -75 | -6.1853 | 174.6017 | -309.7793 | -53.7793 | -17.0471 | 0 | -17.0471 | 84.02 | -17.0471 | 7/26/13:00
7 | 26 | 1900-01-13 | 28.9 | 295 | 590 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 295 | 0 | 0 | 39.791 | 207.5417 | 19.0712 | 86.148 | -75 | -6.1852 | 189.6017 | -299.0857 | -4.0857 | -1.2951 | 0 | -1.2951 | 84.02 | -1.2951 | 7/26/14:00
7 | 26 | 1900-01-14 | 28.9 | 198 | 712 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 198 | 0 | 0 | 39.791 | 207.5833 | 19.0613 | 86.148 | -75 | -6.1851 | 204.6017 | -321.3393 | -123.3393 | -39.0964 | 0 | -39.0964 | 84.02 | -39.0964 | 7/26/15:00
7 | 26 | 1900-01-15 | 30.6 | 196 | 690 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 196 | 0 | 0 | 39.791 | 207.625 | 19.0514 | 86.148 | -75 | -6.1849 | 219.6018 | -241.9858 | -45.9858 | -14.5767 | 0 | -14.5767 | 87.08 | -14.5767 | 7/26/16:00
7 | 26 | 1900-01-16 | 29.4 | 206 | 569 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 206 | 0 | 0 | 39.791 | 207.6667 | 19.0415 | 86.148 | -75 | -6.1848 | 234.6018 | -120.5927 | 85.4073 | 27.0726 | 0 | 27.0726 | 84.92 | 27.0726 | 7/26/17:00
7 | 26 | 1900-01-17 | 29.4 | 139 | 425 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 139 | 0 | 0 | 39.791 | 207.7083 | 19.0316 | 86.148 | -75 | -6.1846 | 249.6019 | -18.9045 | 120.0955 | 38.0682 | 0 | 38.0682 | 84.92 | 38.0682 | 7/26/18:00
7 | 26 | 1900-01-18 | 28.9 | 94 | 282 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 94 | 0 | 0 | 39.791 | 207.75 | 19.0217 | 86.148 | -75 | -6.1844 | 264.6019 | 39.5505 | 133.5505 | 42.3332 | 0 | 42.3332 | 84.02 | 42.3332 | 7/26/19:00
7 | 26 | 1900-01-19 | 26.7 | 30 | 66 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 30 | 0 | 0 | 39.791 | 207.7917 | 19.0117 | 86.148 | -75 | -6.1842 | 279.602 | 21.7576 | 51.7576 | 16.4063 | 0 | 16.4063 | 80.06 | 16.4063 | 7/26/20:00
7 | 26 | 1900-01-20 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 207.8333 | 19.0018 | 86.148 | -75 | -6.184 | 294.602 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/26/21:00
7 | 26 | 1900-01-21 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 207.875 | 18.9919 | 86.148 | -75 | -6.1837 | 309.6021 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 7/26/22:00
7 | 26 | 1900-01-22 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 207.9167 | 18.9819 | 86.148 | -75 | -6.1834 | 324.6021 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/26/23:00
7 | 26 | 1900-01-23 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 207.9583 | 18.9719 | 86.148 | -75 | -6.1832 | 339.6022 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/26/24:00
7 | 27 | 1899-12-31 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 208 | 18.962 | 86.148 | -75 | -6.1829 | -5.3977 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/27/1:00
7 | 27 | 1900-01-01 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 208.0417 | 18.952 | 86.148 | -75 | -6.1825 | 9.6024 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/27/2:00
7 | 27 | 1900-01-02 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 208.0833 | 18.942 | 86.148 | -75 | -6.1822 | 24.6025 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/27/3:00
7 | 27 | 1900-01-03 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 208.125 | 18.932 | 86.148 | -75 | -6.1818 | 39.6025 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/27/4:00
7 | 27 | 1900-01-04 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 208.1667 | 18.9219 | 86.148 | -75 | -6.1815 | 54.6026 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 7/27/5:00
7 | 27 | 1900-01-05 | 20.6 | 1 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 1 | 0 | 0 | 39.791 | 208.2083 | 18.9119 | 86.148 | -75 | -6.1811 | 69.6027 | 0 | 1 | 0.31698 | 0 | 0.31698 | 69.08 | 0.31698 | 7/27/6:00
7 | 27 | 1900-01-06 | 22.2 | 53 | 60 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 53 | 0 | 0 | 39.791 | 208.25 | 18.9019 | 86.148 | -75 | -6.1807 | 84.6028 | 16.542 | 69.542 | 22.0436 | 0 | 22.0436 | 71.96 | 22.0436 | 7/27/7:00
7 | 27 | 1900-01-07 | 23.9 | 122 | 104 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 122 | 0 | 0 | 39.791 | 208.2917 | 18.8918 | 86.148 | -75 | -6.1803 | 99.6029 | 8.9379 | 130.9379 | 41.505 | 0 | 41.505 | 75.02 | 41.505 | 7/27/8:00
7 | 27 | 1900-01-08 | 25 | 205 | 163 | 77 | 0 | 1 | 0 | 77 | 0 | 205 | 0 | 0 | 39.791 | 208.3333 | 18.8818 | 86.148 | -75 | -6.1798 | 114.603 | -15.5788 | 189.4212 | 60.0432 | 0 | 60.0432 | 77 | 60.0432 | 7/27/9:00
7 | 27 | 1900-01-09 | 27.2 | 318 | 179 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 318 | 0 | 0 | 39.791 | 208.375 | 18.8717 | 86.148 | -75 | -6.1794 | 129.6032 | -45.9107 | 272.0893 | 86.2476 | 0 | 86.2476 | 80.96 | 86.2476 | 7/27/10:00
7 | 27 | 1900-01-10 | 27.8 | 282 | 533 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 282 | 0 | 0 | 39.791 | 208.4167 | 18.8616 | 86.148 | -75 | -6.1789 | 144.6033 | -205.6444 | 76.3556 | 24.2034 | 0 | 24.2034 | 82.04 | 24.2034 | 7/27/11:00
7 | 27 | 1900-01-11 | 28.3 | 351 | 368 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 351 | 0 | 0 | 39.791 | 208.4583 | 18.8516 | 86.148 | -75 | -6.1784 | 159.6034 | -174.7205 | 176.2795 | 55.8775 | 0 | 55.8775 | 82.94 | 55.8775 | 7/27/12:00
7 | 27 | 1900-01-12 | 29.4 | 335 | 619 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 335 | 0 | 0 | 39.791 | 208.5 | 18.8415 | 86.148 | -75 | -6.1779 | 174.6035 | -320.2103 | 14.7897 | 4.6881 | 0 | 4.6881 | 84.92 | 4.6881 | 7/27/13:00
7 | 27 | 1900-01-13 | 30 | 380 | 463 | 86 | 0 | 1 | 0 | 86 | 0 | 380 | 0 | 0 | 39.791 | 208.5417 | 18.8314 | 86.148 | -75 | -6.1773 | 189.6037 | -236.3541 | 143.6459 | 45.5332 | 0 | 45.5332 | 86 | 45.5332 | 7/27/14:00
7 | 27 | 1900-01-14 | 31.1 | 332 | 558 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 332 | 0 | 0 | 39.791 | 208.5833 | 18.8213 | 86.148 | -75 | -6.1768 | 204.6038 | -253.7753 | 78.2247 | 24.7959 | 0 | 24.7959 | 87.98 | 24.7959 | 7/27/15:00
7 | 27 | 1900-01-15 | 30.6 | 317 | 500 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 317 | 0 | 0 | 39.791 | 208.625 | 18.8111 | 86.148 | -75 | -6.1762 | 219.6039 | -177.0152 | 139.9848 | 44.3727 | 0 | 44.3727 | 87.08 | 44.3727 | 7/27/16:00
7 | 27 | 1900-01-16 | 30.6 | 270 | 317 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 270 | 0 | 0 | 39.791 | 208.6667 | 18.801 | 86.148 | -75 | -6.1756 | 234.6041 | -68.1745 | 201.8255 | 63.9752 | 0 | 63.9752 | 87.08 | 63.9752 | 7/27/17:00
7 | 27 | 1900-01-17 | 30.6 | 179 | 379 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 179 | 0 | 0 | 39.791 | 208.7083 | 18.7909 | 86.148 | -75 | -6.175 | 249.6042 | -17.9499 | 161.0501 | 51.0501 | 0 | 51.0501 | 87.08 | 51.0501 | 7/27/18:00
7 | 27 | 1900-01-18 | 28.9 | 101 | 176 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 101 | 0 | 0 | 39.791 | 208.75 | 18.7807 | 86.148 | -75 | -6.1744 | 264.6044 | 24.2241 | 125.2241 | 39.6939 | 0 | 39.6939 | 84.02 | 39.6939 | 7/27/19:00
7 | 27 | 1900-01-19 | 27.8 | 33 | 17 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 33 | 0 | 0 | 39.791 | 208.7917 | 18.7706 | 86.148 | -75 | -6.1738 | 279.6046 | 5.5644 | 38.5644 | 12.2243 | 0 | 12.2243 | 82.04 | 12.2243 | 7/27/20:00
7 | 27 | 1900-01-20 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 208.8333 | 18.7604 | 86.148 | -75 | -6.1731 | 294.6047 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 7/27/21:00
7 | 27 | 1900-01-21 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 208.875 | 18.7502 | 86.148 | -75 | -6.1725 | 309.6049 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/27/22:00
7 | 27 | 1900-01-22 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 208.9167 | 18.74 | 86.148 | -75 | -6.1718 | 324.6051 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/27/23:00
7 | 27 | 1900-01-23 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 208.9583 | 18.7298 | 86.148 | -75 | -6.1711 | 339.6052 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/27/24:00
7 | 28 | 1899-12-31 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 209 | 18.7196 | 86.148 | -75 | -6.1704 | -5.3946 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/28/1:00
7 | 28 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 209.0417 | 18.7094 | 86.148 | -75 | -6.1696 | 9.6056 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/28/2:00
7 | 28 | 1900-01-02 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 209.0833 | 18.6992 | 86.148 | -75 | -6.1689 | 24.6058 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/28/3:00
7 | 28 | 1900-01-03 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 209.125 | 18.689 | 86.148 | -75 | -6.1681 | 39.606 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/28/4:00
7 | 28 | 1900-01-04 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 209.1667 | 18.6787 | 86.148 | -75 | -6.1673 | 54.6062 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/28/5:00
7 | 28 | 1900-01-05 | 22.2 | 1 | 1 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 1 | 0 | 0 | 39.791 | 209.2083 | 18.6685 | 86.148 | -75 | -6.1665 | 69.6064 | 0.45852 | 1.4585 | 0.46233 | 0 | 0.46233 | 71.96 | 0.46233 | 7/28/6:00
7 | 28 | 1900-01-06 | 22.8 | 76 | 57 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 76 | 0 | 0 | 39.791 | 209.25 | 18.6582 | 86.148 | -75 | -6.1656 | 84.6066 | 15.5709 | 91.5709 | 29.0264 | 0 | 29.0264 | 73.04 | 29.0264 | 7/28/7:00
7 | 28 | 1900-01-07 | 24.4 | 150 | 160 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 150 | 0 | 0 | 39.791 | 209.2917 | 18.6479 | 86.148 | -75 | -6.1648 | 99.6068 | 13.302 | 163.302 | 51.7639 | 0 | 51.7639 | 75.92 | 51.7639 | 7/28/8:00
7 | 28 | 1900-01-08 | 24.4 | 137 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 137 | 0 | 0 | 39.791 | 209.3333 | 18.6377 | 86.148 | -75 | -6.1639 | 114.607 | 0 | 137 | 43.4266 | 0 | 43.4266 | 75.92 | 43.4266 | 7/28/9:00
7 | 28 | 1900-01-09 | 25 | 192 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 192 | 0 | 0 | 39.791 | 209.375 | 18.6274 | 86.148 | -75 | -6.163 | 129.6072 | 0 | 192 | 60.8606 | 0 | 60.8606 | 77 | 60.8606 | 7/28/10:00
7 | 28 | 1900-01-10 | 25.6 | 235 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 235 | 0 | 0 | 39.791 | 209.4167 | 18.6171 | 86.148 | -75 | -6.1621 | 144.6075 | 0 | 235 | 74.4909 | 0 | 74.4909 | 78.08 | 74.4909 | 7/28/11:00
7 | 28 | 1900-01-11 | 27.2 | 331 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 331 | 0 | 0 | 39.791 | 209.4583 | 18.6068 | 86.148 | -75 | -6.1612 | 159.6077 | 0 | 331 | 104.9212 | 0 | 104.9212 | 80.96 | 104.9212 | 7/28/12:00
7 | 28 | 1900-01-12 | 28.3 | 189 | 462 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 189 | 0 | 0 | 39.791 | 209.5 | 18.5964 | 86.148 | -75 | -6.1603 | 174.6079 | -240.6789 | -51.6789 | -16.3813 | 0 | -16.3813 | 82.94 | -16.3813 | 7/28/13:00
7 | 28 | 1900-01-13 | 29.4 | 181 | 745 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 181 | 0 | 0 | 39.791 | 209.5417 | 18.5861 | 86.148 | -75 | -6.1593 | 189.6082 | -383.0115 | -202.0115 | -64.0341 | 0 | -64.0341 | 84.92 | -64.0341 | 7/28/14:00
7 | 28 | 1900-01-14 | 30 | 190 | 843 | 86 | 0 | 1 | 0 | 86 | 0 | 190 | 0 | 0 | 39.791 | 209.5833 | 18.5758 | 86.148 | -75 | -6.1584 | 204.6084 | -386.3695 | -196.3695 | -62.2457 | 0 | -62.2457 | 86 | -62.2457 | 7/28/15:00
7 | 28 | 1900-01-15 | 31.1 | 190 | 665 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 190 | 0 | 0 | 39.791 | 209.625 | 18.5654 | 86.148 | -75 | -6.1574 | 219.6087 | -237.6746 | -47.6746 | -15.112 | 0 | -15.112 | 87.98 | -15.112 | 7/28/16:00
7 | 28 | 1900-01-16 | 31.1 | 172 | 638 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 172 | 0 | 0 | 39.791 | 209.6667 | 18.5551 | 86.148 | -75 | -6.1564 | 234.6089 | -139.2279 | 32.7721 | 10.3882 | 0 | 10.3882 | 87.98 | 10.3882 | 7/28/17:00
7 | 28 | 1900-01-17 | 31.1 | 159 | 508 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 159 | 0 | 0 | 39.791 | 209.7083 | 18.5447 | 86.148 | -75 | -6.1553 | 249.6092 | -25.54 | 133.46 | 42.3045 | 0 | 42.3045 | 87.98 | 42.3045 | 7/28/18:00
7 | 28 | 1900-01-18 | 30 | 62 | 317 | 86 | 0 | 1 | 0 | 86 | 0 | 62 | 0 | 0 | 39.791 | 209.75 | 18.5344 | 86.148 | -75 | -6.1543 | 264.6094 | 42.7931 | 104.7931 | 33.2176 | 0 | 33.2176 | 86 | 33.2176 | 7/28/19:00
7 | 28 | 1900-01-19 | 27.8 | 26 | 148 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 26 | 0 | 0 | 39.791 | 209.7917 | 18.524 | 86.148 | -75 | -6.1532 | 279.6097 | 48.0927 | 74.0927 | 23.4861 | 0 | 23.4861 | 82.04 | 23.4861 | 7/28/20:00
7 | 28 | 1900-01-20 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 209.8333 | 18.5136 | 86.148 | -75 | -6.1522 | 294.61 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 7/28/21:00
7 | 28 | 1900-01-21 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 209.875 | 18.5032 | 86.148 | -75 | -6.1511 | 309.6102 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 7/28/22:00
7 | 28 | 1900-01-22 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 209.9167 | 18.4928 | 86.148 | -75 | -6.1499 | 324.6105 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/28/23:00
7 | 28 | 1900-01-23 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 209.9583 | 18.4823 | 86.148 | -75 | -6.1488 | 339.6108 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 7/28/24:00
7 | 29 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 210 | 18.4719 | 86.148 | -75 | -6.1477 | -5.3889 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/29/1:00
7 | 29 | 1900-01-01 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 210.0417 | 18.4615 | 86.148 | -75 | -6.1465 | 9.6114 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/29/2:00
7 | 29 | 1900-01-02 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 210.0833 | 18.451 | 86.148 | -75 | -6.1453 | 24.6117 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/29/3:00
7 | 29 | 1900-01-03 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 210.125 | 18.4406 | 86.148 | -75 | -6.1441 | 39.612 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 7/29/4:00
7 | 29 | 1900-01-04 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 210.1667 | 18.4301 | 86.148 | -75 | -6.1429 | 54.6123 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 7/29/5:00
7 | 29 | 1900-01-05 | 20 | 1 | 4 | 68 | 0 | 1 | 0 | 68 | 0 | 1 | 0 | 0 | 39.791 | 210.2083 | 18.4196 | 86.148 | -75 | -6.1416 | 69.6126 | 1.8247 | 2.8247 | 0.89539 | 0 | 0.89539 | 68 | 0.89539 | 7/29/6:00
7 | 29 | 1900-01-06 | 21.7 | 42 | 219 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 42 | 0 | 0 | 39.791 | 210.25 | 18.4092 | 86.148 | -75 | -6.1404 | 84.6129 | 59.2518 | 101.2518 | 32.0951 | 0 | 32.0951 | 71.06 | 32.0951 | 7/29/7:00
7 | 29 | 1900-01-07 | 23.9 | 78 | 507 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 78 | 0 | 0 | 39.791 | 210.2917 | 18.3987 | 86.148 | -75 | -6.1391 | 99.6132 | 40.6815 | 118.6815 | 37.62 | 0 | 37.62 | 75.02 | 37.62 | 7/29/8:00
7 | 29 | 1900-01-08 | 26.7 | 110 | 658 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 110 | 0 | 0 | 39.791 | 210.3333 | 18.3882 | 86.148 | -75 | -6.1378 | 114.6135 | -66.9857 | 43.0143 | 13.6348 | 0 | 13.6348 | 80.06 | 13.6348 | 7/29/9:00
7 | 29 | 1900-01-09 | 28.3 | 137 | 652 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 137 | 0 | 0 | 39.791 | 210.375 | 18.3777 | 86.148 | -75 | -6.1365 | 129.6139 | -171.5854 | -34.5854 | -10.963 | 0 | -10.963 | 82.94 | -10.963 | 7/29/10:00
7 | 29 | 1900-01-10 | 28.3 | 188 | 659 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 188 | 0 | 0 | 39.791 | 210.4167 | 18.3671 | 86.148 | -75 | -6.1352 | 144.6142 | -258.8981 | -70.8981 | -22.4735 | 0 | -22.4735 | 82.94 | -22.4735 | 7/29/11:00
7 | 29 | 1900-01-11 | 30 | 309 | 595 | 86 | 0 | 1 | 0 | 86 | 0 | 309 | 0 | 0 | 39.791 | 210.4583 | 18.3566 | 86.148 | -75 | -6.1338 | 159.6145 | -286.8245 | 22.1755 | 7.0292 | 0 | 7.0292 | 86 | 7.0292 | 7/29/12:00
7 | 29 | 1900-01-12 | 32.2 | 314 | 568 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 314 | 0 | 0 | 39.791 | 210.5 | 18.3461 | 86.148 | -75 | -6.1325 | 174.6149 | -298.0125 | 15.9875 | 5.0677 | 0 | 5.0677 | 89.96 | 5.0677 | 7/29/13:00
7 | 29 | 1900-01-13 | 31.7 | 242 | 616 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 242 | 0 | 0 | 39.791 | 210.5417 | 18.3355 | 86.148 | -75 | -6.1311 | 189.6152 | -318.9641 | -76.9641 | -24.3963 | 0 | -24.3963 | 89.06 | -24.3963 | 7/29/14:00
7 | 29 | 1900-01-14 | 32.2 | 186 | 750 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 186 | 0 | 0 | 39.791 | 210.5833 | 18.325 | 86.148 | -75 | -6.1297 | 204.6156 | -346.4357 | -160.4357 | -50.8553 | 0 | -50.8553 | 89.96 | -50.8553 | 7/29/15:00
7 | 29 | 1900-01-15 | 32.2 | 162 | 647 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 162 | 0 | 0 | 39.791 | 210.625 | 18.3144 | 86.148 | -75 | -6.1283 | 219.6159 | -233.455 | -71.455 | -22.65 | 0 | -22.65 | 89.96 | -22.65 | 7/29/16:00
7 | 29 | 1900-01-16 | 32.2 | 127 | 691 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 127 | 0 | 0 | 39.791 | 210.6667 | 18.3038 | 86.148 | -75 | -6.1268 | 234.6163 | -153.007 | -26.007 | -8.2438 | 0 | -8.2438 | 89.96 | -8.2438 | 7/29/17:00
7 | 29 | 1900-01-17 | 32.2 | 100 | 582 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 100 | 0 | 0 | 39.791 | 210.7083 | 18.2932 | 86.148 | -75 | -6.1254 | 249.6167 | -30.9755 | 69.0245 | 21.8796 | 0 | 21.8796 | 89.96 | 21.8796 | 7/29/18:00
7 | 29 | 1900-01-18 | 31.1 | 68 | 440 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 68 | 0 | 0 | 39.791 | 210.75 | 18.2826 | 86.148 | -75 | -6.1239 | 264.617 | 58.2219 | 126.2219 | 40.0101 | 0 | 40.0101 | 87.98 | 40.0101 | 7/29/19:00
7 | 29 | 1900-01-19 | 28.9 | 27 | 109 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 27 | 0 | 0 | 39.791 | 210.7917 | 18.272 | 86.148 | -75 | -6.1224 | 279.6174 | 35.1585 | 62.1585 | 19.7032 | 0 | 19.7032 | 84.02 | 19.7032 | 7/29/20:00
7 | 29 | 1900-01-20 | 28.3 | 0 | 0 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 0 | 0 | 0 | 39.791 | 210.8333 | 18.2614 | 86.148 | -75 | -6.1209 | 294.6178 | 0 | 0 | 0 | 0 | 0 | 82.94 | 0 | 7/29/21:00
7 | 29 | 1900-01-21 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 210.875 | 18.2508 | 86.148 | -75 | -6.1194 | 309.6182 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 7/29/22:00
7 | 29 | 1900-01-22 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 210.9167 | 18.2402 | 86.148 | -75 | -6.1178 | 324.6185 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 7/29/23:00
7 | 29 | 1900-01-23 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 210.9583 | 18.2295 | 86.148 | -75 | -6.1163 | 339.6189 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/29/24:00
7 | 30 | 1899-12-31 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 211 | 18.2189 | 86.148 | -75 | -6.1147 | -5.3807 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 7/30/1:00
7 | 30 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 211.0417 | 18.2082 | 86.148 | -75 | -6.1131 | 9.6197 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/30/2:00
7 | 30 | 1900-01-02 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 211.0833 | 18.1976 | 86.148 | -75 | -6.1115 | 24.6201 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/30/3:00
7 | 30 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 211.125 | 18.1869 | 86.148 | -75 | -6.1098 | 39.6205 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/30/4:00
7 | 30 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 211.1667 | 18.1762 | 86.148 | -75 | -6.1082 | 54.621 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/30/5:00
7 | 30 | 1900-01-05 | 21.7 | 1 | 4 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 1 | 0 | 0 | 39.791 | 211.2083 | 18.1655 | 86.148 | -75 | -6.1065 | 69.6214 | 1.815 | 2.815 | 0.89232 | 0 | 0.89232 | 71.06 | 0.89232 | 7/30/6:00
7 | 30 | 1900-01-06 | 23.9 | 41 | 220 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 41 | 0 | 0 | 39.791 | 211.25 | 18.1548 | 86.148 | -75 | -6.1048 | 84.6218 | 58.9262 | 99.9262 | 31.6749 | 0 | 31.6749 | 75.02 | 31.6749 | 7/30/7:00
7 | 30 | 1900-01-07 | 26.1 | 76 | 509 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 76 | 0 | 0 | 39.791 | 211.2917 | 18.1441 | 86.148 | -75 | -6.1031 | 99.6222 | 39.3192 | 115.3192 | 36.5542 | 0 | 36.5542 | 78.98 | 36.5542 | 7/30/8:00
7 | 30 | 1900-01-08 | 28.3 | 107 | 659 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 107 | 0 | 0 | 39.791 | 211.3333 | 18.1334 | 86.148 | -75 | -6.1014 | 114.6226 | -69.2317 | 37.7683 | 11.9719 | 0 | 11.9719 | 82.94 | 11.9719 | 7/30/9:00
7 | 30 | 1900-01-09 | 29.4 | 132 | 742 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 132 | 0 | 0 | 39.791 | 211.375 | 18.1227 | 86.148 | -75 | -6.0997 | 129.6231 | -197.8513 | -65.8513 | -20.8737 | 0 | -20.8737 | 84.92 | -20.8737 | 7/30/10:00
7 | 30 | 1900-01-10 | 30.6 | 154 | 783 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 154 | 0 | 0 | 39.791 | 211.4167 | 18.1119 | 86.148 | -75 | -6.0979 | 144.6235 | -310.4709 | -156.4709 | -49.5986 | 0 | -49.5986 | 87.08 | -49.5986 | 7/30/11:00
7 | 30 | 1900-01-11 | 31.1 | 168 | 755 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 168 | 0 | 0 | 39.791 | 211.4583 | 18.1012 | 86.148 | -75 | -6.0961 | 159.624 | -366.7896 | -198.7896 | -63.0128 | 0 | -63.0128 | 87.98 | -63.0128 | 7/30/12:00
7 | 30 | 1900-01-12 | 31.7 | 215 | 679 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 215 | 0 | 0 | 39.791 | 211.5 | 18.0904 | 86.148 | -75 | -6.0943 | 174.6244 | -358.8249 | -143.8249 | -45.59 | 0 | -45.59 | 89.06 | -45.59 | 7/30/13:00
7 | 30 | 1900-01-13 | 32.8 | 234 | 726 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 234 | 0 | 0 | 39.791 | 211.5417 | 18.0797 | 86.148 | -75 | -6.0925 | 189.6249 | -378.6454 | -144.6454 | -45.8501 | 0 | -45.8501 | 91.04 | -45.8501 | 7/30/14:00
7 | 30 | 1900-01-14 | 32.8 | 241 | 633 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 241 | 0 | 0 | 39.791 | 211.5833 | 18.0689 | 86.148 | -75 | -6.0907 | 204.6253 | -294.6962 | -53.6962 | -17.0207 | 0 | -17.0207 | 91.04 | -17.0207 | 7/30/15:00
7 | 30 | 1900-01-15 | 33.3 | 235 | 301 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 235 | 0 | 0 | 39.791 | 211.625 | 18.0581 | 86.148 | -75 | -6.0888 | 219.6258 | -109.6522 | 125.3478 | 39.7331 | 0 | 39.7331 | 91.94 | 39.7331 | 7/30/16:00
7 | 30 | 1900-01-16 | 32.8 | 154 | 639 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 154 | 0 | 0 | 39.791 | 211.6667 | 18.0473 | 86.148 | -75 | -6.087 | 234.6263 | -143.5631 | 10.4369 | 3.3083 | 0 | 3.3083 | 91.04 | 3.3083 | 7/30/17:00
7 | 30 | 1900-01-17 | 31.7 | 129 | 465 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 129 | 0 | 0 | 39.791 | 211.7083 | 18.0365 | 86.148 | -75 | -6.0851 | 249.6267 | -26.1333 | 102.8667 | 32.607 | 0 | 32.607 | 89.06 | 32.607 | 7/30/18:00
7 | 30 | 1900-01-18 | 31.1 | 104 | 231 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 104 | 0 | 0 | 39.791 | 211.75 | 18.0257 | 86.148 | -75 | -6.0832 | 264.6272 | 29.9431 | 133.9431 | 42.4576 | 0 | 42.4576 | 87.98 | 42.4576 | 7/30/19:00
7 | 30 | 1900-01-19 | 28.9 | 26 | 88 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 26 | 0 | 0 | 39.791 | 211.7917 | 18.0149 | 86.148 | -75 | -6.0813 | 279.6277 | 28.1718 | 54.1718 | 17.1715 | 0 | 17.1715 | 84.02 | 17.1715 | 7/30/20:00
7 | 30 | 1900-01-20 | 28.9 | 0 | 0 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 0 | 0 | 0 | 39.791 | 211.8333 | 18.0041 | 86.148 | -75 | -6.0793 | 294.6282 | 0 | 0 | 0 | 0 | 0 | 84.02 | 0 | 7/30/21:00
7 | 30 | 1900-01-21 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 211.875 | 17.9932 | 86.148 | -75 | -6.0774 | 309.6287 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 7/30/22:00
7 | 30 | 1900-01-22 | 27.2 | 0 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 0 | 0 | 0 | 39.791 | 211.9167 | 17.9824 | 86.148 | -75 | -6.0754 | 324.6292 | 0 | 0 | 0 | 0 | 0 | 80.96 | 0 | 7/30/23:00
7 | 30 | 1900-01-23 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 211.9583 | 17.9715 | 86.148 | -75 | -6.0734 | 339.6297 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 7/30/24:00
7 | 31 | 1899-12-31 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 212 | 17.9607 | 86.148 | -75 | -6.0714 | -5.3698 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/31/1:00
7 | 31 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 212.0417 | 17.9498 | 86.148 | -75 | -6.0693 | 9.6307 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 7/31/2:00
7 | 31 | 1900-01-02 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 212.0833 | 17.9389 | 86.148 | -75 | -6.0673 | 24.6312 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 7/31/3:00
7 | 31 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 212.125 | 17.928 | 86.148 | -75 | -6.0652 | 39.6317 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 7/31/4:00
7 | 31 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 212.1667 | 17.9171 | 86.148 | -75 | -6.0631 | 54.6322 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 7/31/5:00
7 | 31 | 1900-01-05 | 21.7 | 0 | 10 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 212.2083 | 17.9062 | 86.148 | -75 | -6.061 | 69.6327 | 4.5124 | 4.5124 | 1.4304 | 0 | 1.4304 | 71.06 | 1.4304 | 7/31/6:00
7 | 31 | 1900-01-06 | 24.4 | 35 | 290 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 35 | 0 | 0 | 39.791 | 212.25 | 17.8953 | 86.148 | -75 | -6.0589 | 84.6333 | 76.8631 | 111.8631 | 35.4586 | 0 | 35.4586 | 75.92 | 35.4586 | 7/31/7:00
7 | 31 | 1900-01-07 | 26.1 | 63 | 575 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 63 | 0 | 0 | 39.791 | 212.2917 | 17.8844 | 86.148 | -75 | -6.0568 | 99.6338 | 42.6438 | 105.6438 | 33.4872 | 0 | 33.4872 | 78.98 | 33.4872 | 7/31/8:00
7 | 31 | 1900-01-08 | 28.3 | 88 | 712 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 88 | 0 | 0 | 39.791 | 212.3333 | 17.8734 | 86.148 | -75 | -6.0546 | 114.6343 | -77.182 | 10.818 | 3.4291 | 0 | 3.4291 | 82.94 | 3.4291 | 7/31/9:00
7 | 31 | 1900-01-09 | 29.4 | 108 | 787 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 108 | 0 | 0 | 39.791 | 212.375 | 17.8625 | 86.148 | -75 | -6.0525 | 129.6349 | -212.6578 | -104.6578 | -33.1747 | 0 | -33.1747 | 84.92 | -33.1747 | 7/31/10:00
7 | 31 | 1900-01-10 | 31.1 | 122 | 779 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 122 | 0 | 0 | 39.791 | 212.4167 | 17.8516 | 86.148 | -75 | -6.0503 | 144.6354 | -311.7931 | -189.7931 | -60.1611 | 0 | -60.1611 | 87.98 | -60.1611 | 7/31/11:00
7 | 31 | 1900-01-11 | 32.2 | 312 | 600 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 312 | 0 | 0 | 39.791 | 212.4583 | 17.8406 | 86.148 | -75 | -6.0481 | 159.636 | -293.7882 | 18.2118 | 5.7728 | 0 | 5.7728 | 89.96 | 5.7728 | 7/31/12:00
7 | 31 | 1900-01-12 | 31.7 | 343 | 504 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 343 | 0 | 0 | 39.791 | 212.5 | 17.8296 | 86.148 | -75 | -6.0458 | 174.6365 | -268.2894 | 74.7106 | 23.682 | 0 | 23.682 | 89.06 | 23.682 | 7/31/13:00
7 | 31 | 1900-01-13 | 33.3 | 284 | 379 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 284 | 0 | 0 | 39.791 | 212.5417 | 17.8186 | 86.148 | -75 | -6.0436 | 189.6371 | -199.1119 | 84.8881 | 26.908 | 0 | 26.908 | 91.94 | 26.908 | 7/31/14:00
7 | 31 | 1900-01-14 | 33.3 | 253 | 746 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 253 | 0 | 0 | 39.791 | 212.5833 | 17.8077 | 86.148 | -75 | -6.0413 | 204.6377 | -350.0575 | -97.0575 | -30.7655 | 0 | -30.7655 | 91.94 | -30.7655 | 7/31/15:00
7 | 31 | 1900-01-15 | 33.3 | 207 | 624 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 207 | 0 | 0 | 39.791 | 212.625 | 17.7967 | 86.148 | -75 | -6.039 | 219.6382 | -229.508 | -22.508 | -7.1346 | 0 | -7.1346 | 91.94 | -7.1346 | 7/31/16:00
7 | 31 | 1900-01-16 | 32.2 | 102 | 769 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 102 | 0 | 0 | 39.791 | 212.6667 | 17.7857 | 86.148 | -75 | -6.0367 | 234.6388 | -175.2885 | -73.2885 | -23.2312 | 0 | -23.2312 | 89.96 | -23.2312 | 7/31/17:00
7 | 31 | 1900-01-17 | 32.2 | 81 | 680 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 81 | 0 | 0 | 39.791 | 212.7083 | 17.7746 | 86.148 | -75 | -6.0344 | 249.6394 | -40.2616 | 40.7384 | 12.9134 | 0 | 12.9134 | 89.96 | 12.9134 | 7/31/18:00
7 | 31 | 1900-01-18 | 30.6 | 55 | 512 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 55 | 0 | 0 | 39.791 | 212.75 | 17.7636 | 86.148 | -75 | -6.0321 | 264.64 | 64.9725 | 119.9725 | 38.0292 | 0 | 38.0292 | 87.08 | 38.0292 | 7/31/19:00
7 | 31 | 1900-01-19 | 28.3 | 23 | 166 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 23 | 0 | 0 | 39.791 | 212.7917 | 17.7526 | 86.148 | -75 | -6.0297 | 279.6406 | 52.7364 | 75.7364 | 24.0071 | 0 | 24.0071 | 82.94 | 24.0071 | 7/31/20:00
7 | 31 | 1900-01-20 | 27.8 | 0 | 0 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 0 | 0 | 0 | 39.791 | 212.8333 | 17.7416 | 86.148 | -75 | -6.0273 | 294.6412 | 0 | 0 | 0 | 0 | 0 | 82.04 | 0 | 7/31/21:00
7 | 31 | 1900-01-21 | 27 | 0 | 0 | 80.6 | 0 | 1 | 0 | 80.6 | 0 | 0 | 0 | 0 | 39.791 | 212.875 | 17.7305 | 86.148 | -75 | -6.025 | 309.6418 | 0 | 0 | 0 | 0 | 0 | 80.6 | 0 | 7/31/22:00
7 | 31 | 1900-01-22 | 26.2 | 0 | 0 | 79.16 | 0 | 1 | 0 | 79.16 | 0 | 0 | 0 | 0 | 39.791 | 212.9167 | 17.7195 | 86.148 | -75 | -6.0225 | 324.6424 | 0 | 0 | 0 | 0 | 0 | 79.16 | 0 | 7/31/23:00
7 | 31 | 1900-01-23 | 25.4 | 0 | 0 | 77.72 | 0 | 1 | 0 | 77.72 | 0 | 0 | 0 | 0 | 39.791 | 212.9583 | 17.7084 | 86.148 | -75 | -6.0201 | 339.643 | 0 | 0 | 0 | 0 | 0 | 77.72 | 0 | 7/31/24:00
8 | 1 | 1899-12-31 | 24.6 | 0 | 0 | 76.28 | 0 | 1 | 0 | 76.28 | 0 | 0 | 0 | 0 | 39.791 | 213 | 17.6973 | 86.148 | -75 | -6.0177 | -5.3564 | 0 | 0 | 0 | 0 | 0 | 76.28 | 0 | 8/1/1:00
8 | 1 | 1900-01-01 | 23.8 | 0 | 0 | 74.84 | 0 | 1 | 0 | 74.84 | 0 | 0 | 0 | 0 | 39.791 | 213.0417 | 17.6862 | 86.148 | -75 | -6.0152 | 9.6442 | 0 | 0 | 0 | 0 | 0 | 74.84 | 0 | 8/1/2:00
8 | 1 | 1900-01-02 | 23 | 0 | 0 | 73.4 | 0 | 1 | 0 | 73.4 | 0 | 0 | 0 | 0 | 39.791 | 213.0833 | 17.6751 | 86.148 | -75 | -6.0127 | 24.6448 | 0 | 0 | 0 | 0 | 0 | 73.4 | 0 | 8/1/3:00
8 | 1 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 213.125 | 17.664 | 86.148 | -75 | -6.0102 | 39.6454 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/1/4:00
8 | 1 | 1900-01-04 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 213.1667 | 17.6529 | 86.148 | -75 | -6.0077 | 54.6461 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/1/5:00
8 | 1 | 1900-01-05 | 21.1 | 3 | 10 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 3 | 0 | 0 | 39.791 | 213.2083 | 17.6418 | 86.148 | -75 | -6.0052 | 69.6467 | 4.4864 | 7.4864 | 2.3731 | 0 | 2.3731 | 69.98 | 2.3731 | 8/1/6:00
8 | 1 | 1900-01-06 | 22.2 | 46 | 172 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 46 | 0 | 0 | 39.791 | 213.25 | 17.6307 | 86.148 | -75 | -6.0026 | 84.6473 | 45.0902 | 91.0902 | 28.874 | 0 | 28.874 | 71.96 | 28.874 | 8/1/7:00
8 | 1 | 1900-01-07 | 23.9 | 93 | 39 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 93 | 0 | 0 | 39.791 | 213.2917 | 17.6196 | 86.148 | -75 | -6 | 99.648 | 2.7684 | 95.7684 | 30.3569 | 0 | 30.3569 | 75.02 | 30.3569 | 8/1/8:00
8 | 1 | 1900-01-08 | 25.6 | 200 | 368 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 200 | 0 | 0 | 39.791 | 213.3333 | 17.6084 | 86.148 | -75 | -5.9975 | 114.6486 | -41.1567 | 158.8433 | 50.3505 | 0 | 50.3505 | 78.08 | 50.3505 | 8/1/9:00
8 | 1 | 1900-01-09 | 27.2 | 314 | 88 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 314 | 0 | 0 | 39.791 | 213.375 | 17.5973 | 86.148 | -75 | -5.9948 | 129.6493 | -24.1004 | 289.8996 | 91.8931 | 0 | 91.8931 | 80.96 | 91.8931 | 8/1/10:00
8 | 1 | 1900-01-10 | 28.3 | 286 | 3 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 286 | 0 | 0 | 39.791 | 213.4167 | 17.5861 | 86.148 | -75 | -5.9922 | 144.6499 | -1.2122 | 284.7878 | 90.2728 | 0 | 90.2728 | 82.94 | 90.2728 | 8/1/11:00
8 | 1 | 1900-01-11 | 30 | 273 | 2 | 86 | 0 | 1 | 0 | 86 | 0 | 273 | 0 | 0 | 39.791 | 213.4583 | 17.5749 | 86.148 | -75 | -5.9896 | 159.6506 | -0.98711 | 272.0129 | 86.2233 | 0 | 86.2233 | 86 | 86.2233 | 8/1/12:00
8 | 1 | 1900-01-12 | 30.6 | 389 | 11 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 389 | 0 | 0 | 39.791 | 213.5 | 17.5637 | 86.148 | -75 | -5.9869 | 174.6513 | -5.8987 | 383.1013 | 121.4364 | 0 | 121.4364 | 87.08 | 121.4364 | 8/1/13:00
8 | 1 | 1900-01-13 | 27.8 | 355 | 12 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 355 | 0 | 0 | 39.791 | 213.5417 | 17.5526 | 86.148 | -75 | -5.9842 | 189.6519 | -6.3508 | 348.6492 | 110.5157 | 0 | 110.5157 | 82.04 | 110.5157 | 8/1/14:00
8 | 1 | 1900-01-14 | 28.9 | 395 | 1 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 395 | 0 | 0 | 39.791 | 213.5833 | 17.5414 | 86.148 | -75 | -5.9815 | 204.6526 | -0.47299 | 394.527 | 125.0582 | 0 | 125.0582 | 84.02 | 125.0582 | 8/1/15:00
8 | 1 | 1900-01-15 | 27.8 | 317 | 3 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 317 | 0 | 0 | 39.791 | 213.625 | 17.5302 | 86.148 | -75 | -5.9788 | 219.6533 | -1.1141 | 315.8859 | 100.1303 | 0 | 100.1303 | 82.04 | 100.1303 | 8/1/16:00
8 | 1 | 1900-01-16 | 26.7 | 220 | 1 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 220 | 0 | 0 | 39.791 | 213.6667 | 17.519 | 86.148 | -75 | -5.9761 | 234.654 | -0.23125 | 219.7687 | 69.6629 | 0 | 69.6629 | 80.06 | 69.6629 | 8/1/17:00
8 | 1 | 1900-01-17 | 26.1 | 121 | 2 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 121 | 0 | 0 | 39.791 | 213.7083 | 17.5077 | 86.148 | -75 | -5.9733 | 249.6547 | -0.12449 | 120.8755 | 38.3154 | 0 | 38.3154 | 78.98 | 38.3154 | 8/1/18:00
8 | 1 | 1900-01-18 | 26.1 | 106 | 49 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 106 | 0 | 0 | 39.791 | 213.75 | 17.4965 | 86.148 | -75 | -5.9705 | 264.6554 | 6.0834 | 112.0834 | 35.5285 | 0 | 35.5285 | 78.98 | 35.5285 | 8/1/19:00
8 | 1 | 1900-01-19 | 25 | 24 | 18 | 77 | 0 | 1 | 0 | 77 | 0 | 24 | 0 | 0 | 39.791 | 213.7917 | 17.4853 | 86.148 | -75 | -5.9678 | 279.6561 | 5.674 | 29.674 | 9.4061 | 0 | 9.4061 | 77 | 9.4061 | 8/1/20:00
8 | 1 | 1900-01-20 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 213.8333 | 17.474 | 86.148 | -75 | -5.9649 | 294.6568 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/1/21:00
8 | 1 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 213.875 | 17.4628 | 86.148 | -75 | -5.9621 | 309.6575 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/1/22:00
8 | 1 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 213.9167 | 17.4515 | 86.148 | -75 | -5.9593 | 324.6582 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/1/23:00
8 | 1 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 213.9583 | 17.4402 | 86.148 | -75 | -5.9564 | 339.6589 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/1/24:00
8 | 2 | 1899-12-31 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 214 | 17.4289 | 86.148 | -75 | -5.9535 | -5.3404 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/2/1:00
8 | 2 | 1900-01-01 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 214.0417 | 17.4176 | 86.148 | -75 | -5.9506 | 9.6603 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/2/2:00
8 | 2 | 1900-01-02 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 214.0833 | 17.4064 | 86.148 | -75 | -5.9477 | 24.6611 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/2/3:00
8 | 2 | 1900-01-03 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 214.125 | 17.395 | 86.148 | -75 | -5.9448 | 39.6618 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/2/4:00
8 | 2 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 214.1667 | 17.3837 | 86.148 | -75 | -5.9418 | 54.6625 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/2/5:00
8 | 2 | 1900-01-05 | 21.1 | 1 | 1 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 1 | 0 | 0 | 39.791 | 214.2083 | 17.3724 | 86.148 | -75 | -5.9389 | 69.6633 | 0.44595 | 1.4459 | 0.45834 | 0 | 0.45834 | 69.98 | 0.45834 | 8/2/6:00
8 | 2 | 1900-01-06 | 22.2 | 41 | 171 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 41 | 0 | 0 | 39.791 | 214.25 | 17.3611 | 86.148 | -75 | -5.9359 | 84.664 | 44.3179 | 85.3179 | 27.0443 | 0 | 27.0443 | 71.96 | 27.0443 | 8/2/7:00
8 | 2 | 1900-01-07 | 24.4 | 79 | 481 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 79 | 0 | 0 | 39.791 | 214.2917 | 17.3497 | 86.148 | -75 | -5.9329 | 99.6648 | 32.5719 | 111.5719 | 35.3663 | 0 | 35.3663 | 75.92 | 35.3663 | 8/2/8:00
8 | 2 | 1900-01-08 | 27.2 | 111 | 634 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 111 | 0 | 0 | 39.791 | 214.3333 | 17.3384 | 86.148 | -75 | -5.9298 | 114.6655 | -73.1421 | 37.8579 | 12.0003 | 0 | 12.0003 | 80.96 | 12.0003 | 8/2/9:00
8 | 2 | 1900-01-09 | 29.4 | 137 | 715 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 137 | 0 | 0 | 39.791 | 214.375 | 17.327 | 86.148 | -75 | -5.9268 | 129.6663 | -198.4905 | -61.4905 | -19.4914 | 0 | -19.4914 | 84.92 | -19.4914 | 8/2/10:00
8 | 2 | 1900-01-10 | 31.1 | 156 | 763 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 156 | 0 | 0 | 39.791 | 214.4167 | 17.3157 | 86.148 | -75 | -5.9237 | 144.6671 | -311.2727 | -155.2727 | -49.2187 | 0 | -49.2187 | 87.98 | -49.2187 | 8/2/11:00
8 | 2 | 1900-01-11 | 32.2 | 167 | 796 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 167 | 0 | 0 | 39.791 | 214.4583 | 17.3043 | 86.148 | -75 | -5.9206 | 159.6678 | -396.0383 | -229.0383 | -72.6011 | 0 | -72.6011 | 89.96 | -72.6011 | 8/2/12:00
8 | 2 | 1900-01-12 | 32.8 | 172 | 807 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 172 | 0 | 0 | 39.791 | 214.5 | 17.2929 | 86.148 | -75 | -5.9175 | 174.6686 | -435.9709 | -263.9709 | -83.6742 | 0 | -83.6742 | 91.04 | -83.6742 | 8/2/13:00
8 | 2 | 1900-01-13 | 33.3 | 171 | 808 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 171 | 0 | 0 | 39.791 | 214.5417 | 17.2815 | 86.148 | -75 | -5.9144 | 189.6694 | -430.7884 | -259.7884 | -82.3484 | 0 | -82.3484 | 91.94 | -82.3484 | 8/2/14:00
8 | 2 | 1900-01-14 | 33.9 | 165 | 792 | 93.02 | 0 | 1 | 0 | 93.02 | 0 | 165 | 0 | 0 | 39.791 | 214.5833 | 17.2701 | 86.148 | -75 | -5.9113 | 204.6702 | -377.6037 | -212.6037 | -67.3917 | 0 | -67.3917 | 93.02 | -67.3917 | 8/2/15:00
8 | 2 | 1900-01-15 | 33.3 | 171 | 562 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 171 | 0 | 0 | 39.791 | 214.625 | 17.2587 | 86.148 | -75 | -5.9081 | 219.671 | -210.7147 | -39.7147 | -12.5889 | 0 | -12.5889 | 91.94 | -12.5889 | 8/2/16:00
8 | 2 | 1900-01-16 | 33.3 | 159 | 618 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 159 | 0 | 0 | 39.791 | 214.6667 | 17.2473 | 86.148 | -75 | -5.905 | 234.6718 | -144.9777 | 14.0223 | 4.4448 | 0 | 4.4448 | 91.94 | 4.4448 | 8/2/17:00
8 | 2 | 1900-01-17 | 32.8 | 103 | 595 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 103 | 0 | 0 | 39.791 | 214.7083 | 17.2359 | 86.148 | -75 | -5.9018 | 249.6726 | -38.8569 | 64.1431 | 20.3322 | 0 | 20.3322 | 91.04 | 20.3322 | 8/2/18:00
8 | 2 | 1900-01-18 | 31.1 | 80 | 319 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 80 | 0 | 0 | 39.791 | 214.75 | 17.2244 | 86.148 | -75 | -5.8986 | 264.6734 | 38.7195 | 118.7195 | 37.632 | 0 | 37.632 | 87.98 | 37.632 | 8/2/19:00
8 | 2 | 1900-01-19 | 28.9 | 30 | 44 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 30 | 0 | 0 | 39.791 | 214.7917 | 17.213 | 86.148 | -75 | -5.8953 | 279.6742 | 13.76 | 43.76 | 13.8712 | 0 | 13.8712 | 84.02 | 13.8712 | 8/2/20:00
8 | 2 | 1900-01-20 | 27.2 | 0 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 0 | 0 | 0 | 39.791 | 214.8333 | 17.2015 | 86.148 | -75 | -5.8921 | 294.675 | 0 | 0 | 0 | 0 | 0 | 80.96 | 0 | 8/2/21:00
8 | 2 | 1900-01-21 | 27.2 | 0 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 0 | 0 | 0 | 39.791 | 214.875 | 17.1901 | 86.148 | -75 | -5.8888 | 309.6758 | 0 | 0 | 0 | 0 | 0 | 80.96 | 0 | 8/2/22:00
8 | 2 | 1900-01-22 | 27.2 | 0 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 0 | 0 | 0 | 39.791 | 214.9167 | 17.1786 | 86.148 | -75 | -5.8856 | 324.6766 | 0 | 0 | 0 | 0 | 0 | 80.96 | 0 | 8/2/23:00
8 | 2 | 1900-01-23 | 28.3 | 0 | 0 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 0 | 0 | 0 | 39.791 | 214.9583 | 17.1671 | 86.148 | -75 | -5.8823 | 339.6774 | 0 | 0 | 0 | 0 | 0 | 82.94 | 0 | 8/2/24:00
8 | 3 | 1899-12-31 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 215 | 17.1556 | 86.148 | -75 | -5.8789 | -5.3217 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 8/3/1:00
8 | 3 | 1900-01-01 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 215.0417 | 17.1441 | 86.148 | -75 | -5.8756 | 9.6791 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 8/3/2:00
8 | 3 | 1900-01-02 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 215.0833 | 17.1326 | 86.148 | -75 | -5.8722 | 24.6799 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 8/3/3:00
8 | 3 | 1900-01-03 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 215.125 | 17.1211 | 86.148 | -75 | -5.8689 | 39.6808 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/3/4:00
8 | 3 | 1900-01-04 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 215.1667 | 17.1096 | 86.148 | -75 | -5.8655 | 54.6816 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/3/5:00
8 | 3 | 1900-01-05 | 22.8 | 4 | 2 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 4 | 0 | 0 | 39.791 | 215.2083 | 17.0981 | 86.148 | -75 | -5.8621 | 69.6825 | 0.88634 | 4.8863 | 1.5489 | 0 | 1.5489 | 73.04 | 1.5489 | 8/3/6:00
8 | 3 | 1900-01-06 | 22.2 | 45 | 202 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 45 | 0 | 0 | 39.791 | 215.25 | 17.0866 | 86.148 | -75 | -5.8586 | 84.6833 | 51.7312 | 96.7312 | 30.6621 | 0 | 30.6621 | 71.96 | 30.6621 | 8/3/7:00
8 | 3 | 1900-01-07 | 23.9 | 104 | 406 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 104 | 0 | 0 | 39.791 | 215.2917 | 17.075 | 86.148 | -75 | -5.8552 | 99.6842 | 26.1291 | 130.1291 | 41.2487 | 0 | 41.2487 | 75.02 | 41.2487 | 8/3/8:00
8 | 3 | 1900-01-08 | 25 | 140 | 494 | 77 | 0 | 1 | 0 | 77 | 0 | 140 | 0 | 0 | 39.791 | 215.3333 | 17.0635 | 86.148 | -75 | -5.8517 | 114.6851 | -58.7772 | 81.2228 | 25.7462 | 0 | 25.7462 | 77 | 25.7462 | 8/3/9:00
8 | 3 | 1900-01-09 | 26.1 | 128 | 597 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 128 | 0 | 0 | 39.791 | 215.375 | 17.0519 | 86.148 | -75 | -5.8483 | 129.6859 | -168.0165 | -40.0165 | -12.6845 | 0 | -12.6845 | 78.98 | -12.6845 | 8/3/10:00
8 | 3 | 1900-01-10 | 28.9 | 113 | 780 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 113 | 0 | 0 | 39.791 | 215.4167 | 17.0403 | 86.148 | -75 | -5.8448 | 144.6868 | -321.3079 | -208.3079 | -66.03 | 0 | -66.03 | 84.02 | -66.03 | 8/3/11:00
8 | 3 | 1900-01-11 | 30.6 | 124 | 807 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 124 | 0 | 0 | 39.791 | 215.4583 | 17.0288 | 86.148 | -75 | -5.8412 | 159.6877 | -404.7809 | -280.7809 | -89.0026 | 0 | -89.0026 | 87.08 | -89.0026 | 8/3/12:00
8 | 3 | 1900-01-12 | 32.2 | 261 | 537 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 261 | 0 | 0 | 39.791 | 215.5 | 17.0172 | 86.148 | -75 | -5.8377 | 174.6886 | -292.2833 | -31.2833 | -9.9163 | 0 | -9.9163 | 89.96 | -9.9163 | 8/3/13:00
8 | 3 | 1900-01-13 | 33.3 | 244 | 663 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 244 | 0 | 0 | 39.791 | 215.5417 | 17.0056 | 86.148 | -75 | -5.8342 | 189.6895 | -356.1179 | -112.1179 | -35.5394 | 0 | -35.5394 | 91.94 | -35.5394 | 8/3/14:00
8 | 3 | 1900-01-14 | 33.3 | 303 | 666 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 303 | 0 | 0 | 39.791 | 215.5833 | 16.994 | 86.148 | -75 | -5.8306 | 204.6904 | -320.0817 | -17.0817 | -5.4146 | 0 | -5.4146 | 91.94 | -5.4146 | 8/3/15:00
8 | 3 | 1900-01-15 | 33.9 | 208 | 639 | 93.02 | 0 | 1 | 0 | 93.02 | 0 | 208 | 0 | 0 | 39.791 | 215.625 | 16.9824 | 86.148 | -75 | -5.827 | 219.6913 | -241.9002 | -33.9002 | -10.7458 | 0 | -10.7458 | 93.02 | -10.7458 | 8/3/16:00
8 | 3 | 1900-01-16 | 32.2 | 273 | 205 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 273 | 0 | 0 | 39.791 | 215.6667 | 16.9707 | 86.148 | -75 | -5.8234 | 234.6922 | -48.7821 | 224.2179 | 71.0732 | 0 | 71.0732 | 89.96 | 71.0732 | 8/3/17:00
8 | 3 | 1900-01-17 | 31.7 | 158 | 77 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 158 | 0 | 0 | 39.791 | 215.7083 | 16.9591 | 86.148 | -75 | -5.8198 | 249.6931 | -5.2662 | 152.7338 | 48.4139 | 0 | 48.4139 | 89.06 | 48.4139 | 8/3/18:00
8 | 3 | 1900-01-18 | 29.4 | 101 | 148 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 101 | 0 | 0 | 39.791 | 215.75 | 16.9475 | 86.148 | -75 | -5.8161 | 264.694 | 17.5503 | 118.5503 | 37.5784 | 0 | 37.5784 | 84.92 | 37.5784 | 8/3/19:00
8 | 3 | 1900-01-19 | 28.3 | 21 | 2 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 21 | 0 | 0 | 39.791 | 215.7917 | 16.9358 | 86.148 | -75 | -5.8125 | 279.6949 | 0.62043 | 21.6204 | 6.8533 | 0 | 6.8533 | 82.94 | 6.8533 | 8/3/20:00
8 | 3 | 1900-01-20 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 215.8333 | 16.9242 | 86.148 | -75 | -5.8088 | 294.6958 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 8/3/21:00
8 | 3 | 1900-01-21 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 215.875 | 16.9125 | 86.148 | -75 | -5.8051 | 309.6967 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 8/3/22:00
8 | 3 | 1900-01-22 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 215.9167 | 16.9009 | 86.148 | -75 | -5.8014 | 324.6977 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 8/3/23:00
8 | 3 | 1900-01-23 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 215.9583 | 16.8892 | 86.148 | -75 | -5.7976 | 339.6986 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/3/24:00
8 | 4 | 1899-12-31 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 216 | 16.8775 | 86.148 | -75 | -5.7939 | -5.3005 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/4/1:00
8 | 4 | 1900-01-01 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 216.0417 | 16.8658 | 86.148 | -75 | -5.7901 | 9.7005 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/4/2:00
8 | 4 | 1900-01-02 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 216.0833 | 16.8541 | 86.148 | -75 | -5.7863 | 24.7014 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/4/3:00
8 | 4 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 216.125 | 16.8424 | 86.148 | -75 | -5.7825 | 39.7024 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/4/4:00
8 | 4 | 1900-01-04 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 216.1667 | 16.8307 | 86.148 | -75 | -5.7787 | 54.7033 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/4/5:00
8 | 4 | 1900-01-05 | 23.3 | 2 | 5 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 2 | 0 | 0 | 39.791 | 216.2083 | 16.819 | 86.148 | -75 | -5.7748 | 69.7043 | 2.2015 | 4.2015 | 1.3318 | 0 | 1.3318 | 73.94 | 1.3318 | 8/4/6:00
8 | 4 | 1900-01-06 | 23.9 | 41 | 142 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 41 | 0 | 0 | 39.791 | 216.25 | 16.8072 | 86.148 | -75 | -5.771 | 84.7053 | 35.9163 | 76.9163 | 24.3811 | 0 | 24.3811 | 75.02 | 24.3811 | 8/4/7:00
8 | 4 | 1900-01-07 | 25.6 | 106 | 163 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 106 | 0 | 0 | 39.791 | 216.2917 | 16.7955 | 86.148 | -75 | -5.7671 | 99.7062 | 9.928 | 115.928 | 36.7472 | 0 | 36.7472 | 78.08 | 36.7472 | 8/4/8:00
8 | 4 | 1900-01-08 | 27.2 | 213 | 194 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 213 | 0 | 0 | 39.791 | 216.3333 | 16.7837 | 86.148 | -75 | -5.7632 | 114.7072 | -23.801 | 189.199 | 59.9728 | 0 | 59.9728 | 80.96 | 59.9728 | 8/4/9:00
8 | 4 | 1900-01-09 | 27.8 | 225 | 4 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 225 | 0 | 0 | 39.791 | 216.375 | 16.772 | 86.148 | -75 | -5.7593 | 129.7082 | -1.1414 | 223.8586 | 70.9593 | 0 | 70.9593 | 82.04 | 70.9593 | 8/4/10:00
8 | 4 | 1900-01-10 | 29.4 | 367 | 12 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 367 | 0 | 0 | 39.791 | 216.4167 | 16.7602 | 86.148 | -75 | -5.7553 | 144.7092 | -4.9918 | 362.0082 | 114.7503 | 0 | 114.7503 | 84.92 | 114.7503 | 8/4/11:00
8 | 4 | 1900-01-11 | 27.8 | 429 | 5 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 429 | 0 | 0 | 39.791 | 216.4583 | 16.7484 | 86.148 | -75 | -5.7514 | 159.7102 | -2.5285 | 426.4715 | 135.184 | 0 | 135.184 | 82.04 | 135.184 | 8/4/12:00
8 | 4 | 1900-01-12 | 27.2 | 380 | 2 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 380 | 0 | 0 | 39.791 | 216.5 | 16.7367 | 86.148 | -75 | -5.7474 | 174.7111 | -1.0968 | 378.9032 | 120.1057 | 0 | 120.1057 | 80.96 | 120.1057 | 8/4/13:00
8 | 4 | 1900-01-13 | 26.7 | 440 | 1 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 440 | 0 | 0 | 39.791 | 216.5417 | 16.7249 | 86.148 | -75 | -5.7434 | 189.7121 | -0.54116 | 439.4588 | 139.3008 | 0 | 139.3008 | 80.06 | 139.3008 | 8/4/14:00
8 | 4 | 1900-01-14 | 27.8 | 308 | 170 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 308 | 0 | 0 | 39.791 | 216.5833 | 16.7131 | 86.148 | -75 | -5.7394 | 204.7131 | -82.3609 | 225.6391 | 71.5236 | 0 | 71.5236 | 82.04 | 71.5236 | 8/4/15:00
8 | 4 | 1900-01-15 | 27.2 | 305 | 1 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 305 | 0 | 0 | 39.791 | 216.625 | 16.7013 | 86.148 | -75 | -5.7354 | 219.7142 | -0.38222 | 304.6178 | 96.5585 | 0 | 96.5585 | 80.96 | 96.5585 | 8/4/16:00
8 | 4 | 1900-01-16 | 27.2 | 209 | 12 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 209 | 0 | 0 | 39.791 | 216.6667 | 16.6894 | 86.148 | -75 | -5.7313 | 234.7152 | -2.8963 | 206.1037 | 65.3313 | 0 | 65.3313 | 80.96 | 65.3313 | 8/4/17:00
8 | 4 | 1900-01-17 | 26.7 | 160 | 2 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 160 | 0 | 0 | 39.791 | 216.7083 | 16.6776 | 86.148 | -75 | -5.7273 | 249.7162 | -0.14301 | 159.857 | 50.6719 | 0 | 50.6719 | 80.06 | 50.6719 | 8/4/18:00
8 | 4 | 1900-01-18 | 26.1 | 73 | 1 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 73 | 0 | 0 | 39.791 | 216.75 | 16.6658 | 86.148 | -75 | -5.7232 | 264.7172 | 0.11577 | 73.1158 | 23.1764 | 0 | 23.1764 | 78.98 | 23.1764 | 8/4/19:00
8 | 4 | 1900-01-19 | 25.6 | 30 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 30 | 0 | 0 | 39.791 | 216.7917 | 16.6539 | 86.148 | -75 | -5.7191 | 279.7182 | 0 | 30 | 9.5095 | 0 | 9.5095 | 78.08 | 9.5095 | 8/4/20:00
8 | 4 | 1900-01-20 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 216.8333 | 16.6421 | 86.148 | -75 | -5.715 | 294.7193 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 8/4/21:00
8 | 4 | 1900-01-21 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 216.875 | 16.6302 | 86.148 | -75 | -5.7108 | 309.7203 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/4/22:00
8 | 4 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 216.9167 | 16.6184 | 86.148 | -75 | -5.7067 | 324.7213 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/4/23:00
8 | 4 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 216.9583 | 16.6065 | 86.148 | -75 | -5.7025 | 339.7224 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/4/24:00
8 | 5 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 217 | 16.5946 | 86.148 | -75 | -5.6983 | -5.2766 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/5/1:00
8 | 5 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 217.0417 | 16.5827 | 86.148 | -75 | -5.6941 | 9.7245 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/5/2:00
8 | 5 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 217.0833 | 16.5708 | 86.148 | -75 | -5.6899 | 24.7255 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 8/5/3:00
8 | 5 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 217.125 | 16.5589 | 86.148 | -75 | -5.6856 | 39.7266 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 8/5/4:00
8 | 5 | 1900-01-04 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 217.1667 | 16.547 | 86.148 | -75 | -5.6814 | 54.7277 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/5/5:00
8 | 5 | 1900-01-05 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 217.2083 | 16.5351 | 86.148 | -75 | -5.6771 | 69.7287 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/5/6:00
8 | 5 | 1900-01-06 | 18.3 | 32 | 4 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 32 | 0 | 0 | 39.791 | 217.25 | 16.5232 | 86.148 | -75 | -5.6728 | 84.7298 | 0.99871 | 32.9987 | 10.46 | 0 | 10.46 | 64.94 | 10.46 | 8/5/7:00
8 | 5 | 1900-01-07 | 21.1 | 68 | 5 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 68 | 0 | 0 | 39.791 | 217.2917 | 16.5112 | 86.148 | -75 | -5.6685 | 99.7309 | 0.28685 | 68.2868 | 21.6457 | 0 | 21.6457 | 69.98 | 21.6457 | 8/5/8:00
8 | 5 | 1900-01-08 | 22.8 | 138 | 4 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 138 | 0 | 0 | 39.791 | 217.3333 | 16.4993 | 86.148 | -75 | -5.6642 | 114.732 | -0.5059 | 137.4941 | 43.5832 | 0 | 43.5832 | 73.04 | 43.5832 | 8/5/9:00
8 | 5 | 1900-01-09 | 23.3 | 240 | 5 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 240 | 0 | 0 | 39.791 | 217.375 | 16.4874 | 86.148 | -75 | -5.6598 | 129.7331 | -1.4467 | 238.5533 | 75.6172 | 0 | 75.6172 | 73.94 | 75.6172 | 8/5/10:00
8 | 5 | 1900-01-10 | 24.4 | 347 | 9 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 347 | 0 | 0 | 39.791 | 217.4167 | 16.4754 | 86.148 | -75 | -5.6554 | 144.7341 | -3.781 | 343.219 | 108.7944 | 0 | 108.7944 | 75.92 | 108.7944 | 8/5/11:00
8 | 5 | 1900-01-11 | 23.9 | 346 | 5 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 346 | 0 | 0 | 39.791 | 217.4583 | 16.4634 | 86.148 | -75 | -5.651 | 159.7352 | -2.5495 | 343.4505 | 108.8678 | 0 | 108.8678 | 75.02 | 108.8678 | 8/5/12:00
8 | 5 | 1900-01-12 | 25 | 428 | 6 | 77 | 0 | 1 | 0 | 77 | 0 | 428 | 0 | 0 | 39.791 | 217.5 | 16.4514 | 86.148 | -75 | -5.6466 | 174.7363 | -3.3154 | 424.6846 | 134.6176 | 0 | 134.6176 | 77 | 134.6176 | 8/5/13:00
8 | 5 | 1900-01-13 | 25.6 | 430 | 25 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 430 | 0 | 0 | 39.791 | 217.5417 | 16.4395 | 86.148 | -75 | -5.6422 | 189.7374 | -13.6309 | 416.3691 | 131.9817 | 0 | 131.9817 | 78.08 | 131.9817 | 8/5/14:00
8 | 5 | 1900-01-14 | 26.7 | 381 | 191 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 381 | 0 | 0 | 39.791 | 217.5833 | 16.4275 | 86.148 | -75 | -5.6378 | 204.7386 | -93.2823 | 287.7177 | 91.2015 | 0 | 91.2015 | 80.06 | 91.2015 | 8/5/15:00
8 | 5 | 1900-01-15 | 27.2 | 259 | 517 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 259 | 0 | 0 | 39.791 | 217.625 | 16.4155 | 86.148 | -75 | -5.6333 | 219.7397 | -199.5147 | 59.4853 | 18.8558 | 0 | 18.8558 | 80.96 | 18.8558 | 8/5/16:00
8 | 5 | 1900-01-16 | 27.8 | 186 | 495 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 186 | 0 | 0 | 39.791 | 217.6667 | 16.4035 | 86.148 | -75 | -5.6288 | 234.7408 | -121.1674 | 64.8326 | 20.5508 | 0 | 20.5508 | 82.04 | 20.5508 | 8/5/17:00
8 | 5 | 1900-01-17 | 27.2 | 185 | 127 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 185 | 0 | 0 | 39.791 | 217.7083 | 16.3915 | 86.148 | -75 | -5.6243 | 249.7419 | -9.4787 | 175.5213 | 55.6372 | 0 | 55.6372 | 80.96 | 55.6372 | 8/5/18:00
8 | 5 | 1900-01-18 | 26.1 | 100 | 224 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 100 | 0 | 0 | 39.791 | 217.75 | 16.3794 | 86.148 | -75 | -5.6198 | 264.743 | 25.2965 | 125.2965 | 39.7168 | 0 | 39.7168 | 78.98 | 39.7168 | 8/5/19:00
8 | 5 | 1900-01-19 | 24.4 | 22 | 25 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 22 | 0 | 0 | 39.791 | 217.7917 | 16.3674 | 86.148 | -75 | -5.6153 | 279.7442 | 7.6281 | 29.6281 | 9.3916 | 0 | 9.3916 | 75.92 | 9.3916 | 8/5/20:00
8 | 5 | 1900-01-20 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 217.8333 | 16.3554 | 86.148 | -75 | -5.6107 | 294.7453 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/5/21:00
8 | 5 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 217.875 | 16.3433 | 86.148 | -75 | -5.6061 | 309.7465 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/5/22:00
8 | 5 | 1900-01-22 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 217.9167 | 16.3313 | 86.148 | -75 | -5.6016 | 324.7476 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/5/23:00
8 | 5 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 217.9583 | 16.3192 | 86.148 | -75 | -5.597 | 339.7488 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/5/24:00
8 | 6 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 218 | 16.3071 | 86.148 | -75 | -5.5923 | -5.2501 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/6/1:00
8 | 6 | 1900-01-01 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 218.0417 | 16.295 | 86.148 | -75 | -5.5877 | 9.7511 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/6/2:00
8 | 6 | 1900-01-02 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 218.0833 | 16.283 | 86.148 | -75 | -5.583 | 24.7522 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/6/3:00
8 | 6 | 1900-01-03 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 218.125 | 16.2709 | 86.148 | -75 | -5.5783 | 39.7534 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/6/4:00
8 | 6 | 1900-01-04 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 218.1667 | 16.2588 | 86.148 | -75 | -5.5736 | 54.7546 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 8/6/5:00
8 | 6 | 1900-01-05 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 218.2083 | 16.2467 | 86.148 | -75 | -5.5689 | 69.7558 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/6/6:00
8 | 6 | 1900-01-06 | 19.4 | 23 | 3 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 23 | 0 | 0 | 39.791 | 218.25 | 16.2345 | 86.148 | -75 | -5.5642 | 84.757 | 0.73901 | 23.739 | 7.5249 | 0 | 7.5249 | 66.92 | 7.5249 | 8/6/7:00
8 | 6 | 1900-01-07 | 21.1 | 118 | 213 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 118 | 0 | 0 | 39.791 | 218.2917 | 16.2224 | 86.148 | -75 | -5.5594 | 99.7581 | 11.4474 | 129.4474 | 41.0326 | 0 | 41.0326 | 69.98 | 41.0326 | 8/6/8:00
8 | 6 | 1900-01-08 | 23.3 | 161 | 419 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 161 | 0 | 0 | 39.791 | 218.3333 | 16.2103 | 86.148 | -75 | -5.5547 | 114.7593 | -54.6166 | 106.3834 | 33.7217 | 0 | 33.7217 | 73.94 | 33.7217 | 8/6/9:00
8 | 6 | 1900-01-09 | 25 | 231 | 565 | 77 | 0 | 1 | 0 | 77 | 0 | 231 | 0 | 0 | 39.791 | 218.375 | 16.1981 | 86.148 | -75 | -5.5499 | 129.7605 | -165.7728 | 65.2272 | 20.6759 | 0 | 20.6759 | 77 | 20.6759 | 8/6/10:00
8 | 6 | 1900-01-10 | 26.7 | 237 | 646 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 237 | 0 | 0 | 39.791 | 218.4167 | 16.186 | 86.148 | -75 | -5.5451 | 144.7617 | -274.1029 | -37.1029 | -11.761 | 0 | -11.761 | 80.06 | -11.761 | 8/6/11:00
8 | 6 | 1900-01-11 | 26.7 | 273 | 627 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 273 | 0 | 0 | 39.791 | 218.4583 | 16.1738 | 86.148 | -75 | -5.5403 | 159.7629 | -322.3697 | -49.3697 | -15.6493 | 0 | -15.6493 | 80.06 | -15.6493 | 8/6/12:00
8 | 6 | 1900-01-12 | 28.3 | 341 | 574 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 341 | 0 | 0 | 39.791 | 218.5 | 16.1617 | 86.148 | -75 | -5.5354 | 174.7641 | -319.6022 | 21.3978 | 6.7827 | 0 | 6.7827 | 82.94 | 6.7827 | 8/6/13:00
8 | 6 | 1900-01-13 | 29.4 | 365 | 443 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 365 | 0 | 0 | 39.791 | 218.5417 | 16.1495 | 86.148 | -75 | -5.5306 | 189.7654 | -243.3663 | 121.6337 | 38.5558 | 0 | 38.5558 | 84.92 | 38.5558 | 8/6/14:00
8 | 6 | 1900-01-14 | 27.8 | 320 | 529 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 320 | 0 | 0 | 39.791 | 218.5833 | 16.1373 | 86.148 | -75 | -5.5257 | 204.7666 | -260.4479 | 59.5521 | 18.877 | 0 | 18.877 | 82.04 | 18.877 | 8/6/15:00
8 | 6 | 1900-01-15 | 29.4 | 336 | 379 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 336 | 0 | 0 | 39.791 | 218.625 | 16.1251 | 86.148 | -75 | -5.5208 | 219.7678 | -147.6694 | 188.3306 | 59.6975 | 0 | 59.6975 | 84.92 | 59.6975 | 8/6/16:00
8 | 6 | 1900-01-16 | 29.4 | 273 | 229 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 273 | 0 | 0 | 39.791 | 218.6667 | 16.1129 | 86.148 | -75 | -5.5159 | 234.769 | -56.8449 | 216.1551 | 68.5174 | 0 | 68.5174 | 84.92 | 68.5174 | 8/6/17:00
8 | 6 | 1900-01-17 | 27.8 | 174 | 255 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 174 | 0 | 0 | 39.791 | 218.7083 | 16.1007 | 86.148 | -75 | -5.5109 | 249.7703 | -19.8359 | 154.1641 | 48.8673 | 0 | 48.8673 | 82.04 | 48.8673 | 8/6/18:00
8 | 6 | 1900-01-18 | 27.2 | 82 | 217 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 82 | 0 | 0 | 39.791 | 218.75 | 16.0885 | 86.148 | -75 | -5.506 | 264.7715 | 23.8865 | 105.8865 | 33.5642 | 0 | 33.5642 | 80.96 | 33.5642 | 8/6/19:00
8 | 6 | 1900-01-19 | 25.6 | 23 | 14 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 23 | 0 | 0 | 39.791 | 218.7917 | 16.0763 | 86.148 | -75 | -5.501 | 279.7727 | 4.2357 | 27.2357 | 8.6332 | 0 | 8.6332 | 78.08 | 8.6332 | 8/6/20:00
8 | 6 | 1900-01-20 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 218.8333 | 16.0641 | 86.148 | -75 | -5.496 | 294.774 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/6/21:00
8 | 6 | 1900-01-21 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 218.875 | 16.0518 | 86.148 | -75 | -5.491 | 309.7752 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/6/22:00
8 | 6 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 218.9167 | 16.0396 | 86.148 | -75 | -5.486 | 324.7765 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/6/23:00
8 | 6 | 1900-01-23 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 218.9583 | 16.0273 | 86.148 | -75 | -5.481 | 339.7778 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/6/24:00
8 | 7 | 1899-12-31 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 219 | 16.0151 | 86.148 | -75 | -5.4759 | -5.221 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/7/1:00
8 | 7 | 1900-01-01 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 219.0417 | 16.0028 | 86.148 | -75 | -5.4708 | 9.7803 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/7/2:00
8 | 7 | 1900-01-02 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 219.0833 | 15.9905 | 86.148 | -75 | -5.4657 | 24.7816 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/7/3:00
8 | 7 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 219.125 | 15.9783 | 86.148 | -75 | -5.4606 | 39.7828 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 8/7/4:00
8 | 7 | 1900-01-04 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 219.1667 | 15.966 | 86.148 | -75 | -5.4555 | 54.7841 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/7/5:00
8 | 7 | 1900-01-05 | 18.3 | 1 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 1 | 0 | 0 | 39.791 | 219.2083 | 15.9537 | 86.148 | -75 | -5.4503 | 69.7854 | 0 | 1 | 0.31698 | 0 | 0.31698 | 64.94 | 0.31698 | 8/7/6:00
8 | 7 | 1900-01-06 | 18.9 | 39 | 128 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 39 | 0 | 0 | 39.791 | 219.25 | 15.9414 | 86.148 | -75 | -5.4452 | 84.7867 | 31.0923 | 70.0923 | 22.218 | 0 | 22.218 | 66.02 | 22.218 | 8/7/7:00
8 | 7 | 1900-01-07 | 22.2 | 82 | 437 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 82 | 0 | 0 | 39.791 | 219.2917 | 15.9291 | 86.148 | -75 | -5.44 | 99.788 | 21.8636 | 103.8636 | 32.9229 | 0 | 32.9229 | 71.96 | 32.9229 | 8/7/8:00
8 | 7 | 1900-01-08 | 25 | 119 | 600 | 77 | 0 | 1 | 0 | 77 | 0 | 119 | 0 | 0 | 39.791 | 219.3333 | 15.9167 | 86.148 | -75 | -5.4348 | 114.7893 | -80.5847 | 38.4153 | 12.177 | 0 | 12.177 | 77 | 12.177 | 8/7/9:00
8 | 7 | 1900-01-09 | 27.2 | 148 | 691 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 148 | 0 | 0 | 39.791 | 219.375 | 15.9044 | 86.148 | -75 | -5.4296 | 129.7906 | -205.6076 | -57.6076 | -18.2606 | 0 | -18.2606 | 80.96 | -18.2606 | 8/7/10:00
8 | 7 | 1900-01-10 | 28.9 | 249 | 670 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 249 | 0 | 0 | 39.791 | 219.4167 | 15.8921 | 86.148 | -75 | -5.4243 | 144.7919 | -287.1467 | -38.1467 | -12.0918 | 0 | -12.0918 | 84.02 | -12.0918 | 8/7/11:00
8 | 7 | 1900-01-11 | 29.4 | 298 | 599 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 298 | 0 | 0 | 39.791 | 219.4583 | 15.8797 | 86.148 | -75 | -5.4191 | 159.7932 | -310.5578 | -12.5578 | -3.9806 | 0 | -3.9806 | 84.92 | -3.9806 | 8/7/12:00
8 | 7 | 1900-01-12 | 28.9 | 307 | 628 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 307 | 0 | 0 | 39.791 | 219.5 | 15.8674 | 86.148 | -75 | -5.4138 | 174.7946 | -352.3568 | -45.3568 | -14.3773 | 0 | -14.3773 | 84.02 | -14.3773 | 8/7/13:00
8 | 7 | 1900-01-13 | 30.6 | 276 | 609 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 276 | 0 | 0 | 39.791 | 219.5417 | 15.855 | 86.148 | -75 | -5.4085 | 189.7959 | -337.0981 | -61.0981 | -19.367 | 0 | -19.367 | 87.08 | -19.367 | 8/7/14:00
8 | 7 | 1900-01-14 | 30.6 | 267 | 589 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 267 | 0 | 0 | 39.791 | 219.5833 | 15.8427 | 86.148 | -75 | -5.4032 | 204.7972 | -292.3364 | -25.3364 | -8.0312 | 0 | -8.0312 | 87.08 | -8.0312 | 8/7/15:00
8 | 7 | 1900-01-15 | 30 | 158 | 727 | 86 | 0 | 1 | 0 | 86 | 0 | 158 | 0 | 0 | 39.791 | 219.625 | 15.8303 | 86.148 | -75 | -5.3978 | 219.7985 | -285.9857 | -127.9857 | -40.5692 | 0 | -40.5692 | 86 | -40.5692 | 8/7/16:00
8 | 7 | 1900-01-16 | 30 | 148 | 640 | 86 | 0 | 1 | 0 | 86 | 0 | 148 | 0 | 0 | 39.791 | 219.6667 | 15.8179 | 86.148 | -75 | -5.3925 | 234.7999 | -161.0891 | -13.0891 | -4.149 | 0 | -4.149 | 86 | -4.149 | 8/7/17:00
8 | 7 | 1900-01-17 | 29.4 | 109 | 541 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 109 | 0 | 0 | 39.791 | 219.7083 | 15.8055 | 86.148 | -75 | -5.3871 | 249.8012 | -43.7993 | 65.2007 | 20.6675 | 0 | 20.6675 | 84.92 | 20.6675 | 8/7/18:00
8 | 7 | 1900-01-18 | 27.8 | 75 | 345 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 75 | 0 | 0 | 39.791 | 219.75 | 15.7931 | 86.148 | -75 | -5.3818 | 264.8026 | 36.9853 | 111.9853 | 35.4974 | 0 | 35.4974 | 82.04 | 35.4974 | 8/7/19:00
8 | 7 | 1900-01-19 | 25.6 | 31 | 27 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 31 | 0 | 0 | 39.791 | 219.7917 | 15.7807 | 86.148 | -75 | -5.3764 | 279.8039 | 8.0988 | 39.0988 | 12.3936 | 0 | 12.3936 | 78.08 | 12.3936 | 8/7/20:00
8 | 7 | 1900-01-20 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 219.8333 | 15.7683 | 86.148 | -75 | -5.3709 | 294.8053 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 8/7/21:00
8 | 7 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 219.875 | 15.7559 | 86.148 | -75 | -5.3655 | 309.8066 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/7/22:00
8 | 7 | 1900-01-22 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 219.9167 | 15.7435 | 86.148 | -75 | -5.36 | 324.808 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/7/23:00
8 | 7 | 1900-01-23 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 219.9583 | 15.731 | 86.148 | -75 | -5.3546 | 339.8094 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/7/24:00
8 | 8 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 220 | 15.7186 | 86.148 | -75 | -5.3491 | -5.1893 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/8/1:00
8 | 8 | 1900-01-01 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 220.0417 | 15.7061 | 86.148 | -75 | -5.3436 | 9.8121 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/8/2:00
8 | 8 | 1900-01-02 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 220.0833 | 15.6937 | 86.148 | -75 | -5.338 | 24.8135 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/8/3:00
8 | 8 | 1900-01-03 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 220.125 | 15.6812 | 86.148 | -75 | -5.3325 | 39.8149 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/8/4:00
8 | 8 | 1900-01-04 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 220.1667 | 15.6688 | 86.148 | -75 | -5.3269 | 54.8163 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/8/5:00
8 | 8 | 1900-01-05 | 20 | 1 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 1 | 0 | 0 | 39.791 | 220.2083 | 15.6563 | 86.148 | -75 | -5.3214 | 69.8177 | 0 | 1 | 0.31698 | 0 | 0.31698 | 68 | 0.31698 | 8/8/6:00
8 | 8 | 1900-01-06 | 20.6 | 53 | 6 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 53 | 0 | 0 | 39.791 | 220.25 | 15.6438 | 86.148 | -75 | -5.3158 | 84.8191 | 1.4364 | 54.4364 | 17.2554 | 0 | 17.2554 | 69.08 | 17.2554 | 8/8/7:00
8 | 8 | 1900-01-07 | 22.8 | 84 | 33 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 84 | 0 | 0 | 39.791 | 220.2917 | 15.6313 | 86.148 | -75 | -5.3101 | 99.8205 | 1.5257 | 85.5257 | 27.1101 | 0 | 27.1101 | 73.04 | 27.1101 | 8/8/8:00
8 | 8 | 1900-01-08 | 24.4 | 222 | 190 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 222 | 0 | 0 | 39.791 | 220.3333 | 15.6188 | 86.148 | -75 | -5.3045 | 114.8219 | -26.286 | 195.714 | 62.0379 | 0 | 62.0379 | 75.92 | 62.0379 | 8/8/9:00
8 | 8 | 1900-01-09 | 26.7 | 218 | 5 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 218 | 0 | 0 | 39.791 | 220.375 | 15.6063 | 86.148 | -75 | -5.2989 | 129.8233 | -1.5089 | 216.4911 | 68.6239 | 0 | 68.6239 | 80.06 | 68.6239 | 8/8/10:00
8 | 8 | 1900-01-10 | 27.8 | 263 | 3 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 263 | 0 | 0 | 39.791 | 220.4167 | 15.5938 | 86.148 | -75 | -5.2932 | 144.8247 | -1.2987 | 261.7013 | 82.9547 | 0 | 82.9547 | 82.04 | 82.9547 | 8/8/11:00
8 | 8 | 1900-01-11 | 29.4 | 317 | 2 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 317 | 0 | 0 | 39.791 | 220.4583 | 15.5812 | 86.148 | -75 | -5.2875 | 159.8261 | -1.0457 | 315.9543 | 100.152 | 0 | 100.152 | 84.92 | 100.152 | 8/8/12:00
8 | 8 | 1900-01-12 | 29.4 | 335 | 3 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 335 | 0 | 0 | 39.791 | 220.5 | 15.5687 | 86.148 | -75 | -5.2818 | 174.8276 | -1.6962 | 333.3038 | 105.6515 | 0 | 105.6515 | 84.92 | 105.6515 | 8/8/13:00
8 | 8 | 1900-01-13 | 28.9 | 496 | 4 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 496 | 0 | 0 | 39.791 | 220.5417 | 15.5562 | 86.148 | -75 | -5.2761 | 189.829 | -2.2309 | 493.7691 | 156.5162 | 0 | 156.5162 | 84.02 | 156.5162 | 8/8/14:00
8 | 8 | 1900-01-14 | 28.3 | 339 | 2 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 339 | 0 | 0 | 39.791 | 220.5833 | 15.5436 | 86.148 | -75 | -5.2703 | 204.8304 | -1.0007 | 337.9993 | 107.1399 | 0 | 107.1399 | 82.94 | 107.1399 | 8/8/15:00
8 | 8 | 1900-01-15 | 28.3 | 284 | 0 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 284 | 0 | 0 | 39.791 | 220.625 | 15.5311 | 86.148 | -75 | -5.2646 | 219.8319 | 0 | 284 | 90.023 | 0 | 90.023 | 82.94 | 90.023 | 8/8/16:00
8 | 8 | 1900-01-16 | 28.3 | 332 | 236 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 332 | 0 | 0 | 39.791 | 220.6667 | 15.5185 | 86.148 | -75 | -5.2588 | 234.8333 | -60.2257 | 271.7743 | 86.1477 | 0 | 86.1477 | 82.94 | 86.1477 | 8/8/17:00
8 | 8 | 1900-01-17 | 27.8 | 168 | 212 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 168 | 0 | 0 | 39.791 | 220.7083 | 15.506 | 86.148 | -75 | -5.253 | 249.8348 | -17.8397 | 150.1603 | 47.5982 | 0 | 47.5982 | 82.04 | 47.5982 | 8/8/18:00
8 | 8 | 1900-01-18 | 27.2 | 78 | 29 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 78 | 0 | 0 | 39.791 | 220.75 | 15.4934 | 86.148 | -75 | -5.2472 | 264.8362 | 3.0251 | 81.0251 | 25.6835 | 0 | 25.6835 | 80.96 | 25.6835 | 8/8/19:00
8 | 8 | 1900-01-19 | 26.7 | 17 | 2 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 17 | 0 | 0 | 39.791 | 220.7917 | 15.4808 | 86.148 | -75 | -5.2413 | 279.8377 | 0.59469 | 17.5947 | 5.5772 | 0 | 5.5772 | 80.06 | 5.5772 | 8/8/20:00
8 | 8 | 1900-01-20 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 220.8333 | 15.4682 | 86.148 | -75 | -5.2355 | 294.8391 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 8/8/21:00
8 | 8 | 1900-01-21 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 220.875 | 15.4556 | 86.148 | -75 | -5.2296 | 309.8406 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 8/8/22:00
8 | 8 | 1900-01-22 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 220.9167 | 15.443 | 86.148 | -75 | -5.2237 | 324.8421 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 8/8/23:00
8 | 8 | 1900-01-23 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 220.9583 | 15.4304 | 86.148 | -75 | -5.2178 | 339.8435 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/8/24:00
8 | 9 | 1899-12-31 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 221 | 15.4178 | 86.148 | -75 | -5.2119 | -5.155 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/9/1:00
8 | 9 | 1900-01-01 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 221.0417 | 15.4051 | 86.148 | -75 | -5.206 | 9.8465 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 8/9/2:00
8 | 9 | 1900-01-02 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 221.0833 | 15.3925 | 86.148 | -75 | -5.2 | 24.848 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/9/3:00
8 | 9 | 1900-01-03 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 221.125 | 15.3799 | 86.148 | -75 | -5.1941 | 39.8495 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/9/4:00
8 | 9 | 1900-01-04 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 221.1667 | 15.3672 | 86.148 | -75 | -5.1881 | 54.851 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/9/5:00
8 | 9 | 1900-01-05 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 221.2083 | 15.3546 | 86.148 | -75 | -5.1821 | 69.8525 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/9/6:00
8 | 9 | 1900-01-06 | 23.3 | 24 | 2 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 24 | 0 | 0 | 39.791 | 221.25 | 15.3419 | 86.148 | -75 | -5.176 | 84.854 | 0.47158 | 24.4716 | 7.7571 | 0 | 7.7571 | 73.94 | 7.7571 | 8/9/7:00
8 | 9 | 1900-01-07 | 23.3 | 111 | 52 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 111 | 0 | 0 | 39.791 | 221.2917 | 15.3292 | 86.148 | -75 | -5.17 | 99.8555 | 2.2022 | 113.2022 | 35.8831 | 0 | 35.8831 | 73.94 | 35.8831 | 8/9/8:00
8 | 9 | 1900-01-08 | 23.9 | 106 | 82 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 106 | 0 | 0 | 39.791 | 221.3333 | 15.3165 | 86.148 | -75 | -5.1639 | 114.857 | -11.6824 | 94.3176 | 29.897 | 0 | 29.897 | 75.02 | 29.897 | 8/9/9:00
8 | 9 | 1900-01-09 | 23.3 | 230 | 6 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 230 | 0 | 0 | 39.791 | 221.375 | 15.3039 | 86.148 | -75 | -5.1578 | 129.8585 | -1.8364 | 228.1636 | 72.3239 | 0 | 72.3239 | 73.94 | 72.3239 | 8/9/10:00
8 | 9 | 1900-01-10 | 25 | 300 | 11 | 77 | 0 | 1 | 0 | 77 | 0 | 300 | 0 | 0 | 39.791 | 221.4167 | 15.2912 | 86.148 | -75 | -5.1517 | 144.8601 | -4.8105 | 295.1895 | 93.5699 | 0 | 93.5699 | 77 | 93.5699 | 8/9/11:00
8 | 9 | 1900-01-11 | 26.1 | 392 | 11 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 392 | 0 | 0 | 39.791 | 221.4583 | 15.2785 | 86.148 | -75 | -5.1456 | 159.8616 | -5.7999 | 386.2001 | 122.4187 | 0 | 122.4187 | 78.98 | 122.4187 | 8/9/12:00
8 | 9 | 1900-01-12 | 26.7 | 419 | 1 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 419 | 0 | 0 | 39.791 | 221.5 | 15.2658 | 86.148 | -75 | -5.1395 | 174.8631 | -0.56979 | 418.4302 | 132.6351 | 0 | 132.6351 | 80.06 | 132.6351 | 8/9/13:00
8 | 9 | 1900-01-13 | 27.8 | 248 | 705 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 248 | 0 | 0 | 39.791 | 221.5417 | 15.253 | 86.148 | -75 | -5.1333 | 189.8647 | -396.2004 | -148.2004 | -46.9769 | 0 | -46.9769 | 82.04 | -46.9769 | 8/9/14:00
8 | 9 | 1900-01-14 | 28.9 | 292 | 530 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 292 | 0 | 0 | 39.791 | 221.5833 | 15.2403 | 86.148 | -75 | -5.1272 | 204.8662 | -267.3312 | 24.6688 | 7.8196 | 0 | 7.8196 | 84.02 | 7.8196 | 8/9/15:00
8 | 9 | 1900-01-15 | 29.4 | 234 | 520 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 234 | 0 | 0 | 39.791 | 221.625 | 15.2276 | 86.148 | -75 | -5.121 | 219.8678 | -208.4955 | 25.5045 | 8.0845 | 0 | 8.0845 | 84.92 | 8.0845 | 8/9/16:00
8 | 9 | 1900-01-16 | 28.3 | 256 | 391 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 256 | 0 | 0 | 39.791 | 221.6667 | 15.2149 | 86.148 | -75 | -5.1148 | 234.8693 | -101.1536 | 154.8464 | 49.0836 | 0 | 49.0836 | 82.94 | 49.0836 | 8/9/17:00
8 | 9 | 1900-01-17 | 27.8 | 161 | 420 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 161 | 0 | 0 | 39.791 | 221.7083 | 15.2021 | 86.148 | -75 | -5.1086 | 249.8709 | -36.6893 | 124.3107 | 39.4043 | 0 | 39.4043 | 82.04 | 39.4043 | 8/9/18:00
8 | 9 | 1900-01-18 | 25 | 83 | 263 | 77 | 0 | 1 | 0 | 77 | 0 | 83 | 0 | 0 | 39.791 | 221.75 | 15.1894 | 86.148 | -75 | -5.1023 | 264.8724 | 26.6706 | 109.6706 | 34.7637 | 0 | 34.7637 | 77 | 34.7637 | 8/9/19:00
8 | 9 | 1900-01-19 | 22.8 | 26 | 71 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 26 | 0 | 0 | 39.791 | 221.7917 | 15.1766 | 86.148 | -75 | -5.0961 | 279.874 | 20.9247 | 46.9247 | 14.8743 | 0 | 14.8743 | 73.04 | 14.8743 | 8/9/20:00
8 | 9 | 1900-01-20 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 221.8333 | 15.1638 | 86.148 | -75 | -5.0898 | 294.8756 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/9/21:00
8 | 9 | 1900-01-21 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 221.875 | 15.1511 | 86.148 | -75 | -5.0835 | 309.8771 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/9/22:00
8 | 9 | 1900-01-22 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 221.9167 | 15.1383 | 86.148 | -75 | -5.0772 | 324.8787 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/9/23:00
8 | 9 | 1900-01-23 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 221.9583 | 15.1255 | 86.148 | -75 | -5.0709 | 339.8803 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/9/24:00
8 | 10 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 222 | 15.1127 | 86.148 | -75 | -5.0645 | -5.1181 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/10/1:00
8 | 10 | 1900-01-01 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 222.0417 | 15.0999 | 86.148 | -75 | -5.0581 | 9.8835 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/10/2:00
8 | 10 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 222.0833 | 15.0871 | 86.148 | -75 | -5.0518 | 24.8851 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 8/10/3:00
8 | 10 | 1900-01-03 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 222.125 | 15.0743 | 86.148 | -75 | -5.0454 | 39.8867 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/10/4:00
8 | 10 | 1900-01-04 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 222.1667 | 15.0615 | 86.148 | -75 | -5.0389 | 54.8883 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/10/5:00
8 | 10 | 1900-01-05 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 222.2083 | 15.0486 | 86.148 | -75 | -5.0325 | 69.8899 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/10/6:00
8 | 10 | 1900-01-06 | 20 | 33 | 1 | 68 | 0 | 1 | 0 | 68 | 0 | 33 | 0 | 0 | 39.791 | 222.25 | 15.0358 | 86.148 | -75 | -5.0261 | 84.8915 | 0.2321 | 33.2321 | 10.534 | 0 | 10.534 | 68 | 10.534 | 8/10/7:00
8 | 10 | 1900-01-07 | 20.6 | 68 | 4 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 68 | 0 | 0 | 39.791 | 222.2917 | 15.0229 | 86.148 | -75 | -5.0196 | 99.8931 | 0.15354 | 68.1535 | 21.6035 | 0 | 21.6035 | 69.08 | 21.6035 | 8/10/8:00
8 | 10 | 1900-01-08 | 21.7 | 187 | 8 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 187 | 0 | 0 | 39.791 | 222.3333 | 15.0101 | 86.148 | -75 | -5.0131 | 114.8947 | -1.1733 | 185.8267 | 58.9038 | 0 | 58.9038 | 71.06 | 58.9038 | 8/10/9:00
8 | 10 | 1900-01-09 | 22.8 | 269 | 6 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 269 | 0 | 0 | 39.791 | 222.375 | 14.9972 | 86.148 | -75 | -5.0066 | 129.8964 | -1.8627 | 267.1373 | 84.6779 | 0 | 84.6779 | 73.04 | 84.6779 | 8/10/10:00
8 | 10 | 1900-01-10 | 23.3 | 316 | 1 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 316 | 0 | 0 | 39.791 | 222.4167 | 14.9844 | 86.148 | -75 | -5.0001 | 144.898 | -0.44179 | 315.5582 | 100.0264 | 0 | 100.0264 | 73.94 | 100.0264 | 8/10/11:00
8 | 10 | 1900-01-11 | 23.9 | 356 | 3 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 356 | 0 | 0 | 39.791 | 222.4583 | 14.9715 | 86.148 | -75 | -4.9935 | 159.8996 | -1.5953 | 354.4047 | 112.3401 | 0 | 112.3401 | 75.02 | 112.3401 | 8/10/12:00
8 | 10 | 1900-01-12 | 24.4 | 384 | 3 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 384 | 0 | 0 | 39.791 | 222.5 | 14.9586 | 86.148 | -75 | -4.987 | 174.9013 | -1.7226 | 382.2774 | 121.1752 | 0 | 121.1752 | 75.92 | 121.1752 | 8/10/13:00
8 | 10 | 1900-01-13 | 25 | 447 | 1 | 77 | 0 | 1 | 0 | 77 | 0 | 447 | 0 | 0 | 39.791 | 222.5417 | 14.9457 | 86.148 | -75 | -4.9804 | 189.9029 | -0.56627 | 446.4337 | 141.5117 | 0 | 141.5117 | 77 | 141.5117 | 8/10/14:00
8 | 10 | 1900-01-14 | 25.6 | 435 | 366 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 435 | 0 | 0 | 39.791 | 222.5833 | 14.9328 | 86.148 | -75 | -4.9738 | 204.9046 | -186.1035 | 248.8965 | 78.8958 | 0 | 78.8958 | 78.08 | 78.8958 | 8/10/15:00
8 | 10 | 1900-01-15 | 25 | 367 | 214 | 77 | 0 | 1 | 0 | 77 | 0 | 367 | 0 | 0 | 39.791 | 222.625 | 14.9199 | 86.148 | -75 | -4.9672 | 219.9062 | -86.6219 | 280.3781 | 88.875 | 0 | 88.875 | 77 | 88.875 | 8/10/16:00
8 | 10 | 1900-01-16 | 25 | 277 | 405 | 77 | 0 | 1 | 0 | 77 | 0 | 277 | 0 | 0 | 39.791 | 222.6667 | 14.907 | 86.148 | -75 | -4.9606 | 234.9079 | -106.2047 | 170.7953 | 54.1391 | 0 | 54.1391 | 77 | 54.1391 | 8/10/17:00
8 | 10 | 1900-01-17 | 23.9 | 190 | 154 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 190 | 0 | 0 | 39.791 | 222.7083 | 14.8941 | 86.148 | -75 | -4.9539 | 249.9095 | -13.9488 | 176.0512 | 55.8052 | 0 | 55.8052 | 75.02 | 55.8052 | 8/10/18:00
8 | 10 | 1900-01-18 | 23.9 | 92 | 68 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 92 | 0 | 0 | 39.791 | 222.75 | 14.8812 | 86.148 | -75 | -4.9472 | 264.9112 | 6.6973 | 98.6973 | 31.2853 | 0 | 31.2853 | 75.02 | 31.2853 | 8/10/19:00
8 | 10 | 1900-01-19 | 22.8 | 29 | 5 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 29 | 0 | 0 | 39.791 | 222.7917 | 14.8683 | 86.148 | -75 | -4.9406 | 279.9129 | 1.4603 | 30.4603 | 9.6554 | 0 | 9.6554 | 73.04 | 9.6554 | 8/10/20:00
8 | 10 | 1900-01-20 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 222.8333 | 14.8553 | 86.148 | -75 | -4.9339 | 294.9145 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/10/21:00
8 | 10 | 1900-01-21 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 222.875 | 14.8424 | 86.148 | -75 | -4.9272 | 309.9162 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/10/22:00
8 | 10 | 1900-01-22 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 222.9167 | 14.8294 | 86.148 | -75 | -4.9204 | 324.9179 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/10/23:00
8 | 10 | 1900-01-23 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 222.9583 | 14.8165 | 86.148 | -75 | -4.9137 | 339.9196 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/10/24:00
8 | 11 | 1899-12-31 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 223 | 14.8035 | 86.148 | -75 | -4.9069 | -5.0787 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/11/1:00
8 | 11 | 1900-01-01 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 223.0417 | 14.7905 | 86.148 | -75 | -4.9001 | 9.923 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/11/2:00
8 | 11 | 1900-01-02 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 223.0833 | 14.7775 | 86.148 | -75 | -4.8933 | 24.9247 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/11/3:00
8 | 11 | 1900-01-03 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 223.125 | 14.7646 | 86.148 | -75 | -4.8865 | 39.9264 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/11/4:00
8 | 11 | 1900-01-04 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 223.1667 | 14.7516 | 86.148 | -75 | -4.8796 | 54.9281 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/11/5:00
8 | 11 | 1900-01-05 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 223.2083 | 14.7386 | 86.148 | -75 | -4.8728 | 69.9298 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/11/6:00
8 | 11 | 1900-01-06 | 17.8 | 39 | 70 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 39 | 0 | 0 | 39.791 | 223.25 | 14.7256 | 86.148 | -75 | -4.8659 | 84.9315 | 15.9833 | 54.9833 | 17.4287 | 0 | 17.4287 | 64.04 | 17.4287 | 8/11/7:00
8 | 11 | 1900-01-07 | 19.4 | 117 | 266 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 117 | 0 | 0 | 39.791 | 223.2917 | 14.7125 | 86.148 | -75 | -4.859 | 99.9332 | 9.1337 | 126.1337 | 39.9822 | 0 | 39.9822 | 66.92 | 39.9822 | 8/11/8:00
8 | 11 | 1900-01-08 | 20.6 | 209 | 176 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 209 | 0 | 0 | 39.791 | 223.3333 | 14.6995 | 86.148 | -75 | -4.8521 | 114.935 | -26.5659 | 182.4341 | 57.8284 | 0 | 57.8284 | 69.08 | 57.8284 | 8/11/9:00
8 | 11 | 1900-01-09 | 22.2 | 257 | 557 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 257 | 0 | 0 | 39.791 | 223.375 | 14.6865 | 86.148 | -75 | -4.8452 | 129.9367 | -175.3908 | 81.6092 | 25.8687 | 0 | 25.8687 | 71.96 | 25.8687 | 8/11/10:00
8 | 11 | 1900-01-10 | 23.9 | 346 | 197 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 346 | 0 | 0 | 39.791 | 223.4167 | 14.6735 | 86.148 | -75 | -4.8382 | 144.9384 | -87.9252 | 258.0748 | 81.8052 | 0 | 81.8052 | 75.02 | 81.8052 | 8/11/11:00
8 | 11 | 1900-01-11 | 25.6 | 247 | 683 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 247 | 0 | 0 | 39.791 | 223.4583 | 14.6604 | 86.148 | -75 | -4.8313 | 159.9402 | -366.2906 | -119.2906 | -37.813 | 0 | -37.813 | 78.08 | -37.813 | 8/11/12:00
8 | 11 | 1900-01-12 | 26.1 | 310 | 619 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 310 | 0 | 0 | 39.791 | 223.5 | 14.6474 | 86.148 | -75 | -4.8243 | 174.9419 | -358.205 | -48.205 | -15.2801 | 0 | -15.2801 | 78.98 | -15.2801 | 8/11/13:00
8 | 11 | 1900-01-13 | 26.7 | 317 | 605 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 317 | 0 | 0 | 39.791 | 223.5417 | 14.6343 | 86.148 | -75 | -4.8173 | 189.9437 | -345.2102 | -28.2102 | -8.9421 | 0 | -8.9421 | 80.06 | -8.9421 | 8/11/14:00
8 | 11 | 1900-01-14 | 26.7 | 278 | 584 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 278 | 0 | 0 | 39.791 | 223.5833 | 14.6213 | 86.148 | -75 | -4.8103 | 204.9454 | -299.3513 | -21.3513 | -6.768 | 0 | -6.768 | 80.06 | -6.768 | 8/11/15:00
8 | 11 | 1900-01-15 | 26.7 | 258 | 454 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 258 | 0 | 0 | 39.791 | 223.625 | 14.6082 | 86.148 | -75 | -4.8033 | 219.9472 | -185.5128 | 72.4872 | 22.9772 | 0 | 22.9772 | 80.06 | 22.9772 | 8/11/16:00
8 | 11 | 1900-01-16 | 26.1 | 183 | 600 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 183 | 0 | 0 | 39.791 | 223.6667 | 14.5951 | 86.148 | -75 | -4.7962 | 234.9489 | -159.4673 | 23.5327 | 7.4595 | 0 | 7.4595 | 78.98 | 7.4595 | 8/11/17:00
8 | 11 | 1900-01-17 | 26.1 | 101 | 580 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 101 | 0 | 0 | 39.791 | 223.7083 | 14.582 | 86.148 | -75 | -4.7891 | 249.9507 | -54.4105 | 46.5895 | 14.7681 | 0 | 14.7681 | 78.98 | 14.7681 | 8/11/18:00
8 | 11 | 1900-01-18 | 25.6 | 65 | 369 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 65 | 0 | 0 | 39.791 | 223.75 | 14.5689 | 86.148 | -75 | -4.7821 | 264.9525 | 35.2601 | 100.2601 | 31.7807 | 0 | 31.7807 | 78.08 | 31.7807 | 8/11/19:00
8 | 11 | 1900-01-19 | 23.9 | 23 | 47 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 23 | 0 | 0 | 39.791 | 223.7917 | 14.5558 | 86.148 | -75 | -4.775 | 279.9543 | 13.6021 | 36.6021 | 11.6022 | 0 | 11.6022 | 75.02 | 11.6022 | 8/11/20:00
8 | 11 | 1900-01-20 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 223.8333 | 14.5427 | 86.148 | -75 | -4.7678 | 294.956 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/11/21:00
8 | 11 | 1900-01-21 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 223.875 | 14.5296 | 86.148 | -75 | -4.7607 | 309.9578 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/11/22:00
8 | 11 | 1900-01-22 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 223.9167 | 14.5165 | 86.148 | -75 | -4.7536 | 324.9596 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/11/23:00
8 | 11 | 1900-01-23 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 223.9583 | 14.5034 | 86.148 | -75 | -4.7464 | 339.9614 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/11/24:00
8 | 12 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 224 | 14.4903 | 86.148 | -75 | -4.7392 | -5.0368 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/12/1:00
8 | 12 | 1900-01-01 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 224.0417 | 14.4771 | 86.148 | -75 | -4.732 | 9.965 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/12/2:00
8 | 12 | 1900-01-02 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 224.0833 | 14.464 | 86.148 | -75 | -4.7248 | 24.9668 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/12/3:00
8 | 12 | 1900-01-03 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 224.125 | 14.4508 | 86.148 | -75 | -4.7175 | 39.9686 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/12/4:00
8 | 12 | 1900-01-04 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 224.1667 | 14.4377 | 86.148 | -75 | -4.7103 | 54.9704 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/12/5:00
8 | 12 | 1900-01-05 | 16.7 | 1 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 1 | 0 | 0 | 39.791 | 224.2083 | 14.4245 | 86.148 | -75 | -4.703 | 69.9722 | 0 | 1 | 0.31698 | 0 | 0.31698 | 62.06 | 0.31698 | 8/12/6:00
8 | 12 | 1900-01-06 | 17.8 | 32 | 76 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 32 | 0 | 0 | 39.791 | 224.25 | 14.4113 | 86.148 | -75 | -4.6957 | 84.9741 | 17.0604 | 49.0604 | 15.5513 | 0 | 15.5513 | 64.04 | 15.5513 | 8/12/7:00
8 | 12 | 1900-01-07 | 20 | 88 | 327 | 68 | 0 | 1 | 0 | 68 | 0 | 88 | 0 | 0 | 39.791 | 224.2917 | 14.3981 | 86.148 | -75 | -4.6884 | 99.9759 | 9.8785 | 97.8785 | 31.0258 | 0 | 31.0258 | 68 | 31.0258 | 8/12/8:00
8 | 12 | 1900-01-08 | 23.3 | 117 | 588 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 117 | 0 | 0 | 39.791 | 224.3333 | 14.385 | 86.148 | -75 | -4.6811 | 114.9777 | -91.3129 | 25.6871 | 8.1424 | 0 | 8.1424 | 73.94 | 8.1424 | 8/12/9:00
8 | 12 | 1900-01-09 | 26.1 | 147 | 691 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 147 | 0 | 0 | 39.791 | 224.375 | 14.3718 | 86.148 | -75 | -4.6737 | 129.9796 | -220.7016 | -73.7016 | -23.3621 | 0 | -23.3621 | 78.98 | -23.3621 | 8/12/10:00
8 | 12 | 1900-01-10 | 27.8 | 168 | 756 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 168 | 0 | 0 | 39.791 | 224.4167 | 14.3586 | 86.148 | -75 | -4.6664 | 144.9814 | -340.8901 | -172.8901 | -54.8031 | 0 | -54.8031 | 82.04 | -54.8031 | 8/12/11:00
8 | 12 | 1900-01-11 | 28.9 | 244 | 691 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 244 | 0 | 0 | 39.791 | 224.4583 | 14.3454 | 86.148 | -75 | -4.659 | 159.9833 | -373.7546 | -129.7546 | -41.1299 | 0 | -41.1299 | 84.02 | -41.1299 | 8/12/12:00
8 | 12 | 1900-01-12 | 30.6 | 327 | 554 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 327 | 0 | 0 | 39.791 | 224.5 | 14.3321 | 86.148 | -75 | -4.6516 | 174.9851 | -323.0902 | 3.9098 | 1.2394 | 0 | 1.2394 | 87.08 | 1.2394 | 8/12/13:00
8 | 12 | 1900-01-13 | 28.9 | 324 | 549 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 324 | 0 | 0 | 39.791 | 224.5417 | 14.3189 | 86.148 | -75 | -4.6442 | 189.987 | -315.6479 | 8.3521 | 2.6475 | 0 | 2.6475 | 84.02 | 2.6475 | 8/12/14:00
8 | 12 | 1900-01-14 | 28.9 | 343 | 336 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 343 | 0 | 0 | 39.791 | 224.5833 | 14.3057 | 86.148 | -75 | -4.6368 | 204.9888 | -173.6183 | 169.3817 | 53.691 | 0 | 53.691 | 84.02 | 53.691 | 8/12/15:00
8 | 12 | 1900-01-15 | 29.4 | 242 | 553 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 242 | 0 | 0 | 39.791 | 224.625 | 14.2925 | 86.148 | -75 | -4.6293 | 219.9907 | -228.1017 | 13.8983 | 4.4055 | 0 | 4.4055 | 84.92 | 4.4055 | 8/12/16:00
8 | 12 | 1900-01-16 | 30 | 264 | 366 | 86 | 0 | 1 | 0 | 86 | 0 | 264 | 0 | 0 | 39.791 | 224.6667 | 14.2792 | 86.148 | -75 | -4.6218 | 234.9925 | -98.5779 | 165.4221 | 52.4359 | 0 | 52.4359 | 86 | 52.4359 | 8/12/17:00
8 | 12 | 1900-01-17 | 28.9 | 141 | 335 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 141 | 0 | 0 | 39.791 | 224.7083 | 14.266 | 86.148 | -75 | -4.6144 | 249.9944 | -32.5146 | 108.4854 | 34.388 | 0 | 34.388 | 84.02 | 34.388 | 8/12/18:00
8 | 12 | 1900-01-18 | 27.2 | 99 | 223 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 99 | 0 | 0 | 39.791 | 224.75 | 14.2527 | 86.148 | -75 | -4.6069 | 264.9963 | 20.6518 | 119.6518 | 37.9275 | 0 | 37.9275 | 80.96 | 37.9275 | 8/12/19:00
8 | 12 | 1900-01-19 | 25.6 | 25 | 18 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 25 | 0 | 0 | 39.791 | 224.7917 | 14.2395 | 86.148 | -75 | -4.5994 | 279.9982 | 5.1611 | 30.1611 | 9.5605 | 0 | 9.5605 | 78.08 | 9.5605 | 8/12/20:00
8 | 12 | 1900-01-20 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 224.8333 | 14.2262 | 86.148 | -75 | -4.5918 | 295 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/12/21:00
8 | 12 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 224.875 | 14.2129 | 86.148 | -75 | -4.5843 | 310.0019 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/12/22:00
8 | 12 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 224.9167 | 14.1996 | 86.148 | -75 | -4.5767 | 325.0038 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/12/23:00
8 | 12 | 1900-01-23 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 224.9583 | 14.1864 | 86.148 | -75 | -4.5691 | 340.0057 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/12/24:00
8 | 13 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 225 | 14.1731 | 86.148 | -75 | -4.5615 | -4.9924 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/13/1:00
8 | 13 | 1900-01-01 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 225.0417 | 14.1598 | 86.148 | -75 | -4.5539 | 10.0095 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/13/2:00
8 | 13 | 1900-01-02 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 225.0833 | 14.1465 | 86.148 | -75 | -4.5463 | 25.0114 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/13/3:00
8 | 13 | 1900-01-03 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 225.125 | 14.1331 | 86.148 | -75 | -4.5386 | 40.0133 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/13/4:00
8 | 13 | 1900-01-04 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 225.1667 | 14.1198 | 86.148 | -75 | -4.5309 | 55.0153 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/13/5:00
8 | 13 | 1900-01-05 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 225.2083 | 14.1065 | 86.148 | -75 | -4.5233 | 70.0172 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/13/6:00
8 | 13 | 1900-01-06 | 20.6 | 24 | 7 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 24 | 0 | 0 | 39.791 | 225.25 | 14.0932 | 86.148 | -75 | -4.5156 | 85.0191 | 1.5438 | 25.5438 | 8.0969 | 0 | 8.0969 | 69.08 | 8.0969 | 8/13/7:00
8 | 13 | 1900-01-07 | 22.8 | 111 | 202 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 111 | 0 | 0 | 39.791 | 225.2917 | 14.0798 | 86.148 | -75 | -4.5078 | 100.021 | 5.2526 | 116.2526 | 36.85 | 0 | 36.85 | 73.04 | 36.85 | 8/13/8:00
8 | 13 | 1900-01-08 | 23.3 | 177 | 227 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 177 | 0 | 0 | 39.791 | 225.3333 | 14.0665 | 86.148 | -75 | -4.5001 | 115.023 | -36.2562 | 140.7438 | 44.6133 | 0 | 44.6133 | 73.94 | 44.6133 | 8/13/9:00
8 | 13 | 1900-01-09 | 26.1 | 218 | 11 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 218 | 0 | 0 | 39.791 | 225.375 | 14.0531 | 86.148 | -75 | -4.4923 | 130.0249 | -3.5637 | 214.4363 | 67.9726 | 0 | 67.9726 | 78.98 | 67.9726 | 8/13/10:00
8 | 13 | 1900-01-10 | 27.8 | 334 | 372 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 334 | 0 | 0 | 39.791 | 225.4167 | 14.0398 | 86.148 | -75 | -4.4846 | 145.0269 | -169.4694 | 164.5306 | 52.1533 | 0 | 52.1533 | 82.04 | 52.1533 | 8/13/11:00
8 | 13 | 1900-01-11 | 28.3 | 335 | 51 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 335 | 0 | 0 | 39.791 | 225.4583 | 14.0264 | 86.148 | -75 | -4.4768 | 160.0288 | -27.8221 | 307.1779 | 97.37 | 0 | 97.37 | 82.94 | 97.37 | 8/13/12:00
8 | 13 | 1900-01-12 | 28.9 | 387 | 7 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 387 | 0 | 0 | 39.791 | 225.5 | 14.013 | 86.148 | -75 | -4.469 | 175.0308 | -4.1142 | 382.8858 | 121.3681 | 0 | 121.3681 | 84.02 | 121.3681 | 8/13/13:00
8 | 13 | 1900-01-13 | 29.4 | 429 | 79 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 429 | 0 | 0 | 39.791 | 225.5417 | 13.9996 | 86.148 | -75 | -4.4612 | 190.0327 | -45.7676 | 383.2324 | 121.478 | 0 | 121.478 | 84.92 | 121.478 | 8/13/14:00
8 | 13 | 1900-01-14 | 29.4 | 406 | 119 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 406 | 0 | 0 | 39.791 | 225.5833 | 13.9863 | 86.148 | -75 | -4.4533 | 205.0347 | -61.9844 | 344.0156 | 109.0469 | 0 | 109.0469 | 84.92 | 109.0469 | 8/13/15:00
8 | 13 | 1900-01-15 | 30 | 333 | 186 | 86 | 0 | 1 | 0 | 86 | 0 | 333 | 0 | 0 | 39.791 | 225.625 | 13.9729 | 86.148 | -75 | -4.4455 | 220.0366 | -77.4428 | 255.5572 | 81.0072 | 0 | 81.0072 | 86 | 81.0072 | 8/13/16:00
8 | 13 | 1900-01-16 | 29.4 | 308 | 65 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 308 | 0 | 0 | 39.791 | 225.6667 | 13.9595 | 86.148 | -75 | -4.4376 | 235.0386 | -17.7392 | 290.2608 | 92.0076 | 0 | 92.0076 | 84.92 | 92.0076 | 8/13/17:00
8 | 13 | 1900-01-17 | 30 | 125 | 58 | 86 | 0 | 1 | 0 | 86 | 0 | 125 | 0 | 0 | 39.791 | 225.7083 | 13.9461 | 86.148 | -75 | -4.4297 | 250.0406 | -5.8184 | 119.1816 | 37.7785 | 0 | 37.7785 | 86 | 37.7785 | 8/13/18:00
8 | 13 | 1900-01-18 | 28.3 | 77 | 68 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 77 | 0 | 0 | 39.791 | 225.75 | 13.9327 | 86.148 | -75 | -4.4218 | 265.0426 | 6.0962 | 83.0962 | 26.3401 | 0 | 26.3401 | 82.94 | 26.3401 | 8/13/19:00
8 | 13 | 1900-01-19 | 26.7 | 22 | 28 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 22 | 0 | 0 | 39.791 | 225.7917 | 13.9192 | 86.148 | -75 | -4.4139 | 280.0445 | 7.9529 | 29.9529 | 9.4946 | 0 | 9.4946 | 80.06 | 9.4946 | 8/13/20:00
8 | 13 | 1900-01-20 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 225.8333 | 13.9058 | 86.148 | -75 | -4.4059 | 295.0465 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 8/13/21:00
8 | 13 | 1900-01-21 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 225.875 | 13.8924 | 86.148 | -75 | -4.398 | 310.0485 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 8/13/22:00
8 | 13 | 1900-01-22 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 225.9167 | 13.8789 | 86.148 | -75 | -4.39 | 325.0505 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 8/13/23:00
8 | 13 | 1900-01-23 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 225.9583 | 13.8655 | 86.148 | -75 | -4.382 | 340.0525 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 8/13/24:00
8 | 14 | 1899-12-31 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 226 | 13.852 | 86.148 | -75 | -4.374 | -4.9455 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 8/14/1:00
8 | 14 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 226.0417 | 13.8386 | 86.148 | -75 | -4.366 | 10.0565 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/14/2:00
8 | 14 | 1900-01-02 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 226.0833 | 13.8251 | 86.148 | -75 | -4.3579 | 25.0585 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/14/3:00
8 | 14 | 1900-01-03 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 226.125 | 13.8117 | 86.148 | -75 | -4.3498 | 40.0605 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/14/4:00
8 | 14 | 1900-01-04 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 226.1667 | 13.7982 | 86.148 | -75 | -4.3418 | 55.0626 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/14/5:00
8 | 14 | 1900-01-05 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 226.2083 | 13.7847 | 86.148 | -75 | -4.3337 | 70.0646 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/14/6:00
8 | 14 | 1900-01-06 | 22.8 | 44 | 38 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 44 | 0 | 0 | 39.791 | 226.25 | 13.7712 | 86.148 | -75 | -4.3256 | 85.0666 | 8.228 | 52.228 | 16.5554 | 0 | 16.5554 | 73.04 | 16.5554 | 8/14/7:00
8 | 14 | 1900-01-07 | 24.4 | 99 | 336 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 99 | 0 | 0 | 39.791 | 226.2917 | 13.7577 | 86.148 | -75 | -4.3174 | 100.0686 | 7.2976 | 106.2976 | 33.6945 | 0 | 33.6945 | 75.92 | 33.6945 | 8/14/8:00
8 | 14 | 1900-01-08 | 26.7 | 182 | 272 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 182 | 0 | 0 | 39.791 | 226.3333 | 13.7442 | 86.148 | -75 | -4.3093 | 115.0707 | -44.6666 | 137.3334 | 43.5323 | 0 | 43.5323 | 80.06 | 43.5323 | 8/14/9:00
8 | 14 | 1900-01-09 | 27.8 | 173 | 597 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 173 | 0 | 0 | 39.791 | 226.375 | 13.7307 | 86.148 | -75 | -4.3011 | 130.0727 | -196.181 | -23.181 | -7.348 | 0 | -7.348 | 82.04 | -7.348 | 8/14/10:00
8 | 14 | 1900-01-10 | 29.4 | 114 | 737 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 114 | 0 | 0 | 39.791 | 226.4167 | 13.7172 | 86.148 | -75 | -4.293 | 145.0748 | -339.2182 | -225.2182 | -71.3902 | 0 | -71.3902 | 84.92 | -71.3902 | 8/14/11:00
8 | 14 | 1900-01-11 | 30.6 | 144 | 840 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 144 | 0 | 0 | 39.791 | 226.4583 | 13.7037 | 86.148 | -75 | -4.2848 | 160.0768 | -462.1842 | -318.1842 | -100.8588 | 0 | -100.8588 | 87.08 | -100.8588 | 8/14/12:00
8 | 14 | 1900-01-12 | 31.1 | 163 | 788 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 163 | 0 | 0 | 39.791 | 226.5 | 13.6901 | 86.148 | -75 | -4.2766 | 175.0789 | -466.7604 | -303.7604 | -96.2868 | 0 | -96.2868 | 87.98 | -96.2868 | 8/14/13:00
8 | 14 | 1900-01-13 | 31.1 | 176 | 764 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 176 | 0 | 0 | 39.791 | 226.5417 | 13.6766 | 86.148 | -75 | -4.2683 | 190.0809 | -445.9858 | -269.9858 | -85.5808 | 0 | -85.5808 | 87.98 | -85.5808 | 8/14/14:00
8 | 14 | 1900-01-14 | 31.7 | 184 | 748 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 184 | 0 | 0 | 39.791 | 226.5833 | 13.663 | 86.148 | -75 | -4.2601 | 205.083 | -392.7413 | -208.7413 | -66.1674 | 0 | -66.1674 | 89.06 | -66.1674 | 8/14/15:00
8 | 14 | 1900-01-15 | 30.6 | 228 | 536 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 228 | 0 | 0 | 39.791 | 226.625 | 13.6495 | 86.148 | -75 | -4.2518 | 220.085 | -225.2559 | 2.7441 | 0.86983 | 0 | 0.86983 | 87.08 | 0.86983 | 8/14/16:00
8 | 14 | 1900-01-16 | 30 | 241 | 134 | 86 | 0 | 1 | 0 | 86 | 0 | 241 | 0 | 0 | 39.791 | 226.6667 | 13.6359 | 86.148 | -75 | -4.2435 | 235.0871 | -37.0504 | 203.9496 | 64.6485 | 0 | 64.6485 | 86 | 64.6485 | 8/14/17:00
8 | 14 | 1900-01-17 | 30 | 118 | 512 | 86 | 0 | 1 | 0 | 86 | 0 | 118 | 0 | 0 | 39.791 | 226.7083 | 13.6224 | 86.148 | -75 | -4.2352 | 250.0892 | -53.036 | 64.964 | 20.5925 | 0 | 20.5925 | 86 | 20.5925 | 8/14/18:00
8 | 14 | 1900-01-18 | 28.9 | 50 | 465 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 50 | 0 | 0 | 39.791 | 226.75 | 13.6088 | 86.148 | -75 | -4.2269 | 265.0913 | 40.3064 | 90.3064 | 28.6255 | 0 | 28.6255 | 84.02 | 28.6255 | 8/14/19:00
8 | 14 | 1900-01-19 | 26.7 | 19 | 99 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 19 | 0 | 0 | 39.791 | 226.7917 | 13.5952 | 86.148 | -75 | -4.2186 | 280.0933 | 27.8512 | 46.8512 | 14.851 | 0 | 14.851 | 80.06 | 14.851 | 8/14/20:00
8 | 14 | 1900-01-20 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 226.8333 | 13.5817 | 86.148 | -75 | -4.2103 | 295.0954 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 8/14/21:00
8 | 14 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 226.875 | 13.5681 | 86.148 | -75 | -4.2019 | 310.0975 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 8/14/22:00
8 | 14 | 1900-01-22 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 226.9167 | 13.5545 | 86.148 | -75 | -4.1935 | 325.0996 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/14/23:00
8 | 14 | 1900-01-23 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 226.9583 | 13.5409 | 86.148 | -75 | -4.1851 | 340.1017 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/14/24:00
8 | 15 | 1899-12-31 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 227 | 13.5273 | 86.148 | -75 | -4.1767 | -4.8962 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 8/15/1:00
8 | 15 | 1900-01-01 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 227.0417 | 13.5137 | 86.148 | -75 | -4.1683 | 10.1059 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/15/2:00
8 | 15 | 1900-01-02 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 227.0833 | 13.5001 | 86.148 | -75 | -4.1598 | 25.108 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/15/3:00
8 | 15 | 1900-01-03 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 227.125 | 13.4864 | 86.148 | -75 | -4.1514 | 40.1102 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/15/4:00
8 | 15 | 1900-01-04 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 227.1667 | 13.4728 | 86.148 | -75 | -4.1429 | 55.1123 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/15/5:00
8 | 15 | 1900-01-05 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 227.2083 | 13.4592 | 86.148 | -75 | -4.1344 | 70.1144 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/15/6:00
8 | 15 | 1900-01-06 | 21.7 | 32 | 23 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 32 | 0 | 0 | 39.791 | 227.25 | 13.4455 | 86.148 | -75 | -4.1259 | 85.1165 | 4.8859 | 36.8859 | 11.6922 | 0 | 11.6922 | 71.06 | 11.6922 | 8/15/7:00
8 | 15 | 1900-01-07 | 23.9 | 127 | 117 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 127 | 0 | 0 | 39.791 | 227.2917 | 13.4319 | 86.148 | -75 | -4.1174 | 100.1187 | 2.0311 | 129.0311 | 40.9006 | 0 | 40.9006 | 75.02 | 40.9006 | 8/15/8:00
8 | 15 | 1900-01-08 | 26.1 | 143 | 485 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 143 | 0 | 0 | 39.791 | 227.3333 | 13.4182 | 86.148 | -75 | -4.1088 | 115.1208 | -81.8593 | 61.1407 | 19.3805 | 0 | 19.3805 | 78.98 | 19.3805 | 8/15/9:00
8 | 15 | 1900-01-09 | 27.2 | 279 | 233 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 279 | 0 | 0 | 39.791 | 227.375 | 13.4046 | 86.148 | -75 | -4.1003 | 130.1229 | -77.6622 | 201.3378 | 63.8206 | 0 | 63.8206 | 80.96 | 63.8206 | 8/15/10:00
8 | 15 | 1900-01-10 | 29.4 | 212 | 648 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 212 | 0 | 0 | 39.791 | 227.4167 | 13.3909 | 86.148 | -75 | -4.0917 | 145.1251 | -301.3385 | -89.3385 | -28.3187 | 0 | -28.3187 | 84.92 | -28.3187 | 8/15/11:00
8 | 15 | 1900-01-11 | 30.6 | 229 | 699 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 229 | 0 | 0 | 39.791 | 227.4583 | 13.3772 | 86.148 | -75 | -4.0831 | 160.1272 | -387.9113 | -158.9113 | -50.3721 | 0 | -50.3721 | 87.08 | -50.3721 | 8/15/12:00
8 | 15 | 1900-01-12 | 31.7 | 267 | 643 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 267 | 0 | 0 | 39.791 | 227.5 | 13.3635 | 86.148 | -75 | -4.0745 | 175.1294 | -383.8449 | -116.8449 | -37.0378 | 0 | -37.0378 | 89.06 | -37.0378 | 8/15/13:00
8 | 15 | 1900-01-13 | 32.2 | 335 | 448 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 335 | 0 | 0 | 39.791 | 227.5417 | 13.3498 | 86.148 | -75 | -4.0658 | 190.1315 | -263.51 | 71.49 | 22.6611 | 0 | 22.6611 | 89.96 | 22.6611 | 8/15/14:00
8 | 15 | 1900-01-14 | 32.2 | 255 | 632 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 255 | 0 | 0 | 39.791 | 227.5833 | 13.3362 | 86.148 | -75 | -4.0572 | 205.1337 | -334.4871 | -79.4871 | -25.196 | 0 | -25.196 | 89.96 | -25.196 | 8/15/15:00
8 | 15 | 1900-01-15 | 32.2 | 207 | 608 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 207 | 0 | 0 | 39.791 | 227.625 | 13.3225 | 86.148 | -75 | -4.0485 | 220.1359 | -257.89 | -50.89 | -16.1313 | 0 | -16.1313 | 89.96 | -16.1313 | 8/15/16:00
8 | 15 | 1900-01-16 | 31.7 | 207 | 483 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 207 | 0 | 0 | 39.791 | 227.6667 | 13.3087 | 86.148 | -75 | -4.0399 | 235.138 | -135.2832 | 71.7168 | 22.733 | 0 | 22.733 | 89.06 | 22.733 | 8/15/17:00
8 | 15 | 1900-01-17 | 30.6 | 136 | 423 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 136 | 0 | 0 | 39.791 | 227.7083 | 13.295 | 86.148 | -75 | -4.0312 | 250.1402 | -45.2034 | 90.7966 | 28.7809 | 0 | 28.7809 | 87.08 | 28.7809 | 8/15/18:00
8 | 15 | 1900-01-18 | 29.4 | 79 | 209 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 79 | 0 | 0 | 39.791 | 227.75 | 13.2813 | 86.148 | -75 | -4.0225 | 265.1424 | 17.4933 | 96.4933 | 30.5867 | 0 | 30.5867 | 84.92 | 30.5867 | 8/15/19:00
8 | 15 | 1900-01-19 | 26.7 | 17 | 7 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 17 | 0 | 0 | 39.791 | 227.7917 | 13.2676 | 86.148 | -75 | -4.0137 | 280.1446 | 1.9502 | 18.9502 | 6.0069 | 0 | 6.0069 | 80.06 | 6.0069 | 8/15/20:00
8 | 15 | 1900-01-20 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 227.8333 | 13.2539 | 86.148 | -75 | -4.005 | 295.1468 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 8/15/21:00
8 | 15 | 1900-01-21 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 227.875 | 13.2401 | 86.148 | -75 | -3.9962 | 310.1489 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 8/15/22:00
8 | 15 | 1900-01-22 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 227.9167 | 13.2264 | 86.148 | -75 | -3.9875 | 325.1511 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 8/15/23:00
8 | 15 | 1900-01-23 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 227.9583 | 13.2126 | 86.148 | -75 | -3.9787 | 340.1533 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/15/24:00
8 | 16 | 1899-12-31 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 228 | 13.1989 | 86.148 | -75 | -3.9699 | -4.8445 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/16/1:00
8 | 16 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 228.0417 | 13.1851 | 86.148 | -75 | -3.961 | 10.1577 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/16/2:00
8 | 16 | 1900-01-02 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 228.0833 | 13.1714 | 86.148 | -75 | -3.9522 | 25.16 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/16/3:00
8 | 16 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 228.125 | 13.1576 | 86.148 | -75 | -3.9433 | 40.1622 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/16/4:00
8 | 16 | 1900-01-04 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 228.1667 | 13.1438 | 86.148 | -75 | -3.9345 | 55.1644 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/16/5:00
8 | 16 | 1900-01-05 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 228.2083 | 13.13 | 86.148 | -75 | -3.9256 | 70.1666 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/16/6:00
8 | 16 | 1900-01-06 | 23.9 | 38 | 18 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 38 | 0 | 0 | 39.791 | 228.25 | 13.1162 | 86.148 | -75 | -3.9167 | 85.1688 | 3.7486 | 41.7486 | 13.2336 | 0 | 13.2336 | 75.02 | 13.2336 | 8/16/7:00
8 | 16 | 1900-01-07 | 26.1 | 118 | 154 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 118 | 0 | 0 | 39.791 | 228.2917 | 13.1024 | 86.148 | -75 | -3.9077 | 100.1711 | 1.9906 | 119.9906 | 38.0349 | 0 | 38.0349 | 78.98 | 38.0349 | 8/16/8:00
8 | 16 | 1900-01-08 | 26.7 | 157 | 286 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 157 | 0 | 0 | 39.791 | 228.3333 | 13.0886 | 86.148 | -75 | -3.8988 | 115.1733 | -49.5971 | 107.4029 | 34.0448 | 0 | 34.0448 | 80.06 | 34.0448 | 8/16/9:00
8 | 16 | 1900-01-09 | 28.3 | 170 | 616 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 170 | 0 | 0 | 39.791 | 228.375 | 13.0748 | 86.148 | -75 | -3.8898 | 130.1755 | -208.2557 | -38.2557 | -12.1264 | 0 | -12.1264 | 82.94 | -12.1264 | 8/16/10:00
8 | 16 | 1900-01-10 | 29.4 | 144 | 671 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 144 | 0 | 0 | 39.791 | 228.4167 | 13.061 | 86.148 | -75 | -3.8809 | 145.1778 | -315.2622 | -171.2622 | -54.2871 | 0 | -54.2871 | 84.92 | -54.2871 | 8/16/11:00
8 | 16 | 1900-01-11 | 30.6 | 137 | 842 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 137 | 0 | 0 | 39.791 | 228.4583 | 13.0472 | 86.148 | -75 | -3.8719 | 160.18 | -471.2895 | -334.2895 | -105.9639 | 0 | -105.9639 | 87.08 | -105.9639 | 8/16/12:00
8 | 16 | 1900-01-12 | 31.7 | 141 | 845 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 141 | 0 | 0 | 39.791 | 228.5 | 13.0334 | 86.148 | -75 | -3.8629 | 175.1823 | -508.3653 | -367.3653 | -116.4484 | 0 | -116.4484 | 89.06 | -116.4484 | 8/16/13:00
8 | 16 | 1900-01-13 | 32.8 | 136 | 783 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 136 | 0 | 0 | 39.791 | 228.5417 | 13.0195 | 86.148 | -75 | -3.8539 | 190.1845 | -464.0504 | -328.0504 | -103.9863 | 0 | -103.9863 | 91.04 | -103.9863 | 8/16/14:00
8 | 16 | 1900-01-14 | 33.3 | 203 | 701 | 91.94 | 0 | 1 | 0 | 91.94 | 0 | 203 | 0 | 0 | 39.791 | 228.5833 | 13.0057 | 86.148 | -75 | -3.8448 | 205.1868 | -373.9592 | -170.9592 | -54.1911 | 0 | -54.1911 | 91.94 | -54.1911 | 8/16/15:00
8 | 16 | 1900-01-15 | 32.8 | 157 | 697 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 157 | 0 | 0 | 39.791 | 228.625 | 12.9918 | 86.148 | -75 | -3.8358 | 220.1891 | -298.3722 | -141.3722 | -44.8125 | 0 | -44.8125 | 91.04 | -44.8125 | 8/16/16:00
8 | 16 | 1900-01-16 | 32.2 | 101 | 696 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 101 | 0 | 0 | 39.791 | 228.6667 | 12.978 | 86.148 | -75 | -3.8267 | 235.1913 | -197.4498 | -96.4498 | -30.5729 | 0 | -30.5729 | 89.96 | -30.5729 | 8/16/17:00
8 | 16 | 1900-01-17 | 31.7 | 83 | 625 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 83 | 0 | 0 | 39.791 | 228.7083 | 12.9641 | 86.148 | -75 | -3.8176 | 250.1936 | -68.8435 | 14.1565 | 4.4874 | 0 | 4.4874 | 89.06 | 4.4874 | 8/16/18:00
8 | 16 | 1900-01-18 | 30 | 52 | 418 | 86 | 0 | 1 | 0 | 86 | 0 | 52 | 0 | 0 | 39.791 | 228.75 | 12.9503 | 86.148 | -75 | -3.8085 | 265.1959 | 33.7366 | 85.7366 | 27.177 | 0 | 27.177 | 86 | 27.177 | 8/16/19:00
8 | 16 | 1900-01-19 | 27.8 | 18 | 59 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 18 | 0 | 0 | 39.791 | 228.7917 | 12.9364 | 86.148 | -75 | -3.7994 | 280.1981 | 16.2761 | 34.2761 | 10.8649 | 0 | 10.8649 | 82.04 | 10.8649 | 8/16/20:00
8 | 16 | 1900-01-20 | 27.2 | 0 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 0 | 0 | 0 | 39.791 | 228.8333 | 12.9225 | 86.148 | -75 | -3.7903 | 295.2004 | 0 | 0 | 0 | 0 | 0 | 80.96 | 0 | 8/16/21:00
8 | 16 | 1900-01-21 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 228.875 | 12.9086 | 86.148 | -75 | -3.7811 | 310.2027 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 8/16/22:00
8 | 16 | 1900-01-22 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 228.9167 | 12.8947 | 86.148 | -75 | -3.772 | 325.205 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 8/16/23:00
8 | 16 | 1900-01-23 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 228.9583 | 12.8808 | 86.148 | -75 | -3.7628 | 340.2073 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 8/16/24:00
8 | 17 | 1899-12-31 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 229 | 12.8669 | 86.148 | -75 | -3.7536 | -4.7904 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/17/1:00
8 | 17 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 229.0417 | 12.853 | 86.148 | -75 | -3.7444 | 10.2119 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/17/2:00
8 | 17 | 1900-01-02 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 229.0833 | 12.8391 | 86.148 | -75 | -3.7351 | 25.2142 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/17/3:00
8 | 17 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 229.125 | 12.8252 | 86.148 | -75 | -3.7259 | 40.2165 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/17/4:00
8 | 17 | 1900-01-04 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 229.1667 | 12.8113 | 86.148 | -75 | -3.7166 | 55.2188 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/17/5:00
8 | 17 | 1900-01-05 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 229.2083 | 12.7974 | 86.148 | -75 | -3.7074 | 70.2212 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 8/17/6:00
8 | 17 | 1900-01-06 | 22.2 | 27 | 1 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 27 | 0 | 0 | 39.791 | 229.25 | 12.7834 | 86.148 | -75 | -3.6981 | 85.2235 | 0.20401 | 27.204 | 8.6232 | 0 | 8.6232 | 71.96 | 8.6232 | 8/17/7:00
8 | 17 | 1900-01-07 | 23.9 | 88 | 17 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 88 | 0 | 0 | 39.791 | 229.2917 | 12.7695 | 86.148 | -75 | -3.6888 | 100.2258 | 0.14314 | 88.1431 | 27.9398 | 0 | 27.9398 | 75.02 | 27.9398 | 8/17/8:00
8 | 17 | 1900-01-08 | 25 | 211 | 7 | 77 | 0 | 1 | 0 | 77 | 0 | 211 | 0 | 0 | 39.791 | 229.3333 | 12.7555 | 86.148 | -75 | -3.6794 | 115.2281 | -1.2468 | 209.7532 | 66.4881 | 0 | 66.4881 | 77 | 66.4881 | 8/17/9:00
8 | 17 | 1900-01-09 | 25 | 213 | 9 | 77 | 0 | 1 | 0 | 77 | 0 | 213 | 0 | 0 | 39.791 | 229.375 | 12.7416 | 86.148 | -75 | -3.6701 | 130.2305 | -3.0861 | 209.9139 | 66.539 | 0 | 66.539 | 77 | 66.539 | 8/17/10:00
8 | 17 | 1900-01-10 | 27.2 | 347 | 386 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 347 | 0 | 0 | 39.791 | 229.4167 | 12.7276 | 86.148 | -75 | -3.6607 | 145.2328 | -183.2339 | 163.7661 | 51.911 | 0 | 51.911 | 80.96 | 51.911 | 8/17/11:00
8 | 17 | 1900-01-11 | 29.4 | 267 | 660 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 267 | 0 | 0 | 39.791 | 229.4583 | 12.7137 | 86.148 | -75 | -3.6514 | 160.2352 | -372.5965 | -105.5965 | -33.4722 | 0 | -33.4722 | 84.92 | -33.4722 | 8/17/12:00
8 | 17 | 1900-01-12 | 30 | 221 | 714 | 86 | 0 | 1 | 0 | 86 | 0 | 221 | 0 | 0 | 39.791 | 229.5 | 12.6997 | 86.148 | -75 | -3.642 | 175.2375 | -432.8999 | -211.8999 | -67.1686 | 0 | -67.1686 | 86 | -67.1686 | 8/17/13:00
8 | 17 | 1900-01-13 | 31.1 | 226 | 712 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 226 | 0 | 0 | 39.791 | 229.5417 | 12.6857 | 86.148 | -75 | -3.6326 | 190.2399 | -425.1665 | -199.1665 | -63.1323 | 0 | -63.1323 | 87.98 | -63.1323 | 8/17/14:00
8 | 17 | 1900-01-14 | 30.6 | 281 | 557 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 281 | 0 | 0 | 39.791 | 229.5833 | 12.6717 | 86.148 | -75 | -3.6231 | 205.2422 | -299.4955 | -18.4955 | -5.8627 | 0 | -5.8627 | 87.08 | -5.8627 | 8/17/15:00
8 | 17 | 1900-01-15 | 30.6 | 154 | 732 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 154 | 0 | 0 | 39.791 | 229.625 | 12.6577 | 86.148 | -75 | -3.6137 | 220.2446 | -316.2313 | -162.2313 | -51.4245 | 0 | -51.4245 | 87.08 | -51.4245 | 8/17/16:00
8 | 17 | 1900-01-16 | 30 | 129 | 688 | 86 | 0 | 1 | 0 | 86 | 0 | 129 | 0 | 0 | 39.791 | 229.6667 | 12.6437 | 86.148 | -75 | -3.6042 | 235.2469 | -197.664 | -68.664 | -21.7653 | 0 | -21.7653 | 86 | -21.7653 | 8/17/17:00
8 | 17 | 1900-01-17 | 28.9 | 98 | 566 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 98 | 0 | 0 | 39.791 | 229.7083 | 12.6297 | 86.148 | -75 | -3.5948 | 250.2493 | -64.2083 | 33.7917 | 10.7114 | 0 | 10.7114 | 84.02 | 10.7114 | 8/17/18:00
8 | 17 | 1900-01-18 | 27.2 | 61 | 332 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 61 | 0 | 0 | 39.791 | 229.75 | 12.6157 | 86.148 | -75 | -3.5853 | 265.2517 | 25.7998 | 86.7998 | 27.514 | 0 | 27.514 | 80.96 | 27.514 | 8/17/19:00
8 | 17 | 1900-01-19 | 22.8 | 19 | 27 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 19 | 0 | 0 | 39.791 | 229.7917 | 12.6017 | 86.148 | -75 | -3.5758 | 280.2541 | 7.3741 | 26.3741 | 8.3601 | 0 | 8.3601 | 73.04 | 8.3601 | 8/17/20:00
8 | 17 | 1900-01-20 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 229.8333 | 12.5877 | 86.148 | -75 | -3.5663 | 295.2564 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/17/21:00
8 | 17 | 1900-01-21 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 229.875 | 12.5737 | 86.148 | -75 | -3.5567 | 310.2588 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/17/22:00
8 | 17 | 1900-01-22 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 229.9167 | 12.5597 | 86.148 | -75 | -3.5472 | 325.2612 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/17/23:00
8 | 17 | 1900-01-23 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 229.9583 | 12.5456 | 86.148 | -75 | -3.5376 | 340.2636 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/17/24:00
8 | 18 | 1899-12-31 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 230 | 12.5316 | 86.148 | -75 | -3.5281 | -4.734 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/18/1:00
8 | 18 | 1900-01-01 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 230.0417 | 12.5175 | 86.148 | -75 | -3.5185 | 10.2684 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/18/2:00
8 | 18 | 1900-01-02 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 230.0833 | 12.5035 | 86.148 | -75 | -3.5089 | 25.2708 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 8/18/3:00
8 | 18 | 1900-01-03 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 230.125 | 12.4894 | 86.148 | -75 | -3.4992 | 40.2732 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 8/18/4:00
8 | 18 | 1900-01-04 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 230.1667 | 12.4754 | 86.148 | -75 | -3.4896 | 55.2756 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/18/5:00
8 | 18 | 1900-01-05 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 230.2083 | 12.4613 | 86.148 | -75 | -3.4799 | 70.278 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 8/18/6:00
8 | 18 | 1900-01-06 | 16.1 | 28 | 201 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 28 | 0 | 0 | 39.791 | 230.25 | 12.4472 | 86.148 | -75 | -3.4703 | 85.2804 | 40.1355 | 68.1355 | 21.5978 | 0 | 21.5978 | 60.98 | 21.5978 | 8/18/7:00
8 | 18 | 1900-01-07 | 20.6 | 53 | 570 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 53 | 0 | 0 | 39.791 | 230.2917 | 12.4331 | 86.148 | -75 | -3.4606 | 100.2829 | 2.191 | 55.191 | 17.4946 | 0 | 17.4946 | 69.08 | 17.4946 | 8/18/8:00
8 | 18 | 1900-01-08 | 22.8 | 87 | 712 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 87 | 0 | 0 | 39.791 | 230.3333 | 12.419 | 86.148 | -75 | -3.4509 | 115.2853 | -130.2113 | -43.2113 | -13.6972 | 0 | -13.6972 | 73.04 | -13.6972 | 8/18/9:00
8 | 18 | 1900-01-09 | 25.6 | 116 | 708 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 116 | 0 | 0 | 39.791 | 230.375 | 12.405 | 86.148 | -75 | -3.4411 | 130.2877 | -246.2249 | -130.2249 | -41.279 | 0 | -41.279 | 78.08 | -41.279 | 8/18/10:00
8 | 18 | 1900-01-10 | 27.2 | 155 | 735 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 155 | 0 | 0 | 39.791 | 230.4167 | 12.3909 | 86.148 | -75 | -3.4314 | 145.2901 | -352.51 | -197.51 | -62.6072 | 0 | -62.6072 | 80.96 | -62.6072 | 8/18/11:00
8 | 18 | 1900-01-11 | 27.8 | 193 | 715 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 193 | 0 | 0 | 39.791 | 230.4583 | 12.3767 | 86.148 | -75 | -3.4217 | 160.2926 | -407.1146 | -214.1146 | -67.8706 | 0 | -67.8706 | 82.04 | -67.8706 | 8/18/12:00
8 | 18 | 1900-01-12 | 28.9 | 204 | 757 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 204 | 0 | 0 | 39.791 | 230.5 | 12.3626 | 86.148 | -75 | -3.4119 | 175.295 | -462.5399 | -258.5399 | -81.9526 | 0 | -81.9526 | 84.02 | -81.9526 | 8/18/13:00
8 | 18 | 1900-01-13 | 30 | 107 | 842 | 86 | 0 | 1 | 0 | 86 | 0 | 107 | 0 | 0 | 39.791 | 230.5417 | 12.3485 | 86.148 | -75 | -3.4021 | 190.2975 | -506.5898 | -399.5898 | -126.663 | 0 | -126.663 | 86 | -126.663 | 8/18/14:00
8 | 18 | 1900-01-14 | 30.6 | 199 | 702 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 199 | 0 | 0 | 39.791 | 230.5833 | 12.3344 | 86.148 | -75 | -3.3923 | 205.2999 | -380.4387 | -181.4387 | -57.5129 | 0 | -57.5129 | 87.08 | -57.5129 | 8/18/15:00
8 | 18 | 1900-01-15 | 29.4 | 273 | 431 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 273 | 0 | 0 | 39.791 | 230.625 | 12.3203 | 86.148 | -75 | -3.3825 | 220.3024 | -187.8934 | 85.1066 | 26.9773 | 0 | 26.9773 | 84.92 | 26.9773 | 8/18/16:00
8 | 18 | 1900-01-16 | 30 | 149 | 600 | 86 | 0 | 1 | 0 | 86 | 0 | 149 | 0 | 0 | 39.791 | 230.6667 | 12.3061 | 86.148 | -75 | -3.3727 | 235.3048 | -174.5509 | -25.5509 | -8.0992 | 0 | -8.0992 | 86 | -8.0992 | 8/18/17:00
8 | 18 | 1900-01-17 | 29.4 | 67 | 648 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 67 | 0 | 0 | 39.791 | 230.7083 | 12.292 | 86.148 | -75 | -3.3628 | 250.3073 | -75.6481 | -8.6481 | -2.7413 | 0 | -2.7413 | 84.92 | -2.7413 | 8/18/18:00
8 | 18 | 1900-01-18 | 27.8 | 48 | 450 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 48 | 0 | 0 | 39.791 | 230.75 | 12.2779 | 86.148 | -75 | -3.353 | 265.3098 | 33.6162 | 81.6162 | 25.8709 | 0 | 25.8709 | 82.04 | 25.8709 | 8/18/19:00
8 | 18 | 1900-01-19 | 23.9 | 15 | 86 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 15 | 0 | 0 | 39.791 | 230.7917 | 12.2637 | 86.148 | -75 | -3.3431 | 280.3122 | 23.2503 | 38.2503 | 12.1247 | 0 | 12.1247 | 75.02 | 12.1247 | 8/18/20:00
8 | 18 | 1900-01-20 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 230.8333 | 12.2496 | 86.148 | -75 | -3.3332 | 295.3147 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/18/21:00
8 | 18 | 1900-01-21 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 230.875 | 12.2354 | 86.148 | -75 | -3.3233 | 310.3172 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/18/22:00
8 | 18 | 1900-01-22 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 230.9167 | 12.2212 | 86.148 | -75 | -3.3134 | 325.3197 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/18/23:00
8 | 18 | 1900-01-23 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 230.9583 | 12.2071 | 86.148 | -75 | -3.3034 | 340.3221 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/18/24:00
8 | 19 | 1899-12-31 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 231 | 12.1929 | 86.148 | -75 | -3.2935 | -4.6754 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/19/1:00
8 | 19 | 1900-01-01 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 231.0417 | 12.1787 | 86.148 | -75 | -3.2835 | 10.3271 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/19/2:00
8 | 19 | 1900-01-02 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 231.0833 | 12.1645 | 86.148 | -75 | -3.2735 | 25.3296 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/19/3:00
8 | 19 | 1900-01-03 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 231.125 | 12.1503 | 86.148 | -75 | -3.2635 | 40.3321 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/19/4:00
8 | 19 | 1900-01-04 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 231.1667 | 12.1361 | 86.148 | -75 | -3.2535 | 55.3346 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/19/5:00
8 | 19 | 1900-01-05 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 231.2083 | 12.1219 | 86.148 | -75 | -3.2435 | 70.3371 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/19/6:00
8 | 19 | 1900-01-06 | 18.3 | 31 | 37 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 31 | 0 | 0 | 39.791 | 231.25 | 12.1077 | 86.148 | -75 | -3.2334 | 85.3396 | 7.2253 | 38.2253 | 12.1168 | 0 | 12.1168 | 64.94 | 12.1168 | 8/19/7:00
8 | 19 | 1900-01-07 | 21.7 | 88 | 307 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 88 | 0 | 0 | 39.791 | 231.2917 | 12.0935 | 86.148 | -75 | -3.2234 | 100.3422 | -0.24599 | 87.754 | 27.8165 | 0 | 27.8165 | 71.06 | 27.8165 | 8/19/8:00
8 | 19 | 1900-01-08 | 23.9 | 137 | 507 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 137 | 0 | 0 | 39.791 | 231.3333 | 12.0793 | 86.148 | -75 | -3.2133 | 115.3447 | -95.1675 | 41.8325 | 13.2602 | 0 | 13.2602 | 75.02 | 13.2602 | 8/19/9:00
8 | 19 | 1900-01-09 | 25.6 | 198 | 484 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 198 | 0 | 0 | 39.791 | 231.375 | 12.065 | 86.148 | -75 | -3.2032 | 130.3472 | -170.7094 | 27.2906 | 8.6506 | 0 | 8.6506 | 78.08 | 8.6506 | 8/19/10:00
8 | 19 | 1900-01-10 | 26.7 | 259 | 504 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 259 | 0 | 0 | 39.791 | 231.4167 | 12.0508 | 86.148 | -75 | -3.1931 | 145.3497 | -244.2162 | 14.7838 | 4.6862 | 0 | 4.6862 | 80.06 | 4.6862 | 8/19/11:00
8 | 19 | 1900-01-11 | 26.7 | 252 | 646 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 252 | 0 | 0 | 39.791 | 231.4583 | 12.0366 | 86.148 | -75 | -3.183 | 160.3523 | -370.9828 | -118.9828 | -37.7155 | 0 | -37.7155 | 80.06 | -37.7155 | 8/19/12:00
8 | 19 | 1900-01-12 | 27.8 | 225 | 744 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 225 | 0 | 0 | 39.791 | 231.5 | 12.0223 | 86.148 | -75 | -3.1728 | 175.3548 | -458.1234 | -233.1234 | -73.8961 | 0 | -73.8961 | 82.04 | -73.8961 | 8/19/13:00
8 | 19 | 1900-01-13 | 27.8 | 225 | 719 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 225 | 0 | 0 | 39.791 | 231.5417 | 12.0081 | 86.148 | -75 | -3.1627 | 190.3573 | -435.8398 | -210.8398 | -66.8325 | 0 | -66.8325 | 82.04 | -66.8325 | 8/19/14:00
8 | 19 | 1900-01-14 | 28.3 | 215 | 714 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 215 | 0 | 0 | 39.791 | 231.5833 | 11.9938 | 86.148 | -75 | -3.1525 | 205.3599 | -389.9784 | -174.9784 | -55.4651 | 0 | -55.4651 | 82.94 | -55.4651 | 8/19/15:00
8 | 19 | 1900-01-15 | 28.9 | 194 | 661 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 194 | 0 | 0 | 39.791 | 231.625 | 11.9795 | 86.148 | -75 | -3.1423 | 220.3624 | -290.7686 | -96.7686 | -30.674 | 0 | -30.674 | 84.02 | -30.674 | 8/19/16:00
8 | 19 | 1900-01-16 | 28.3 | 163 | 592 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 163 | 0 | 0 | 39.791 | 231.6667 | 11.9653 | 86.148 | -75 | -3.1321 | 235.365 | -174.367 | -11.367 | -3.6031 | 0 | -3.6031 | 82.94 | -3.6031 | 8/19/17:00
8 | 19 | 1900-01-17 | 27.2 | 124 | 417 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 124 | 0 | 0 | 39.791 | 231.7083 | 11.951 | 86.148 | -75 | -3.1219 | 250.3675 | -50.0585 | 73.9415 | 23.4382 | 0 | 23.4382 | 80.96 | 23.4382 | 8/19/18:00
8 | 19 | 1900-01-18 | 25 | 60 | 139 | 77 | 0 | 1 | 0 | 77 | 0 | 60 | 0 | 0 | 39.791 | 231.75 | 11.9367 | 86.148 | -75 | -3.1117 | 265.3701 | 9.9645 | 69.9645 | 22.1775 | 0 | 22.1775 | 77 | 22.1775 | 8/19/19:00
8 | 19 | 1900-01-19 | 21.7 | 12 | 4 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 12 | 0 | 0 | 39.791 | 231.7917 | 11.9224 | 86.148 | -75 | -3.1015 | 280.3726 | 1.0703 | 13.0703 | 4.1431 | 0 | 4.1431 | 71.06 | 4.1431 | 8/19/20:00
8 | 19 | 1900-01-20 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 231.8333 | 11.9082 | 86.148 | -75 | -3.0912 | 295.3752 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/19/21:00
8 | 19 | 1900-01-21 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 231.875 | 11.8939 | 86.148 | -75 | -3.0809 | 310.3778 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/19/22:00
8 | 19 | 1900-01-22 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 231.9167 | 11.8796 | 86.148 | -75 | -3.0706 | 325.3803 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/19/23:00
8 | 19 | 1900-01-23 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 231.9583 | 11.8653 | 86.148 | -75 | -3.0603 | 340.3829 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/19/24:00
8 | 20 | 1899-12-31 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 232 | 11.8509 | 86.148 | -75 | -3.05 | -4.6145 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/20/1:00
8 | 20 | 1900-01-01 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 232.0417 | 11.8366 | 86.148 | -75 | -3.0397 | 10.3881 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/20/2:00
8 | 20 | 1900-01-02 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 232.0833 | 11.8223 | 86.148 | -75 | -3.0293 | 25.3907 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/20/3:00
8 | 20 | 1900-01-03 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 232.125 | 11.808 | 86.148 | -75 | -3.019 | 40.3933 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/20/4:00
8 | 20 | 1900-01-04 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 232.1667 | 11.7936 | 86.148 | -75 | -3.0086 | 55.3959 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/20/5:00
8 | 20 | 1900-01-05 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 232.2083 | 11.7793 | 86.148 | -75 | -2.9982 | 70.3985 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/20/6:00
8 | 20 | 1900-01-06 | 18.3 | 17 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 17 | 0 | 0 | 39.791 | 232.25 | 11.765 | 86.148 | -75 | -2.9878 | 85.4011 | 0 | 17 | 5.3887 | 0 | 5.3887 | 64.94 | 5.3887 | 8/20/7:00
8 | 20 | 1900-01-07 | 19.4 | 87 | 97 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 87 | 0 | 0 | 39.791 | 232.2917 | 11.7506 | 86.148 | -75 | -2.9774 | 100.4037 | -0.53478 | 86.4652 | 27.408 | 0 | 27.408 | 66.92 | 27.408 | 8/20/8:00
8 | 20 | 1900-01-08 | 22.8 | 153 | 497 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 153 | 0 | 0 | 39.791 | 232.3333 | 11.7363 | 86.148 | -75 | -2.9669 | 115.4063 | -95.7186 | 57.2814 | 18.1572 | 0 | 18.1572 | 73.04 | 18.1572 | 8/20/9:00
8 | 20 | 1900-01-09 | 24.4 | 144 | 696 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 144 | 0 | 0 | 39.791 | 232.375 | 11.7219 | 86.148 | -75 | -2.9565 | 130.4089 | -248.95 | -104.95 | -33.2673 | 0 | -33.2673 | 75.92 | -33.2673 | 8/20/10:00
8 | 20 | 1900-01-10 | 26.1 | 165 | 756 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 165 | 0 | 0 | 39.791 | 232.4167 | 11.7075 | 86.148 | -75 | -2.946 | 145.4115 | -370.0985 | -205.0985 | -65.0127 | 0 | -65.0127 | 78.98 | -65.0127 | 8/20/11:00
8 | 20 | 1900-01-11 | 27.2 | 178 | 791 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 178 | 0 | 0 | 39.791 | 232.4583 | 11.6932 | 86.148 | -75 | -2.9355 | 160.4141 | -458.1431 | -280.1431 | -88.8005 | 0 | -88.8005 | 80.96 | -88.8005 | 8/20/12:00
8 | 20 | 1900-01-12 | 28.9 | 184 | 797 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 184 | 0 | 0 | 39.791 | 232.5 | 11.6788 | 86.148 | -75 | -2.925 | 175.4167 | -494.5551 | -310.5551 | -98.4406 | 0 | -98.4406 | 84.02 | -98.4406 | 8/20/13:00
8 | 20 | 1900-01-13 | 29.4 | 183 | 801 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 183 | 0 | 0 | 39.791 | 232.5417 | 11.6644 | 86.148 | -75 | -2.9145 | 190.4194 | -489.1825 | -306.1825 | -97.0545 | 0 | -97.0545 | 84.92 | -97.0545 | 8/20/14:00
8 | 20 | 1900-01-14 | 30.6 | 240 | 649 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 240 | 0 | 0 | 39.791 | 232.5833 | 11.65 | 86.148 | -75 | -2.904 | 205.422 | -357.2422 | -117.2422 | -37.1637 | 0 | -37.1637 | 87.08 | -37.1637 | 8/20/15:00
8 | 20 | 1900-01-15 | 30.6 | 195 | 658 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 195 | 0 | 0 | 39.791 | 232.625 | 11.6356 | 86.148 | -75 | -2.8934 | 220.4246 | -292.0477 | -97.0477 | -30.7624 | 0 | -30.7624 | 87.08 | -30.7624 | 8/20/16:00
8 | 20 | 1900-01-16 | 30 | 153 | 574 | 86 | 0 | 1 | 0 | 86 | 0 | 153 | 0 | 0 | 39.791 | 232.6667 | 11.6212 | 86.148 | -75 | -2.8829 | 235.4273 | -171.1454 | -18.1454 | -5.7518 | 0 | -5.7518 | 86 | -5.7518 | 8/20/17:00
8 | 20 | 1900-01-17 | 28.9 | 133 | 400 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 133 | 0 | 0 | 39.791 | 232.7083 | 11.6068 | 86.148 | -75 | -2.8723 | 250.4299 | -49.3408 | 83.6592 | 26.5185 | 0 | 26.5185 | 84.02 | 26.5185 | 8/20/18:00
8 | 20 | 1900-01-18 | 25 | 83 | 80 | 77 | 0 | 1 | 0 | 77 | 0 | 83 | 0 | 0 | 39.791 | 232.75 | 11.5924 | 86.148 | -75 | -2.8617 | 265.4326 | 5.4932 | 88.4932 | 28.0508 | 0 | 28.0508 | 77 | 28.0508 | 8/20/19:00
8 | 20 | 1900-01-19 | 23.9 | 15 | 5 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 15 | 0 | 0 | 39.791 | 232.7917 | 11.578 | 86.148 | -75 | -2.8511 | 280.4352 | 1.3239 | 16.3239 | 5.1744 | 0 | 5.1744 | 75.02 | 5.1744 | 8/20/20:00
8 | 20 | 1900-01-20 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 232.8333 | 11.5636 | 86.148 | -75 | -2.8405 | 295.4379 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/20/21:00
8 | 20 | 1900-01-21 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 232.875 | 11.5492 | 86.148 | -75 | -2.8299 | 310.4405 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 8/20/22:00
8 | 20 | 1900-01-22 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 232.9167 | 11.5348 | 86.148 | -75 | -2.8192 | 325.4432 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/20/23:00
8 | 20 | 1900-01-23 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 232.9583 | 11.5203 | 86.148 | -75 | -2.8086 | 340.4459 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/20/24:00
8 | 21 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 233 | 11.5059 | 86.148 | -75 | -2.7979 | -4.5515 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/21/1:00
8 | 21 | 1900-01-01 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 233.0417 | 11.4914 | 86.148 | -75 | -2.7872 | 10.4512 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/21/2:00
8 | 21 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 233.0833 | 11.477 | 86.148 | -75 | -2.7765 | 25.4539 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/21/3:00
8 | 21 | 1900-01-03 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 233.125 | 11.4625 | 86.148 | -75 | -2.7658 | 40.4566 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/21/4:00
8 | 21 | 1900-01-04 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 233.1667 | 11.4481 | 86.148 | -75 | -2.755 | 55.4592 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/21/5:00
8 | 21 | 1900-01-05 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 233.2083 | 11.4336 | 86.148 | -75 | -2.7443 | 70.4619 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/21/6:00
8 | 21 | 1900-01-06 | 21.1 | 12 | 1 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 12 | 0 | 0 | 39.791 | 233.25 | 11.4191 | 86.148 | -75 | -2.7335 | 85.4646 | 0.18627 | 12.1863 | 3.8628 | 0 | 3.8628 | 69.98 | 3.8628 | 8/21/7:00
8 | 21 | 1900-01-07 | 21.7 | 65 | 3 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 65 | 0 | 0 | 39.791 | 233.2917 | 11.4047 | 86.148 | -75 | -2.7228 | 100.4673 | -0.03087 | 64.9691 | 20.5941 | 0 | 20.5941 | 71.06 | 20.5941 | 8/21/8:00
8 | 21 | 1900-01-08 | 21.1 | 119 | 12 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 119 | 0 | 0 | 39.791 | 233.3333 | 11.3902 | 86.148 | -75 | -2.712 | 115.47 | -2.3704 | 116.6296 | 36.9695 | 0 | 36.9695 | 69.98 | 36.9695 | 8/21/9:00
8 | 21 | 1900-01-09 | 21.1 | 125 | 2 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 125 | 0 | 0 | 39.791 | 233.375 | 11.3757 | 86.148 | -75 | -2.7012 | 130.4727 | -0.72543 | 124.2746 | 39.3929 | 0 | 39.3929 | 69.98 | 39.3929 | 8/21/10:00
8 | 21 | 1900-01-10 | 21.1 | 233 | 4 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 233 | 0 | 0 | 39.791 | 233.4167 | 11.3612 | 86.148 | -75 | -2.6903 | 145.4754 | -1.9783 | 231.0217 | 73.2298 | 0 | 73.2298 | 69.98 | 73.2298 | 8/21/11:00
8 | 21 | 1900-01-11 | 22.8 | 339 | 1 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 339 | 0 | 0 | 39.791 | 233.4583 | 11.3467 | 86.148 | -75 | -2.6795 | 160.4781 | -0.58414 | 338.4159 | 107.2719 | 0 | 107.2719 | 73.04 | 107.2719 | 8/21/12:00
8 | 21 | 1900-01-12 | 22.2 | 223 | 2 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 223 | 0 | 0 | 39.791 | 233.5 | 11.3322 | 86.148 | -75 | -2.6687 | 175.4808 | -1.2506 | 221.7494 | 70.2907 | 0 | 70.2907 | 71.96 | 70.2907 | 8/21/13:00
8 | 21 | 1900-01-13 | 25 | 384 | 3 | 77 | 0 | 1 | 0 | 77 | 0 | 384 | 0 | 0 | 39.791 | 233.5417 | 11.3177 | 86.148 | -75 | -2.6578 | 190.4836 | -1.8458 | 382.1542 | 121.1362 | 0 | 121.1362 | 77 | 121.1362 | 8/21/14:00
8 | 21 | 1900-01-14 | 27.8 | 341 | 436 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 341 | 0 | 0 | 39.791 | 233.5833 | 11.3032 | 86.148 | -75 | -2.6469 | 205.4863 | -241.8578 | 99.1422 | 31.4264 | 0 | 31.4264 | 82.04 | 31.4264 | 8/21/15:00
8 | 21 | 1900-01-15 | 29.4 | 150 | 697 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 150 | 0 | 0 | 39.791 | 233.625 | 11.2887 | 86.148 | -75 | -2.636 | 220.489 | -312.1129 | -162.1129 | -51.3869 | 0 | -51.3869 | 84.92 | -51.3869 | 8/21/16:00
8 | 21 | 1900-01-16 | 29.4 | 127 | 626 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 127 | 0 | 0 | 39.791 | 233.6667 | 11.2741 | 86.148 | -75 | -2.6251 | 235.4917 | -188.9197 | -61.9197 | -19.6275 | 0 | -19.6275 | 84.92 | -19.6275 | 8/21/17:00
8 | 21 | 1900-01-17 | 28.9 | 99 | 531 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 99 | 0 | 0 | 39.791 | 233.7083 | 11.2596 | 86.148 | -75 | -2.6142 | 250.4945 | -67.2579 | 31.7421 | 10.0617 | 0 | 10.0617 | 84.02 | 10.0617 | 8/21/18:00
8 | 21 | 1900-01-18 | 27.2 | 61 | 256 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 61 | 0 | 0 | 39.791 | 233.75 | 11.2451 | 86.148 | -75 | -2.6033 | 265.4972 | 16.8027 | 77.8027 | 24.6621 | 0 | 24.6621 | 80.96 | 24.6621 | 8/21/19:00
8 | 21 | 1900-01-19 | 25.6 | 17 | 15 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 17 | 0 | 0 | 39.791 | 233.7917 | 11.2306 | 86.148 | -75 | -2.5923 | 280.4999 | 3.9298 | 20.9298 | 6.6344 | 0 | 6.6344 | 78.08 | 6.6344 | 8/21/20:00
8 | 21 | 1900-01-20 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 233.8333 | 11.216 | 86.148 | -75 | -2.5813 | 295.5027 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 8/21/21:00
8 | 21 | 1900-01-21 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 233.875 | 11.2015 | 86.148 | -75 | -2.5704 | 310.5054 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 8/21/22:00
8 | 21 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 233.9167 | 11.1869 | 86.148 | -75 | -2.5594 | 325.5082 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 8/21/23:00
8 | 21 | 1900-01-23 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 233.9583 | 11.1723 | 86.148 | -75 | -2.5484 | 340.5109 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 8/21/24:00
8 | 22 | 1899-12-31 | 26.7 | 0 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 0 | 0 | 0 | 39.791 | 234 | 11.1578 | 86.148 | -75 | -2.5373 | -4.4863 | 0 | 0 | 0 | 0 | 0 | 80.06 | 0 | 8/22/1:00
8 | 22 | 1900-01-01 | 27.2 | 0 | 0 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 0 | 0 | 0 | 39.791 | 234.0417 | 11.1432 | 86.148 | -75 | -2.5263 | 10.5164 | 0 | 0 | 0 | 0 | 0 | 80.96 | 0 | 8/22/2:00
8 | 22 | 1900-01-02 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 234.0833 | 11.1286 | 86.148 | -75 | -2.5152 | 25.5192 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 8/22/3:00
8 | 22 | 1900-01-03 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 234.125 | 11.1141 | 86.148 | -75 | -2.5042 | 40.522 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 8/22/4:00
8 | 22 | 1900-01-04 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 234.1667 | 11.0995 | 86.148 | -75 | -2.4931 | 55.5247 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 8/22/5:00
8 | 22 | 1900-01-05 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 234.2083 | 11.0849 | 86.148 | -75 | -2.482 | 70.5275 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 8/22/6:00
8 | 22 | 1900-01-06 | 25.6 | 27 | 66 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 27 | 0 | 0 | 39.791 | 234.25 | 11.0703 | 86.148 | -75 | -2.4709 | 85.5303 | 11.9892 | 38.9892 | 12.3589 | 0 | 12.3589 | 78.08 | 12.3589 | 8/22/7:00
8 | 22 | 1900-01-07 | 26.7 | 56 | 501 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 56 | 0 | 0 | 39.791 | 234.2917 | 11.0557 | 86.148 | -75 | -2.4598 | 100.5331 | -7.5799 | 48.4201 | 15.3483 | 0 | 15.3483 | 80.06 | 15.3483 | 8/22/8:00
8 | 22 | 1900-01-08 | 28.9 | 88 | 594 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 88 | 0 | 0 | 39.791 | 234.3333 | 11.0411 | 86.148 | -75 | -2.4486 | 115.5358 | -120.3053 | -32.3053 | -10.2402 | 0 | -10.2402 | 84.02 | -10.2402 | 8/22/9:00
8 | 22 | 1900-01-09 | 30 | 345 | 220 | 86 | 0 | 1 | 0 | 86 | 0 | 345 | 0 | 0 | 39.791 | 234.375 | 11.0265 | 86.148 | -75 | -2.4375 | 130.5386 | -80.9145 | 264.0855 | 83.7105 | 0 | 83.7105 | 86 | 83.7105 | 8/22/10:00
8 | 22 | 1900-01-10 | 30.6 | 282 | 116 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 282 | 0 | 0 | 39.791 | 234.4167 | 11.0119 | 86.148 | -75 | -2.4263 | 145.5414 | -57.9592 | 224.0408 | 71.017 | 0 | 71.017 | 87.08 | 71.017 | 8/22/11:00
8 | 22 | 1900-01-11 | 30 | 338 | 12 | 86 | 0 | 1 | 0 | 86 | 0 | 338 | 0 | 0 | 39.791 | 234.4583 | 10.9973 | 86.148 | -75 | -2.4152 | 160.5442 | -7.0694 | 330.9306 | 104.8992 | 0 | 104.8992 | 86 | 104.8992 | 8/22/12:00
8 | 22 | 1900-01-12 | 28.9 | 310 | 10 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 310 | 0 | 0 | 39.791 | 234.5 | 10.9826 | 86.148 | -75 | -2.404 | 175.547 | -6.3011 | 303.6989 | 96.2673 | 0 | 96.2673 | 84.02 | 96.2673 | 8/22/13:00
8 | 22 | 1900-01-13 | 26.1 | 309 | 5 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 309 | 0 | 0 | 39.791 | 234.5417 | 10.968 | 86.148 | -75 | -2.3928 | 190.5498 | -3.0992 | 305.9008 | 96.9652 | 0 | 96.9652 | 78.98 | 96.9652 | 8/22/14:00
8 | 22 | 1900-01-14 | 24.4 | 296 | 11 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 296 | 0 | 0 | 39.791 | 234.5833 | 10.9534 | 86.148 | -75 | -2.3815 | 205.5526 | -6.1489 | 289.8511 | 91.8777 | 0 | 91.8777 | 75.92 | 91.8777 | 8/22/15:00
8 | 22 | 1900-01-15 | 25 | 305 | 4 | 77 | 0 | 1 | 0 | 77 | 0 | 305 | 0 | 0 | 39.791 | 234.625 | 10.9387 | 86.148 | -75 | -2.3703 | 220.5554 | -1.807 | 303.193 | 96.1069 | 0 | 96.1069 | 77 | 96.1069 | 8/22/16:00
8 | 22 | 1900-01-16 | 26.1 | 213 | 7 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 213 | 0 | 0 | 39.791 | 234.6667 | 10.9241 | 86.148 | -75 | -2.3591 | 235.5582 | -2.1379 | 210.8621 | 66.8396 | 0 | 66.8396 | 78.98 | 66.8396 | 8/22/17:00
8 | 22 | 1900-01-17 | 25 | 176 | 1 | 77 | 0 | 1 | 0 | 77 | 0 | 176 | 0 | 0 | 39.791 | 234.7083 | 10.9094 | 86.148 | -75 | -2.3478 | 250.5611 | -0.12998 | 175.87 | 55.7477 | 0 | 55.7477 | 77 | 55.7477 | 8/22/18:00
8 | 22 | 1900-01-18 | 22.2 | 75 | 224 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 75 | 0 | 0 | 39.791 | 234.75 | 10.8948 | 86.148 | -75 | -2.3365 | 265.5639 | 14.0225 | 89.0225 | 28.2186 | 0 | 28.2186 | 71.96 | 28.2186 | 8/22/19:00
8 | 22 | 1900-01-19 | 20 | 16 | 20 | 68 | 0 | 1 | 0 | 68 | 0 | 16 | 0 | 0 | 39.791 | 234.7917 | 10.8801 | 86.148 | -75 | -2.3252 | 280.5667 | 5.1835 | 21.1835 | 6.7148 | 0 | 6.7148 | 68 | 6.7148 | 8/22/20:00
8 | 22 | 1900-01-20 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 234.8333 | 10.8655 | 86.148 | -75 | -2.3139 | 295.5695 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/22/21:00
8 | 22 | 1900-01-21 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 234.875 | 10.8508 | 86.148 | -75 | -2.3026 | 310.5723 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/22/22:00
8 | 22 | 1900-01-22 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 234.9167 | 10.8361 | 86.148 | -75 | -2.2913 | 325.5752 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/22/23:00
8 | 22 | 1900-01-23 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 234.9583 | 10.8214 | 86.148 | -75 | -2.2799 | 340.578 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/22/24:00
8 | 23 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 235 | 10.8068 | 86.148 | -75 | -2.2686 | -4.4191 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/23/1:00
8 | 23 | 1900-01-01 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 235.0417 | 10.7921 | 86.148 | -75 | -2.2572 | 10.5837 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/23/2:00
8 | 23 | 1900-01-02 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 235.0833 | 10.7774 | 86.148 | -75 | -2.2458 | 25.5865 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 8/23/3:00
8 | 23 | 1900-01-03 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 235.125 | 10.7627 | 86.148 | -75 | -2.2344 | 40.5894 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 8/23/4:00
8 | 23 | 1900-01-04 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 235.1667 | 10.748 | 86.148 | -75 | -2.223 | 55.5923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/23/5:00
8 | 23 | 1900-01-05 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 235.2083 | 10.7333 | 86.148 | -75 | -2.2116 | 70.5951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/23/6:00
8 | 23 | 1900-01-06 | 13.3 | 30 | 93 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 30 | 0 | 0 | 39.791 | 235.25 | 10.7186 | 86.148 | -75 | -2.2001 | 85.598 | 16.4588 | 46.4588 | 14.7266 | 0 | 14.7266 | 55.94 | 14.7266 | 8/23/7:00
8 | 23 | 1900-01-07 | 17.2 | 77 | 284 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 77 | 0 | 0 | 39.791 | 235.2917 | 10.7038 | 86.148 | -75 | -2.1887 | 100.6008 | -5.6885 | 71.3115 | 22.6045 | 0 | 22.6045 | 62.96 | 22.6045 | 8/23/8:00
8 | 23 | 1900-01-08 | 20 | 119 | 480 | 68 | 0 | 1 | 0 | 68 | 0 | 119 | 0 | 0 | 39.791 | 235.3333 | 10.6891 | 86.148 | -75 | -2.1772 | 115.6037 | -99.6411 | 19.3589 | 6.1364 | 0 | 6.1364 | 68 | 6.1364 | 8/23/9:00
8 | 23 | 1900-01-09 | 21.7 | 101 | 754 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 101 | 0 | 0 | 39.791 | 235.375 | 10.6744 | 86.148 | -75 | -2.1657 | 130.6066 | -281.177 | -180.177 | -57.113 | 0 | -57.113 | 71.06 | -57.113 | 8/23/10:00
8 | 23 | 1900-01-10 | 23.3 | 340 | 216 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 340 | 0 | 0 | 39.791 | 235.4167 | 10.6597 | 86.148 | -75 | -2.1542 | 145.6094 | -109.0264 | 230.9736 | 73.2146 | 0 | 73.2146 | 73.94 | 73.2146 | 8/23/11:00
8 | 23 | 1900-01-11 | 23.3 | 235 | 747 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 235 | 0 | 0 | 39.791 | 235.4583 | 10.6449 | 86.148 | -75 | -2.1427 | 160.6123 | -443.8066 | -208.8066 | -66.188 | 0 | -66.188 | 73.94 | -66.188 | 8/23/12:00
8 | 23 | 1900-01-12 | 23.9 | 387 | 210 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 387 | 0 | 0 | 39.791 | 235.5 | 10.6302 | 86.148 | -75 | -2.1312 | 175.6152 | -133.335 | 253.665 | 80.4074 | 0 | 80.4074 | 75.02 | 80.4074 | 8/23/13:00
8 | 23 | 1900-01-13 | 24.4 | 243 | 549 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 243 | 0 | 0 | 39.791 | 235.5417 | 10.6154 | 86.148 | -75 | -2.1196 | 190.6181 | -342.7987 | -99.7987 | -31.6345 | 0 | -31.6345 | 75.92 | -31.6345 | 8/23/14:00
8 | 23 | 1900-01-14 | 25.6 | 223 | 732 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 223 | 0 | 0 | 39.791 | 235.5833 | 10.6007 | 86.148 | -75 | -2.1081 | 205.621 | -412.316 | -189.316 | -60.0099 | 0 | -60.0099 | 78.08 | -60.0099 | 8/23/15:00
8 | 23 | 1900-01-15 | 25.6 | 176 | 711 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 176 | 0 | 0 | 39.791 | 235.625 | 10.5859 | 86.148 | -75 | -2.0965 | 220.6239 | -324.0065 | -148.0065 | -46.9155 | 0 | -46.9155 | 78.08 | -46.9155 | 8/23/16:00
8 | 23 | 1900-01-16 | 25 | 158 | 595 | 77 | 0 | 1 | 0 | 77 | 0 | 158 | 0 | 0 | 39.791 | 235.6667 | 10.5712 | 86.148 | -75 | -2.085 | 235.6268 | -183.8802 | -25.8802 | -8.2036 | 0 | -8.2036 | 77 | -8.2036 | 8/23/17:00
8 | 23 | 1900-01-17 | 23.9 | 90 | 560 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 90 | 0 | 0 | 39.791 | 235.7083 | 10.5564 | 86.148 | -75 | -2.0734 | 250.6297 | -74.6427 | 15.3573 | 4.868 | 0 | 4.868 | 75.02 | 4.868 | 8/23/18:00
8 | 23 | 1900-01-18 | 21.7 | 47 | 371 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 47 | 0 | 0 | 39.791 | 235.75 | 10.5416 | 86.148 | -75 | -2.0618 | 265.6326 | 22.0965 | 69.0965 | 21.9024 | 0 | 21.9024 | 71.06 | 21.9024 | 8/23/19:00
8 | 23 | 1900-01-19 | 19.4 | 11 | 41 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 11 | 0 | 0 | 39.791 | 235.7917 | 10.5269 | 86.148 | -75 | -2.0501 | 280.6355 | 10.5103 | 21.5103 | 6.8184 | 0 | 6.8184 | 66.92 | 6.8184 | 8/23/20:00
8 | 23 | 1900-01-20 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 235.8333 | 10.5121 | 86.148 | -75 | -2.0385 | 295.6384 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/23/21:00
8 | 23 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 235.875 | 10.4973 | 86.148 | -75 | -2.0269 | 310.6413 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/23/22:00
8 | 23 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 235.9167 | 10.4825 | 86.148 | -75 | -2.0152 | 325.6442 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 8/23/23:00
8 | 23 | 1900-01-23 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 235.9583 | 10.4677 | 86.148 | -75 | -2.0035 | 340.6471 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 8/23/24:00
8 | 24 | 1899-12-31 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 236 | 10.4529 | 86.148 | -75 | -1.9918 | -4.35 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 8/24/1:00
8 | 24 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 236.0417 | 10.4381 | 86.148 | -75 | -1.9801 | 10.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/24/2:00
8 | 24 | 1900-01-02 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 236.0833 | 10.4233 | 86.148 | -75 | -1.9684 | 25.6559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/24/3:00
8 | 24 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 236.125 | 10.4085 | 86.148 | -75 | -1.9567 | 40.6588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/24/4:00
8 | 24 | 1900-01-04 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 236.1667 | 10.3937 | 86.148 | -75 | -1.945 | 55.6618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/24/5:00
8 | 24 | 1900-01-05 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 236.2083 | 10.3789 | 86.148 | -75 | -1.9332 | 70.6647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/24/6:00
8 | 24 | 1900-01-06 | 11.7 | 30 | 48 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 30 | 0 | 0 | 39.791 | 236.25 | 10.364 | 86.148 | -75 | -1.9214 | 85.6676 | 8.2672 | 38.2672 | 12.13 | 12.13 | 0 | 0 | 0 | 8/24/7:00
8 | 24 | 1900-01-07 | 15.6 | 96 | 267 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 96 | 0 | 0 | 39.791 | 236.2917 | 10.3492 | 86.148 | -75 | -1.9097 | 100.6706 | -6.672 | 89.328 | 28.3154 | 0 | 28.3154 | 60.08 | 28.3154 | 8/24/8:00
8 | 24 | 1900-01-08 | 18.3 | 152 | 474 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 152 | 0 | 0 | 39.791 | 236.3333 | 10.3344 | 86.148 | -75 | -1.8979 | 115.6735 | -100.8139 | 51.1861 | 16.2251 | 0 | 16.2251 | 64.94 | 16.2251 | 8/24/9:00
8 | 24 | 1900-01-09 | 20 | 126 | 707 | 68 | 0 | 1 | 0 | 68 | 0 | 126 | 0 | 0 | 39.791 | 236.375 | 10.3195 | 86.148 | -75 | -1.8861 | 130.6765 | -267.2995 | -141.2995 | -44.7895 | 0 | -44.7895 | 68 | -44.7895 | 8/24/10:00
8 | 24 | 1900-01-10 | 21.1 | 248 | 562 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 248 | 0 | 0 | 39.791 | 236.4167 | 10.3047 | 86.148 | -75 | -1.8742 | 145.6794 | -286.5563 | -38.5563 | -12.2217 | 0 | -12.2217 | 69.98 | -12.2217 | 8/24/11:00
8 | 24 | 1900-01-11 | 22.2 | 224 | 709 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 224 | 0 | 0 | 39.791 | 236.4583 | 10.2898 | 86.148 | -75 | -1.8624 | 160.6824 | -424.7915 | -200.7915 | -63.6474 | 0 | -63.6474 | 71.96 | -63.6474 | 8/24/12:00
8 | 24 | 1900-01-12 | 22.8 | 269 | 683 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 269 | 0 | 0 | 39.791 | 236.5 | 10.275 | 86.148 | -75 | -1.8506 | 175.6854 | -436.9578 | -167.9578 | -53.2397 | 0 | -53.2397 | 73.04 | -53.2397 | 8/24/13:00
8 | 24 | 1900-01-13 | 23.3 | 273 | 662 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 273 | 0 | 0 | 39.791 | 236.5417 | 10.2601 | 86.148 | -75 | -1.8387 | 190.6883 | -416.3889 | -143.3889 | -45.4518 | 0 | -45.4518 | 73.94 | -45.4518 | 8/24/14:00
8 | 24 | 1900-01-14 | 23.9 | 350 | 333 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 350 | 0 | 0 | 39.791 | 236.5833 | 10.2452 | 86.148 | -75 | -1.8268 | 205.6913 | -188.9955 | 161.0045 | 51.0356 | 0 | 51.0356 | 75.02 | 51.0356 | 8/24/15:00
8 | 24 | 1900-01-15 | 22.8 | 322 | 261 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 322 | 0 | 0 | 39.791 | 236.625 | 10.2304 | 86.148 | -75 | -1.815 | 220.6943 | -119.9713 | 202.0287 | 64.0396 | 0 | 64.0396 | 73.04 | 64.0396 | 8/24/16:00
8 | 24 | 1900-01-16 | 23.3 | 210 | 185 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 210 | 0 | 0 | 39.791 | 236.6667 | 10.2155 | 86.148 | -75 | -1.8031 | 235.6972 | -57.8435 | 152.1565 | 48.2309 | 0 | 48.2309 | 73.94 | 48.2309 | 8/24/17:00
8 | 24 | 1900-01-17 | 22.2 | 114 | 20 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 114 | 0 | 0 | 39.791 | 236.7083 | 10.2006 | 86.148 | -75 | -1.7911 | 250.7002 | -2.7321 | 111.2679 | 35.27 | 0 | 35.27 | 71.96 | 35.27 | 8/24/18:00
8 | 24 | 1900-01-18 | 20.6 | 33 | 7 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 33 | 0 | 0 | 39.791 | 236.75 | 10.1857 | 86.148 | -75 | -1.7792 | 265.7032 | 0.39559 | 33.3956 | 10.5858 | 0 | 10.5858 | 69.08 | 10.5858 | 8/24/19:00
8 | 24 | 1900-01-19 | 20 | 9 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 9 | 0 | 0 | 39.791 | 236.7917 | 10.1708 | 86.148 | -75 | -1.7673 | 280.7062 | 0 | 9 | 2.8528 | 0 | 2.8528 | 68 | 2.8528 | 8/24/20:00
8 | 24 | 1900-01-20 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 236.8333 | 10.156 | 86.148 | -75 | -1.7553 | 295.7092 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 8/24/21:00
8 | 24 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 236.875 | 10.1411 | 86.148 | -75 | -1.7434 | 310.7122 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/24/22:00
8 | 24 | 1900-01-22 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 236.9167 | 10.1262 | 86.148 | -75 | -1.7314 | 325.7152 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/24/23:00
8 | 24 | 1900-01-23 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 236.9583 | 10.1113 | 86.148 | -75 | -1.7194 | 340.7181 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/24/24:00
8 | 25 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 237 | 10.0963 | 86.148 | -75 | -1.7074 | -4.2789 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/25/1:00
8 | 25 | 1900-01-01 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 237.0417 | 10.0814 | 86.148 | -75 | -1.6954 | 10.7242 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/25/2:00
8 | 25 | 1900-01-02 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 237.0833 | 10.0665 | 86.148 | -75 | -1.6834 | 25.7272 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/25/3:00
8 | 25 | 1900-01-03 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 237.125 | 10.0516 | 86.148 | -75 | -1.6713 | 40.7302 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/25/4:00
8 | 25 | 1900-01-04 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 237.1667 | 10.0367 | 86.148 | -75 | -1.6593 | 55.7332 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/25/5:00
8 | 25 | 1900-01-05 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 237.2083 | 10.0217 | 86.148 | -75 | -1.6472 | 70.7362 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/25/6:00
8 | 25 | 1900-01-06 | 17.2 | 29 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 29 | 0 | 0 | 39.791 | 237.25 | 10.0068 | 86.148 | -75 | -1.6351 | 85.7392 | 0 | 29 | 9.1925 | 0 | 9.1925 | 62.96 | 9.1925 | 8/25/7:00
8 | 25 | 1900-01-07 | 16.1 | 47 | 4 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 47 | 0 | 0 | 39.791 | 237.2917 | 9.9918 | 86.148 | -75 | -1.623 | 100.7422 | -0.12002 | 46.88 | 14.8601 | 0 | 14.8601 | 60.98 | 14.8601 | 8/25/8:00
8 | 25 | 1900-01-08 | 16.7 | 172 | 1 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 172 | 0 | 0 | 39.791 | 237.3333 | 9.9769 | 86.148 | -75 | -1.6109 | 115.7453 | -0.21784 | 171.7822 | 54.4519 | 0 | 54.4519 | 62.06 | 54.4519 | 8/25/9:00
8 | 25 | 1900-01-09 | 16.7 | 227 | 3 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 227 | 0 | 0 | 39.791 | 237.375 | 9.9619 | 86.148 | -75 | -1.5988 | 130.7483 | -1.1498 | 225.8502 | 71.5906 | 0 | 71.5906 | 62.06 | 71.5906 | 8/25/10:00
8 | 25 | 1900-01-10 | 17.2 | 335 | 1 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 335 | 0 | 0 | 39.791 | 237.4167 | 9.947 | 86.148 | -75 | -1.5867 | 145.7513 | -0.51505 | 334.4849 | 106.0259 | 0 | 106.0259 | 62.96 | 106.0259 | 8/25/11:00
8 | 25 | 1900-01-11 | 16.7 | 218 | 1 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 218 | 0 | 0 | 39.791 | 237.4583 | 9.932 | 86.148 | -75 | -1.5745 | 160.7544 | -0.60418 | 217.3958 | 68.9107 | 0 | 68.9107 | 62.06 | 68.9107 | 8/25/12:00
8 | 25 | 1900-01-12 | 18.3 | 459 | 1 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 459 | 0 | 0 | 39.791 | 237.5 | 9.9171 | 86.148 | -75 | -1.5624 | 175.7574 | -0.64461 | 458.3554 | 145.2907 | 0 | 145.2907 | 64.94 | 145.2907 | 8/25/13:00
8 | 25 | 1900-01-13 | 16.7 | 436 | 1 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 436 | 0 | 0 | 39.791 | 237.5417 | 9.9021 | 86.148 | -75 | -1.5502 | 190.7604 | -0.63357 | 435.3664 | 138.0036 | 0 | 138.0036 | 62.06 | 138.0036 | 8/25/14:00
8 | 25 | 1900-01-14 | 16.7 | 359 | 1 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 359 | 0 | 0 | 39.791 | 237.5833 | 9.8871 | 86.148 | -75 | -1.538 | 205.7635 | -0.57183 | 358.4282 | 113.6155 | 0 | 113.6155 | 62.06 | 113.6155 | 8/25/15:00
8 | 25 | 1900-01-15 | 16.7 | 185 | 1 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 185 | 0 | 0 | 39.791 | 237.625 | 9.8721 | 86.148 | -75 | -1.5258 | 220.7665 | -0.46361 | 184.5364 | 58.4948 | 0 | 58.4948 | 62.06 | 58.4948 | 8/25/16:00
8 | 25 | 1900-01-16 | 16.7 | 231 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 231 | 0 | 0 | 39.791 | 237.6667 | 9.8572 | 86.148 | -75 | -1.5136 | 235.7696 | 0 | 231 | 73.223 | 0 | 73.223 | 62.06 | 73.223 | 8/25/17:00
8 | 25 | 1900-01-17 | 16.1 | 145 | 1 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 145 | 0 | 0 | 39.791 | 237.7083 | 9.8422 | 86.148 | -75 | -1.5014 | 250.7726 | -0.13992 | 144.8601 | 45.9181 | 0 | 45.9181 | 60.98 | 45.9181 | 8/25/18:00
8 | 25 | 1900-01-18 | 15.6 | 59 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 59 | 0 | 0 | 39.791 | 237.75 | 9.8272 | 86.148 | -75 | -1.4892 | 265.7757 | 0 | 59 | 18.702 | 0 | 18.702 | 60.08 | 18.702 | 8/25/19:00
8 | 25 | 1900-01-19 | 15.6 | 13 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 13 | 0 | 0 | 39.791 | 237.7917 | 9.8122 | 86.148 | -75 | -1.4769 | 280.7788 | 0 | 13 | 4.1208 | 0 | 4.1208 | 60.08 | 4.1208 | 8/25/20:00
8 | 25 | 1900-01-20 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 237.8333 | 9.7972 | 86.148 | -75 | -1.4647 | 295.7818 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 8/25/21:00
8 | 25 | 1900-01-21 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 237.875 | 9.7822 | 86.148 | -75 | -1.4524 | 310.7849 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 8/25/22:00
8 | 25 | 1900-01-22 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 237.9167 | 9.7672 | 86.148 | -75 | -1.4401 | 325.788 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 8/25/23:00
8 | 25 | 1900-01-23 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 237.9583 | 9.7522 | 86.148 | -75 | -1.4278 | 340.791 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 8/25/24:00
8 | 26 | 1899-12-31 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 238 | 9.7371 | 86.148 | -75 | -1.4155 | -4.2059 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 8/26/1:00
8 | 26 | 1900-01-01 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 238.0417 | 9.7221 | 86.148 | -75 | -1.4032 | 10.7972 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 8/26/2:00
8 | 26 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 238.0833 | 9.7071 | 86.148 | -75 | -1.3909 | 25.8003 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 8/26/3:00
8 | 26 | 1900-01-03 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 238.125 | 9.6921 | 86.148 | -75 | -1.3785 | 40.8034 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 8/26/4:00
8 | 26 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 238.1667 | 9.677 | 86.148 | -75 | -1.3662 | 55.8065 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 8/26/5:00
8 | 26 | 1900-01-05 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 238.2083 | 9.662 | 86.148 | -75 | -1.3538 | 70.8096 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 8/26/6:00
8 | 26 | 1900-01-06 | 16.1 | 24 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 24 | 0 | 0 | 39.791 | 238.25 | 9.6469 | 86.148 | -75 | -1.3414 | 85.8126 | 0 | 24 | 7.6076 | 0 | 7.6076 | 60.98 | 7.6076 | 8/26/7:00
8 | 26 | 1900-01-07 | 17.2 | 105 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 105 | 0 | 0 | 39.791 | 238.2917 | 9.6319 | 86.148 | -75 | -1.329 | 100.8157 | 0 | 105 | 33.2832 | 0 | 33.2832 | 62.96 | 33.2832 | 8/26/8:00
8 | 26 | 1900-01-08 | 20.6 | 189 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 189 | 0 | 0 | 39.791 | 238.3333 | 9.6168 | 86.148 | -75 | -1.3166 | 115.8188 | 0 | 189 | 59.9097 | 0 | 59.9097 | 69.08 | 59.9097 | 8/26/9:00
8 | 26 | 1900-01-09 | 23.9 | 285 | 1 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 285 | 0 | 0 | 39.791 | 238.375 | 9.6018 | 86.148 | -75 | -1.3042 | 130.8219 | -0.38851 | 284.6115 | 90.2169 | 0 | 90.2169 | 75.02 | 90.2169 | 8/26/10:00
8 | 26 | 1900-01-10 | 27.2 | 282 | 284 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 282 | 0 | 0 | 39.791 | 238.4167 | 9.5867 | 86.148 | -75 | -1.2918 | 145.8251 | -147.7489 | 134.2511 | 42.5553 | 0 | 42.5553 | 80.96 | 42.5553 | 8/26/11:00
8 | 26 | 1900-01-11 | 30 | 284 | 461 | 86 | 0 | 1 | 0 | 86 | 0 | 284 | 0 | 0 | 39.791 | 238.4583 | 9.5717 | 86.148 | -75 | -1.2793 | 160.8282 | -280.8624 | 3.1376 | 0.99456 | 0 | 0.99456 | 86 | 0.99456 | 8/26/12:00
8 | 26 | 1900-01-12 | 30.6 | 289 | 540 | 87.08 | 0 | 1 | 0 | 87.08 | 0 | 289 | 0 | 0 | 39.791 | 238.5 | 9.5566 | 86.148 | -75 | -1.2669 | 175.8313 | -350.7105 | -61.7105 | -19.5611 | 0 | -19.5611 | 87.08 | -19.5611 | 8/26/13:00
8 | 26 | 1900-01-13 | 32.2 | 287 | 613 | 89.96 | 0 | 1 | 0 | 89.96 | 0 | 287 | 0 | 0 | 39.791 | 238.5417 | 9.5415 | 86.148 | -75 | -1.2544 | 190.8344 | -391.1926 | -104.1926 | -33.0272 | 0 | -33.0272 | 89.96 | -33.0272 | 8/26/14:00
8 | 26 | 1900-01-14 | 32.8 | 226 | 496 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 226 | 0 | 0 | 39.791 | 238.5833 | 9.5264 | 86.148 | -75 | -1.2419 | 205.8375 | -285.7527 | -59.7527 | -18.9406 | 0 | -18.9406 | 91.04 | -18.9406 | 8/26/15:00
8 | 26 | 1900-01-15 | 32.8 | 316 | 278 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 316 | 0 | 0 | 39.791 | 238.625 | 9.5114 | 86.148 | -75 | -1.2294 | 220.8406 | -129.9821 | 186.0179 | 58.9644 | 0 | 58.9644 | 91.04 | 58.9644 | 8/26/16:00
8 | 26 | 1900-01-16 | 32.8 | 102 | 753 | 91.04 | 0 | 1 | 0 | 91.04 | 0 | 102 | 0 | 0 | 39.791 | 238.6667 | 9.4963 | 86.148 | -75 | -1.2169 | 235.8438 | -240.8929 | -138.8929 | -44.0266 | 0 | -44.0266 | 91.04 | -44.0266 | 8/26/17:00
8 | 26 | 1900-01-17 | 31.7 | 65 | 662 | 89.06 | 0 | 1 | 0 | 89.06 | 0 | 65 | 0 | 0 | 39.791 | 238.7083 | 9.4812 | 86.148 | -75 | -1.2044 | 250.8469 | -94.8228 | -29.8228 | -9.4533 | 0 | -9.4533 | 89.06 | -9.4533 | 8/26/18:00
8 | 26 | 1900-01-18 | 29.4 | 65 | 256 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 65 | 0 | 0 | 39.791 | 238.75 | 9.4661 | 86.148 | -75 | -1.1919 | 265.85 | 12.904 | 77.904 | 24.6942 | 0 | 24.6942 | 84.92 | 24.6942 | 8/26/19:00
8 | 26 | 1900-01-19 | 27.8 | 16 | 7 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 16 | 0 | 0 | 39.791 | 238.7917 | 9.451 | 86.148 | -75 | -1.1793 | 280.8532 | 1.7346 | 17.7346 | 5.6216 | 0 | 5.6216 | 82.04 | 5.6216 | 8/26/20:00
8 | 26 | 1900-01-20 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 238.8333 | 9.4359 | 86.148 | -75 | -1.1668 | 295.8563 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/26/21:00
8 | 26 | 1900-01-21 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 238.875 | 9.4208 | 86.148 | -75 | -1.1542 | 310.8594 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/26/22:00
8 | 26 | 1900-01-22 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 238.9167 | 9.4057 | 86.148 | -75 | -1.1417 | 325.8626 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/26/23:00
8 | 26 | 1900-01-23 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 238.9583 | 9.3905 | 86.148 | -75 | -1.1291 | 340.8657 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 8/26/24:00
8 | 27 | 1899-12-31 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 239 | 9.3754 | 86.148 | -75 | -1.1165 | -4.1311 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/27/1:00
8 | 27 | 1900-01-01 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 239.0417 | 9.3603 | 86.148 | -75 | -1.1039 | 10.872 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/27/2:00
8 | 27 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 239.0833 | 9.3452 | 86.148 | -75 | -1.0912 | 25.8752 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/27/3:00
8 | 27 | 1900-01-03 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 239.125 | 9.33 | 86.148 | -75 | -1.0786 | 40.8784 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/27/4:00
8 | 27 | 1900-01-04 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 239.1667 | 9.3149 | 86.148 | -75 | -1.0659 | 55.8815 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 8/27/5:00
8 | 27 | 1900-01-05 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 239.2083 | 9.2997 | 86.148 | -75 | -1.0533 | 70.8847 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 8/27/6:00
8 | 27 | 1900-01-06 | 20.6 | 25 | 10 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 25 | 0 | 0 | 39.791 | 239.25 | 9.2846 | 86.148 | -75 | -1.0406 | 85.8878 | 1.5763 | 26.5763 | 8.4242 | 0 | 8.4242 | 69.08 | 8.4242 | 8/27/7:00
8 | 27 | 1900-01-07 | 21.1 | 108 | 3 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 108 | 0 | 0 | 39.791 | 239.2917 | 9.2695 | 86.148 | -75 | -1.0279 | 100.891 | -0.12059 | 107.8794 | 34.1959 | 0 | 34.1959 | 69.98 | 34.1959 | 8/27/8:00
8 | 27 | 1900-01-08 | 21.7 | 133 | 2 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 133 | 0 | 0 | 39.791 | 239.3333 | 9.2543 | 86.148 | -75 | -1.0152 | 115.8942 | -0.45655 | 132.5435 | 42.014 | 0 | 42.014 | 71.06 | 42.014 | 8/27/9:00
8 | 27 | 1900-01-09 | 21.7 | 268 | 10 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 268 | 0 | 0 | 39.791 | 239.375 | 9.2391 | 86.148 | -75 | -1.0025 | 130.8974 | -3.9379 | 264.0621 | 83.7031 | 0 | 83.7031 | 71.06 | 83.7031 | 8/27/10:00
8 | 27 | 1900-01-10 | 21.7 | 179 | 3 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 179 | 0 | 0 | 39.791 | 239.4167 | 9.224 | 86.148 | -75 | -0.98981 | 145.9005 | -1.5764 | 177.4236 | 56.2402 | 0 | 56.2402 | 71.06 | 56.2402 | 8/27/11:00
8 | 27 | 1900-01-11 | 22.2 | 209 | 1 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 209 | 0 | 0 | 39.791 | 239.4583 | 9.2088 | 86.148 | -75 | -0.97708 | 160.9037 | -0.61432 | 208.3857 | 66.0546 | 0 | 66.0546 | 71.96 | 66.0546 | 8/27/12:00
8 | 27 | 1900-01-12 | 21.7 | 364 | 7 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 364 | 0 | 0 | 39.791 | 239.5 | 9.1936 | 86.148 | -75 | -0.96434 | 175.9069 | -4.5803 | 359.4197 | 113.9298 | 0 | 113.9298 | 71.06 | 113.9298 | 8/27/13:00
8 | 27 | 1900-01-13 | 22.2 | 218 | 7 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 218 | 0 | 0 | 39.791 | 239.5417 | 9.1785 | 86.148 | -75 | -0.95159 | 190.9101 | -4.4993 | 213.5007 | 67.676 | 0 | 67.676 | 71.96 | 67.676 | 8/27/14:00
8 | 27 | 1900-01-14 | 22.2 | 219 | 3 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 219 | 0 | 0 | 39.791 | 239.5833 | 9.1633 | 86.148 | -75 | -0.93882 | 205.9133 | -1.7412 | 217.2588 | 68.8673 | 0 | 68.8673 | 71.96 | 68.8673 | 8/27/15:00
8 | 27 | 1900-01-15 | 22.2 | 350 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 350 | 0 | 0 | 39.791 | 239.625 | 9.1481 | 86.148 | -75 | -0.92604 | 220.9165 | 0 | 350 | 110.9439 | 0 | 110.9439 | 71.96 | 110.9439 | 8/27/16:00
8 | 27 | 1900-01-16 | 21.7 | 272 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 272 | 0 | 0 | 39.791 | 239.6667 | 9.1329 | 86.148 | -75 | -0.91325 | 235.9197 | 0 | 272 | 86.2192 | 0 | 86.2192 | 71.06 | 86.2192 | 8/27/17:00
8 | 27 | 1900-01-17 | 21.7 | 160 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 160 | 0 | 0 | 39.791 | 239.7083 | 9.1177 | 86.148 | -75 | -0.90045 | 250.9229 | 0 | 160 | 50.7172 | 0 | 50.7172 | 71.06 | 50.7172 | 8/27/18:00
8 | 27 | 1900-01-18 | 20.6 | 38 | 1 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 38 | 0 | 0 | 39.791 | 239.75 | 9.1025 | 86.148 | -75 | -0.88764 | 265.9261 | 0.047346 | 38.0473 | 12.0603 | 0 | 12.0603 | 69.08 | 12.0603 | 8/27/19:00
8 | 27 | 1900-01-19 | 20 | 7 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 7 | 0 | 0 | 39.791 | 239.7917 | 9.0873 | 86.148 | -75 | -0.87482 | 280.9293 | 0 | 7 | 2.2189 | 0 | 2.2189 | 68 | 2.2189 | 8/27/20:00
8 | 27 | 1900-01-20 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 239.8333 | 9.0721 | 86.148 | -75 | -0.86198 | 295.9325 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/27/21:00
8 | 27 | 1900-01-21 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 239.875 | 9.0569 | 86.148 | -75 | -0.84914 | 310.9357 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 8/27/22:00
8 | 27 | 1900-01-22 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 239.9167 | 9.0417 | 86.148 | -75 | -0.83628 | 325.9389 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 8/27/23:00
8 | 27 | 1900-01-23 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 239.9583 | 9.0265 | 86.148 | -75 | -0.82341 | 340.9421 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/27/24:00
8 | 28 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 240 | 9.0113 | 86.148 | -75 | -0.81053 | -4.0546 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/28/1:00
8 | 28 | 1900-01-01 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 240.0417 | 8.996 | 86.148 | -75 | -0.79764 | 10.9486 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/28/2:00
8 | 28 | 1900-01-02 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 240.0833 | 8.9808 | 86.148 | -75 | -0.78473 | 25.9518 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/28/3:00
8 | 28 | 1900-01-03 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 240.125 | 8.9656 | 86.148 | -75 | -0.77182 | 40.955 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/28/4:00
8 | 28 | 1900-01-04 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 240.1667 | 8.9503 | 86.148 | -75 | -0.75889 | 55.9583 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/28/5:00
8 | 28 | 1900-01-05 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 240.2083 | 8.9351 | 86.148 | -75 | -0.74595 | 70.9615 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/28/6:00
8 | 28 | 1900-01-06 | 17.8 | 17 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 17 | 0 | 0 | 39.791 | 240.25 | 8.9199 | 86.148 | -75 | -0.733 | 85.9647 | 0 | 17 | 5.3887 | 0 | 5.3887 | 64.04 | 5.3887 | 8/28/7:00
8 | 28 | 1900-01-07 | 17.8 | 112 | 1 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 112 | 0 | 0 | 39.791 | 240.2917 | 8.9046 | 86.148 | -75 | -0.72004 | 100.968 | -0.045367 | 111.9546 | 35.4877 | 0 | 35.4877 | 64.04 | 35.4877 | 8/28/8:00
8 | 28 | 1900-01-08 | 18.3 | 205 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 205 | 0 | 0 | 39.791 | 240.3333 | 8.8894 | 86.148 | -75 | -0.70707 | 115.9712 | 0 | 205 | 64.9814 | 0 | 64.9814 | 64.94 | 64.9814 | 8/28/9:00
8 | 28 | 1900-01-09 | 19.4 | 288 | 1 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 288 | 0 | 0 | 39.791 | 240.375 | 8.8741 | 86.148 | -75 | -0.69409 | 130.9745 | -0.39909 | 287.6009 | 91.1645 | 0 | 91.1645 | 66.92 | 91.1645 | 8/28/10:00
8 | 28 | 1900-01-10 | 18.9 | 389 | 1 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 389 | 0 | 0 | 39.791 | 240.4167 | 8.8588 | 86.148 | -75 | -0.68109 | 145.9777 | -0.5307 | 388.4693 | 123.138 | 0 | 123.138 | 66.02 | 123.138 | 8/28/11:00
8 | 28 | 1900-01-11 | 18.9 | 387 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 387 | 0 | 0 | 39.791 | 240.4583 | 8.8436 | 86.148 | -75 | -0.66809 | 160.981 | 0 | 387 | 122.6722 | 0 | 122.6722 | 66.02 | 122.6722 | 8/28/12:00
8 | 28 | 1900-01-12 | 18.9 | 460 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 460 | 0 | 0 | 39.791 | 240.5 | 8.8283 | 86.148 | -75 | -0.65507 | 175.9842 | 0 | 460 | 145.812 | 0 | 145.812 | 66.02 | 145.812 | 8/28/13:00
8 | 28 | 1900-01-13 | 20.6 | 418 | 1 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 418 | 0 | 0 | 39.791 | 240.5417 | 8.813 | 86.148 | -75 | -0.64204 | 190.9875 | -0.64734 | 417.3527 | 132.2935 | 0 | 132.2935 | 69.08 | 132.2935 | 8/28/14:00
8 | 28 | 1900-01-14 | 21.7 | 401 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 401 | 0 | 0 | 39.791 | 240.5833 | 8.7978 | 86.148 | -75 | -0.629 | 205.9907 | 0 | 401 | 127.11 | 0 | 127.11 | 71.06 | 127.11 | 8/28/15:00
8 | 28 | 1900-01-15 | 20.6 | 316 | 2 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 316 | 0 | 0 | 39.791 | 240.625 | 8.7825 | 86.148 | -75 | -0.61595 | 220.994 | -0.95089 | 315.0491 | 99.8651 | 0 | 99.8651 | 69.08 | 99.8651 | 8/28/16:00
8 | 28 | 1900-01-16 | 20.6 | 257 | 1 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 257 | 0 | 0 | 39.791 | 240.6667 | 8.7672 | 86.148 | -75 | -0.60289 | 235.9973 | -0.32714 | 256.6729 | 81.3608 | 0 | 81.3608 | 69.08 | 81.3608 | 8/28/17:00
8 | 28 | 1900-01-17 | 21.7 | 122 | 268 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 122 | 0 | 0 | 39.791 | 240.7083 | 8.7519 | 86.148 | -75 | -0.58982 | 251.0005 | -40.1634 | 81.8366 | 25.9408 | 0 | 25.9408 | 71.06 | 25.9408 | 8/28/18:00
8 | 28 | 1900-01-18 | 20 | 47 | 391 | 68 | 0 | 1 | 0 | 68 | 0 | 47 | 0 | 0 | 39.791 | 240.75 | 8.7366 | 86.148 | -75 | -0.57673 | 266.0038 | 17.3144 | 64.3144 | 20.3865 | 0 | 20.3865 | 68 | 20.3865 | 8/28/19:00
8 | 28 | 1900-01-19 | 18.3 | 10 | 7 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 10 | 0 | 0 | 39.791 | 240.7917 | 8.7213 | 86.148 | -75 | -0.56364 | 281.0071 | 1.6944 | 11.6944 | 3.7069 | 0 | 3.7069 | 64.94 | 3.7069 | 8/28/20:00
8 | 28 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 240.8333 | 8.706 | 86.148 | -75 | -0.55053 | 296.0104 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/28/21:00
8 | 28 | 1900-01-21 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 240.875 | 8.6907 | 86.148 | -75 | -0.53742 | 311.0136 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 8/28/22:00
8 | 28 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 240.9167 | 8.6754 | 86.148 | -75 | -0.52429 | 326.0169 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 8/28/23:00
8 | 28 | 1900-01-23 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 240.9583 | 8.6601 | 86.148 | -75 | -0.51115 | 341.0202 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 8/28/24:00
8 | 29 | 1899-12-31 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 241 | 8.6448 | 86.148 | -75 | -0.498 | -3.9765 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 8/29/1:00
8 | 29 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 241.0417 | 8.6295 | 86.148 | -75 | -0.48484 | 11.0268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/29/2:00
8 | 29 | 1900-01-02 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 241.0833 | 8.6142 | 86.148 | -75 | -0.47167 | 26.0301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/29/3:00
8 | 29 | 1900-01-03 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 241.125 | 8.5988 | 86.148 | -75 | -0.45849 | 41.0334 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 8/29/4:00
8 | 29 | 1900-01-04 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 241.1667 | 8.5835 | 86.148 | -75 | -0.44529 | 56.0367 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 8/29/5:00
8 | 29 | 1900-01-05 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 241.2083 | 8.5682 | 86.148 | -75 | -0.43209 | 71.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8/29/6:00
8 | 29 | 1900-01-06 | 13.9 | 24 | 85 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 24 | 0 | 0 | 39.791 | 241.25 | 8.5528 | 86.148 | -75 | -0.41888 | 86.0433 | 12.5469 | 36.5469 | 11.5847 | 0 | 11.5847 | 57.02 | 11.5847 | 8/29/7:00
8 | 29 | 1900-01-07 | 13.9 | 58 | 442 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 58 | 0 | 0 | 39.791 | 241.2917 | 8.5375 | 86.148 | -75 | -0.40565 | 101.0466 | -22.359 | 35.641 | 11.2976 | 0 | 11.2976 | 57.02 | 11.2976 | 8/29/8:00
8 | 29 | 1900-01-08 | 16.7 | 113 | 571 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 113 | 0 | 0 | 39.791 | 241.3333 | 8.5221 | 86.148 | -75 | -0.39241 | 116.0499 | -136.3959 | -23.3959 | -7.4161 | 0 | -7.4161 | 62.06 | -7.4161 | 8/29/9:00
8 | 29 | 1900-01-09 | 19.4 | 110 | 758 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 110 | 0 | 0 | 39.791 | 241.375 | 8.5068 | 86.148 | -75 | -0.37917 | 131.0532 | -306.5506 | -196.5506 | -62.3031 | 0 | -62.3031 | 66.92 | -62.3031 | 8/29/10:00
8 | 29 | 1900-01-10 | 21.1 | 126 | 821 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 126 | 0 | 0 | 39.791 | 241.4167 | 8.4914 | 86.148 | -75 | -0.36591 | 146.0565 | -440.0177 | -314.0177 | -99.5381 | 0 | -99.5381 | 69.98 | -99.5381 | 8/29/11:00
8 | 29 | 1900-01-11 | 22.8 | 136 | 838 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 136 | 0 | 0 | 39.791 | 241.4583 | 8.4761 | 86.148 | -75 | -0.35264 | 161.0598 | -523.3409 | -387.3409 | -122.7803 | 0 | -122.7803 | 73.04 | -122.7803 | 8/29/12:00
8 | 29 | 1900-01-12 | 23.3 | 141 | 864 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 141 | 0 | 0 | 39.791 | 241.5 | 8.4607 | 86.148 | -75 | -0.33936 | 176.0632 | -573.7529 | -432.7529 | -137.1751 | 0 | -137.1751 | 73.94 | -137.1751 | 8/29/13:00
8 | 29 | 1900-01-13 | 24.4 | 170 | 769 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 170 | 0 | 0 | 39.791 | 241.5417 | 8.4454 | 86.148 | -75 | -0.32607 | 191.0665 | -501.3313 | -331.3313 | -105.0262 | 0 | -105.0262 | 75.92 | -105.0262 | 8/29/14:00
8 | 29 | 1900-01-14 | 25.6 | 274 | 395 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 274 | 0 | 0 | 39.791 | 241.5833 | 8.43 | 86.148 | -75 | -0.31277 | 206.0698 | -232.6266 | 41.3734 | 13.1147 | 0 | 13.1147 | 78.08 | 13.1147 | 8/29/15:00
8 | 29 | 1900-01-15 | 25.6 | 211 | 452 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 211 | 0 | 0 | 39.791 | 241.625 | 8.4146 | 86.148 | -75 | -0.29946 | 221.0731 | -216.6771 | -5.6771 | -1.7995 | 0 | -1.7995 | 78.08 | -1.7995 | 8/29/16:00
8 | 29 | 1900-01-16 | 25 | 135 | 649 | 77 | 0 | 1 | 0 | 77 | 0 | 135 | 0 | 0 | 39.791 | 241.6667 | 8.3992 | 86.148 | -75 | -0.28614 | 236.0765 | -214.6514 | -79.6514 | -25.2481 | 0 | -25.2481 | 77 | -25.2481 | 8/29/17:00
8 | 29 | 1900-01-17 | 24.4 | 95 | 508 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 95 | 0 | 0 | 39.791 | 241.7083 | 8.3839 | 86.148 | -75 | -0.27281 | 251.0798 | -77.8122 | 17.1878 | 5.4482 | 0 | 5.4482 | 75.92 | 5.4482 | 8/29/18:00
8 | 29 | 1900-01-18 | 22.8 | 51 | 268 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 51 | 0 | 0 | 39.791 | 241.75 | 8.3685 | 86.148 | -75 | -0.25947 | 266.0831 | 11.0455 | 62.0455 | 19.6673 | 0 | 19.6673 | 73.04 | 19.6673 | 8/29/19:00
8 | 29 | 1900-01-19 | 18.9 | 8 | 13 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 8 | 0 | 0 | 39.791 | 241.7917 | 8.3531 | 86.148 | -75 | -0.24611 | 281.0865 | 3.1091 | 11.1091 | 3.5214 | 0 | 3.5214 | 66.02 | 3.5214 | 8/29/20:00
8 | 29 | 1900-01-20 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 241.8333 | 8.3377 | 86.148 | -75 | -0.23275 | 296.0898 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/29/21:00
8 | 29 | 1900-01-21 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 241.875 | 8.3223 | 86.148 | -75 | -0.21938 | 311.0932 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 8/29/22:00
8 | 29 | 1900-01-22 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 241.9167 | 8.3069 | 86.148 | -75 | -0.20599 | 326.0965 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/29/23:00
8 | 29 | 1900-01-23 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 241.9583 | 8.2915 | 86.148 | -75 | -0.1926 | 341.0999 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 8/29/24:00
8 | 30 | 1899-12-31 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 242 | 8.2761 | 86.148 | -75 | -0.17919 | -3.8968 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 8/30/1:00
8 | 30 | 1900-01-01 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 242.0417 | 8.2607 | 86.148 | -75 | -0.16578 | 11.1066 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 8/30/2:00
8 | 30 | 1900-01-02 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 242.0833 | 8.2453 | 86.148 | -75 | -0.15235 | 26.1099 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 8/30/3:00
8 | 30 | 1900-01-03 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 242.125 | 8.2299 | 86.148 | -75 | -0.13891 | 41.1133 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 8/30/4:00
8 | 30 | 1900-01-04 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 242.1667 | 8.2144 | 86.148 | -75 | -0.12547 | 56.1166 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 8/30/5:00
8 | 30 | 1900-01-05 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 242.2083 | 8.199 | 86.148 | -75 | -0.11201 | 71.12 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 8/30/6:00
8 | 30 | 1900-01-06 | 13.9 | 23 | 102 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 23 | 0 | 0 | 39.791 | 242.25 | 8.1836 | 86.148 | -75 | -0.098543 | 86.1234 | 14.537 | 37.537 | 11.8986 | 0 | 11.8986 | 57.02 | 11.8986 | 8/30/7:00
8 | 30 | 1900-01-07 | 16.7 | 76 | 307 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 76 | 0 | 0 | 39.791 | 242.2917 | 8.1682 | 86.148 | -75 | -0.085066 | 101.1267 | -17.1458 | 58.8542 | 18.6558 | 0 | 18.6558 | 62.06 | 18.6558 | 8/30/8:00
8 | 30 | 1900-01-08 | 19.4 | 89 | 622 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 89 | 0 | 0 | 39.791 | 242.3333 | 8.1527 | 86.148 | -75 | -0.071579 | 116.1301 | -151.9088 | -62.9088 | -19.941 | 0 | -19.941 | 66.92 | -19.941 | 8/30/9:00
8 | 30 | 1900-01-09 | 22.2 | 145 | 642 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 145 | 0 | 0 | 39.791 | 242.375 | 8.1373 | 86.148 | -75 | -0.058081 | 131.1335 | -263.0776 | -118.0776 | -37.4286 | 0 | -37.4286 | 71.96 | -37.4286 | 8/30/10:00
8 | 30 | 1900-01-10 | 23.3 | 240 | 561 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 240 | 0 | 0 | 39.791 | 242.4167 | 8.1218 | 86.148 | -75 | -0.044573 | 146.1369 | -303.6285 | -63.6285 | -20.1691 | 0 | -20.1691 | 73.94 | -20.1691 | 8/30/11:00
8 | 30 | 1900-01-11 | 25 | 244 | 453 | 77 | 0 | 1 | 0 | 77 | 0 | 244 | 0 | 0 | 39.791 | 242.4583 | 8.1064 | 86.148 | -75 | -0.031055 | 161.1402 | -285.2178 | -41.2178 | -13.0653 | 0 | -13.0653 | 77 | -13.0653 | 8/30/12:00
8 | 30 | 1900-01-12 | 26.1 | 291 | 521 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 291 | 0 | 0 | 39.791 | 242.5 | 8.091 | 86.148 | -75 | -0.017527 | 176.1436 | -348.5166 | -57.5166 | -18.2318 | 0 | -18.2318 | 78.98 | -18.2318 | 8/30/13:00
8 | 30 | 1900-01-13 | 26.7 | 269 | 513 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 269 | 0 | 0 | 39.791 | 242.5417 | 8.0755 | 86.148 | -75 | -0.0039891 | 191.147 | -336.7886 | -67.7886 | -21.4878 | 0 | -21.4878 | 80.06 | -21.4878 | 8/30/14:00
8 | 30 | 1900-01-14 | 26.7 | 234 | 680 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 234 | 0 | 0 | 39.791 | 242.5833 | 8.06 | 86.148 | -75 | 0.0095591 | 206.1504 | -403.3663 | -169.3663 | -53.6862 | 0 | -53.6862 | 80.06 | -53.6862 | 8/30/15:00
8 | 30 | 1900-01-15 | 26.7 | 191 | 651 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 191 | 0 | 0 | 39.791 | 242.625 | 8.0446 | 86.148 | -75 | 0.023117 | 221.1538 | -314.6257 | -123.6257 | -39.1872 | 0 | -39.1872 | 80.06 | -39.1872 | 8/30/16:00
8 | 30 | 1900-01-16 | 26.1 | 161 | 542 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 161 | 0 | 0 | 39.791 | 242.6667 | 8.0291 | 86.148 | -75 | 0.036686 | 236.1572 | -181.2121 | -20.2121 | -6.4069 | 0 | -6.4069 | 78.98 | -6.4069 | 8/30/17:00
8 | 30 | 1900-01-17 | 25.6 | 130 | 347 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 130 | 0 | 0 | 39.791 | 242.7083 | 8.0137 | 86.148 | -75 | 0.050264 | 251.1606 | -54.299 | 75.701 | 23.9959 | 0 | 23.9959 | 78.08 | 23.9959 | 8/30/18:00
8 | 30 | 1900-01-18 | 23.9 | 55 | 254 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 55 | 0 | 0 | 39.791 | 242.75 | 7.9982 | 86.148 | -75 | 0.063852 | 266.164 | 9.6884 | 64.6884 | 20.5051 | 0 | 20.5051 | 75.02 | 20.5051 | 8/30/19:00
8 | 30 | 1900-01-19 | 19.4 | 8 | 11 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 8 | 0 | 0 | 39.791 | 242.7917 | 7.9827 | 86.148 | -75 | 0.07745 | 281.1674 | 2.5988 | 10.5988 | 3.3596 | 0 | 3.3596 | 66.92 | 3.3596 | 8/30/20:00
8 | 30 | 1900-01-20 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 242.8333 | 7.9672 | 86.148 | -75 | 0.091058 | 296.1708 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 8/30/21:00
8 | 30 | 1900-01-21 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 242.875 | 7.9518 | 86.148 | -75 | 0.10468 | 311.1742 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 8/30/22:00
8 | 30 | 1900-01-22 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 242.9167 | 7.9363 | 86.148 | -75 | 0.1183 | 326.1776 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/30/23:00
8 | 30 | 1900-01-23 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 242.9583 | 7.9208 | 86.148 | -75 | 0.13194 | 341.181 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/30/24:00
8 | 31 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 243 | 7.9053 | 86.148 | -75 | 0.14559 | -3.8156 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/31/1:00
8 | 31 | 1900-01-01 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 243.0417 | 7.8898 | 86.148 | -75 | 0.15925 | 11.1878 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/31/2:00
8 | 31 | 1900-01-02 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 243.0833 | 7.8743 | 86.148 | -75 | 0.17291 | 26.1912 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 8/31/3:00
8 | 31 | 1900-01-03 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 243.125 | 7.8588 | 86.148 | -75 | 0.18659 | 41.1946 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/31/4:00
8 | 31 | 1900-01-04 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 243.1667 | 7.8433 | 86.148 | -75 | 0.20028 | 56.1981 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 8/31/5:00
8 | 31 | 1900-01-05 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 243.2083 | 7.8278 | 86.148 | -75 | 0.21397 | 71.2015 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 8/31/6:00
8 | 31 | 1900-01-06 | 17.2 | 10 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 10 | 0 | 0 | 39.791 | 243.25 | 7.8123 | 86.148 | -75 | 0.22768 | 86.2049 | 0 | 10 | 3.1698 | 0 | 3.1698 | 62.96 | 3.1698 | 8/31/7:00
8 | 31 | 1900-01-07 | 17.8 | 86 | 3 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 86 | 0 | 0 | 39.791 | 243.2917 | 7.7967 | 86.148 | -75 | 0.2414 | 101.2083 | -0.18347 | 85.8165 | 27.2023 | 0 | 27.2023 | 64.04 | 27.2023 | 8/31/8:00
8 | 31 | 1900-01-08 | 18.3 | 146 | 11 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 146 | 0 | 0 | 39.791 | 243.3333 | 7.7812 | 86.148 | -75 | 0.25512 | 116.2118 | -2.7458 | 143.2542 | 45.4091 | 0 | 45.4091 | 64.94 | 45.4091 | 8/31/9:00
8 | 31 | 1900-01-09 | 22.2 | 247 | 348 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 247 | 0 | 0 | 39.791 | 243.375 | 7.7657 | 86.148 | -75 | 0.26886 | 131.2152 | -144.4757 | 102.5243 | 32.4984 | 0 | 32.4984 | 71.96 | 32.4984 | 8/31/10:00
8 | 31 | 1900-01-10 | 22.8 | 222 | 630 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 222 | 0 | 0 | 39.791 | 243.4167 | 7.7502 | 86.148 | -75 | 0.2826 | 146.2187 | -344.3047 | -122.3047 | -38.7685 | 0 | -38.7685 | 73.04 | -38.7685 | 8/31/11:00
8 | 31 | 1900-01-11 | 23.9 | 230 | 819 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 230 | 0 | 0 | 39.791 | 243.4583 | 7.7346 | 86.148 | -75 | 0.29635 | 161.2221 | -519.8469 | -289.8469 | -91.8764 | 0 | -91.8764 | 75.02 | -91.8764 | 8/31/12:00
8 | 31 | 1900-01-12 | 25 | 246 | 827 | 77 | 0 | 1 | 0 | 77 | 0 | 246 | 0 | 0 | 39.791 | 243.5 | 7.7191 | 86.148 | -75 | 0.31012 | 176.2255 | -557.2396 | -311.2396 | -98.6575 | 0 | -98.6575 | 77 | -98.6575 | 8/31/13:00
8 | 31 | 1900-01-13 | 24.4 | 217 | 604 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 217 | 0 | 0 | 39.791 | 243.5417 | 7.7036 | 86.148 | -75 | 0.32389 | 191.229 | -399.2944 | -182.2944 | -57.7841 | 0 | -57.7841 | 75.92 | -57.7841 | 8/31/14:00
8 | 31 | 1900-01-14 | 25 | 210 | 587 | 77 | 0 | 1 | 0 | 77 | 0 | 210 | 0 | 0 | 39.791 | 243.5833 | 7.688 | 86.148 | -75 | 0.33767 | 206.2324 | -350.6939 | -140.6939 | -44.5975 | 0 | -44.5975 | 77 | -44.5975 | 8/31/15:00
8 | 31 | 1900-01-15 | 24.4 | 106 | 831 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 106 | 0 | 0 | 39.791 | 243.625 | 7.6725 | 86.148 | -75 | 0.35147 | 221.2359 | -404.8702 | -298.8702 | -94.7366 | 0 | -94.7366 | 75.92 | -94.7366 | 8/31/16:00
8 | 31 | 1900-01-16 | 24.4 | 88 | 762 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 88 | 0 | 0 | 39.791 | 243.6667 | 7.6569 | 86.148 | -75 | 0.36527 | 236.2393 | -257.5026 | -169.5026 | -53.7294 | 0 | -53.7294 | 75.92 | -53.7294 | 8/31/17:00
8 | 31 | 1900-01-17 | 23.3 | 65 | 633 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 65 | 0 | 0 | 39.791 | 243.7083 | 7.6414 | 86.148 | -75 | 0.37908 | 251.2428 | -101.1443 | -36.1443 | -11.4571 | 0 | -11.4571 | 73.94 | -11.4571 | 8/31/18:00
8 | 31 | 1900-01-18 | 21.1 | 39 | 354 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 39 | 0 | 0 | 39.791 | 243.75 | 7.6258 | 86.148 | -75 | 0.3929 | 266.2462 | 12.4142 | 51.4142 | 16.2974 | 0 | 16.2974 | 69.98 | 16.2974 | 8/31/19:00
8 | 31 | 1900-01-19 | 17.2 | 6 | 15 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 6 | 0 | 0 | 39.791 | 243.7917 | 7.6103 | 86.148 | -75 | 0.40673 | 281.2497 | 3.5 | 9.5 | 3.0113 | 0 | 3.0113 | 62.96 | 3.0113 | 8/31/20:00
8 | 31 | 1900-01-20 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 243.8333 | 7.5947 | 86.148 | -75 | 0.42057 | 296.2531 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 8/31/21:00
8 | 31 | 1900-01-21 | 14.6 | 0 | 0 | 58.28 | 0 | 1 | 0 | 58.28 | 0 | 0 | 0 | 0 | 39.791 | 243.875 | 7.5792 | 86.148 | -75 | 0.43442 | 311.2566 | 0 | 0 | 0 | 0 | 0 | 58.28 | 0 | 8/31/22:00
8 | 31 | 1900-01-22 | 14.7 | 0 | 0 | 58.46 | 0 | 1 | 0 | 58.46 | 0 | 0 | 0 | 0 | 39.791 | 243.9167 | 7.5636 | 86.148 | -75 | 0.44827 | 326.2601 | 0 | 0 | 0 | 0 | 0 | 58.46 | 0 | 8/31/23:00
8 | 31 | 1900-01-23 | 14.9 | 0 | 0 | 58.82 | 0 | 1 | 0 | 58.82 | 0 | 0 | 0 | 0 | 39.791 | 243.9583 | 7.548 | 86.148 | -75 | 0.46214 | 341.2635 | 0 | 0 | 0 | 0 | 0 | 58.82 | 0 | 8/31/24:00
9 | 1 | 1899-12-31 | 15.1 | 0 | 0 | 59.18 | 0 | 1 | 0 | 59.18 | 0 | 0 | 0 | 0 | 39.791 | 244 | 7.5324 | 86.148 | -75 | 0.47602 | -3.733 | 0 | 0 | 0 | 0 | 0 | 59.18 | 0 | 9/1/1:00
9 | 1 | 1900-01-01 | 15.3 | 0 | 0 | 59.54 | 0 | 1 | 0 | 59.54 | 0 | 0 | 0 | 0 | 39.791 | 244.0417 | 7.5169 | 86.148 | -75 | 0.4899 | 11.2705 | 0 | 0 | 0 | 0 | 0 | 59.54 | 0 | 9/1/2:00
9 | 1 | 1900-01-02 | 15.4 | 0 | 0 | 59.72 | 0 | 1 | 0 | 59.72 | 0 | 0 | 0 | 0 | 39.791 | 244.0833 | 7.5013 | 86.148 | -75 | 0.5038 | 26.2739 | 0 | 0 | 0 | 0 | 0 | 59.72 | 0 | 9/1/3:00
9 | 1 | 1900-01-03 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 244.125 | 7.4857 | 86.148 | -75 | 0.5177 | 41.2774 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/1/4:00
9 | 1 | 1900-01-04 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 244.1667 | 7.4701 | 86.148 | -75 | 0.53162 | 56.2809 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/1/5:00
9 | 1 | 1900-01-05 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 244.2083 | 7.4545 | 86.148 | -75 | 0.54554 | 71.2844 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 9/1/6:00
9 | 1 | 1900-01-06 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 244.25 | 7.4389 | 86.148 | -75 | 0.55947 | 86.2879 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/1/7:00
9 | 1 | 1900-01-07 | 15.6 | 116 | 256 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 116 | 0 | 0 | 39.791 | 244.2917 | 7.4233 | 86.148 | -75 | 0.57341 | 101.2914 | -17.0242 | 98.9758 | 31.3736 | 0 | 31.3736 | 60.08 | 31.3736 | 9/1/8:00
9 | 1 | 1900-01-08 | 17.2 | 187 | 69 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 187 | 0 | 0 | 39.791 | 244.3333 | 7.4077 | 86.148 | -75 | 0.58736 | 116.2948 | -17.5972 | 169.4028 | 53.6977 | 0 | 53.6977 | 62.96 | 53.6977 | 9/1/9:00
9 | 1 | 1900-01-09 | 18.9 | 277 | 73 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 277 | 0 | 0 | 39.791 | 244.375 | 7.3921 | 86.148 | -75 | 0.60132 | 131.2983 | -30.7011 | 246.2989 | 78.0725 | 0 | 78.0725 | 66.02 | 78.0725 | 9/1/10:00
9 | 1 | 1900-01-10 | 20.6 | 242 | 563 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 242 | 0 | 0 | 39.791 | 244.4167 | 7.3765 | 86.148 | -75 | 0.61528 | 146.3018 | -310.6721 | -68.6721 | -21.7678 | 0 | -21.7678 | 69.08 | -21.7678 | 9/1/11:00
9 | 1 | 1900-01-11 | 21.1 | 377 | 241 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 377 | 0 | 0 | 39.791 | 244.4583 | 7.3609 | 86.148 | -75 | 0.62926 | 161.3053 | -154.2041 | 222.7959 | 70.6224 | 0 | 70.6224 | 69.98 | 70.6224 | 9/1/12:00
9 | 1 | 1900-01-12 | 22.2 | 386 | 264 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 386 | 0 | 0 | 39.791 | 244.5 | 7.3453 | 86.148 | -75 | 0.64325 | 176.3088 | -179.1704 | 206.8296 | 65.5614 | 0 | 65.5614 | 71.96 | 65.5614 | 9/1/13:00
9 | 1 | 1900-01-13 | 22.8 | 364 | 359 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 364 | 0 | 0 | 39.791 | 244.5417 | 7.3297 | 86.148 | -75 | 0.65724 | 191.3123 | -238.9686 | 125.0314 | 39.6328 | 0 | 39.6328 | 73.04 | 39.6328 | 9/1/14:00
9 | 1 | 1900-01-14 | 23.9 | 331 | 346 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 331 | 0 | 0 | 39.791 | 244.5833 | 7.3141 | 86.148 | -75 | 0.67124 | 206.3158 | -208.1785 | 122.8215 | 38.9323 | 0 | 38.9323 | 75.02 | 38.9323 | 9/1/15:00
9 | 1 | 1900-01-15 | 25 | 236 | 498 | 77 | 0 | 1 | 0 | 77 | 0 | 236 | 0 | 0 | 39.791 | 244.625 | 7.2984 | 86.148 | -75 | 0.68526 | 221.3193 | -244.5728 | -8.5728 | -2.7174 | 0 | -2.7174 | 77 | -2.7174 | 9/1/16:00
9 | 1 | 1900-01-16 | 24.4 | 240 | 211 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 240 | 0 | 0 | 39.791 | 244.6667 | 7.2828 | 86.148 | -75 | 0.69928 | 236.3228 | -72.059 | 167.941 | 53.2344 | 0 | 53.2344 | 75.92 | 53.2344 | 9/1/17:00
9 | 1 | 1900-01-17 | 23.3 | 115 | 451 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 115 | 0 | 0 | 39.791 | 244.7083 | 7.2672 | 86.148 | -75 | 0.71331 | 251.3263 | -73.5522 | 41.4478 | 13.1382 | 0 | 13.1382 | 73.94 | 13.1382 | 9/1/18:00
9 | 1 | 1900-01-18 | 21.7 | 51 | 141 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 51 | 0 | 0 | 39.791 | 244.75 | 7.2516 | 86.148 | -75 | 0.72735 | 266.3298 | 4.5106 | 55.5106 | 17.5959 | 0 | 17.5959 | 71.06 | 17.5959 | 9/1/19:00
9 | 1 | 1900-01-19 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 244.7917 | 7.2359 | 86.148 | -75 | 0.74139 | 281.3333 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/1/20:00
9 | 1 | 1900-01-20 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 244.8333 | 7.2203 | 86.148 | -75 | 0.75545 | 296.3369 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/1/21:00
9 | 1 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 244.875 | 7.2046 | 86.148 | -75 | 0.76952 | 311.3404 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/1/22:00
9 | 1 | 1900-01-22 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 244.9167 | 7.189 | 86.148 | -75 | 0.78359 | 326.3439 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/1/23:00
9 | 1 | 1900-01-23 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 244.9583 | 7.1733 | 86.148 | -75 | 0.79767 | 341.3474 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/1/24:00
9 | 2 | 1899-12-31 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 245 | 7.1577 | 86.148 | -75 | 0.81176 | -3.6491 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/2/1:00
9 | 2 | 1900-01-01 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 245.0417 | 7.142 | 86.148 | -75 | 0.82586 | 11.3545 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/2/2:00
9 | 2 | 1900-01-02 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 245.0833 | 7.1264 | 86.148 | -75 | 0.83997 | 26.358 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/2/3:00
9 | 2 | 1900-01-03 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 245.125 | 7.1107 | 86.148 | -75 | 0.85409 | 41.3615 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/2/4:00
9 | 2 | 1900-01-04 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 245.1667 | 7.095 | 86.148 | -75 | 0.86821 | 56.3651 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/2/5:00
9 | 2 | 1900-01-05 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 245.2083 | 7.0794 | 86.148 | -75 | 0.88235 | 71.3686 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/2/6:00
9 | 2 | 1900-01-06 | 16.1 | 6 | 106 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 6 | 0 | 0 | 39.791 | 245.25 | 7.0637 | 86.148 | -75 | 0.89649 | 86.3721 | 13.457 | 19.457 | 6.1675 | 0 | 6.1675 | 60.98 | 6.1675 | 9/2/7:00
9 | 2 | 1900-01-07 | 17.2 | 105 | 311 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 105 | 0 | 0 | 39.791 | 245.2917 | 7.048 | 86.148 | -75 | 0.91064 | 101.3757 | -22.3559 | 82.6441 | 26.1967 | 0 | 26.1967 | 62.96 | 26.1967 | 9/2/8:00
9 | 2 | 1900-01-08 | 19.4 | 139 | 512 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 139 | 0 | 0 | 39.791 | 245.3333 | 7.0324 | 86.148 | -75 | 0.9248 | 116.3792 | -133.3651 | 5.6349 | 1.7862 | 0 | 1.7862 | 66.92 | 1.7862 | 9/2/9:00
9 | 2 | 1900-01-09 | 21.7 | 144 | 654 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 144 | 0 | 0 | 39.791 | 245.375 | 7.0167 | 86.148 | -75 | 0.93897 | 131.3827 | -278.5933 | -134.5933 | -42.6637 | 0 | -42.6637 | 71.06 | -42.6637 | 9/2/10:00
9 | 2 | 1900-01-10 | 22.8 | 199 | 600 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 199 | 0 | 0 | 39.791 | 245.4167 | 7.001 | 86.148 | -75 | 0.95314 | 146.3863 | -334.2747 | -135.2747 | -42.8797 | 0 | -42.8797 | 73.04 | -42.8797 | 9/2/11:00
9 | 2 | 1900-01-11 | 23.9 | 279 | 524 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 279 | 0 | 0 | 39.791 | 245.4583 | 6.9853 | 86.148 | -75 | 0.96733 | 161.3898 | -337.9639 | -58.9639 | -18.6905 | 0 | -18.6905 | 75.02 | -18.6905 | 9/2/12:00
9 | 2 | 1900-01-12 | 25 | 330 | 438 | 77 | 0 | 1 | 0 | 77 | 0 | 330 | 0 | 0 | 39.791 | 245.5 | 6.9696 | 86.148 | -75 | 0.98152 | 176.3934 | -299.3894 | 30.6106 | 9.703 | 0 | 9.703 | 77 | 9.703 | 9/2/13:00
9 | 2 | 1900-01-13 | 25.6 | 273 | 569 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 273 | 0 | 0 | 39.791 | 245.5417 | 6.9539 | 86.148 | -75 | 0.99572 | 191.3969 | -381.3482 | -108.3482 | -34.3445 | 0 | -34.3445 | 78.08 | -34.3445 | 9/2/14:00
9 | 2 | 1900-01-14 | 26.1 | 195 | 722 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 195 | 0 | 0 | 39.791 | 245.5833 | 6.9382 | 86.148 | -75 | 1.0099 | 206.4005 | -437.458 | -242.458 | -76.855 | 0 | -76.855 | 78.98 | -76.855 | 9/2/15:00
9 | 2 | 1900-01-15 | 26.1 | 145 | 718 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 145 | 0 | 0 | 39.791 | 245.625 | 6.9225 | 86.148 | -75 | 1.0242 | 221.404 | -355.41 | -210.41 | -66.6963 | 0 | -66.6963 | 78.98 | -66.6963 | 9/2/16:00
9 | 2 | 1900-01-16 | 25.6 | 111 | 681 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 111 | 0 | 0 | 39.791 | 245.6667 | 6.9068 | 86.148 | -75 | 1.0384 | 236.4076 | -235.0031 | -124.0031 | -39.3068 | 0 | -39.3068 | 78.08 | -39.3068 | 9/2/17:00
9 | 2 | 1900-01-17 | 25 | 87 | 479 | 77 | 0 | 1 | 0 | 77 | 0 | 87 | 0 | 0 | 39.791 | 245.7083 | 6.8911 | 86.148 | -75 | 1.0526 | 251.4112 | -79.698 | 7.302 | 2.3146 | 0 | 2.3146 | 77 | 2.3146 | 9/2/18:00
9 | 2 | 1900-01-18 | 23.3 | 40 | 275 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 40 | 0 | 0 | 39.791 | 245.75 | 6.8754 | 86.148 | -75 | 1.0669 | 266.4147 | 7.9499 | 47.9499 | 15.1993 | 0 | 15.1993 | 73.94 | 15.1993 | 9/2/19:00
9 | 2 | 1900-01-19 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 245.7917 | 6.8597 | 86.148 | -75 | 1.0811 | 281.4183 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 9/2/20:00
9 | 2 | 1900-01-20 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 245.8333 | 6.844 | 86.148 | -75 | 1.0954 | 296.4218 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 9/2/21:00
9 | 2 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 245.875 | 6.8283 | 86.148 | -75 | 1.1096 | 311.4254 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/2/22:00
9 | 2 | 1900-01-22 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 245.9167 | 6.8126 | 86.148 | -75 | 1.1239 | 326.429 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/2/23:00
9 | 2 | 1900-01-23 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 245.9583 | 6.7968 | 86.148 | -75 | 1.1382 | 341.4325 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/2/24:00
9 | 3 | 1899-12-31 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 246 | 6.7811 | 86.148 | -75 | 1.1525 | -3.5639 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/3/1:00
9 | 3 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 246.0417 | 6.7654 | 86.148 | -75 | 1.1668 | 11.4397 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/3/2:00
9 | 3 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 246.0833 | 6.7496 | 86.148 | -75 | 1.1811 | 26.4433 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/3/3:00
9 | 3 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 246.125 | 6.7339 | 86.148 | -75 | 1.1954 | 41.4469 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/3/4:00
9 | 3 | 1900-01-04 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 246.1667 | 6.7182 | 86.148 | -75 | 1.2097 | 56.4504 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/3/5:00
9 | 3 | 1900-01-05 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 246.2083 | 6.7024 | 86.148 | -75 | 1.2241 | 71.454 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/3/6:00
9 | 3 | 1900-01-06 | 18.9 | 6 | 89 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 6 | 0 | 0 | 39.791 | 246.25 | 6.6867 | 86.148 | -75 | 1.2384 | 86.4576 | 10.8289 | 16.8289 | 5.3345 | 0 | 5.3345 | 66.02 | 5.3345 | 9/3/7:00
9 | 3 | 1900-01-07 | 19.4 | 108 | 271 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 108 | 0 | 0 | 39.791 | 246.2917 | 6.6709 | 86.148 | -75 | 1.2527 | 101.4612 | -20.9488 | 87.0512 | 27.5937 | 0 | 27.5937 | 66.92 | 27.5937 | 9/3/8:00
9 | 3 | 1900-01-08 | 21.1 | 140 | 481 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 140 | 0 | 0 | 39.791 | 246.3333 | 6.6552 | 86.148 | -75 | 1.2671 | 116.4648 | -127.9221 | 12.0779 | 3.8285 | 0 | 3.8285 | 69.98 | 3.8285 | 9/3/9:00
9 | 3 | 1900-01-09 | 23.9 | 150 | 636 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 150 | 0 | 0 | 39.791 | 246.375 | 6.6394 | 86.148 | -75 | 1.2815 | 131.4684 | -274.3833 | -124.3833 | -39.4273 | 0 | -39.4273 | 75.02 | -39.4273 | 9/3/10:00
9 | 3 | 1900-01-10 | 26.1 | 160 | 709 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 160 | 0 | 0 | 39.791 | 246.4167 | 6.6237 | 86.148 | -75 | 1.2958 | 146.472 | -398.7701 | -238.7701 | -75.686 | 0 | -75.686 | 78.98 | -75.686 | 9/3/11:00
9 | 3 | 1900-01-11 | 26.7 | 235 | 627 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 235 | 0 | 0 | 39.791 | 246.4583 | 6.6079 | 86.148 | -75 | 1.3102 | 161.4756 | -407.6041 | -172.6041 | -54.7125 | 0 | -54.7125 | 80.06 | -54.7125 | 9/3/12:00
9 | 3 | 1900-01-12 | 27.8 | 257 | 613 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 257 | 0 | 0 | 39.791 | 246.5 | 6.5922 | 86.148 | -75 | 1.3246 | 176.4792 | -421.9841 | -164.9841 | -52.2971 | 0 | -52.2971 | 82.04 | -52.2971 | 9/3/13:00
9 | 3 | 1900-01-13 | 28.3 | 232 | 671 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 232 | 0 | 0 | 39.791 | 246.5417 | 6.5764 | 86.148 | -75 | 1.339 | 191.4827 | -452.7595 | -220.7595 | -69.9769 | 0 | -69.9769 | 82.94 | -69.9769 | 9/3/14:00
9 | 3 | 1900-01-14 | 28.9 | 183 | 680 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 183 | 0 | 0 | 39.791 | 246.5833 | 6.5606 | 86.148 | -75 | 1.3534 | 206.4863 | -414.8746 | -231.8746 | -73.5002 | 0 | -73.5002 | 84.02 | -73.5002 | 9/3/15:00
9 | 3 | 1900-01-15 | 28.9 | 194 | 629 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 194 | 0 | 0 | 39.791 | 246.625 | 6.5449 | 86.148 | -75 | 1.3678 | 221.49 | -313.7938 | -119.7938 | -37.9725 | 0 | -37.9725 | 84.02 | -37.9725 | 9/3/16:00
9 | 3 | 1900-01-16 | 28.3 | 232 | 176 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 232 | 0 | 0 | 39.791 | 246.6667 | 6.5291 | 86.148 | -75 | 1.3822 | 236.4936 | -61.3622 | 170.6378 | 54.0892 | 0 | 54.0892 | 82.94 | 54.0892 | 9/3/17:00
9 | 3 | 1900-01-17 | 28.3 | 146 | 148 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 146 | 0 | 0 | 39.791 | 246.7083 | 6.5133 | 86.148 | -75 | 1.3967 | 251.4972 | -25.1123 | 120.8877 | 38.3193 | 0 | 38.3193 | 82.94 | 38.3193 | 9/3/18:00
9 | 3 | 1900-01-18 | 25.6 | 39 | 168 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 39 | 0 | 0 | 39.791 | 246.75 | 6.4975 | 86.148 | -75 | 1.4111 | 266.5008 | 4.3385 | 43.3385 | 13.7375 | 0 | 13.7375 | 78.08 | 13.7375 | 9/3/19:00
9 | 3 | 1900-01-19 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 246.7917 | 6.4817 | 86.148 | -75 | 1.4255 | 281.5044 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 9/3/20:00
9 | 3 | 1900-01-20 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 246.8333 | 6.466 | 86.148 | -75 | 1.44 | 296.508 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 9/3/21:00
9 | 3 | 1900-01-21 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 246.875 | 6.4502 | 86.148 | -75 | 1.4544 | 311.5116 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 9/3/22:00
9 | 3 | 1900-01-22 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 246.9167 | 6.4344 | 86.148 | -75 | 1.4689 | 326.5152 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/3/23:00
9 | 3 | 1900-01-23 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 246.9583 | 6.4186 | 86.148 | -75 | 1.4834 | 341.5188 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/3/24:00
9 | 4 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 247 | 6.4028 | 86.148 | -75 | 1.4978 | -3.4775 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/4/1:00
9 | 4 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 247.0417 | 6.387 | 86.148 | -75 | 1.5123 | 11.5261 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/4/2:00
9 | 4 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 247.0833 | 6.3712 | 86.148 | -75 | 1.5268 | 26.5297 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/4/3:00
9 | 4 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 247.125 | 6.3554 | 86.148 | -75 | 1.5413 | 41.5333 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/4/4:00
9 | 4 | 1900-01-04 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 247.1667 | 6.3396 | 86.148 | -75 | 1.5558 | 56.537 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/4/5:00
9 | 4 | 1900-01-05 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 247.2083 | 6.3238 | 86.148 | -75 | 1.5703 | 71.5406 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/4/6:00
9 | 4 | 1900-01-06 | 20.6 | 5 | 92 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 5 | 0 | 0 | 39.791 | 247.25 | 6.308 | 86.148 | -75 | 1.5849 | 86.5442 | 10.7045 | 15.7045 | 4.9781 | 0 | 4.9781 | 69.08 | 4.9781 | 9/4/7:00
9 | 4 | 1900-01-07 | 22.2 | 105 | 292 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 105 | 0 | 0 | 39.791 | 247.2917 | 6.2921 | 86.148 | -75 | 1.5994 | 101.5478 | -24.1635 | 80.8365 | 25.6238 | 0 | 25.6238 | 71.96 | 25.6238 | 9/4/8:00
9 | 4 | 1900-01-08 | 24.4 | 134 | 500 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 134 | 0 | 0 | 39.791 | 247.3333 | 6.2763 | 86.148 | -75 | 1.6139 | 116.5515 | -135.7222 | -1.7222 | -0.54591 | 0 | -0.54591 | 75.92 | -0.54591 | 9/4/9:00
9 | 4 | 1900-01-09 | 26.1 | 171 | 581 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 171 | 0 | 0 | 39.791 | 247.375 | 6.2605 | 86.148 | -75 | 1.6285 | 131.5551 | -253.8215 | -82.8215 | -26.253 | 0 | -26.253 | 78.98 | -26.253 | 9/4/10:00
9 | 4 | 1900-01-10 | 27.8 | 154 | 703 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 154 | 0 | 0 | 39.791 | 247.4167 | 6.2447 | 86.148 | -75 | 1.643 | 146.5588 | -399.1353 | -245.1353 | -77.7036 | 0 | -77.7036 | 82.04 | -77.7036 | 9/4/11:00
9 | 4 | 1900-01-11 | 28.9 | 227 | 693 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 227 | 0 | 0 | 39.791 | 247.4583 | 6.2289 | 86.148 | -75 | 1.6576 | 161.5624 | -454.0534 | -227.0534 | -71.972 | 0 | -71.972 | 84.02 | -71.972 | 9/4/12:00
9 | 4 | 1900-01-12 | 28.3 | 383 | 342 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 383 | 0 | 0 | 39.791 | 247.5 | 6.213 | 86.148 | -75 | 1.6721 | 176.566 | -237.0868 | 145.9132 | 46.2519 | 0 | 46.2519 | 82.94 | 46.2519 | 9/4/13:00
9 | 4 | 1900-01-13 | 28.9 | 292 | 84 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 292 | 0 | 0 | 39.791 | 247.5417 | 6.1972 | 86.148 | -75 | 1.6867 | 191.5697 | -57.06 | 234.94 | 74.4719 | 0 | 74.4719 | 84.02 | 74.4719 | 9/4/14:00
9 | 4 | 1900-01-14 | 28.9 | 277 | 567 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 277 | 0 | 0 | 39.791 | 247.5833 | 6.1814 | 86.148 | -75 | 1.7013 | 206.5733 | -348.3122 | -71.3122 | -22.6047 | 0 | -22.6047 | 84.02 | -22.6047 | 9/4/15:00
9 | 4 | 1900-01-15 | 29.4 | 135 | 724 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 135 | 0 | 0 | 39.791 | 247.625 | 6.1655 | 86.148 | -75 | 1.7159 | 221.577 | -363.9844 | -228.9844 | -72.584 | 0 | -72.584 | 84.92 | -72.584 | 9/4/16:00
9 | 4 | 1900-01-16 | 28.9 | 109 | 663 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 109 | 0 | 0 | 39.791 | 247.6667 | 6.1497 | 86.148 | -75 | 1.7305 | 236.5806 | -233.5104 | -124.5104 | -39.4676 | 0 | -39.4676 | 84.02 | -39.4676 | 9/4/17:00
9 | 4 | 1900-01-17 | 27.8 | 84 | 483 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 84 | 0 | 0 | 39.791 | 247.7083 | 6.1338 | 86.148 | -75 | 1.7451 | 251.5843 | -83.5428 | 0.45716 | 0.14491 | 0 | 0.14491 | 82.04 | 0.14491 | 9/4/18:00
9 | 4 | 1900-01-18 | 26.1 | 36 | 275 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 36 | 0 | 0 | 39.791 | 247.75 | 6.118 | 86.148 | -75 | 1.7597 | 266.5879 | 6.2525 | 42.2525 | 13.3933 | 0 | 13.3933 | 78.98 | 13.3933 | 9/4/19:00
9 | 4 | 1900-01-19 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 247.7917 | 6.1021 | 86.148 | -75 | 1.7743 | 281.5916 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 9/4/20:00
9 | 4 | 1900-01-20 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 247.8333 | 6.0863 | 86.148 | -75 | 1.7889 | 296.5952 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 9/4/21:00
9 | 4 | 1900-01-21 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 247.875 | 6.0704 | 86.148 | -75 | 1.8035 | 311.5989 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/4/22:00
9 | 4 | 1900-01-22 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 247.9167 | 6.0546 | 86.148 | -75 | 1.8182 | 326.6025 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/4/23:00
9 | 4 | 1900-01-23 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 247.9583 | 6.0387 | 86.148 | -75 | 1.8328 | 341.6062 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/4/24:00
9 | 5 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 248 | 6.0229 | 86.148 | -75 | 1.8475 | -3.3901 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/5/1:00
9 | 5 | 1900-01-01 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 248.0417 | 6.007 | 86.148 | -75 | 1.8621 | 11.6135 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/5/2:00
9 | 5 | 1900-01-02 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 248.0833 | 5.9911 | 86.148 | -75 | 1.8768 | 26.6172 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/5/3:00
9 | 5 | 1900-01-03 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 248.125 | 5.9753 | 86.148 | -75 | 1.8915 | 41.6209 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/5/4:00
9 | 5 | 1900-01-04 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 248.1667 | 5.9594 | 86.148 | -75 | 1.9061 | 56.6245 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/5/5:00
9 | 5 | 1900-01-05 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 248.2083 | 5.9435 | 86.148 | -75 | 1.9208 | 71.6282 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/5/6:00
9 | 5 | 1900-01-06 | 16.1 | 4 | 120 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 4 | 0 | 0 | 39.791 | 248.25 | 5.9276 | 86.148 | -75 | 1.9355 | 86.6319 | 13.3194 | 17.3194 | 5.49 | 0 | 5.49 | 60.98 | 5.49 | 9/5/7:00
9 | 5 | 1900-01-07 | 18.3 | 92 | 395 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 92 | 0 | 0 | 39.791 | 248.2917 | 5.9118 | 86.148 | -75 | 1.9502 | 101.6355 | -34.8513 | 57.1487 | 18.1151 | 0 | 18.1151 | 64.94 | 18.1151 | 9/5/8:00
9 | 5 | 1900-01-08 | 19.4 | 129 | 532 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 129 | 0 | 0 | 39.791 | 248.3333 | 5.8959 | 86.148 | -75 | 1.9649 | 116.6392 | -147.3419 | -18.3419 | -5.8141 | 0 | -5.8141 | 66.92 | -5.8141 | 9/5/9:00
9 | 5 | 1900-01-09 | 21.7 | 132 | 697 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 132 | 0 | 0 | 39.791 | 248.375 | 5.88 | 86.148 | -75 | 1.9796 | 131.6429 | -308.3042 | -176.3042 | -55.8854 | 0 | -55.8854 | 71.06 | -55.8854 | 9/5/10:00
9 | 5 | 1900-01-10 | 23.3 | 145 | 745 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 145 | 0 | 0 | 39.791 | 248.4167 | 5.8641 | 86.148 | -75 | 1.9943 | 146.6466 | -426.9457 | -281.9457 | -89.3719 | 0 | -89.3719 | 73.94 | -89.3719 | 9/5/11:00
9 | 5 | 1900-01-11 | 25 | 144 | 808 | 77 | 0 | 1 | 0 | 77 | 0 | 144 | 0 | 0 | 39.791 | 248.4583 | 5.8482 | 86.148 | -75 | 2.009 | 161.6503 | -533.5282 | -389.5282 | -123.4736 | 0 | -123.4736 | 77 | -123.4736 | 9/5/12:00
9 | 5 | 1900-01-12 | 26.1 | 177 | 763 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 177 | 0 | 0 | 39.791 | 248.5 | 5.8323 | 86.148 | -75 | 2.0238 | 176.6539 | -532.6269 | -355.6269 | -112.7275 | 0 | -112.7275 | 78.98 | -112.7275 | 9/5/13:00
9 | 5 | 1900-01-13 | 26.7 | 225 | 671 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 225 | 0 | 0 | 39.791 | 248.5417 | 5.8164 | 86.148 | -75 | 2.0385 | 191.6576 | -458.8315 | -233.8315 | -74.1205 | 0 | -74.1205 | 80.06 | -74.1205 | 9/5/14:00
9 | 5 | 1900-01-14 | 27.2 | 189 | 686 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 189 | 0 | 0 | 39.791 | 248.5833 | 5.8005 | 86.148 | -75 | 2.0532 | 206.6613 | -424.2831 | -235.2831 | -74.5806 | 0 | -74.5806 | 80.96 | -74.5806 | 9/5/15:00
9 | 5 | 1900-01-15 | 27.8 | 131 | 735 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 131 | 0 | 0 | 39.791 | 248.625 | 5.7846 | 86.148 | -75 | 2.068 | 221.665 | -372.3436 | -241.3436 | -76.5017 | 0 | -76.5017 | 82.04 | -76.5017 | 9/5/16:00
9 | 5 | 1900-01-16 | 27.2 | 102 | 692 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 102 | 0 | 0 | 39.791 | 248.6667 | 5.7687 | 86.148 | -75 | 2.0827 | 236.6687 | -246.1761 | -144.1761 | -45.7013 | 0 | -45.7013 | 80.96 | -45.7013 | 9/5/17:00
9 | 5 | 1900-01-17 | 26.7 | 82 | 477 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 82 | 0 | 0 | 39.791 | 248.7083 | 5.7528 | 86.148 | -75 | 2.0975 | 251.6724 | -84.0717 | -2.0717 | -0.6567 | 0 | -0.6567 | 80.06 | -0.6567 | 9/5/18:00
9 | 5 | 1900-01-18 | 25.6 | 37 | 238 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 37 | 0 | 0 | 39.791 | 248.75 | 5.7369 | 86.148 | -75 | 2.1123 | 266.6761 | 4.6756 | 41.6756 | 13.2104 | 0 | 13.2104 | 78.08 | 13.2104 | 9/5/19:00
9 | 5 | 1900-01-19 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 248.7917 | 5.721 | 86.148 | -75 | 2.127 | 281.6798 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 9/5/20:00
9 | 5 | 1900-01-20 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 248.8333 | 5.7051 | 86.148 | -75 | 2.1418 | 296.6835 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 9/5/21:00
9 | 5 | 1900-01-21 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 248.875 | 5.6892 | 86.148 | -75 | 2.1566 | 311.6872 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 9/5/22:00
9 | 5 | 1900-01-22 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 248.9167 | 5.6733 | 86.148 | -75 | 2.1714 | 326.6909 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/5/23:00
9 | 5 | 1900-01-23 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 248.9583 | 5.6573 | 86.148 | -75 | 2.1862 | 341.6946 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/5/24:00
9 | 6 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 249 | 5.6414 | 86.148 | -75 | 2.201 | -3.3017 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/6/1:00
9 | 6 | 1900-01-01 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 249.0417 | 5.6255 | 86.148 | -75 | 2.2158 | 11.702 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/6/2:00
9 | 6 | 1900-01-02 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 249.0833 | 5.6096 | 86.148 | -75 | 2.2306 | 26.7057 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/6/3:00
9 | 6 | 1900-01-03 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 249.125 | 5.5936 | 86.148 | -75 | 2.2455 | 41.7094 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/6/4:00
9 | 6 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 249.1667 | 5.5777 | 86.148 | -75 | 2.2603 | 56.7131 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/6/5:00
9 | 6 | 1900-01-05 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 249.2083 | 5.5618 | 86.148 | -75 | 2.2751 | 71.7168 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/6/6:00
9 | 6 | 1900-01-06 | 16.1 | 4 | 78 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 4 | 0 | 0 | 39.791 | 249.25 | 5.5458 | 86.148 | -75 | 2.29 | 86.7205 | 8.2369 | 12.2369 | 3.8789 | 0 | 3.8789 | 60.98 | 3.8789 | 9/6/7:00
9 | 6 | 1900-01-07 | 17.8 | 106 | 267 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 106 | 0 | 0 | 39.791 | 249.2917 | 5.5299 | 86.148 | -75 | 2.3048 | 101.7242 | -25.0279 | 80.9721 | 25.6668 | 0 | 25.6668 | 64.04 | 25.6668 | 9/6/8:00
9 | 6 | 1900-01-08 | 20.5 | 124 | 532 | 68.9 | 0 | 1 | 0 | 68.9 | 0 | 124 | 0 | 0 | 39.791 | 249.3333 | 5.5139 | 86.148 | -75 | 2.3197 | 116.7279 | -150.2845 | -26.2845 | -8.3317 | 0 | -8.3317 | 68.9 | -8.3317 | 9/6/9:00
9 | 6 | 1900-01-09 | 23.3 | 149 | 648 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 149 | 0 | 0 | 39.791 | 249.375 | 5.498 | 86.148 | -75 | 2.3345 | 131.7316 | -290.1732 | -141.1732 | -44.7494 | 0 | -44.7494 | 73.94 | -44.7494 | 9/6/10:00
9 | 6 | 1900-01-10 | 25.6 | 130 | 788 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 130 | 0 | 0 | 39.791 | 249.4167 | 5.482 | 86.148 | -75 | 2.3494 | 146.7353 | -455.7808 | -325.7808 | -103.2668 | 0 | -103.2668 | 78.08 | -103.2668 | 9/6/11:00
9 | 6 | 1900-01-11 | 26.7 | 141 | 814 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 141 | 0 | 0 | 39.791 | 249.4583 | 5.4661 | 86.148 | -75 | 2.3643 | 161.7391 | -541.6408 | -400.6408 | -126.9961 | 0 | -126.9961 | 80.06 | -126.9961 | 9/6/12:00
9 | 6 | 1900-01-12 | 28.3 | 157 | 805 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 157 | 0 | 0 | 39.791 | 249.5 | 5.4501 | 86.148 | -75 | 2.3791 | 176.7428 | -565.8255 | -408.8255 | -129.5905 | 0 | -129.5905 | 82.94 | -129.5905 | 9/6/13:00
9 | 6 | 1900-01-13 | 29.4 | 195 | 724 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 195 | 0 | 0 | 39.791 | 249.5417 | 5.4342 | 86.148 | -75 | 2.394 | 191.7465 | -498.3314 | -303.3314 | -96.1507 | 0 | -96.1507 | 84.92 | -96.1507 | 9/6/14:00
9 | 6 | 1900-01-14 | 30 | 146 | 769 | 86 | 0 | 1 | 0 | 86 | 0 | 146 | 0 | 0 | 39.791 | 249.5833 | 5.4182 | 86.148 | -75 | 2.4089 | 206.7502 | -478.8199 | -332.8199 | -105.4981 | 0 | -105.4981 | 86 | -105.4981 | 9/6/15:00
9 | 6 | 1900-01-15 | 30 | 139 | 717 | 86 | 0 | 1 | 0 | 86 | 0 | 139 | 0 | 0 | 39.791 | 249.625 | 5.4023 | 86.148 | -75 | 2.4238 | 221.7539 | -365.9738 | -226.9738 | -71.9467 | 0 | -71.9467 | 86 | -71.9467 | 9/6/16:00
9 | 6 | 1900-01-16 | 29.4 | 118 | 609 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 118 | 0 | 0 | 39.791 | 249.6667 | 5.3863 | 86.148 | -75 | 2.4387 | 236.7577 | -218.8002 | -100.8002 | -31.9519 | 0 | -31.9519 | 84.92 | -31.9519 | 9/6/17:00
9 | 6 | 1900-01-17 | 28.3 | 104 | 380 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 104 | 0 | 0 | 39.791 | 249.7083 | 5.3703 | 86.148 | -75 | 2.4536 | 251.7614 | -68.2217 | 35.7783 | 11.3411 | 0 | 11.3411 | 82.94 | 11.3411 | 9/6/18:00
9 | 6 | 1900-01-18 | 27.2 | 37 | 58 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 37 | 0 | 0 | 39.791 | 249.75 | 5.3544 | 86.148 | -75 | 2.4685 | 266.7651 | 0.95995 | 37.9599 | 12.0326 | 0 | 12.0326 | 80.96 | 12.0326 | 9/6/19:00
9 | 6 | 1900-01-19 | 26.1 | 0 | 0 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 0 | 0 | 0 | 39.791 | 249.7917 | 5.3384 | 86.148 | -75 | 2.4834 | 281.7689 | 0 | 0 | 0 | 0 | 0 | 78.98 | 0 | 9/6/20:00
9 | 6 | 1900-01-20 | 25.6 | 0 | 0 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 0 | 0 | 0 | 39.791 | 249.8333 | 5.3224 | 86.148 | -75 | 2.4984 | 296.7726 | 0 | 0 | 0 | 0 | 0 | 78.08 | 0 | 9/6/21:00
9 | 6 | 1900-01-21 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 249.875 | 5.3065 | 86.148 | -75 | 2.5133 | 311.7763 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 9/6/22:00
9 | 6 | 1900-01-22 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 249.9167 | 5.2905 | 86.148 | -75 | 2.5282 | 326.7801 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 9/6/23:00
9 | 6 | 1900-01-23 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 249.9583 | 5.2745 | 86.148 | -75 | 2.5432 | 341.7838 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 9/6/24:00
9 | 7 | 1899-12-31 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 250 | 5.2585 | 86.148 | -75 | 2.5581 | -3.2125 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 9/7/1:00
9 | 7 | 1900-01-01 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 250.0417 | 5.2425 | 86.148 | -75 | 2.573 | 11.7913 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 9/7/2:00
9 | 7 | 1900-01-02 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 250.0833 | 5.2266 | 86.148 | -75 | 2.588 | 26.795 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 9/7/3:00
9 | 7 | 1900-01-03 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 250.125 | 5.2106 | 86.148 | -75 | 2.603 | 41.7987 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 9/7/4:00
9 | 7 | 1900-01-04 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 250.1667 | 5.1946 | 86.148 | -75 | 2.6179 | 56.8025 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 9/7/5:00
9 | 7 | 1900-01-05 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 250.2083 | 5.1786 | 86.148 | -75 | 2.6329 | 71.8062 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 9/7/6:00
9 | 7 | 1900-01-06 | 22.2 | 3 | 73 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 3 | 0 | 0 | 39.791 | 250.25 | 5.1626 | 86.148 | -75 | 2.6479 | 86.81 | 7.3126 | 10.3126 | 3.2689 | 0 | 3.2689 | 71.96 | 3.2689 | 9/7/7:00
9 | 7 | 1900-01-07 | 23.9 | 91 | 261 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 91 | 0 | 0 | 39.791 | 250.2917 | 5.1466 | 86.148 | -75 | 2.6629 | 101.8137 | -25.9088 | 65.0912 | 20.6328 | 0 | 20.6328 | 75.02 | 20.6328 | 9/7/8:00
9 | 7 | 1900-01-08 | 25.6 | 161 | 413 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 161 | 0 | 0 | 39.791 | 250.3333 | 5.1306 | 86.148 | -75 | 2.6779 | 116.8175 | -118.9586 | 42.0414 | 13.3264 | 0 | 13.3264 | 78.08 | 13.3264 | 9/7/9:00
9 | 7 | 1900-01-09 | 26.1 | 193 | 6 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 193 | 0 | 0 | 39.791 | 250.375 | 5.1146 | 86.148 | -75 | 2.6928 | 131.8212 | -2.7196 | 190.2804 | 60.3156 | 0 | 60.3156 | 78.98 | 60.3156 | 9/7/10:00
9 | 7 | 1900-01-10 | 28.9 | 320 | 48 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 320 | 0 | 0 | 39.791 | 250.4167 | 5.0986 | 86.148 | -75 | 2.7078 | 146.825 | -28.0185 | 291.9815 | 92.553 | 0 | 92.553 | 84.02 | 92.553 | 9/7/11:00
9 | 7 | 1900-01-11 | 29.4 | 373 | 121 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 373 | 0 | 0 | 39.791 | 250.4583 | 5.0826 | 86.148 | -75 | 2.7228 | 161.8287 | -81.1299 | 291.8701 | 92.5177 | 0 | 92.5177 | 84.92 | 92.5177 | 9/7/12:00
9 | 7 | 1900-01-12 | 30 | 332 | 444 | 86 | 0 | 1 | 0 | 86 | 0 | 332 | 0 | 0 | 39.791 | 250.5 | 5.0666 | 86.148 | -75 | 2.7379 | 176.8325 | -314.2156 | 17.7844 | 5.6373 | 0 | 5.6373 | 86 | 5.6373 | 9/7/13:00
9 | 7 | 1900-01-13 | 31.1 | 322 | 48 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 322 | 0 | 0 | 39.791 | 250.5417 | 5.0506 | 86.148 | -75 | 2.7529 | 191.8362 | -33.2537 | 288.7463 | 91.5275 | 0 | 91.5275 | 87.98 | 91.5275 | 9/7/14:00
9 | 7 | 1900-01-14 | 31.1 | 341 | 149 | 87.98 | 0 | 1 | 0 | 87.98 | 0 | 341 | 0 | 0 | 39.791 | 250.5833 | 5.0346 | 86.148 | -75 | 2.7679 | 206.84 | -93.393 | 247.607 | 78.4871 | 0 | 78.4871 | 87.98 | 78.4871 | 9/7/15:00
9 | 7 | 1900-01-15 | 27.8 | 242 | 462 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 242 | 0 | 0 | 39.791 | 250.625 | 5.0185 | 86.148 | -75 | 2.7829 | 221.8437 | -237.5795 | 4.4205 | 1.4012 | 0 | 1.4012 | 82.04 | 1.4012 | 9/7/16:00
9 | 7 | 1900-01-16 | 23.9 | 159 | 6 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 159 | 0 | 0 | 39.791 | 250.6667 | 5.0025 | 86.148 | -75 | 2.7979 | 236.8475 | -2.1768 | 156.8232 | 49.7102 | 0 | 49.7102 | 75.02 | 49.7102 | 9/7/17:00
9 | 7 | 1900-01-17 | 20.6 | 39 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 39 | 0 | 0 | 39.791 | 250.7083 | 4.9865 | 86.148 | -75 | 2.813 | 251.8512 | 0 | 39 | 12.3623 | 0 | 12.3623 | 69.08 | 12.3623 | 9/7/18:00
9 | 7 | 1900-01-18 | 21.1 | 10 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 10 | 0 | 0 | 39.791 | 250.75 | 4.9705 | 86.148 | -75 | 2.828 | 266.855 | 0 | 10 | 3.1698 | 0 | 3.1698 | 69.98 | 3.1698 | 9/7/19:00
9 | 7 | 1900-01-19 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 250.7917 | 4.9545 | 86.148 | -75 | 2.8431 | 281.8588 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 9/7/20:00
9 | 7 | 1900-01-20 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 250.8333 | 4.9384 | 86.148 | -75 | 2.8581 | 296.8625 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 9/7/21:00
9 | 7 | 1900-01-21 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 250.875 | 4.9224 | 86.148 | -75 | 2.8732 | 311.8663 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 9/7/22:00
9 | 7 | 1900-01-22 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 250.9167 | 4.9064 | 86.148 | -75 | 2.8882 | 326.8701 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 9/7/23:00
9 | 7 | 1900-01-23 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 250.9583 | 4.8904 | 86.148 | -75 | 2.9033 | 341.8738 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/7/24:00
9 | 8 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 251 | 4.8743 | 86.148 | -75 | 2.9184 | -3.1224 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/8/1:00
9 | 8 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 251.0417 | 4.8583 | 86.148 | -75 | 2.9334 | 11.8814 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/8/2:00
9 | 8 | 1900-01-02 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 251.0833 | 4.8422 | 86.148 | -75 | 2.9485 | 26.8851 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/8/3:00
9 | 8 | 1900-01-03 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 251.125 | 4.8262 | 86.148 | -75 | 2.9636 | 41.8889 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 9/8/4:00
9 | 8 | 1900-01-04 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 251.1667 | 4.8102 | 86.148 | -75 | 2.9787 | 56.8927 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 9/8/5:00
9 | 8 | 1900-01-05 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 251.2083 | 4.7941 | 86.148 | -75 | 2.9938 | 71.8964 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 9/8/6:00
9 | 8 | 1900-01-06 | 22.2 | 2 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 2 | 0 | 0 | 39.791 | 251.25 | 4.7781 | 86.148 | -75 | 3.0089 | 86.9002 | 0 | 2 | 0.63397 | 0 | 0.63397 | 71.96 | 0.63397 | 9/8/7:00
9 | 8 | 1900-01-07 | 22.8 | 71 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 71 | 0 | 0 | 39.791 | 251.2917 | 4.762 | 86.148 | -75 | 3.024 | 101.904 | 0 | 71 | 22.5058 | 0 | 22.5058 | 73.04 | 22.5058 | 9/8/8:00
9 | 8 | 1900-01-08 | 23.3 | 99 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 99 | 0 | 0 | 39.791 | 251.3333 | 4.746 | 86.148 | -75 | 3.0391 | 116.9078 | 0 | 99 | 31.3813 | 0 | 31.3813 | 73.94 | 31.3813 | 9/8/9:00
9 | 8 | 1900-01-09 | 25 | 267 | 141 | 77 | 0 | 1 | 0 | 77 | 0 | 267 | 0 | 0 | 39.791 | 251.375 | 4.7299 | 86.148 | -75 | 3.0542 | 131.9116 | -64.6832 | 202.3168 | 64.1309 | 0 | 64.1309 | 77 | 64.1309 | 9/8/10:00
9 | 8 | 1900-01-10 | 26.1 | 309 | 370 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 309 | 0 | 0 | 39.791 | 251.4167 | 4.7139 | 86.148 | -75 | 3.0693 | 146.9153 | -217.9412 | 91.0588 | 28.8641 | 0 | 28.8641 | 78.98 | 28.8641 | 9/8/11:00
9 | 8 | 1900-01-11 | 27.2 | 201 | 18 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 201 | 0 | 0 | 39.791 | 251.4583 | 4.6978 | 86.148 | -75 | 3.0844 | 161.9191 | -12.1603 | 188.8397 | 59.8589 | 0 | 59.8589 | 80.96 | 59.8589 | 9/8/12:00
9 | 8 | 1900-01-12 | 28.9 | 379 | 330 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 379 | 0 | 0 | 39.791 | 251.5 | 4.6818 | 86.148 | -75 | 3.0996 | 176.9229 | -235.1183 | 143.8817 | 45.608 | 0 | 45.608 | 84.02 | 45.608 | 9/8/13:00
9 | 8 | 1900-01-13 | 30 | 382 | 216 | 86 | 0 | 1 | 0 | 86 | 0 | 382 | 0 | 0 | 39.791 | 251.5417 | 4.6657 | 86.148 | -75 | 3.1147 | 191.9267 | -150.6055 | 231.3945 | 73.348 | 0 | 73.348 | 86 | 73.348 | 9/8/14:00
9 | 8 | 1900-01-14 | 29.4 | 321 | 83 | 84.92 | 0 | 1 | 0 | 84.92 | 0 | 321 | 0 | 0 | 39.791 | 251.5833 | 4.6496 | 86.148 | -75 | 3.1298 | 206.9305 | -52.3667 | 268.6333 | 85.152 | 0 | 85.152 | 84.92 | 85.152 | 9/8/15:00
9 | 8 | 1900-01-15 | 28.9 | 272 | 338 | 84.02 | 0 | 1 | 0 | 84.02 | 0 | 272 | 0 | 0 | 39.791 | 251.625 | 4.6336 | 86.148 | -75 | 3.145 | 221.9342 | -175.0982 | 96.9018 | 30.7162 | 0 | 30.7162 | 84.02 | 30.7162 | 9/8/16:00
9 | 8 | 1900-01-16 | 28.3 | 179 | 392 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 179 | 0 | 0 | 39.791 | 251.6667 | 4.6175 | 86.148 | -75 | 3.1601 | 236.938 | -143.5923 | 35.4077 | 11.2236 | 0 | 11.2236 | 82.94 | 11.2236 | 9/8/17:00
9 | 8 | 1900-01-17 | 27.2 | 124 | 158 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 124 | 0 | 0 | 39.791 | 251.7083 | 4.6014 | 86.148 | -75 | 3.1753 | 251.9418 | -29.4 | 94.6 | 29.9866 | 0 | 29.9866 | 80.96 | 29.9866 | 9/8/18:00
9 | 8 | 1900-01-18 | 26.1 | 29 | 216 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 29 | 0 | 0 | 39.791 | 251.75 | 4.5854 | 86.148 | -75 | 3.1904 | 266.9456 | 2.236 | 31.236 | 9.9013 | 0 | 9.9013 | 78.98 | 9.9013 | 9/8/19:00
9 | 8 | 1900-01-19 | 25 | 0 | 0 | 77 | 0 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 39.791 | 251.7917 | 4.5693 | 86.148 | -75 | 3.2056 | 281.9494 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 9/8/20:00
9 | 8 | 1900-01-20 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 251.8333 | 4.5532 | 86.148 | -75 | 3.2207 | 296.9532 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 9/8/21:00
9 | 8 | 1900-01-21 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 251.875 | 4.5371 | 86.148 | -75 | 3.2359 | 311.957 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 9/8/22:00
9 | 8 | 1900-01-22 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 251.9167 | 4.521 | 86.148 | -75 | 3.2511 | 326.9608 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 9/8/23:00
9 | 8 | 1900-01-23 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 251.9583 | 4.505 | 86.148 | -75 | 3.2662 | 341.9646 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 9/8/24:00
9 | 9 | 1899-12-31 | 23.3 | 0 | 0 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 0 | 0 | 0 | 39.791 | 252 | 4.4889 | 86.148 | -75 | 3.2814 | -3.0316 | 0 | 0 | 0 | 0 | 0 | 73.94 | 0 | 9/9/1:00
9 | 9 | 1900-01-01 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 252.0417 | 4.4728 | 86.148 | -75 | 3.2966 | 11.9722 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 9/9/2:00
9 | 9 | 1900-01-02 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 252.0833 | 4.4567 | 86.148 | -75 | 3.3118 | 26.9759 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 9/9/3:00
9 | 9 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 252.125 | 4.4406 | 86.148 | -75 | 3.327 | 41.9797 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 9/9/4:00
9 | 9 | 1900-01-04 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 252.1667 | 4.4245 | 86.148 | -75 | 3.3422 | 56.9835 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 9/9/5:00
9 | 9 | 1900-01-05 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 252.2083 | 4.4084 | 86.148 | -75 | 3.3574 | 71.9873 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 9/9/6:00
9 | 9 | 1900-01-06 | 20.6 | 2 | 42 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 2 | 0 | 0 | 39.791 | 252.25 | 4.3923 | 86.148 | -75 | 3.3726 | 86.9911 | 3.7476 | 5.7476 | 1.8219 | 0 | 1.8219 | 69.08 | 1.8219 | 9/9/7:00
9 | 9 | 1900-01-07 | 21.1 | 89 | 166 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 89 | 0 | 0 | 39.791 | 252.2917 | 4.3763 | 86.148 | -75 | 3.3878 | 101.9949 | -18.3246 | 70.6754 | 22.4029 | 0 | 22.4029 | 69.98 | 22.4029 | 9/9/8:00
9 | 9 | 1900-01-08 | 21.1 | 85 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 85 | 0 | 0 | 39.791 | 252.3333 | 4.3602 | 86.148 | -75 | 3.403 | 116.9988 | 0 | 85 | 26.9435 | 0 | 26.9435 | 69.98 | 26.9435 | 9/9/9:00
9 | 9 | 1900-01-09 | 21.7 | 85 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 85 | 0 | 0 | 39.791 | 252.375 | 4.3441 | 86.148 | -75 | 3.4182 | 132.0026 | 0 | 85 | 26.9435 | 0 | 26.9435 | 71.06 | 26.9435 | 9/9/10:00
9 | 9 | 1900-01-10 | 22.8 | 107 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 107 | 0 | 0 | 39.791 | 252.4167 | 4.3279 | 86.148 | -75 | 3.4334 | 147.0064 | 0 | 107 | 33.9171 | 0 | 33.9171 | 73.04 | 33.9171 | 9/9/11:00
9 | 9 | 1900-01-11 | 23.9 | 216 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 216 | 0 | 0 | 39.791 | 252.4583 | 4.3118 | 86.148 | -75 | 3.4487 | 162.0102 | 0 | 216 | 68.4682 | 0 | 68.4682 | 75.02 | 68.4682 | 9/9/12:00
9 | 9 | 1900-01-12 | 25 | 262 | 12 | 77 | 0 | 1 | 0 | 77 | 0 | 262 | 0 | 0 | 39.791 | 252.5 | 4.2957 | 86.148 | -75 | 3.4639 | 177.014 | -8.607 | 253.393 | 80.3212 | 0 | 80.3212 | 77 | 80.3212 | 9/9/13:00
9 | 9 | 1900-01-13 | 26.7 | 237 | 0 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 237 | 0 | 0 | 39.791 | 252.5417 | 4.2796 | 86.148 | -75 | 3.4791 | 192.0178 | 0 | 237 | 75.1249 | 0 | 75.1249 | 80.06 | 75.1249 | 9/9/14:00
9 | 9 | 1900-01-14 | 26.7 | 235 | 12 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 235 | 0 | 0 | 39.791 | 252.5833 | 4.2635 | 86.148 | -75 | 3.4943 | 207.0216 | -7.6204 | 227.3796 | 72.0754 | 0 | 72.0754 | 80.06 | 72.0754 | 9/9/15:00
9 | 9 | 1900-01-15 | 21.1 | 101 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 101 | 0 | 0 | 39.791 | 252.625 | 4.2474 | 86.148 | -75 | 3.5096 | 222.0254 | 0 | 101 | 32.0152 | 0 | 32.0152 | 69.98 | 32.0152 | 9/9/16:00
9 | 9 | 1900-01-16 | 22.2 | 75 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 75 | 0 | 0 | 39.791 | 252.6667 | 4.2313 | 86.148 | -75 | 3.5248 | 237.0292 | 0 | 75 | 23.7737 | 0 | 23.7737 | 71.96 | 23.7737 | 9/9/17:00
9 | 9 | 1900-01-17 | 20 | 44 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 44 | 0 | 0 | 39.791 | 252.7083 | 4.2152 | 86.148 | -75 | 3.5401 | 252.033 | 0 | 44 | 13.9472 | 0 | 13.9472 | 68 | 13.9472 | 9/9/18:00
9 | 9 | 1900-01-18 | 19.4 | 9 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 9 | 0 | 0 | 39.791 | 252.75 | 4.1991 | 86.148 | -75 | 3.5553 | 267.0368 | 0 | 9 | 2.8528 | 0 | 2.8528 | 66.92 | 2.8528 | 9/9/19:00
9 | 9 | 1900-01-19 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 252.7917 | 4.1829 | 86.148 | -75 | 3.5706 | 282.0406 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/9/20:00
9 | 9 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 252.8333 | 4.1668 | 86.148 | -75 | 3.5858 | 297.0445 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/9/21:00
9 | 9 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 252.875 | 4.1507 | 86.148 | -75 | 3.6011 | 312.0483 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/9/22:00
9 | 9 | 1900-01-22 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 252.9167 | 4.1346 | 86.148 | -75 | 3.6164 | 327.0521 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/9/23:00
9 | 9 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 252.9583 | 4.1185 | 86.148 | -75 | 3.6316 | 342.0559 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/9/24:00
9 | 10 | 1899-12-31 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 253 | 4.1023 | 86.148 | -75 | 3.6469 | -2.9403 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/10/1:00
9 | 10 | 1900-01-01 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 253.0417 | 4.0862 | 86.148 | -75 | 3.6622 | 12.0635 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 9/10/2:00
9 | 10 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 253.0833 | 4.0701 | 86.148 | -75 | 3.6775 | 27.0674 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/10/3:00
9 | 10 | 1900-01-03 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 253.125 | 4.0539 | 86.148 | -75 | 3.6927 | 42.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/10/4:00
9 | 10 | 1900-01-04 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 253.1667 | 4.0378 | 86.148 | -75 | 3.708 | 57.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/10/5:00
9 | 10 | 1900-01-05 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 253.2083 | 4.0217 | 86.148 | -75 | 3.7233 | 72.0788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/10/6:00
9 | 10 | 1900-01-06 | 11.7 | 2 | 53 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 2 | 0 | 0 | 39.791 | 253.25 | 4.0055 | 86.148 | -75 | 3.7386 | 87.0826 | 4.437 | 6.437 | 2.0404 | 2.0404 | 0 | 0 | 0 | 9/10/7:00
9 | 10 | 1900-01-07 | 11.7 | 87 | 221 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 87 | 0 | 0 | 39.791 | 253.2917 | 3.9894 | 86.148 | -75 | 3.7539 | 102.0865 | -25.6306 | 61.3694 | 19.453 | 19.453 | 0 | 0 | 0 | 9/10/8:00
9 | 10 | 1900-01-08 | 12.8 | 182 | 232 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 182 | 0 | 0 | 39.791 | 253.3333 | 3.9732 | 86.148 | -75 | 3.7692 | 117.0903 | -70.6977 | 111.3023 | 35.2809 | 0 | 35.2809 | 55.04 | 35.2809 | 9/10/9:00
9 | 10 | 1900-01-09 | 16.1 | 172 | 612 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 172 | 0 | 0 | 39.791 | 253.375 | 3.9571 | 86.148 | -75 | 3.7845 | 132.0941 | -287.4524 | -115.4524 | -36.5964 | 0 | -36.5964 | 60.98 | -36.5964 | 9/10/10:00
9 | 10 | 1900-01-10 | 18.9 | 130 | 757 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 130 | 0 | 0 | 39.791 | 253.4167 | 3.9409 | 86.148 | -75 | 3.7998 | 147.0979 | -453.916 | -323.916 | -102.6757 | 0 | -102.6757 | 66.02 | -102.6757 | 9/10/11:00
9 | 10 | 1900-01-11 | 20.6 | 153 | 790 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 153 | 0 | 0 | 39.791 | 253.4583 | 3.9248 | 86.148 | -75 | 3.8151 | 162.1018 | -541.6849 | -388.6849 | -123.2063 | 0 | -123.2063 | 69.08 | -123.2063 | 9/10/12:00
9 | 10 | 1900-01-12 | 22.2 | 154 | 793 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 154 | 0 | 0 | 39.791 | 253.5 | 3.9086 | 86.148 | -75 | 3.8304 | 177.1056 | -572.5408 | -418.5408 | -132.6701 | 0 | -132.6701 | 71.96 | -132.6701 | 9/10/13:00
9 | 10 | 1900-01-13 | 22.8 | 141 | 820 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 141 | 0 | 0 | 39.791 | 253.5417 | 3.8925 | 86.148 | -75 | 3.8457 | 192.1094 | -579.0086 | -438.0086 | -138.8411 | 0 | -138.8411 | 73.04 | -138.8411 | 9/10/14:00
9 | 10 | 1900-01-14 | 23.3 | 138 | 781 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 138 | 0 | 0 | 39.791 | 253.5833 | 3.8763 | 86.148 | -75 | 3.861 | 207.1133 | -499.1482 | -361.1482 | -114.4777 | 0 | -114.4777 | 73.94 | -114.4777 | 9/10/15:00
9 | 10 | 1900-01-15 | 23.9 | 123 | 752 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 123 | 0 | 0 | 39.791 | 253.625 | 3.8602 | 86.148 | -75 | 3.8764 | 222.1171 | -395.2439 | -272.2439 | -86.2965 | 0 | -86.2965 | 75.02 | -86.2965 | 9/10/16:00
9 | 10 | 1900-01-16 | 23.9 | 98 | 672 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 98 | 0 | 0 | 39.791 | 253.6667 | 3.844 | 86.148 | -75 | 3.8917 | 237.1209 | -250.849 | -152.849 | -48.4505 | 0 | -48.4505 | 75.02 | -48.4505 | 9/10/17:00
9 | 10 | 1900-01-17 | 22.8 | 65 | 529 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 65 | 0 | 0 | 39.791 | 253.7083 | 3.8279 | 86.148 | -75 | 3.907 | 252.1248 | -101.8857 | -36.8857 | -11.6921 | 0 | -11.6921 | 73.04 | -11.6921 | 9/10/18:00
9 | 10 | 1900-01-18 | 18.9 | 24 | 224 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 24 | 0 | 0 | 39.791 | 253.75 | 3.8117 | 86.148 | -75 | 3.9224 | 267.1286 | 0.927 | 24.927 | 7.9014 | 0 | 7.9014 | 66.02 | 7.9014 | 9/10/19:00
9 | 10 | 1900-01-19 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 253.7917 | 3.7956 | 86.148 | -75 | 3.9377 | 282.1324 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/10/20:00
9 | 10 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 253.8333 | 3.7794 | 86.148 | -75 | 3.953 | 297.1363 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/10/21:00
9 | 10 | 1900-01-21 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 253.875 | 3.7632 | 86.148 | -75 | 3.9684 | 312.1401 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/10/22:00
9 | 10 | 1900-01-22 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 253.9167 | 3.7471 | 86.148 | -75 | 3.9837 | 327.1439 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/10/23:00
9 | 10 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 253.9583 | 3.7309 | 86.148 | -75 | 3.999 | 342.1478 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/10/24:00
9 | 11 | 1899-12-31 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 254 | 3.7147 | 86.148 | -75 | 4.0144 | -2.8484 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/11/1:00
9 | 11 | 1900-01-01 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 254.0417 | 3.6986 | 86.148 | -75 | 4.0297 | 12.1554 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/11/2:00
9 | 11 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 254.0833 | 3.6824 | 86.148 | -75 | 4.0451 | 27.1593 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/11/3:00
9 | 11 | 1900-01-03 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 254.125 | 3.6662 | 86.148 | -75 | 4.0605 | 42.1631 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/11/4:00
9 | 11 | 1900-01-04 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 254.1667 | 3.65 | 86.148 | -75 | 4.0758 | 57.167 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 9/11/5:00
9 | 11 | 1900-01-05 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 254.2083 | 3.6339 | 86.148 | -75 | 4.0912 | 72.1708 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/11/6:00
9 | 11 | 1900-01-06 | 13.9 | 2 | 68 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 2 | 0 | 0 | 39.791 | 254.25 | 3.6177 | 86.148 | -75 | 4.1065 | 87.1746 | 5.3164 | 7.3164 | 2.3192 | 0 | 2.3192 | 57.02 | 2.3192 | 9/11/7:00
9 | 11 | 1900-01-07 | 16.7 | 82 | 299 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 82 | 0 | 0 | 39.791 | 254.2917 | 3.6015 | 86.148 | -75 | 4.1219 | 102.1785 | -36.3507 | 45.6493 | 14.47 | 0 | 14.47 | 62.06 | 14.47 | 9/11/8:00
9 | 11 | 1900-01-08 | 19.4 | 109 | 615 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 109 | 0 | 0 | 39.791 | 254.3333 | 3.5853 | 86.148 | -75 | 4.1373 | 117.1823 | -190.839 | -81.839 | -25.9415 | 0 | -25.9415 | 66.92 | -25.9415 | 9/11/9:00
9 | 11 | 1900-01-09 | 21.7 | 115 | 728 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 115 | 0 | 0 | 39.791 | 254.375 | 3.5691 | 86.148 | -75 | 4.1526 | 132.1862 | -345.9164 | -230.9164 | -73.1965 | 0 | -73.1965 | 71.06 | -73.1965 | 9/11/10:00
9 | 11 | 1900-01-10 | 22.2 | 135 | 745 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 135 | 0 | 0 | 39.791 | 254.4167 | 3.553 | 86.148 | -75 | 4.168 | 147.19 | -450.653 | -315.653 | -100.0565 | 0 | -100.0565 | 71.96 | -100.0565 | 9/11/11:00
9 | 11 | 1900-01-11 | 23.3 | 168 | 766 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 168 | 0 | 0 | 39.791 | 254.4583 | 3.5368 | 86.148 | -75 | 4.1834 | 162.1938 | -529.0779 | -361.0779 | -114.4554 | 0 | -114.4554 | 73.94 | -114.4554 | 9/11/12:00
9 | 11 | 1900-01-12 | 23.9 | 139 | 823 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 139 | 0 | 0 | 39.791 | 254.5 | 3.5206 | 86.148 | -75 | 4.1988 | 177.1977 | -598.0881 | -459.0881 | -145.5229 | 0 | -145.5229 | 75.02 | -145.5229 | 9/11/13:00
9 | 11 | 1900-01-13 | 25 | 158 | 796 | 77 | 0 | 1 | 0 | 77 | 0 | 158 | 0 | 0 | 39.791 | 254.5417 | 3.5044 | 86.148 | -75 | 4.2142 | 192.2015 | -565.5602 | -407.5602 | -129.1895 | 0 | -129.1895 | 77 | -129.1895 | 9/11/14:00
9 | 11 | 1900-01-14 | 25.6 | 184 | 692 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 184 | 0 | 0 | 39.791 | 254.5833 | 3.4882 | 86.148 | -75 | 4.2295 | 207.2054 | -445.0774 | -261.0774 | -82.757 | 0 | -82.757 | 78.08 | -82.757 | 9/11/15:00
9 | 11 | 1900-01-15 | 26.1 | 139 | 705 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 139 | 0 | 0 | 39.791 | 254.625 | 3.472 | 86.148 | -75 | 4.2449 | 222.2092 | -373.1821 | -234.1821 | -74.2316 | 0 | -74.2316 | 78.98 | -74.2316 | 9/11/16:00
9 | 11 | 1900-01-16 | 25.6 | 134 | 532 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 134 | 0 | 0 | 39.791 | 254.6667 | 3.4558 | 86.148 | -75 | 4.2603 | 237.2131 | -200.4354 | -66.4354 | -21.0588 | 0 | -21.0588 | 78.08 | -21.0588 | 9/11/17:00
9 | 11 | 1900-01-17 | 25 | 88 | 405 | 77 | 0 | 1 | 0 | 77 | 0 | 88 | 0 | 0 | 39.791 | 254.7083 | 3.4396 | 86.148 | -75 | 4.2757 | 252.2169 | -79.3214 | 8.6786 | 2.751 | 0 | 2.751 | 77 | 2.751 | 9/11/18:00
9 | 11 | 1900-01-18 | 24.4 | 25 | 180 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 25 | 0 | 0 | 39.791 | 254.75 | 3.4234 | 86.148 | -75 | 4.2911 | 267.2208 | 0.18466 | 25.1847 | 7.9831 | 0 | 7.9831 | 75.92 | 7.9831 | 9/11/19:00
9 | 11 | 1900-01-19 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 254.7917 | 3.4072 | 86.148 | -75 | 4.3065 | 282.2246 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 9/11/20:00
9 | 11 | 1900-01-20 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 254.8333 | 3.391 | 86.148 | -75 | 4.3219 | 297.2285 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 9/11/21:00
9 | 11 | 1900-01-21 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 254.875 | 3.3748 | 86.148 | -75 | 4.3373 | 312.2323 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/11/22:00
9 | 11 | 1900-01-22 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 254.9167 | 3.3586 | 86.148 | -75 | 4.3527 | 327.2362 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/11/23:00
9 | 11 | 1900-01-23 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 254.9583 | 3.3424 | 86.148 | -75 | 4.3681 | 342.24 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/11/24:00
9 | 12 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 255 | 3.3262 | 86.148 | -75 | 4.3835 | -2.7561 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/12/1:00
9 | 12 | 1900-01-01 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 255.0417 | 3.31 | 86.148 | -75 | 4.3989 | 12.2477 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/12/2:00
9 | 12 | 1900-01-02 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 255.0833 | 3.2938 | 86.148 | -75 | 4.4143 | 27.2516 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/12/3:00
9 | 12 | 1900-01-03 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 255.125 | 3.2776 | 86.148 | -75 | 4.4298 | 42.2554 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/12/4:00
9 | 12 | 1900-01-04 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 255.1667 | 3.2614 | 86.148 | -75 | 4.4452 | 57.2593 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/12/5:00
9 | 12 | 1900-01-05 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 255.2083 | 3.2452 | 86.148 | -75 | 4.4606 | 72.2631 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/12/6:00
9 | 12 | 1900-01-06 | 15 | 1 | 54 | 59 | 0 | 1 | 0 | 59 | 0 | 1 | 0 | 0 | 39.791 | 255.25 | 3.2289 | 86.148 | -75 | 4.476 | 87.267 | 3.9219 | 4.9219 | 1.5602 | 0 | 1.5602 | 59 | 1.5602 | 9/12/7:00
9 | 12 | 1900-01-07 | 16.7 | 94 | 251 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 94 | 0 | 0 | 39.791 | 255.2917 | 3.2127 | 86.148 | -75 | 4.4914 | 102.2709 | -31.9231 | 62.0769 | 19.6773 | 0 | 19.6773 | 62.06 | 19.6773 | 9/12/8:00
9 | 12 | 1900-01-08 | 19.4 | 120 | 502 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 120 | 0 | 0 | 39.791 | 255.3333 | 3.1965 | 86.148 | -75 | 4.5069 | 117.2747 | -158.5736 | -38.5736 | -12.2272 | 0 | -12.2272 | 66.92 | -12.2272 | 9/12/9:00
9 | 12 | 1900-01-09 | 21.1 | 125 | 692 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 125 | 0 | 0 | 39.791 | 255.375 | 3.1803 | 86.148 | -75 | 4.5223 | 132.2786 | -332.5877 | -207.5877 | -65.8017 | 0 | -65.8017 | 69.98 | -65.8017 | 9/12/10:00
9 | 12 | 1900-01-10 | 23.3 | 152 | 697 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 152 | 0 | 0 | 39.791 | 255.4167 | 3.1641 | 86.148 | -75 | 4.5377 | 147.2824 | -425.2859 | -273.2859 | -86.6268 | 0 | -86.6268 | 73.94 | -86.6268 | 9/12/11:00
9 | 12 | 1900-01-11 | 24.4 | 161 | 778 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 161 | 0 | 0 | 39.791 | 255.4583 | 3.1478 | 86.148 | -75 | 4.5531 | 162.2863 | -541.2593 | -380.2593 | -120.5356 | 0 | -120.5356 | 75.92 | -120.5356 | 9/12/12:00
9 | 12 | 1900-01-12 | 25.6 | 191 | 733 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 191 | 0 | 0 | 39.791 | 255.5 | 3.1316 | 86.148 | -75 | 4.5686 | 177.2901 | -536.128 | -345.128 | -109.3996 | 0 | -109.3996 | 78.08 | -109.3996 | 9/12/13:00
9 | 12 | 1900-01-13 | 26.1 | 258 | 563 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 258 | 0 | 0 | 39.791 | 255.5417 | 3.1154 | 86.148 | -75 | 4.584 | 192.294 | -402.4731 | -144.4731 | -45.7954 | 0 | -45.7954 | 78.98 | -45.7954 | 9/12/14:00
9 | 12 | 1900-01-14 | 26.1 | 188 | 697 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 188 | 0 | 0 | 39.791 | 255.5833 | 3.0992 | 86.148 | -75 | 4.5994 | 207.2979 | -451.1076 | -263.1076 | -83.4005 | 0 | -83.4005 | 78.98 | -83.4005 | 9/12/15:00
9 | 12 | 1900-01-15 | 26.7 | 140 | 699 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 140 | 0 | 0 | 39.791 | 255.625 | 3.0829 | 86.148 | -75 | 4.6149 | 222.3017 | -372.6111 | -232.6111 | -73.7337 | 0 | -73.7337 | 80.06 | -73.7337 | 9/12/16:00
9 | 12 | 1900-01-16 | 26.7 | 120 | 590 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 120 | 0 | 0 | 39.791 | 255.6667 | 3.0667 | 86.148 | -75 | 4.6303 | 237.3056 | -224.3275 | -104.3275 | -33.07 | 0 | -33.07 | 80.06 | -33.07 | 9/12/17:00
9 | 12 | 1900-01-17 | 26.1 | 79 | 404 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 79 | 0 | 0 | 39.791 | 255.7083 | 3.0505 | 86.148 | -75 | 4.6457 | 252.3094 | -80.4385 | -1.4385 | -0.45597 | 0 | -0.45597 | 78.98 | -0.45597 | 9/12/18:00
9 | 12 | 1900-01-18 | 23.3 | 23 | 155 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 23 | 0 | 0 | 39.791 | 255.75 | 3.0343 | 86.148 | -75 | 4.6612 | 267.3133 | -0.32405 | 22.6759 | 7.1879 | 0 | 7.1879 | 73.94 | 7.1879 | 9/12/19:00
9 | 12 | 1900-01-19 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 255.7917 | 3.018 | 86.148 | -75 | 4.6766 | 282.3172 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 9/12/20:00
9 | 12 | 1900-01-20 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 255.8333 | 3.0018 | 86.148 | -75 | 4.6921 | 297.321 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/12/21:00
9 | 12 | 1900-01-21 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 255.875 | 2.9856 | 86.148 | -75 | 4.7075 | 312.3249 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/12/22:00
9 | 12 | 1900-01-22 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 255.9167 | 2.9693 | 86.148 | -75 | 4.723 | 327.3287 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/12/23:00
9 | 12 | 1900-01-23 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 255.9583 | 2.9531 | 86.148 | -75 | 4.7384 | 342.3326 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/12/24:00
9 | 13 | 1899-12-31 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 256 | 2.9368 | 86.148 | -75 | 4.7539 | -2.6635 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/13/1:00
9 | 13 | 1900-01-01 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 256.0417 | 2.9206 | 86.148 | -75 | 4.7693 | 12.3403 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/13/2:00
9 | 13 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 256.0833 | 2.9044 | 86.148 | -75 | 4.7848 | 27.3442 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/13/3:00
9 | 13 | 1900-01-03 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 256.125 | 2.8881 | 86.148 | -75 | 4.8002 | 42.3481 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/13/4:00
9 | 13 | 1900-01-04 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 256.1667 | 2.8719 | 86.148 | -75 | 4.8157 | 57.3519 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/13/5:00
9 | 13 | 1900-01-05 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 256.2083 | 2.8556 | 86.148 | -75 | 4.8311 | 72.3558 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/13/6:00
9 | 13 | 1900-01-06 | 14.4 | 1 | 49 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 1 | 0 | 0 | 39.791 | 256.25 | 2.8394 | 86.148 | -75 | 4.8466 | 87.3597 | 3.2857 | 4.2857 | 1.3585 | 0 | 1.3585 | 57.92 | 1.3585 | 9/13/7:00
9 | 13 | 1900-01-07 | 17.2 | 88 | 245 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 88 | 0 | 0 | 39.791 | 256.2917 | 2.8231 | 86.148 | -75 | 4.8621 | 102.3635 | -32.536 | 55.464 | 17.5811 | 0 | 17.5811 | 62.96 | 17.5811 | 9/13/8:00
9 | 13 | 1900-01-08 | 20 | 143 | 396 | 68 | 0 | 1 | 0 | 68 | 0 | 143 | 0 | 0 | 39.791 | 256.3333 | 2.8069 | 86.148 | -75 | 4.8775 | 117.3674 | -127.2973 | 15.7027 | 4.9775 | 0 | 4.9775 | 68 | 4.9775 | 9/13/9:00
9 | 13 | 1900-01-09 | 22.8 | 176 | 557 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 176 | 0 | 0 | 39.791 | 256.375 | 2.7906 | 86.148 | -75 | 4.893 | 132.3712 | -270.7384 | -94.7384 | -30.0304 | 0 | -30.0304 | 73.04 | -30.0304 | 9/13/10:00
9 | 13 | 1900-01-10 | 25.6 | 156 | 721 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 156 | 0 | 0 | 39.791 | 256.4167 | 2.7744 | 86.148 | -75 | 4.9085 | 147.3751 | -443.7113 | -287.7113 | -91.1995 | 0 | -91.1995 | 78.08 | -91.1995 | 9/13/11:00
9 | 13 | 1900-01-11 | 27.2 | 199 | 693 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 199 | 0 | 0 | 39.791 | 256.4583 | 2.7581 | 86.148 | -75 | 4.9239 | 162.379 | -485.5758 | -286.5758 | -90.8395 | 0 | -90.8395 | 80.96 | -90.8395 | 9/13/12:00
9 | 13 | 1900-01-12 | 27.8 | 205 | 667 | 82.04 | 0 | 1 | 0 | 82.04 | 0 | 205 | 0 | 0 | 39.791 | 256.5 | 2.7419 | 86.148 | -75 | 4.9394 | 177.3828 | -490.9713 | -285.9713 | -90.6479 | 0 | -90.6479 | 82.04 | -90.6479 | 9/13/13:00
9 | 13 | 1900-01-13 | 28.3 | 228 | 640 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 228 | 0 | 0 | 39.791 | 256.5417 | 2.7256 | 86.148 | -75 | 4.9549 | 192.3867 | -460.2976 | -232.2976 | -73.6343 | 0 | -73.6343 | 82.94 | -73.6343 | 9/13/14:00
9 | 13 | 1900-01-14 | 28.3 | 249 | 513 | 82.94 | 0 | 1 | 0 | 82.94 | 0 | 249 | 0 | 0 | 39.791 | 256.5833 | 2.7094 | 86.148 | -75 | 4.9703 | 207.3906 | -334.0792 | -85.0792 | -26.9686 | 0 | -26.9686 | 82.94 | -26.9686 | 9/13/15:00
9 | 13 | 1900-01-15 | 26.7 | 271 | 284 | 80.06 | 0 | 1 | 0 | 80.06 | 0 | 271 | 0 | 0 | 39.791 | 256.625 | 2.6931 | 86.148 | -75 | 4.9858 | 222.3944 | -152.4427 | 118.5573 | 37.5806 | 0 | 37.5806 | 80.06 | 37.5806 | 9/13/16:00
9 | 13 | 1900-01-16 | 23.9 | 204 | 47 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 204 | 0 | 0 | 39.791 | 256.6667 | 2.6769 | 86.148 | -75 | 5.0013 | 237.3983 | -18.0321 | 185.9679 | 58.9486 | 0 | 58.9486 | 75.02 | 58.9486 | 9/13/17:00
9 | 13 | 1900-01-17 | 20.6 | 86 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 86 | 0 | 0 | 39.791 | 256.7083 | 2.6606 | 86.148 | -75 | 5.0167 | 252.4022 | 0 | 86 | 27.2605 | 0 | 27.2605 | 69.08 | 27.2605 | 9/13/18:00
9 | 13 | 1900-01-18 | 18.3 | 13 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 13 | 0 | 0 | 39.791 | 256.75 | 2.6443 | 86.148 | -75 | 5.0322 | 267.4061 | 0 | 13 | 4.1208 | 0 | 4.1208 | 64.94 | 4.1208 | 9/13/19:00
9 | 13 | 1900-01-19 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 256.7917 | 2.6281 | 86.148 | -75 | 5.0477 | 282.4099 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/13/20:00
9 | 13 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 256.8333 | 2.6118 | 86.148 | -75 | 5.0632 | 297.4138 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/13/21:00
9 | 13 | 1900-01-21 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 256.875 | 2.5955 | 86.148 | -75 | 5.0786 | 312.4177 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/13/22:00
9 | 13 | 1900-01-22 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 256.9167 | 2.5793 | 86.148 | -75 | 5.0941 | 327.4215 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/13/23:00
9 | 13 | 1900-01-23 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 256.9583 | 2.563 | 86.148 | -75 | 5.1096 | 342.4254 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/13/24:00
9 | 14 | 1899-12-31 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 257 | 2.5468 | 86.148 | -75 | 5.1251 | -2.5707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/14/1:00
9 | 14 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 257.0417 | 2.5305 | 86.148 | -75 | 5.1405 | 12.4331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/14/2:00
9 | 14 | 1900-01-02 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 257.0833 | 2.5142 | 86.148 | -75 | 5.156 | 27.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/14/3:00
9 | 14 | 1900-01-03 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 257.125 | 2.4979 | 86.148 | -75 | 5.1715 | 42.4409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/14/4:00
9 | 14 | 1900-01-04 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 257.1667 | 2.4817 | 86.148 | -75 | 5.187 | 57.4447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/14/5:00
9 | 14 | 1900-01-05 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 257.2083 | 2.4654 | 86.148 | -75 | 5.2025 | 72.4486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/14/6:00
9 | 14 | 1900-01-06 | 10 | 1 | 49 | 50 | 1 | 0 | 50 | 0 | 0 | 1 | 0 | 0 | 39.791 | 257.25 | 2.4491 | 86.148 | -75 | 5.2179 | 87.4525 | 3.012 | 4.012 | 1.2717 | 1.2717 | 0 | 0 | 0 | 9/14/7:00
9 | 14 | 1900-01-07 | 11.1 | 87 | 260 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 87 | 0 | 0 | 39.791 | 257.2917 | 2.4328 | 86.148 | -75 | 5.2334 | 102.4564 | -35.9895 | 51.0105 | 16.1694 | 16.1694 | 0 | 0 | 0 | 9/14/8:00
9 | 14 | 1900-01-08 | 12.8 | 112 | 534 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 112 | 0 | 0 | 39.791 | 257.3333 | 2.4166 | 86.148 | -75 | 5.2489 | 117.4602 | -174.6324 | -62.6324 | -19.8534 | 0 | -19.8534 | 55.04 | -19.8534 | 9/14/9:00
9 | 14 | 1900-01-09 | 14.4 | 178 | 557 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 178 | 0 | 0 | 39.791 | 257.375 | 2.4003 | 86.148 | -75 | 5.2644 | 132.4641 | -273.7651 | -95.7651 | -30.3559 | 0 | -30.3559 | 57.92 | -30.3559 | 9/14/10:00
9 | 14 | 1900-01-10 | 15.6 | 166 | 655 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 166 | 0 | 0 | 39.791 | 257.4167 | 2.384 | 86.148 | -75 | 5.2799 | 147.468 | -406.5161 | -240.5161 | -76.2394 | 0 | -76.2394 | 60.08 | -76.2394 | 9/14/11:00
9 | 14 | 1900-01-11 | 17.2 | 156 | 784 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 156 | 0 | 0 | 39.791 | 257.4583 | 2.3677 | 86.148 | -75 | 5.2954 | 162.4718 | -553.2232 | -397.2232 | -125.9128 | 0 | -125.9128 | 62.96 | -125.9128 | 9/14/12:00
9 | 14 | 1900-01-12 | 17.8 | 184 | 733 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 184 | 0 | 0 | 39.791 | 257.5 | 2.3515 | 86.148 | -75 | 5.3108 | 177.4757 | -542.9579 | -358.9579 | -113.7834 | 0 | -113.7834 | 64.04 | -113.7834 | 9/14/13:00
9 | 14 | 1900-01-13 | 18.9 | 171 | 754 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 171 | 0 | 0 | 39.791 | 257.5417 | 2.3352 | 86.148 | -75 | 5.3263 | 192.4796 | -545.5416 | -374.5416 | -118.7231 | 0 | -118.7231 | 66.02 | -118.7231 | 9/14/14:00
9 | 14 | 1900-01-14 | 19.4 | 140 | 781 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 140 | 0 | 0 | 39.791 | 257.5833 | 2.3189 | 86.148 | -75 | 5.3418 | 207.4835 | -511.7225 | -371.7225 | -117.8295 | 0 | -117.8295 | 66.92 | -117.8295 | 9/14/15:00
9 | 14 | 1900-01-15 | 19.4 | 125 | 734 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 125 | 0 | 0 | 39.791 | 257.625 | 2.3026 | 86.148 | -75 | 5.3573 | 222.4873 | -396.695 | -271.695 | -86.1226 | 0 | -86.1226 | 66.92 | -86.1226 | 9/14/16:00
9 | 14 | 1900-01-16 | 18.9 | 133 | 583 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 133 | 0 | 0 | 39.791 | 257.6667 | 2.2863 | 86.148 | -75 | 5.3728 | 237.4912 | -225.6746 | -92.6746 | -29.3762 | 0 | -29.3762 | 66.02 | -29.3762 | 9/14/17:00
9 | 14 | 1900-01-17 | 18.3 | 106 | 84 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 106 | 0 | 0 | 39.791 | 257.7083 | 2.27 | 86.148 | -75 | 5.3883 | 252.4951 | -17.2695 | 88.7305 | 28.126 | 0 | 28.126 | 64.94 | 28.126 | 9/14/18:00
9 | 14 | 1900-01-18 | 17.2 | 21 | 64 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 21 | 0 | 0 | 39.791 | 257.75 | 2.2538 | 86.148 | -75 | 5.4038 | 267.4989 | -0.53356 | 20.4664 | 6.4875 | 0 | 6.4875 | 62.96 | 6.4875 | 9/14/19:00
9 | 14 | 1900-01-19 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 257.7917 | 2.2375 | 86.148 | -75 | 5.4192 | 282.5028 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/14/20:00
9 | 14 | 1900-01-20 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 257.8333 | 2.2212 | 86.148 | -75 | 5.4347 | 297.5067 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/14/21:00
9 | 14 | 1900-01-21 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 257.875 | 2.2049 | 86.148 | -75 | 5.4502 | 312.5106 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/14/22:00
9 | 14 | 1900-01-22 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 257.9167 | 2.1886 | 86.148 | -75 | 5.4657 | 327.5144 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/14/23:00
9 | 14 | 1900-01-23 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 257.9583 | 2.1723 | 86.148 | -75 | 5.4812 | 342.5183 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/14/24:00
9 | 15 | 1899-12-31 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 258 | 2.156 | 86.148 | -75 | 5.4967 | -2.4778 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/15/1:00
9 | 15 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 258.0417 | 2.1397 | 86.148 | -75 | 5.5122 | 12.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/15/2:00
9 | 15 | 1900-01-02 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 258.0833 | 2.1234 | 86.148 | -75 | 5.5276 | 27.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/15/3:00
9 | 15 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 258.125 | 2.1071 | 86.148 | -75 | 5.5431 | 42.5338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/15/4:00
9 | 15 | 1900-01-04 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 258.1667 | 2.0908 | 86.148 | -75 | 5.5586 | 57.5377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/15/5:00
9 | 15 | 1900-01-05 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 258.2083 | 2.0745 | 86.148 | -75 | 5.5741 | 72.5415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/15/6:00
9 | 15 | 1900-01-06 | 10 | 0 | 7 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 258.25 | 2.0582 | 86.148 | -75 | 5.5896 | 87.5454 | 0.39111 | 0.39111 | 0.12397 | 0.12397 | 0 | 0 | 0 | 9/15/7:00
9 | 15 | 1900-01-07 | 11.7 | 85 | 42 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 85 | 0 | 0 | 39.791 | 258.2917 | 2.042 | 86.148 | -75 | 5.6051 | 102.5493 | -6.0499 | 78.9501 | 25.0258 | 25.0258 | 0 | 0 | 0 | 9/15/8:00
9 | 15 | 1900-01-08 | 14.4 | 148 | 447 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 148 | 0 | 0 | 39.791 | 258.3333 | 2.0257 | 86.148 | -75 | 5.6206 | 117.5531 | -148.6671 | -0.66707 | -0.21145 | 0 | -0.21145 | 57.92 | -0.21145 | 9/15/9:00
9 | 15 | 1900-01-09 | 16.1 | 239 | 319 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 239 | 0 | 0 | 39.791 | 258.375 | 2.0094 | 86.148 | -75 | 5.6361 | 132.557 | -158.5165 | 80.4835 | 25.5119 | 0 | 25.5119 | 60.98 | 25.5119 | 9/15/10:00
9 | 15 | 1900-01-10 | 17.2 | 190 | 661 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 190 | 0 | 0 | 39.791 | 258.4167 | 1.9931 | 86.148 | -75 | 5.6515 | 147.5609 | -413.6782 | -223.6782 | -70.9021 | 0 | -70.9021 | 62.96 | -70.9021 | 9/15/11:00
9 | 15 | 1900-01-11 | 18.3 | 243 | 585 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 243 | 0 | 0 | 39.791 | 258.4583 | 1.9767 | 86.148 | -75 | 5.667 | 162.5648 | -415.6832 | -172.6832 | -54.7376 | 0 | -54.7376 | 64.94 | -54.7376 | 9/15/12:00
9 | 15 | 1900-01-12 | 20 | 216 | 697 | 68 | 0 | 1 | 0 | 68 | 0 | 216 | 0 | 0 | 39.791 | 258.5 | 1.9604 | 86.148 | -75 | 5.6825 | 177.5686 | -519.5084 | -303.5084 | -96.2069 | 0 | -96.2069 | 68 | -96.2069 | 9/15/13:00
9 | 15 | 1900-01-13 | 21.1 | 164 | 766 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 164 | 0 | 0 | 39.791 | 258.5417 | 1.9441 | 86.148 | -75 | 5.698 | 192.5725 | -557.5069 | -393.5069 | -124.7348 | 0 | -124.7348 | 69.98 | -124.7348 | 9/15/14:00
9 | 15 | 1900-01-14 | 21.7 | 125 | 799 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 125 | 0 | 0 | 39.791 | 258.5833 | 1.9278 | 86.148 | -75 | 5.7135 | 207.5764 | -526.6818 | -401.6818 | -127.3261 | 0 | -127.3261 | 71.06 | -127.3261 | 9/15/15:00
9 | 15 | 1900-01-15 | 21.7 | 117 | 752 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 117 | 0 | 0 | 39.791 | 258.625 | 1.9115 | 86.148 | -75 | 5.729 | 222.5802 | -409.1798 | -292.1798 | -92.6159 | 0 | -92.6159 | 71.06 | -92.6159 | 9/15/16:00
9 | 15 | 1900-01-16 | 21.1 | 114 | 583 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 114 | 0 | 0 | 39.791 | 258.6667 | 1.8952 | 86.148 | -75 | 5.7445 | 237.5841 | -227.6671 | -113.6671 | -36.0305 | 0 | -36.0305 | 69.98 | -36.0305 | 9/15/17:00
9 | 15 | 1900-01-17 | 20.6 | 63 | 480 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 63 | 0 | 0 | 39.791 | 258.7083 | 1.8789 | 86.148 | -75 | 5.7599 | 252.588 | -100.2358 | -37.2358 | -11.8031 | 0 | -11.8031 | 69.08 | -11.8031 | 9/15/18:00
9 | 15 | 1900-01-18 | 18.9 | 19 | 79 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 19 | 0 | 0 | 39.791 | 258.75 | 1.8626 | 86.148 | -75 | 5.7754 | 267.5919 | -0.9059 | 18.0941 | 5.7355 | 0 | 5.7355 | 66.02 | 5.7355 | 9/15/19:00
9 | 15 | 1900-01-19 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 258.7917 | 1.8463 | 86.148 | -75 | 5.7909 | 282.5957 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/15/20:00
9 | 15 | 1900-01-20 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 258.8333 | 1.83 | 86.148 | -75 | 5.8064 | 297.5996 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/15/21:00
9 | 15 | 1900-01-21 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 258.875 | 1.8137 | 86.148 | -75 | 5.8219 | 312.6035 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/15/22:00
9 | 15 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 258.9167 | 1.7974 | 86.148 | -75 | 5.8374 | 327.6073 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/15/23:00
9 | 15 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 258.9583 | 1.7811 | 86.148 | -75 | 5.8528 | 342.6112 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/15/24:00
9 | 16 | 1899-12-31 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 259 | 1.7648 | 86.148 | -75 | 5.8683 | -2.3849 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 9/16/1:00
9 | 16 | 1900-01-01 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 259.0417 | 1.7484 | 86.148 | -75 | 5.8838 | 12.6189 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/16/2:00
9 | 16 | 1900-01-02 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 259.0833 | 1.7321 | 86.148 | -75 | 5.8993 | 27.6228 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/16/3:00
9 | 16 | 1900-01-03 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 259.125 | 1.7158 | 86.148 | -75 | 5.9147 | 42.6267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/16/4:00
9 | 16 | 1900-01-04 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 259.1667 | 1.6995 | 86.148 | -75 | 5.9302 | 57.6306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/16/5:00
9 | 16 | 1900-01-05 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 259.2083 | 1.6832 | 86.148 | -75 | 5.9457 | 72.6344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/16/6:00
9 | 16 | 1900-01-06 | 11.7 | 0 | 8 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 259.25 | 1.6669 | 86.148 | -75 | 5.9612 | 87.6383 | 0.40213 | 0.40213 | 0.12747 | 0.12747 | 0 | 0 | 0 | 9/16/7:00
9 | 16 | 1900-01-07 | 12.2 | 85 | 50 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 85 | 0 | 0 | 39.791 | 259.2917 | 1.6505 | 86.148 | -75 | 5.9767 | 102.6422 | -7.4833 | 77.5167 | 24.5714 | 24.5714 | 0 | 0 | 0 | 9/16/8:00
9 | 16 | 1900-01-08 | 14.4 | 150 | 352 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 150 | 0 | 0 | 39.791 | 259.3333 | 1.6342 | 86.148 | -75 | 5.9921 | 117.646 | -119.0251 | 30.9749 | 9.8185 | 0 | 9.8185 | 57.92 | 9.8185 | 9/16/9:00
9 | 16 | 1900-01-09 | 16.7 | 138 | 662 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 138 | 0 | 0 | 39.791 | 259.375 | 1.6179 | 86.148 | -75 | 6.0076 | 132.6499 | -332.5333 | -194.5333 | -61.6636 | 0 | -61.6636 | 62.06 | -61.6636 | 9/16/10:00
9 | 16 | 1900-01-10 | 18.3 | 167 | 661 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 167 | 0 | 0 | 39.791 | 259.4167 | 1.6016 | 86.148 | -75 | 6.0231 | 147.6538 | -417.0998 | -250.0998 | -79.2773 | 0 | -79.2773 | 64.94 | -79.2773 | 9/16/11:00
9 | 16 | 1900-01-11 | 19.4 | 197 | 681 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 197 | 0 | 0 | 39.791 | 259.4583 | 1.5853 | 86.148 | -75 | 6.0385 | 162.6576 | -487.2338 | -290.2338 | -91.999 | 0 | -91.999 | 66.92 | -91.999 | 9/16/12:00
9 | 16 | 1900-01-12 | 20.6 | 202 | 703 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 202 | 0 | 0 | 39.791 | 259.5 | 1.5689 | 86.148 | -75 | 6.054 | 177.6615 | -527.2033 | -325.2033 | -103.0838 | 0 | -103.0838 | 69.08 | -103.0838 | 9/16/13:00
9 | 16 | 1900-01-13 | 22.2 | 160 | 784 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 160 | 0 | 0 | 39.791 | 259.5417 | 1.5526 | 86.148 | -75 | 6.0695 | 192.6654 | -573.944 | -413.944 | -131.213 | 0 | -131.213 | 71.96 | -131.213 | 9/16/14:00
9 | 16 | 1900-01-14 | 22.2 | 138 | 769 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 138 | 0 | 0 | 39.791 | 259.5833 | 1.5363 | 86.148 | -75 | 6.0849 | 207.6692 | -509.9324 | -371.9324 | -117.8961 | 0 | -117.8961 | 71.96 | -117.8961 | 9/16/15:00
9 | 16 | 1900-01-15 | 22.2 | 118 | 728 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 118 | 0 | 0 | 39.791 | 259.625 | 1.52 | 86.148 | -75 | 6.1004 | 222.6731 | -398.7739 | -280.7739 | -89.0004 | 0 | -89.0004 | 71.96 | -89.0004 | 9/16/16:00
9 | 16 | 1900-01-16 | 22.2 | 92 | 664 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 92 | 0 | 0 | 39.791 | 259.6667 | 1.5037 | 86.148 | -75 | 6.1159 | 237.677 | -261.5586 | -169.5586 | -53.7471 | 0 | -53.7471 | 71.96 | -53.7471 | 9/16/17:00
9 | 16 | 1900-01-17 | 21.7 | 58 | 506 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 58 | 0 | 0 | 39.791 | 259.7083 | 1.4873 | 86.148 | -75 | 6.1313 | 252.6808 | -107.2998 | -49.2998 | -15.6272 | 0 | -15.6272 | 71.06 | -15.6272 | 9/16/18:00
9 | 16 | 1900-01-18 | 21.1 | 17 | 98 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 17 | 0 | 0 | 39.791 | 259.75 | 1.471 | 86.148 | -75 | 6.1468 | 267.6847 | -1.431 | 15.569 | 4.9351 | 0 | 4.9351 | 69.98 | 4.9351 | 9/16/19:00
9 | 16 | 1900-01-19 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 259.7917 | 1.4547 | 86.148 | -75 | 6.1623 | 282.6886 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/16/20:00
9 | 16 | 1900-01-20 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 259.8333 | 1.4384 | 86.148 | -75 | 6.1777 | 297.6924 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/16/21:00
9 | 16 | 1900-01-21 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 259.875 | 1.422 | 86.148 | -75 | 6.1932 | 312.6963 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/16/22:00
9 | 16 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 259.9167 | 1.4057 | 86.148 | -75 | 6.2087 | 327.7002 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/16/23:00
9 | 16 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 259.9583 | 1.3894 | 86.148 | -75 | 6.2241 | 342.704 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/16/24:00
9 | 17 | 1899-12-31 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 260 | 1.373 | 86.148 | -75 | 6.2396 | -2.2921 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/17/1:00
9 | 17 | 1900-01-01 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 260.0417 | 1.3567 | 86.148 | -75 | 6.255 | 12.7118 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/17/2:00
9 | 17 | 1900-01-02 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 260.0833 | 1.3404 | 86.148 | -75 | 6.2705 | 27.7156 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/17/3:00
9 | 17 | 1900-01-03 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 260.125 | 1.3241 | 86.148 | -75 | 6.2859 | 42.7195 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/17/4:00
9 | 17 | 1900-01-04 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 260.1667 | 1.3077 | 86.148 | -75 | 6.3014 | 57.7233 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/17/5:00
9 | 17 | 1900-01-05 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 260.2083 | 1.2914 | 86.148 | -75 | 6.3168 | 72.7272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/17/6:00
9 | 17 | 1900-01-06 | 12.8 | 0 | 5 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 260.25 | 1.2751 | 86.148 | -75 | 6.3323 | 87.7311 | 0.22327 | 0.22327 | 0.070773 | 0 | 0.070773 | 55.04 | 0.070773 | 9/17/7:00
9 | 17 | 1900-01-07 | 13.9 | 88 | 36 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 88 | 0 | 0 | 39.791 | 260.2917 | 1.2587 | 86.148 | -75 | 6.3477 | 102.7349 | -5.5902 | 82.4098 | 26.1225 | 0 | 26.1225 | 57.02 | 26.1225 | 9/17/8:00
9 | 17 | 1900-01-08 | 16.7 | 173 | 202 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 173 | 0 | 0 | 39.791 | 260.3333 | 1.2424 | 86.148 | -75 | 6.3632 | 117.7388 | -69.4228 | 103.5772 | 32.8322 | 0 | 32.8322 | 62.06 | 32.8322 | 9/17/9:00
9 | 17 | 1900-01-09 | 18.9 | 237 | 61 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 237 | 0 | 0 | 39.791 | 260.375 | 1.2261 | 86.148 | -75 | 6.3786 | 132.7427 | -30.9693 | 206.0307 | 65.3081 | 0 | 65.3081 | 66.02 | 65.3081 | 9/17/10:00
9 | 17 | 1900-01-10 | 21.1 | 207 | 643 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 207 | 0 | 0 | 39.791 | 260.4167 | 1.2097 | 86.148 | -75 | 6.394 | 147.7465 | -409.0525 | -202.0525 | -64.0471 | 0 | -64.0471 | 69.98 | -64.0471 | 9/17/11:00
9 | 17 | 1900-01-11 | 23.3 | 246 | 603 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 246 | 0 | 0 | 39.791 | 260.4583 | 1.1934 | 86.148 | -75 | 6.4095 | 162.7504 | -434.3622 | -188.3622 | -59.7075 | 0 | -59.7075 | 73.94 | -59.7075 | 9/17/12:00
9 | 17 | 1900-01-12 | 23.9 | 365 | 294 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 365 | 0 | 0 | 39.791 | 260.5 | 1.1771 | 86.148 | -75 | 6.4249 | 177.7542 | -221.8187 | 143.1813 | 45.386 | 0 | 45.386 | 75.02 | 45.386 | 9/17/13:00
9 | 17 | 1900-01-13 | 23.9 | 361 | 138 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 361 | 0 | 0 | 39.791 | 260.5417 | 1.1607 | 86.148 | -75 | 6.4404 | 192.7581 | -101.6088 | 259.3912 | 82.2225 | 0 | 82.2225 | 75.02 | 82.2225 | 9/17/14:00
9 | 17 | 1900-01-14 | 23.9 | 278 | 24 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 278 | 0 | 0 | 39.791 | 260.5833 | 1.1444 | 86.148 | -75 | 6.4558 | 207.7619 | -16.0084 | 261.9916 | 83.0467 | 0 | 83.0467 | 75.02 | 83.0467 | 9/17/15:00
9 | 17 | 1900-01-15 | 23.3 | 267 | 136 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 267 | 0 | 0 | 39.791 | 260.625 | 1.128 | 86.148 | -75 | 6.4712 | 222.7658 | -74.9889 | 192.0111 | 60.8642 | 0 | 60.8642 | 73.94 | 60.8642 | 9/17/16:00
9 | 17 | 1900-01-16 | 22.8 | 192 | 23 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 192 | 0 | 0 | 39.791 | 260.6667 | 1.1117 | 86.148 | -75 | 6.4866 | 237.7697 | -9.138 | 182.862 | 57.9641 | 0 | 57.9641 | 73.04 | 57.9641 | 9/17/17:00
9 | 17 | 1900-01-17 | 22.2 | 94 | 17 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 94 | 0 | 0 | 39.791 | 260.7083 | 1.0954 | 86.148 | -75 | 6.5021 | 252.7735 | -3.6598 | 90.3402 | 28.6363 | 0 | 28.6363 | 71.96 | 28.6363 | 9/17/18:00
9 | 17 | 1900-01-18 | 21.7 | 9 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 9 | 0 | 0 | 39.791 | 260.75 | 1.079 | 86.148 | -75 | 6.5175 | 267.7774 | 0 | 9 | 2.8528 | 0 | 2.8528 | 71.06 | 2.8528 | 9/17/19:00
9 | 17 | 1900-01-19 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 260.7917 | 1.0627 | 86.148 | -75 | 6.5329 | 282.7812 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 9/17/20:00
9 | 17 | 1900-01-20 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 260.8333 | 1.0464 | 86.148 | -75 | 6.5484 | 297.7851 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/17/21:00
9 | 17 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 260.875 | 1.03 | 86.148 | -75 | 6.5638 | 312.7889 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/17/22:00
9 | 17 | 1900-01-22 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 260.9167 | 1.0137 | 86.148 | -75 | 6.5792 | 327.7928 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/17/23:00
9 | 17 | 1900-01-23 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 260.9583 | 0.99733 | 86.148 | -75 | 6.5946 | 342.7967 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/17/24:00
9 | 18 | 1899-12-31 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 261 | 0.98099 | 86.148 | -75 | 6.61 | -2.1995 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/18/1:00
9 | 18 | 1900-01-01 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 261.0417 | 0.96465 | 86.148 | -75 | 6.6254 | 12.8044 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/18/2:00
9 | 18 | 1900-01-02 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 261.0833 | 0.9483 | 86.148 | -75 | 6.6408 | 27.8082 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/18/3:00
9 | 18 | 1900-01-03 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 261.125 | 0.93196 | 86.148 | -75 | 6.6563 | 42.8121 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/18/4:00
9 | 18 | 1900-01-04 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 261.1667 | 0.91562 | 86.148 | -75 | 6.6717 | 57.8159 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/18/5:00
9 | 18 | 1900-01-05 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 261.2083 | 0.89928 | 86.148 | -75 | 6.6871 | 72.8198 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/18/6:00
9 | 18 | 1900-01-06 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 261.25 | 0.88293 | 86.148 | -75 | 6.7025 | 87.8236 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/18/7:00
9 | 18 | 1900-01-07 | 18.3 | 58 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 58 | 0 | 0 | 39.791 | 261.2917 | 0.86659 | 86.148 | -75 | 6.7179 | 102.8275 | 0 | 58 | 18.385 | 0 | 18.385 | 64.94 | 18.385 | 9/18/8:00
9 | 18 | 1900-01-08 | 18.9 | 143 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 143 | 0 | 0 | 39.791 | 261.3333 | 0.85024 | 86.148 | -75 | 6.7333 | 117.8313 | 0 | 143 | 45.3285 | 0 | 45.3285 | 66.02 | 45.3285 | 9/18/9:00
9 | 18 | 1900-01-09 | 19.4 | 132 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 132 | 0 | 0 | 39.791 | 261.375 | 0.8339 | 86.148 | -75 | 6.7487 | 132.8352 | 0 | 132 | 41.8417 | 0 | 41.8417 | 66.92 | 41.8417 | 9/18/10:00
9 | 18 | 1900-01-10 | 20.6 | 120 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 120 | 0 | 0 | 39.791 | 261.4167 | 0.81756 | 86.148 | -75 | 6.764 | 147.839 | 0 | 120 | 38.0379 | 0 | 38.0379 | 69.08 | 38.0379 | 9/18/11:00
9 | 18 | 1900-01-11 | 20.6 | 228 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 228 | 0 | 0 | 39.791 | 261.4583 | 0.80121 | 86.148 | -75 | 6.7794 | 162.8429 | 0 | 228 | 72.272 | 0 | 72.272 | 69.08 | 72.272 | 9/18/12:00
9 | 18 | 1900-01-12 | 21.7 | 200 | 6 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 200 | 0 | 0 | 39.791 | 261.5 | 0.78486 | 86.148 | -75 | 6.7948 | 177.8467 | -4.554 | 195.446 | 61.953 | 0 | 61.953 | 71.06 | 61.953 | 9/18/13:00
9 | 18 | 1900-01-13 | 22.8 | 333 | 36 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 333 | 0 | 0 | 39.791 | 261.5417 | 0.76852 | 86.148 | -75 | 6.8102 | 192.8506 | -26.6575 | 306.3425 | 97.1052 | 0 | 97.1052 | 73.04 | 97.1052 | 9/18/14:00
9 | 18 | 1900-01-14 | 23.3 | 334 | 83 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 334 | 0 | 0 | 39.791 | 261.5833 | 0.75217 | 86.148 | -75 | 6.8256 | 207.8544 | -55.6845 | 278.3155 | 88.2212 | 0 | 88.2212 | 73.94 | 88.2212 | 9/18/15:00
9 | 18 | 1900-01-15 | 23.3 | 263 | 77 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 263 | 0 | 0 | 39.791 | 261.625 | 0.73582 | 86.148 | -75 | 6.841 | 222.8582 | -42.7342 | 220.2658 | 69.8204 | 0 | 69.8204 | 73.94 | 69.8204 | 9/18/16:00
9 | 18 | 1900-01-16 | 23.3 | 178 | 17 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 178 | 0 | 0 | 39.791 | 261.6667 | 0.71948 | 86.148 | -75 | 6.8564 | 237.8621 | -6.8116 | 171.1884 | 54.2637 | 0 | 54.2637 | 73.94 | 54.2637 | 9/18/17:00
9 | 18 | 1900-01-17 | 22.8 | 93 | 17 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 93 | 0 | 0 | 39.791 | 261.7083 | 0.70313 | 86.148 | -75 | 6.8717 | 252.8659 | -3.7145 | 89.2855 | 28.3019 | 0 | 28.3019 | 73.04 | 28.3019 | 9/18/18:00
9 | 18 | 1900-01-18 | 21.1 | 8 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 8 | 0 | 0 | 39.791 | 261.75 | 0.68678 | 86.148 | -75 | 6.8871 | 267.8698 | 0 | 8 | 2.5359 | 0 | 2.5359 | 69.98 | 2.5359 | 9/18/19:00
9 | 18 | 1900-01-19 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 261.7917 | 0.67043 | 86.148 | -75 | 6.9025 | 282.8736 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/18/20:00
9 | 18 | 1900-01-20 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 261.8333 | 0.65409 | 86.148 | -75 | 6.9178 | 297.8775 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/18/21:00
9 | 18 | 1900-01-21 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 261.875 | 0.63774 | 86.148 | -75 | 6.9332 | 312.8813 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 9/18/22:00
9 | 18 | 1900-01-22 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 261.9167 | 0.62139 | 86.148 | -75 | 6.9486 | 327.8851 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/18/23:00
9 | 18 | 1900-01-23 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 261.9583 | 0.60504 | 86.148 | -75 | 6.9639 | 342.889 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/18/24:00
9 | 19 | 1899-12-31 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 262 | 0.58869 | 86.148 | -75 | 6.9793 | -2.1072 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/19/1:00
9 | 19 | 1900-01-01 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 262.0417 | 0.57234 | 86.148 | -75 | 6.9946 | 12.8967 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/19/2:00
9 | 19 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 262.0833 | 0.55599 | 86.148 | -75 | 7.01 | 27.9005 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/19/3:00
9 | 19 | 1900-01-03 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 262.125 | 0.53964 | 86.148 | -75 | 7.0253 | 42.9043 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/19/4:00
9 | 19 | 1900-01-04 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 262.1667 | 0.52329 | 86.148 | -75 | 7.0407 | 57.9082 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/19/5:00
9 | 19 | 1900-01-05 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 262.2083 | 0.50694 | 86.148 | -75 | 7.056 | 72.912 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/19/6:00
9 | 19 | 1900-01-06 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 262.25 | 0.49059 | 86.148 | -75 | 7.0714 | 87.9158 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/19/7:00
9 | 19 | 1900-01-07 | 20.6 | 19 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 19 | 0 | 0 | 39.791 | 262.2917 | 0.47424 | 86.148 | -75 | 7.0867 | 102.9197 | 0 | 19 | 6.0227 | 0 | 6.0227 | 69.08 | 6.0227 | 9/19/8:00
9 | 19 | 1900-01-08 | 20.6 | 72 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 72 | 0 | 0 | 39.791 | 262.3333 | 0.45789 | 86.148 | -75 | 7.102 | 117.9235 | 0 | 72 | 22.8227 | 0 | 22.8227 | 69.08 | 22.8227 | 9/19/9:00
9 | 19 | 1900-01-09 | 18.9 | 79 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 79 | 0 | 0 | 39.791 | 262.375 | 0.44154 | 86.148 | -75 | 7.1174 | 132.9273 | 0 | 79 | 25.0416 | 0 | 25.0416 | 66.02 | 25.0416 | 9/19/10:00
9 | 19 | 1900-01-10 | 18.9 | 261 | 36 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 261 | 0 | 0 | 39.791 | 262.4167 | 0.42518 | 86.148 | -75 | 7.1327 | 147.9312 | -23.2693 | 237.7307 | 75.3565 | 0 | 75.3565 | 66.02 | 75.3565 | 9/19/11:00
9 | 19 | 1900-01-11 | 18.3 | 205 | 6 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 205 | 0 | 0 | 39.791 | 262.4583 | 0.40883 | 86.148 | -75 | 7.148 | 162.935 | -4.3798 | 200.6202 | 63.5931 | 0 | 63.5931 | 64.94 | 63.5931 | 9/19/12:00
9 | 19 | 1900-01-12 | 19.4 | 151 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 151 | 0 | 0 | 39.791 | 262.5 | 0.39248 | 86.148 | -75 | 7.1633 | 177.9388 | 0 | 151 | 47.8644 | 0 | 47.8644 | 66.92 | 47.8644 | 9/19/13:00
9 | 19 | 1900-01-13 | 20.6 | 160 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 160 | 0 | 0 | 39.791 | 262.5417 | 0.37613 | 86.148 | -75 | 7.1786 | 192.9427 | 0 | 160 | 50.7172 | 0 | 50.7172 | 69.08 | 50.7172 | 9/19/14:00
9 | 19 | 1900-01-14 | 20.6 | 144 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 144 | 0 | 0 | 39.791 | 262.5833 | 0.35978 | 86.148 | -75 | 7.194 | 207.9465 | 0 | 144 | 45.6455 | 0 | 45.6455 | 69.08 | 45.6455 | 9/19/15:00
9 | 19 | 1900-01-15 | 22.2 | 151 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 151 | 0 | 0 | 39.791 | 262.625 | 0.34342 | 86.148 | -75 | 7.2093 | 222.9503 | 0 | 151 | 47.8644 | 0 | 47.8644 | 71.96 | 47.8644 | 9/19/16:00
9 | 19 | 1900-01-16 | 20.6 | 90 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 90 | 0 | 0 | 39.791 | 262.6667 | 0.32707 | 86.148 | -75 | 7.2246 | 237.9541 | 0 | 90 | 28.5284 | 0 | 28.5284 | 69.08 | 28.5284 | 9/19/17:00
9 | 19 | 1900-01-17 | 19.4 | 69 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 69 | 0 | 0 | 39.791 | 262.7083 | 0.31072 | 86.148 | -75 | 7.2399 | 252.958 | 0 | 69 | 21.8718 | 0 | 21.8718 | 66.92 | 21.8718 | 9/19/18:00
9 | 19 | 1900-01-18 | 18.3 | 10 | 22 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 10 | 0 | 0 | 39.791 | 262.75 | 0.29437 | 86.148 | -75 | 7.2552 | 267.9618 | -0.52888 | 9.4711 | 3.0022 | 0 | 3.0022 | 64.94 | 3.0022 | 9/19/19:00
9 | 19 | 1900-01-19 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 262.7917 | 0.27801 | 86.148 | -75 | 7.2705 | 282.9656 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/19/20:00
9 | 19 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 262.8333 | 0.26166 | 86.148 | -75 | 7.2858 | 297.9694 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/19/21:00
9 | 19 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 262.875 | 0.24531 | 86.148 | -75 | 7.3011 | 312.9733 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/19/22:00
9 | 19 | 1900-01-22 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 262.9167 | 0.22895 | 86.148 | -75 | 7.3163 | 327.9771 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/19/23:00
9 | 19 | 1900-01-23 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 262.9583 | 0.2126 | 86.148 | -75 | 7.3316 | 342.9809 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/19/24:00
9 | 20 | 1899-12-31 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 263 | 0.19625 | 86.148 | -75 | 7.3469 | -2.0153 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/20/1:00
9 | 20 | 1900-01-01 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 263.0417 | 0.17989 | 86.148 | -75 | 7.3622 | 12.9885 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 9/20/2:00
9 | 20 | 1900-01-02 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 263.0833 | 0.16354 | 86.148 | -75 | 7.3775 | 27.9924 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/20/3:00
9 | 20 | 1900-01-03 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 263.125 | 0.14719 | 86.148 | -75 | 7.3927 | 42.9962 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/20/4:00
9 | 20 | 1900-01-04 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 263.1667 | 0.13083 | 86.148 | -75 | 7.408 | 58 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/20/5:00
9 | 20 | 1900-01-05 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 263.2083 | 0.11448 | 86.148 | -75 | 7.4233 | 73.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/20/6:00
9 | 20 | 1900-01-06 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 263.25 | 0.098124 | 86.148 | -75 | 7.4385 | 88.0076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/20/7:00
9 | 20 | 1900-01-07 | 13.9 | 93 | 187 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 93 | 0 | 0 | 39.791 | 263.2917 | 0.08177 | 86.148 | -75 | 7.4538 | 103.0114 | -32.1799 | 60.8201 | 19.2789 | 0 | 19.2789 | 57.02 | 19.2789 | 9/20/8:00
9 | 20 | 1900-01-08 | 15 | 159 | 133 | 59 | 0 | 1 | 0 | 59 | 0 | 159 | 0 | 0 | 39.791 | 263.3333 | 0.065416 | 86.148 | -75 | 7.469 | 118.0153 | -47.9045 | 111.0955 | 35.2153 | 0 | 35.2153 | 59 | 35.2153 | 9/20/9:00
9 | 20 | 1900-01-09 | 16.7 | 216 | 435 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 216 | 0 | 0 | 39.791 | 263.375 | 0.049062 | 86.148 | -75 | 7.4843 | 133.0191 | -227.7988 | -11.7988 | -3.74 | 0 | -3.74 | 62.06 | -3.74 | 9/20/10:00
9 | 20 | 1900-01-10 | 19.4 | 169 | 673 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 169 | 0 | 0 | 39.791 | 263.4167 | 0.032708 | 86.148 | -75 | 7.4995 | 148.0229 | -438.4082 | -269.4082 | -85.3977 | 0 | -85.3977 | 66.92 | -85.3977 | 9/20/11:00
9 | 20 | 1900-01-11 | 20.6 | 198 | 669 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 198 | 0 | 0 | 39.791 | 263.4583 | 0.016354 | 86.148 | -75 | 7.5148 | 163.0267 | -491.5352 | -293.5352 | -93.0455 | 0 | -93.0455 | 69.08 | -93.0455 | 9/20/12:00
9 | 20 | 1900-01-12 | 21.1 | 222 | 607 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 222 | 0 | 0 | 39.791 | 263.5 | 7.8197e-12 | 86.148 | -75 | 7.53 | 178.0305 | -466.1336 | -244.1336 | -77.3861 | 0 | -77.3861 | 69.98 | -77.3861 | 9/20/13:00
9 | 20 | 1900-01-13 | 22.8 | 246 | 562 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 246 | 0 | 0 | 39.791 | 263.5417 | -0.016354 | 86.148 | -75 | 7.5452 | 193.0343 | -420.8084 | -174.8084 | -55.4112 | 0 | -55.4112 | 73.04 | -55.4112 | 9/20/14:00
9 | 20 | 1900-01-14 | 21.7 | 281 | 405 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 281 | 0 | 0 | 39.791 | 263.5833 | -0.032708 | 86.148 | -75 | 7.5605 | 208.0381 | -274.82 | 6.18 | 1.9589 | 0 | 1.9589 | 71.06 | 1.9589 | 9/20/15:00
9 | 20 | 1900-01-15 | 23.3 | 165 | 562 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 165 | 0 | 0 | 39.791 | 263.625 | -0.049062 | 86.148 | -75 | 7.5757 | 223.0419 | -315.9141 | -150.9141 | -47.8371 | 0 | -47.8371 | 73.94 | -47.8371 | 9/20/16:00
9 | 20 | 1900-01-16 | 22.8 | 118 | 552 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 118 | 0 | 0 | 39.791 | 263.6667 | -0.065416 | 86.148 | -75 | 7.5909 | 238.0457 | -224.8803 | -106.8803 | -33.8792 | 0 | -33.8792 | 73.04 | -33.8792 | 9/20/17:00
9 | 20 | 1900-01-17 | 21.7 | 75 | 303 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 75 | 0 | 0 | 39.791 | 263.7083 | -0.08177 | 86.148 | -75 | 7.6061 | 253.0495 | -68.1543 | 6.8457 | 2.17 | 0 | 2.17 | 71.06 | 2.17 | 9/20/18:00
9 | 20 | 1900-01-18 | 20 | 9 | 61 | 68 | 0 | 1 | 0 | 68 | 0 | 9 | 0 | 0 | 39.791 | 263.75 | -0.098124 | 86.148 | -75 | 7.6213 | 268.0533 | -1.659 | 7.341 | 2.327 | 0 | 2.327 | 68 | 2.327 | 9/20/19:00
9 | 20 | 1900-01-19 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 263.7917 | -0.11448 | 86.148 | -75 | 7.6365 | 283.0571 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/20/20:00
9 | 20 | 1900-01-20 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 263.8333 | -0.13083 | 86.148 | -75 | 7.6518 | 298.0609 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/20/21:00
9 | 20 | 1900-01-21 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 263.875 | -0.14719 | 86.148 | -75 | 7.667 | 313.0647 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/20/22:00
9 | 20 | 1900-01-22 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 263.9167 | -0.16354 | 86.148 | -75 | 7.6821 | 328.0685 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/20/23:00
9 | 20 | 1900-01-23 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 263.9583 | -0.17989 | 86.148 | -75 | 7.6973 | 343.0723 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/20/24:00
9 | 21 | 1899-12-31 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 264 | -0.19625 | 86.148 | -75 | 7.7125 | -1.9239 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/21/1:00
9 | 21 | 1900-01-01 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 264.0417 | -0.2126 | 86.148 | -75 | 7.7277 | 13.0799 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/21/2:00
9 | 21 | 1900-01-02 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 264.0833 | -0.22895 | 86.148 | -75 | 7.7429 | 28.0837 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/21/3:00
9 | 21 | 1900-01-03 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 264.125 | -0.24531 | 86.148 | -75 | 7.7581 | 43.0875 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/21/4:00
9 | 21 | 1900-01-04 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 264.1667 | -0.26166 | 86.148 | -75 | 7.7732 | 58.0913 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/21/5:00
9 | 21 | 1900-01-05 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 264.2083 | -0.27801 | 86.148 | -75 | 7.7884 | 73.0951 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/21/6:00
9 | 21 | 1900-01-06 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 264.25 | -0.29437 | 86.148 | -75 | 7.8036 | 88.0989 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/21/7:00
9 | 21 | 1900-01-07 | 17.8 | 40 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 40 | 0 | 0 | 39.791 | 264.2917 | -0.31072 | 86.148 | -75 | 7.8187 | 103.1027 | 0 | 40 | 12.6793 | 0 | 12.6793 | 64.04 | 12.6793 | 9/21/8:00
9 | 21 | 1900-01-08 | 17.8 | 50 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 50 | 0 | 0 | 39.791 | 264.3333 | -0.32707 | 86.148 | -75 | 7.8339 | 118.1065 | 0 | 50 | 15.8491 | 0 | 15.8491 | 64.04 | 15.8491 | 9/21/9:00
9 | 21 | 1900-01-09 | 18.9 | 79 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 79 | 0 | 0 | 39.791 | 264.375 | -0.34342 | 86.148 | -75 | 7.849 | 133.1103 | 0 | 79 | 25.0416 | 0 | 25.0416 | 66.02 | 25.0416 | 9/21/10:00
9 | 21 | 1900-01-10 | 21.1 | 276 | 321 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 276 | 0 | 0 | 39.791 | 264.4167 | -0.35978 | 86.148 | -75 | 7.8642 | 148.114 | -210.7178 | 65.2822 | 20.6933 | 0 | 20.6933 | 69.98 | 20.6933 | 9/21/11:00
9 | 21 | 1900-01-11 | 22.8 | 327 | 90 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 327 | 0 | 0 | 39.791 | 264.4583 | -0.37613 | 86.148 | -75 | 7.8793 | 163.1178 | -66.551 | 260.449 | 82.5578 | 0 | 82.5578 | 73.04 | 82.5578 | 9/21/12:00
9 | 21 | 1900-01-12 | 23.3 | 241 | 601 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 241 | 0 | 0 | 39.791 | 264.5 | -0.39248 | 86.148 | -75 | 7.8944 | 178.1216 | -464.1746 | -223.1746 | -70.7424 | 0 | -70.7424 | 73.94 | -70.7424 | 9/21/13:00
9 | 21 | 1900-01-13 | 25 | 262 | 568 | 77 | 0 | 1 | 0 | 77 | 0 | 262 | 0 | 0 | 39.791 | 264.5417 | -0.40883 | 86.148 | -75 | 7.9096 | 193.1254 | -427.6233 | -165.6233 | -52.4997 | 0 | -52.4997 | 77 | -52.4997 | 9/21/14:00
9 | 21 | 1900-01-14 | 24.4 | 319 | 250 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 319 | 0 | 0 | 39.791 | 264.5833 | -0.42518 | 86.148 | -75 | 7.9247 | 208.1292 | -170.5896 | 148.4104 | 47.0435 | 0 | 47.0435 | 75.92 | 47.0435 | 9/21/15:00
9 | 21 | 1900-01-15 | 23.9 | 160 | 603 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 160 | 0 | 0 | 39.791 | 264.625 | -0.44154 | 86.148 | -75 | 7.9398 | 223.133 | -341.0919 | -181.0919 | -57.403 | 0 | -57.403 | 75.02 | -57.403 | 9/21/16:00
9 | 21 | 1900-01-16 | 23.9 | 124 | 505 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 124 | 0 | 0 | 39.791 | 264.6667 | -0.45789 | 86.148 | -75 | 7.9549 | 238.1367 | -207.417 | -83.417 | -26.4417 | 0 | -26.4417 | 75.02 | -26.4417 | 9/21/17:00
9 | 21 | 1900-01-17 | 22.2 | 74 | 351 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 74 | 0 | 0 | 39.791 | 264.7083 | -0.47424 | 86.148 | -75 | 7.9701 | 253.1405 | -80.0773 | -6.0773 | -1.9264 | 0 | -1.9264 | 71.96 | -1.9264 | 9/21/18:00
9 | 21 | 1900-01-18 | 21.1 | 6 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 6 | 0 | 0 | 39.791 | 264.75 | -0.49059 | 86.148 | -75 | 7.9852 | 268.1443 | 0 | 6 | 1.9019 | 0 | 1.9019 | 69.98 | 1.9019 | 9/21/19:00
9 | 21 | 1900-01-19 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 264.7917 | -0.50694 | 86.148 | -75 | 8.0003 | 283.1481 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 9/21/20:00
9 | 21 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 264.8333 | -0.52329 | 86.148 | -75 | 8.0154 | 298.1518 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/21/21:00
9 | 21 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 264.875 | -0.53964 | 86.148 | -75 | 8.0305 | 313.1556 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/21/22:00
9 | 21 | 1900-01-22 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 264.9167 | -0.55599 | 86.148 | -75 | 8.0455 | 328.1594 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/21/23:00
9 | 21 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 264.9583 | -0.57234 | 86.148 | -75 | 8.0606 | 343.1632 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/21/24:00
9 | 22 | 1899-12-31 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 265 | -0.58869 | 86.148 | -75 | 8.0757 | -1.8331 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/22/1:00
9 | 22 | 1900-01-01 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 265.0417 | -0.60504 | 86.148 | -75 | 8.0908 | 13.1707 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/22/2:00
9 | 22 | 1900-01-02 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 265.0833 | -0.62139 | 86.148 | -75 | 8.1058 | 28.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/22/3:00
9 | 22 | 1900-01-03 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 265.125 | -0.63774 | 86.148 | -75 | 8.1209 | 43.1782 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/22/4:00
9 | 22 | 1900-01-04 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 265.1667 | -0.65409 | 86.148 | -75 | 8.136 | 58.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/22/5:00
9 | 22 | 1900-01-05 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 265.2083 | -0.67043 | 86.148 | -75 | 8.151 | 73.1858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/22/6:00
9 | 22 | 1900-01-06 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 265.25 | -0.68678 | 86.148 | -75 | 8.1661 | 88.1895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/22/7:00
9 | 22 | 1900-01-07 | 13.9 | 74 | 320 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 74 | 0 | 0 | 39.791 | 265.2917 | -0.70313 | 86.148 | -75 | 8.1811 | 103.1933 | -58.6285 | 15.3715 | 4.8725 | 0 | 4.8725 | 57.02 | 4.8725 | 9/22/8:00
9 | 22 | 1900-01-08 | 16.1 | 107 | 518 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 107 | 0 | 0 | 39.791 | 265.3333 | -0.71948 | 86.148 | -75 | 8.1962 | 118.197 | -192.2159 | -85.2159 | -27.0119 | 0 | -27.0119 | 60.98 | -27.0119 | 9/22/9:00
9 | 22 | 1900-01-09 | 18.3 | 181 | 521 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 181 | 0 | 0 | 39.791 | 265.375 | -0.73582 | 86.148 | -75 | 8.2112 | 133.2008 | -278.3069 | -97.3069 | -30.8446 | 0 | -30.8446 | 64.94 | -30.8446 | 9/22/10:00
9 | 22 | 1900-01-10 | 20 | 166 | 637 | 68 | 0 | 1 | 0 | 68 | 0 | 166 | 0 | 0 | 39.791 | 265.4167 | -0.75217 | 86.148 | -75 | 8.2262 | 148.2046 | -421.3254 | -255.3254 | -80.9337 | 0 | -80.9337 | 68 | -80.9337 | 9/22/11:00
9 | 22 | 1900-01-11 | 20 | 280 | 464 | 68 | 0 | 1 | 0 | 68 | 0 | 280 | 0 | 0 | 39.791 | 265.4583 | -0.76852 | 86.148 | -75 | 8.2412 | 163.2083 | -345.2805 | -65.2805 | -20.6928 | 0 | -20.6928 | 68 | -20.6928 | 9/22/12:00
9 | 22 | 1900-01-12 | 21.7 | 313 | 408 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 313 | 0 | 0 | 39.791 | 265.5 | -0.78486 | 86.148 | -75 | 8.2563 | 178.2121 | -316.8954 | -3.8954 | -1.2348 | 0 | -1.2348 | 71.06 | -1.2348 | 9/22/13:00
9 | 22 | 1900-01-13 | 22.2 | 286 | 461 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 286 | 0 | 0 | 39.791 | 265.5417 | -0.80121 | 86.148 | -75 | 8.2713 | 193.2158 | -348.9355 | -62.9355 | -19.9495 | 0 | -19.9495 | 71.96 | -19.9495 | 9/22/14:00
9 | 22 | 1900-01-14 | 23.3 | 216 | 548 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 216 | 0 | 0 | 39.791 | 265.5833 | -0.81756 | 86.148 | -75 | 8.2863 | 208.2196 | -375.9928 | -159.9928 | -50.7149 | 0 | -50.7149 | 73.94 | -50.7149 | 9/22/15:00
9 | 22 | 1900-01-15 | 23.3 | 123 | 674 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 123 | 0 | 0 | 39.791 | 265.625 | -0.8339 | 86.148 | -75 | 8.3013 | 223.2233 | -383.6197 | -260.6197 | -82.6119 | 0 | -82.6119 | 73.94 | -82.6119 | 9/22/16:00
9 | 22 | 1900-01-16 | 23.9 | 109 | 586 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 109 | 0 | 0 | 39.791 | 265.6667 | -0.85024 | 86.148 | -75 | 8.3163 | 238.2271 | -242.6322 | -133.6322 | -42.3591 | 0 | -42.3591 | 75.02 | -42.3591 | 9/22/17:00
9 | 22 | 1900-01-17 | 21.7 | 66 | 410 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 66 | 0 | 0 | 39.791 | 265.7083 | -0.86659 | 86.148 | -75 | 8.3313 | 253.2308 | -94.8518 | -28.8518 | -9.1455 | 0 | -9.1455 | 71.06 | -9.1455 | 9/22/18:00
9 | 22 | 1900-01-18 | 20 | 6 | 56 | 68 | 0 | 1 | 0 | 68 | 0 | 6 | 0 | 0 | 39.791 | 265.75 | -0.88293 | 86.148 | -75 | 8.3462 | 268.2346 | -1.8778 | 4.1222 | 1.3067 | 0 | 1.3067 | 68 | 1.3067 | 9/22/19:00
9 | 22 | 1900-01-19 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 265.7917 | -0.89928 | 86.148 | -75 | 8.3612 | 283.2383 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/22/20:00
9 | 22 | 1900-01-20 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 265.8333 | -0.91562 | 86.148 | -75 | 8.3762 | 298.242 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/22/21:00
9 | 22 | 1900-01-21 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 265.875 | -0.93196 | 86.148 | -75 | 8.3912 | 313.2458 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 9/22/22:00
9 | 22 | 1900-01-22 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 265.9167 | -0.9483 | 86.148 | -75 | 8.4061 | 328.2495 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/22/23:00
9 | 22 | 1900-01-23 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 265.9583 | -0.96465 | 86.148 | -75 | 8.4211 | 343.2533 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/22/24:00
9 | 23 | 1899-12-31 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 266 | -0.98099 | 86.148 | -75 | 8.436 | -1.743 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/23/1:00
9 | 23 | 1900-01-01 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 266.0417 | -0.99733 | 86.148 | -75 | 8.451 | 13.2607 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/23/2:00
9 | 23 | 1900-01-02 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 266.0833 | -1.0137 | 86.148 | -75 | 8.4659 | 28.2645 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 9/23/3:00
9 | 23 | 1900-01-03 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 266.125 | -1.03 | 86.148 | -75 | 8.4809 | 43.2682 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 9/23/4:00
9 | 23 | 1900-01-04 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 266.1667 | -1.0464 | 86.148 | -75 | 8.4958 | 58.2719 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/23/5:00
9 | 23 | 1900-01-05 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 266.2083 | -1.0627 | 86.148 | -75 | 8.5107 | 73.2757 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/23/6:00
9 | 23 | 1900-01-06 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 266.25 | -1.079 | 86.148 | -75 | 8.5256 | 88.2794 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 9/23/7:00
9 | 23 | 1900-01-07 | 15.6 | 76 | 205 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 76 | 0 | 0 | 39.791 | 266.2917 | -1.0954 | 86.148 | -75 | 8.5405 | 103.2831 | -38.6935 | 37.3065 | 11.8255 | 0 | 11.8255 | 60.08 | 11.8255 | 9/23/8:00
9 | 23 | 1900-01-08 | 18.3 | 106 | 506 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 106 | 0 | 0 | 39.791 | 266.3333 | -1.1117 | 86.148 | -75 | 8.5554 | 118.2869 | -190.4963 | -84.4963 | -26.7839 | 0 | -26.7839 | 64.94 | -26.7839 | 9/23/9:00
9 | 23 | 1900-01-09 | 21.1 | 151 | 595 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 151 | 0 | 0 | 39.791 | 266.375 | -1.128 | 86.148 | -75 | 8.5703 | 133.2906 | -320.9294 | -169.9294 | -53.8647 | 0 | -53.8647 | 69.98 | -53.8647 | 9/23/10:00
9 | 23 | 1900-01-10 | 23.3 | 142 | 698 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 142 | 0 | 0 | 39.791 | 266.4167 | -1.1444 | 86.148 | -75 | 8.5852 | 148.2943 | -465.12 | -323.12 | -102.4234 | 0 | -102.4234 | 73.94 | -102.4234 | 9/23/11:00
9 | 23 | 1900-01-11 | 24.4 | 212 | 627 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 212 | 0 | 0 | 39.791 | 266.4583 | -1.1607 | 86.148 | -75 | 8.6001 | 163.298 | -469.4858 | -257.4858 | -81.6185 | 0 | -81.6185 | 75.92 | -81.6185 | 9/23/12:00
9 | 23 | 1900-01-12 | 25.6 | 239 | 625 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 239 | 0 | 0 | 39.791 | 266.5 | -1.1771 | 86.148 | -75 | 8.615 | 178.3018 | -488.1445 | -249.1445 | -78.9744 | 0 | -78.9744 | 78.08 | -78.9744 | 9/23/13:00
9 | 23 | 1900-01-13 | 25 | 314 | 419 | 77 | 0 | 1 | 0 | 77 | 0 | 314 | 0 | 0 | 39.791 | 266.5417 | -1.1934 | 86.148 | -75 | 8.6299 | 193.3055 | -318.8276 | -4.8276 | -1.5303 | 0 | -1.5303 | 77 | -1.5303 | 9/23/14:00
9 | 23 | 1900-01-14 | 25 | 313 | 202 | 77 | 0 | 1 | 0 | 77 | 0 | 313 | 0 | 0 | 39.791 | 266.5833 | -1.2097 | 86.148 | -75 | 8.6448 | 208.3092 | -139.3491 | 173.6509 | 55.0443 | 0 | 55.0443 | 77 | 55.0443 | 9/23/15:00
9 | 23 | 1900-01-15 | 25 | 208 | 18 | 77 | 0 | 1 | 0 | 77 | 0 | 208 | 0 | 0 | 39.791 | 266.625 | -1.2261 | 86.148 | -75 | 8.6596 | 223.3129 | -10.3078 | 197.6922 | 62.665 | 0 | 62.665 | 77 | 62.665 | 9/23/16:00
9 | 23 | 1900-01-16 | 20 | 116 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 116 | 0 | 0 | 39.791 | 266.6667 | -1.2424 | 86.148 | -75 | 8.6745 | 238.3166 | 0 | 116 | 36.77 | 0 | 36.77 | 68 | 36.77 | 9/23/17:00
9 | 23 | 1900-01-17 | 19.4 | 40 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 40 | 0 | 0 | 39.791 | 266.7083 | -1.2587 | 86.148 | -75 | 8.6893 | 253.3203 | 0 | 40 | 12.6793 | 0 | 12.6793 | 66.92 | 12.6793 | 9/23/18:00
9 | 23 | 1900-01-18 | 20 | 1 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 1 | 0 | 0 | 39.791 | 266.75 | -1.2751 | 86.148 | -75 | 8.7042 | 268.324 | 0 | 1 | 0.31698 | 0 | 0.31698 | 68 | 0.31698 | 9/23/19:00
9 | 23 | 1900-01-19 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 266.7917 | -1.2914 | 86.148 | -75 | 8.719 | 283.3278 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 9/23/20:00
9 | 23 | 1900-01-20 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 266.8333 | -1.3077 | 86.148 | -75 | 8.7338 | 298.3315 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/23/21:00
9 | 23 | 1900-01-21 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 266.875 | -1.3241 | 86.148 | -75 | 8.7487 | 313.3352 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/23/22:00
9 | 23 | 1900-01-22 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 266.9167 | -1.3404 | 86.148 | -75 | 8.7635 | 328.3389 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 9/23/23:00
9 | 23 | 1900-01-23 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 266.9583 | -1.3567 | 86.148 | -75 | 8.7783 | 343.3426 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 9/23/24:00
9 | 24 | 1899-12-31 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 267 | -1.373 | 86.148 | -75 | 8.7931 | -1.6537 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/24/1:00
9 | 24 | 1900-01-01 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 267.0417 | -1.3894 | 86.148 | -75 | 8.8079 | 13.35 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/24/2:00
9 | 24 | 1900-01-02 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 267.0833 | -1.4057 | 86.148 | -75 | 8.8227 | 28.3537 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 9/24/3:00
9 | 24 | 1900-01-03 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 267.125 | -1.422 | 86.148 | -75 | 8.8375 | 43.3574 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/24/4:00
9 | 24 | 1900-01-04 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 267.1667 | -1.4384 | 86.148 | -75 | 8.8523 | 58.3611 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/24/5:00
9 | 24 | 1900-01-05 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 267.2083 | -1.4547 | 86.148 | -75 | 8.8671 | 73.3648 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/24/6:00
9 | 24 | 1900-01-06 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 267.25 | -1.471 | 86.148 | -75 | 8.8818 | 88.3685 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/24/7:00
9 | 24 | 1900-01-07 | 12.8 | 78 | 147 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 78 | 0 | 0 | 39.791 | 267.2917 | -1.4873 | 86.148 | -75 | 8.8966 | 103.3721 | -28.5562 | 49.4438 | 15.6728 | 0 | 15.6728 | 55.04 | 15.6728 | 9/24/8:00
9 | 24 | 1900-01-08 | 13.3 | 125 | 399 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 125 | 0 | 0 | 39.791 | 267.3333 | -1.5037 | 86.148 | -75 | 8.9113 | 118.3758 | -152.3561 | -27.3561 | -8.6714 | 0 | -8.6714 | 55.94 | -8.6714 | 9/24/9:00
9 | 24 | 1900-01-09 | 14.4 | 213 | 430 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 213 | 0 | 0 | 39.791 | 267.375 | -1.52 | 86.148 | -75 | 8.9261 | 133.3795 | -234.1513 | -21.1513 | -6.7046 | 0 | -6.7046 | 57.92 | -6.7046 | 9/24/10:00
9 | 24 | 1900-01-10 | 14.4 | 275 | 85 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 275 | 0 | 0 | 39.791 | 267.4167 | -1.5363 | 86.148 | -75 | 8.9408 | 148.3832 | -57.057 | 217.943 | 69.0841 | 0 | 69.0841 | 57.92 | 69.0841 | 9/24/11:00
9 | 24 | 1900-01-11 | 15.6 | 322 | 404 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 322 | 0 | 0 | 39.791 | 267.4583 | -1.5526 | 86.148 | -75 | 8.9556 | 163.3869 | -304.3654 | 17.6346 | 5.5899 | 0 | 5.5899 | 60.08 | 5.5899 | 9/24/12:00
9 | 24 | 1900-01-12 | 16.1 | 374 | 150 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 374 | 0 | 0 | 39.791 | 267.5 | -1.5689 | 86.148 | -75 | 8.9703 | 178.3906 | -117.7974 | 256.2026 | 81.2118 | 0 | 81.2118 | 60.98 | 81.2118 | 9/24/13:00
9 | 24 | 1900-01-13 | 17.2 | 369 | 132 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 369 | 0 | 0 | 39.791 | 267.5417 | -1.5853 | 86.148 | -75 | 8.985 | 193.3943 | -100.9671 | 268.0329 | 84.9617 | 0 | 84.9617 | 62.96 | 84.9617 | 9/24/14:00
9 | 24 | 1900-01-14 | 15 | 297 | 30 | 59 | 0 | 1 | 0 | 59 | 0 | 297 | 0 | 0 | 39.791 | 267.5833 | -1.6016 | 86.148 | -75 | 8.9997 | 208.3979 | -20.8063 | 276.1937 | 87.5486 | 0 | 87.5486 | 59 | 87.5486 | 9/24/15:00
9 | 24 | 1900-01-15 | 15 | 237 | 35 | 59 | 0 | 1 | 0 | 59 | 0 | 237 | 0 | 0 | 39.791 | 267.625 | -1.6179 | 86.148 | -75 | 9.0145 | 223.4016 | -20.1642 | 216.8358 | 68.7332 | 0 | 68.7332 | 59 | 68.7332 | 9/24/16:00
9 | 24 | 1900-01-16 | 13.9 | 171 | 255 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 171 | 0 | 0 | 39.791 | 267.6667 | -1.6342 | 86.148 | -75 | 9.0292 | 238.4053 | -107.2657 | 63.7343 | 20.2026 | 0 | 20.2026 | 57.02 | 20.2026 | 9/24/17:00
9 | 24 | 1900-01-17 | 13.9 | 62 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 62 | 0 | 0 | 39.791 | 267.7083 | -1.6505 | 86.148 | -75 | 9.0438 | 253.409 | 0 | 62 | 19.6529 | 0 | 19.6529 | 57.02 | 19.6529 | 9/24/18:00
9 | 24 | 1900-01-18 | 11.7 | 4 | 33 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 4 | 0 | 0 | 39.791 | 267.75 | -1.6669 | 86.148 | -75 | 9.0585 | 268.4126 | -1.3164 | 2.6836 | 0.85064 | 0.85064 | 0 | 0 | 0 | 9/24/19:00
9 | 24 | 1900-01-19 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 267.7917 | -1.6832 | 86.148 | -75 | 9.0732 | 283.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/24/20:00
9 | 24 | 1900-01-20 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 267.8333 | -1.6995 | 86.148 | -75 | 9.0879 | 298.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/24/21:00
9 | 24 | 1900-01-21 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 267.875 | -1.7158 | 86.148 | -75 | 9.1026 | 313.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/24/22:00
9 | 24 | 1900-01-22 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 267.9167 | -1.7321 | 86.148 | -75 | 9.1172 | 328.4273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/24/23:00
9 | 24 | 1900-01-23 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 267.9583 | -1.7484 | 86.148 | -75 | 9.1319 | 343.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/24/24:00
9 | 25 | 1899-12-31 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268 | -1.7648 | 86.148 | -75 | 9.1465 | -1.5654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/1:00
9 | 25 | 1900-01-01 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.0417 | -1.7811 | 86.148 | -75 | 9.1612 | 13.4383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/2:00
9 | 25 | 1900-01-02 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.0833 | -1.7974 | 86.148 | -75 | 9.1758 | 28.442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/3:00
9 | 25 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.125 | -1.8137 | 86.148 | -75 | 9.1904 | 43.4456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/4:00
9 | 25 | 1900-01-04 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.1667 | -1.83 | 86.148 | -75 | 9.205 | 58.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/5:00
9 | 25 | 1900-01-05 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.2083 | -1.8463 | 86.148 | -75 | 9.2197 | 73.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/6:00
9 | 25 | 1900-01-06 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.25 | -1.8626 | 86.148 | -75 | 9.2343 | 88.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/7:00
9 | 25 | 1900-01-07 | 7.2 | 86 | 170 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 86 | 0 | 0 | 39.791 | 268.2917 | -1.8789 | 86.148 | -75 | 9.2489 | 103.4602 | -33.9565 | 52.0435 | 16.4969 | 16.4969 | 0 | 0 | 0 | 9/25/8:00
9 | 25 | 1900-01-08 | 8.9 | 159 | 146 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 159 | 0 | 0 | 39.791 | 268.3333 | -1.8952 | 86.148 | -75 | 9.2634 | 118.4639 | -56.5284 | 102.4716 | 32.4817 | 32.4817 | 0 | 0 | 0 | 9/25/9:00
9 | 25 | 1900-01-09 | 9.4 | 233 | 49 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 233 | 0 | 0 | 39.791 | 268.375 | -1.9115 | 86.148 | -75 | 9.278 | 133.4675 | -26.9332 | 206.0668 | 65.3196 | 65.3196 | 0 | 0 | 0 | 9/25/10:00
9 | 25 | 1900-01-10 | 9.4 | 159 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 159 | 0 | 0 | 39.791 | 268.4167 | -1.9278 | 86.148 | -75 | 9.2926 | 148.4712 | 0 | 159 | 50.4002 | 50.4002 | 0 | 0 | 0 | 9/25/11:00
9 | 25 | 1900-01-11 | 10.6 | 347 | 151 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 347 | 0 | 0 | 39.791 | 268.4583 | -1.9441 | 86.148 | -75 | 9.3072 | 163.4748 | -114.4479 | 232.5521 | 73.7149 | 73.7149 | 0 | 0 | 0 | 9/25/12:00
9 | 25 | 1900-01-12 | 10.6 | 222 | 18 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 222 | 0 | 0 | 39.791 | 268.5 | -1.9604 | 86.148 | -75 | 9.3217 | 178.4784 | -14.212 | 207.788 | 65.8652 | 65.8652 | 0 | 0 | 0 | 9/25/13:00
9 | 25 | 1900-01-13 | 12.2 | 315 | 78 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 315 | 0 | 0 | 39.791 | 268.5417 | -1.9767 | 86.148 | -75 | 9.3363 | 193.4821 | -59.9696 | 255.0304 | 80.8402 | 80.8402 | 0 | 0 | 0 | 9/25/14:00
9 | 25 | 1900-01-14 | 11.7 | 104 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 104 | 0 | 0 | 39.791 | 268.5833 | -1.9931 | 86.148 | -75 | 9.3508 | 208.4857 | 0 | 104 | 32.9662 | 32.9662 | 0 | 0 | 0 | 9/25/15:00
9 | 25 | 1900-01-15 | 12.2 | 221 | 53 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 221 | 0 | 0 | 39.791 | 268.625 | -2.0094 | 86.148 | -75 | 9.3654 | 223.4893 | -30.7168 | 190.2832 | 60.3165 | 60.3165 | 0 | 0 | 0 | 9/25/16:00
9 | 25 | 1900-01-16 | 12.8 | 157 | 307 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 157 | 0 | 0 | 39.791 | 268.6667 | -2.0257 | 86.148 | -75 | 9.3799 | 238.493 | -130.1467 | 26.8533 | 8.512 | 0 | 8.512 | 55.04 | 8.512 | 9/25/17:00
9 | 25 | 1900-01-17 | 12.8 | 82 | 114 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 82 | 0 | 0 | 39.791 | 268.7083 | -2.042 | 86.148 | -75 | 9.3944 | 253.4966 | -27.4673 | 54.5327 | 17.2859 | 0 | 17.2859 | 55.04 | 17.2859 | 9/25/18:00
9 | 25 | 1900-01-18 | 11.7 | 2 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 2 | 0 | 0 | 39.791 | 268.75 | -2.0582 | 86.148 | -75 | 9.4089 | 268.5002 | 0 | 2 | 0.63397 | 0.63397 | 0 | 0 | 0 | 9/25/19:00
9 | 25 | 1900-01-19 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.7917 | -2.0745 | 86.148 | -75 | 9.4235 | 283.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/20:00
9 | 25 | 1900-01-20 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.8333 | -2.0908 | 86.148 | -75 | 9.438 | 298.5075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/21:00
9 | 25 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.875 | -2.1071 | 86.148 | -75 | 9.4524 | 313.5111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/22:00
9 | 25 | 1900-01-22 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.9167 | -2.1234 | 86.148 | -75 | 9.4669 | 328.5147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/23:00
9 | 25 | 1900-01-23 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 268.9583 | -2.1397 | 86.148 | -75 | 9.4814 | 343.5184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/25/24:00
9 | 26 | 1899-12-31 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269 | -2.156 | 86.148 | -75 | 9.4959 | -1.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/1:00
9 | 26 | 1900-01-01 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.0417 | -2.1723 | 86.148 | -75 | 9.5103 | 13.5256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/2:00
9 | 26 | 1900-01-02 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.0833 | -2.1886 | 86.148 | -75 | 9.5248 | 28.5292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/3:00
9 | 26 | 1900-01-03 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.125 | -2.2049 | 86.148 | -75 | 9.5392 | 43.5328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/4:00
9 | 26 | 1900-01-04 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.1667 | -2.2212 | 86.148 | -75 | 9.5537 | 58.5364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/5:00
9 | 26 | 1900-01-05 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.2083 | -2.2375 | 86.148 | -75 | 9.5681 | 73.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/6:00
9 | 26 | 1900-01-06 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.25 | -2.2538 | 86.148 | -75 | 9.5825 | 88.5436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/7:00
9 | 26 | 1900-01-07 | 8.3 | 63 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 63 | 0 | 0 | 39.791 | 269.2917 | -2.27 | 86.148 | -75 | 9.5969 | 103.5472 | 0 | 63 | 19.9699 | 19.9699 | 0 | 0 | 0 | 9/26/8:00
9 | 26 | 1900-01-08 | 9.4 | 87 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 87 | 0 | 0 | 39.791 | 269.3333 | -2.2863 | 86.148 | -75 | 9.6114 | 118.5508 | 0 | 87 | 27.5775 | 27.5775 | 0 | 0 | 0 | 9/26/9:00
9 | 26 | 1900-01-09 | 12.2 | 133 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 133 | 0 | 0 | 39.791 | 269.375 | -2.3026 | 86.148 | -75 | 9.6258 | 133.5544 | 0 | 133 | 42.1587 | 42.1587 | 0 | 0 | 0 | 9/26/10:00
9 | 26 | 1900-01-10 | 15.6 | 254 | 455 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 254 | 0 | 0 | 39.791 | 269.4167 | -2.3189 | 86.148 | -75 | 9.6401 | 148.558 | -309.8183 | -55.8183 | -17.6934 | 0 | -17.6934 | 60.08 | -17.6934 | 9/26/11:00
9 | 26 | 1900-01-11 | 17.2 | 182 | 706 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 182 | 0 | 0 | 39.791 | 269.4583 | -2.3352 | 86.148 | -75 | 9.6545 | 163.5616 | -538.2831 | -356.2831 | -112.9355 | 0 | -112.9355 | 62.96 | -112.9355 | 9/26/12:00
9 | 26 | 1900-01-12 | 18.3 | 223 | 625 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 223 | 0 | 0 | 39.791 | 269.5 | -2.3515 | 86.148 | -75 | 9.6689 | 178.5652 | -496.0966 | -273.0966 | -86.5669 | 0 | -86.5669 | 64.94 | -86.5669 | 9/26/13:00
9 | 26 | 1900-01-13 | 20 | 222 | 616 | 68 | 0 | 1 | 0 | 68 | 0 | 222 | 0 | 0 | 39.791 | 269.5417 | -2.3677 | 86.148 | -75 | 9.6833 | 193.5688 | -476.0077 | -254.0077 | -80.516 | 0 | -80.516 | 68 | -80.516 | 9/26/14:00
9 | 26 | 1900-01-14 | 19.4 | 187 | 607 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 187 | 0 | 0 | 39.791 | 269.5833 | -2.384 | 86.148 | -75 | 9.6976 | 208.5724 | -425.4115 | -238.4115 | -75.5723 | 0 | -75.5723 | 66.92 | -75.5723 | 9/26/15:00
9 | 26 | 1900-01-15 | 20 | 121 | 679 | 68 | 0 | 1 | 0 | 68 | 0 | 121 | 0 | 0 | 39.791 | 269.625 | -2.4003 | 86.148 | -75 | 9.712 | 223.576 | -395.8427 | -274.8427 | -87.1203 | 0 | -87.1203 | 68 | -87.1203 | 9/26/16:00
9 | 26 | 1900-01-16 | 19.4 | 111 | 509 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 111 | 0 | 0 | 39.791 | 269.6667 | -2.4166 | 86.148 | -75 | 9.7263 | 238.5796 | -217.4437 | -106.4437 | -33.7408 | 0 | -33.7408 | 66.92 | -33.7408 | 9/26/17:00
9 | 26 | 1900-01-17 | 18.9 | 71 | 232 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 71 | 0 | 0 | 39.791 | 269.7083 | -2.4328 | 86.148 | -75 | 9.7407 | 253.5832 | -56.6391 | 14.3609 | 4.5522 | 0 | 4.5522 | 66.02 | 4.5522 | 9/26/18:00
9 | 26 | 1900-01-18 | 16.7 | 1 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 1 | 0 | 0 | 39.791 | 269.75 | -2.4491 | 86.148 | -75 | 9.755 | 268.5867 | 0 | 1 | 0.31698 | 0 | 0.31698 | 62.06 | 0.31698 | 9/26/19:00
9 | 26 | 1900-01-19 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 269.7917 | -2.4654 | 86.148 | -75 | 9.7693 | 283.5903 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/26/20:00
9 | 26 | 1900-01-20 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.8333 | -2.4817 | 86.148 | -75 | 9.7836 | 298.5939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/21:00
9 | 26 | 1900-01-21 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.875 | -2.4979 | 86.148 | -75 | 9.7979 | 313.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/22:00
9 | 26 | 1900-01-22 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.9167 | -2.5142 | 86.148 | -75 | 9.8122 | 328.6011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/23:00
9 | 26 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 269.9583 | -2.5305 | 86.148 | -75 | 9.8265 | 343.6046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/26/24:00
9 | 27 | 1899-12-31 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270 | -2.5468 | 86.148 | -75 | 9.8408 | -1.3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/1:00
9 | 27 | 1900-01-01 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.0417 | -2.563 | 86.148 | -75 | 9.855 | 13.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/2:00
9 | 27 | 1900-01-02 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.0833 | -2.5793 | 86.148 | -75 | 9.8693 | 28.6153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/3:00
9 | 27 | 1900-01-03 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.125 | -2.5955 | 86.148 | -75 | 9.8835 | 43.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/4:00
9 | 27 | 1900-01-04 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.1667 | -2.6118 | 86.148 | -75 | 9.8978 | 58.6224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/5:00
9 | 27 | 1900-01-05 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.2083 | -2.6281 | 86.148 | -75 | 9.912 | 73.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/6:00
9 | 27 | 1900-01-06 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.25 | -2.6443 | 86.148 | -75 | 9.9262 | 88.6296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/7:00
9 | 27 | 1900-01-07 | 9.4 | 76 | 195 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 76 | 0 | 0 | 39.791 | 270.2917 | -2.6606 | 86.148 | -75 | 9.9405 | 103.6331 | -41.0716 | 34.9284 | 11.0717 | 11.0717 | 0 | 0 | 0 | 9/27/8:00
9 | 27 | 1900-01-08 | 12.8 | 121 | 406 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 121 | 0 | 0 | 39.791 | 270.3333 | -2.6769 | 86.148 | -75 | 9.9547 | 118.6367 | -161.4818 | -40.4818 | -12.832 | 0 | -12.832 | 55.04 | -12.832 | 9/27/9:00
9 | 27 | 1900-01-09 | 14.4 | 160 | 571 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 160 | 0 | 0 | 39.791 | 270.375 | -2.6931 | 86.148 | -75 | 9.9689 | 133.6402 | -319.6277 | -159.6277 | -50.5992 | 0 | -50.5992 | 57.92 | -50.5992 | 9/27/10:00
9 | 27 | 1900-01-10 | 16.1 | 162 | 674 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 162 | 0 | 0 | 39.791 | 270.4167 | -2.7094 | 86.148 | -75 | 9.9831 | 148.6438 | -462.1477 | -300.1477 | -95.1416 | 0 | -95.1416 | 60.98 | -95.1416 | 9/27/11:00
9 | 27 | 1900-01-11 | 16.7 | 231 | 555 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 231 | 0 | 0 | 39.791 | 270.4583 | -2.7256 | 86.148 | -75 | 9.9972 | 163.6473 | -425.6294 | -194.6294 | -61.6941 | 0 | -61.6941 | 62.06 | -61.6941 | 9/27/12:00
9 | 27 | 1900-01-12 | 17.2 | 256 | 528 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 256 | 0 | 0 | 39.791 | 270.5 | -2.7419 | 86.148 | -75 | 10.0114 | 178.6509 | -421.2947 | -165.2947 | -52.3955 | 0 | -52.3955 | 62.96 | -52.3955 | 9/27/13:00
9 | 27 | 1900-01-13 | 17.8 | 227 | 580 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 227 | 0 | 0 | 39.791 | 270.5417 | -2.7581 | 86.148 | -75 | 10.0256 | 193.6544 | -450.4273 | -223.4273 | -70.8225 | 0 | -70.8225 | 64.04 | -70.8225 | 9/27/14:00
9 | 27 | 1900-01-14 | 17.8 | 247 | 458 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 247 | 0 | 0 | 39.791 | 270.5833 | -2.7744 | 86.148 | -75 | 10.0397 | 208.6579 | -322.635 | -75.635 | -23.975 | 0 | -23.975 | 64.04 | -23.975 | 9/27/15:00
9 | 27 | 1900-01-15 | 16.7 | 257 | 224 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 257 | 0 | 0 | 39.791 | 270.625 | -2.7906 | 86.148 | -75 | 10.0539 | 223.6615 | -131.3476 | 125.6524 | 39.8296 | 0 | 39.8296 | 62.06 | 39.8296 | 9/27/16:00
9 | 27 | 1900-01-16 | 16.7 | 128 | 457 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 128 | 0 | 0 | 39.791 | 270.6667 | -2.8069 | 86.148 | -75 | 10.068 | 238.665 | -196.7165 | -68.7165 | -21.7819 | 0 | -21.7819 | 62.06 | -21.7819 | 9/27/17:00
9 | 27 | 1900-01-17 | 15.6 | 51 | 419 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 51 | 0 | 0 | 39.791 | 270.7083 | -2.8231 | 86.148 | -75 | 10.0821 | 253.6685 | -103.6288 | -52.6288 | -16.6824 | 0 | -16.6824 | 60.08 | -16.6824 | 9/27/18:00
9 | 27 | 1900-01-18 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 270.75 | -2.8394 | 86.148 | -75 | 10.0963 | 268.6721 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/27/19:00
9 | 27 | 1900-01-19 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 270.7917 | -2.8556 | 86.148 | -75 | 10.1104 | 283.6756 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/27/20:00
9 | 27 | 1900-01-20 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.8333 | -2.8719 | 86.148 | -75 | 10.1245 | 298.6791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/21:00
9 | 27 | 1900-01-21 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.875 | -2.8881 | 86.148 | -75 | 10.1386 | 313.6826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/22:00
9 | 27 | 1900-01-22 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.9167 | -2.9044 | 86.148 | -75 | 10.1526 | 328.6862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/23:00
9 | 27 | 1900-01-23 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 270.9583 | -2.9206 | 86.148 | -75 | 10.1667 | 343.6897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/27/24:00
9 | 28 | 1899-12-31 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271 | -2.9368 | 86.148 | -75 | 10.1808 | -1.3068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/1:00
9 | 28 | 1900-01-01 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.0417 | -2.9531 | 86.148 | -75 | 10.1948 | 13.6967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/2:00
9 | 28 | 1900-01-02 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.0833 | -2.9693 | 86.148 | -75 | 10.2089 | 28.7002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/3:00
9 | 28 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.125 | -2.9856 | 86.148 | -75 | 10.2229 | 43.7037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/4:00
9 | 28 | 1900-01-04 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.1667 | -3.0018 | 86.148 | -75 | 10.237 | 58.7072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/5:00
9 | 28 | 1900-01-05 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.2083 | -3.018 | 86.148 | -75 | 10.251 | 73.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/6:00
9 | 28 | 1900-01-06 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.25 | -3.0343 | 86.148 | -75 | 10.265 | 88.7142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/7:00
9 | 28 | 1900-01-07 | 10.6 | 74 | 151 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 74 | 0 | 0 | 39.791 | 271.2917 | -3.0505 | 86.148 | -75 | 10.279 | 103.7177 | -32.618 | 41.382 | 13.1174 | 13.1174 | 0 | 0 | 0 | 9/28/8:00
9 | 28 | 1900-01-08 | 12.2 | 138 | 426 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 138 | 0 | 0 | 39.791 | 271.3333 | -3.0667 | 86.148 | -75 | 10.293 | 118.7212 | -171.6592 | -33.6592 | -10.6694 | -10.6694 | 0 | 0 | 0 | 9/28/9:00
9 | 28 | 1900-01-09 | 12.2 | 210 | 31 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 210 | 0 | 0 | 39.791 | 271.375 | -3.0829 | 86.148 | -75 | 10.307 | 133.7247 | -17.5074 | 192.4926 | 61.0168 | 61.0168 | 0 | 0 | 0 | 9/28/10:00
9 | 28 | 1900-01-10 | 13.3 | 270 | 24 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 270 | 0 | 0 | 39.791 | 271.4167 | -3.0992 | 86.148 | -75 | 10.3209 | 148.7282 | -16.5693 | 253.4307 | 80.3331 | 0 | 80.3331 | 55.94 | 80.3331 | 9/28/11:00
9 | 28 | 1900-01-11 | 13.9 | 338 | 96 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 338 | 0 | 0 | 39.791 | 271.4583 | -3.1154 | 86.148 | -75 | 10.3349 | 163.7317 | -74.0457 | 263.9543 | 83.6689 | 0 | 83.6689 | 57.02 | 83.6689 | 9/28/12:00
9 | 28 | 1900-01-12 | 13.9 | 308 | 24 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 308 | 0 | 0 | 39.791 | 271.5 | -3.1316 | 86.148 | -75 | 10.3489 | 178.7352 | -19.2483 | 288.7517 | 91.5292 | 0 | 91.5292 | 57.02 | 91.5292 | 9/28/13:00
9 | 28 | 1900-01-13 | 13.9 | 232 | 6 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 232 | 0 | 0 | 39.791 | 271.5417 | -3.1478 | 86.148 | -75 | 10.3628 | 193.7387 | -4.6825 | 227.3175 | 72.0557 | 0 | 72.0557 | 57.02 | 72.0557 | 9/28/14:00
9 | 28 | 1900-01-14 | 13.9 | 138 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 138 | 0 | 0 | 39.791 | 271.5833 | -3.1641 | 86.148 | -75 | 10.3767 | 208.7422 | 0 | 138 | 43.7436 | 0 | 43.7436 | 57.02 | 43.7436 | 9/28/15:00
9 | 28 | 1900-01-15 | 14.4 | 225 | 47 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 225 | 0 | 0 | 39.791 | 271.625 | -3.1803 | 86.148 | -75 | 10.3907 | 223.7457 | -27.7179 | 197.2821 | 62.535 | 0 | 62.535 | 57.92 | 62.535 | 9/28/16:00
9 | 28 | 1900-01-16 | 14.4 | 127 | 451 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 127 | 0 | 0 | 39.791 | 271.6667 | -3.1965 | 86.148 | -75 | 10.4046 | 238.7491 | -195.5955 | -68.5955 | -21.7436 | 0 | -21.7436 | 57.92 | -21.7436 | 9/28/17:00
9 | 28 | 1900-01-17 | 14.4 | 61 | 332 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 61 | 0 | 0 | 39.791 | 271.7083 | -3.2127 | 86.148 | -75 | 10.4185 | 253.7526 | -83.1698 | -22.1698 | -7.0275 | 0 | -7.0275 | 57.92 | -7.0275 | 9/28/18:00
9 | 28 | 1900-01-18 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.75 | -3.2289 | 86.148 | -75 | 10.4324 | 268.7561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/19:00
9 | 28 | 1900-01-19 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.7917 | -3.2452 | 86.148 | -75 | 10.4463 | 283.7596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/20:00
9 | 28 | 1900-01-20 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 271.8333 | -3.2614 | 86.148 | -75 | 10.4601 | 298.763 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/28/21:00
9 | 28 | 1900-01-21 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.875 | -3.2776 | 86.148 | -75 | 10.474 | 313.7665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/22:00
9 | 28 | 1900-01-22 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.9167 | -3.2938 | 86.148 | -75 | 10.4879 | 328.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/23:00
9 | 28 | 1900-01-23 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 271.9583 | -3.31 | 86.148 | -75 | 10.5017 | 343.7734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/28/24:00
9 | 29 | 1899-12-31 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 272 | -3.3262 | 86.148 | -75 | 10.5156 | -1.2231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/29/1:00
9 | 29 | 1900-01-01 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 272.0417 | -3.3424 | 86.148 | -75 | 10.5294 | 13.7803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/29/2:00
9 | 29 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 272.0833 | -3.3586 | 86.148 | -75 | 10.5432 | 28.7838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/29/3:00
9 | 29 | 1900-01-03 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 272.125 | -3.3748 | 86.148 | -75 | 10.557 | 43.7873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/29/4:00
9 | 29 | 1900-01-04 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 272.1667 | -3.391 | 86.148 | -75 | 10.5708 | 58.7907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/29/5:00
9 | 29 | 1900-01-05 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 272.2083 | -3.4072 | 86.148 | -75 | 10.5846 | 73.7942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/29/6:00
9 | 29 | 1900-01-06 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 272.25 | -3.4234 | 86.148 | -75 | 10.5984 | 88.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/29/7:00
9 | 29 | 1900-01-07 | 10.6 | 73 | 243 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 73 | 0 | 0 | 39.791 | 272.2917 | -3.4396 | 86.148 | -75 | 10.6122 | 103.801 | -53.7919 | 19.2081 | 6.0886 | 6.0886 | 0 | 0 | 0 | 9/29/8:00
9 | 29 | 1900-01-08 | 12.2 | 103 | 515 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 103 | 0 | 0 | 39.791 | 272.3333 | -3.4558 | 86.148 | -75 | 10.6259 | 118.8045 | -210.1864 | -107.1864 | -33.9762 | -33.9762 | 0 | 0 | 0 | 9/29/9:00
9 | 29 | 1900-01-09 | 14.4 | 154 | 565 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 154 | 0 | 0 | 39.791 | 272.375 | -3.472 | 86.148 | -75 | 10.6397 | 133.8079 | -321.875 | -167.875 | -53.2135 | 0 | -53.2135 | 57.92 | -53.2135 | 9/29/10:00
9 | 29 | 1900-01-10 | 16.1 | 165 | 637 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 165 | 0 | 0 | 39.791 | 272.4167 | -3.4882 | 86.148 | -75 | 10.6534 | 148.8113 | -442.7456 | -277.7456 | -88.0405 | 0 | -88.0405 | 60.98 | -88.0405 | 9/29/11:00
9 | 29 | 1900-01-11 | 17.2 | 311 | 380 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 311 | 0 | 0 | 39.791 | 272.4583 | -3.5044 | 86.148 | -75 | 10.6671 | 163.8148 | -294.7543 | 16.2457 | 5.1496 | 0 | 5.1496 | 62.96 | 5.1496 | 9/29/12:00
9 | 29 | 1900-01-12 | 17.8 | 227 | 607 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 227 | 0 | 0 | 39.791 | 272.5 | -3.5206 | 86.148 | -75 | 10.6808 | 178.8182 | -489.2849 | -262.2849 | -83.1397 | 0 | -83.1397 | 64.04 | -83.1397 | 9/29/13:00
9 | 29 | 1900-01-13 | 18.3 | 179 | 712 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 179 | 0 | 0 | 39.791 | 272.5417 | -3.5368 | 86.148 | -75 | 10.6946 | 193.8216 | -558.3461 | -379.3461 | -120.2461 | 0 | -120.2461 | 64.94 | -120.2461 | 9/29/14:00
9 | 29 | 1900-01-14 | 18.9 | 157 | 684 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 157 | 0 | 0 | 39.791 | 272.5833 | -3.553 | 86.148 | -75 | 10.7083 | 208.8251 | -486.6967 | -329.6967 | -104.5081 | 0 | -104.5081 | 66.02 | -104.5081 | 9/29/15:00
9 | 29 | 1900-01-15 | 19.4 | 114 | 690 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 114 | 0 | 0 | 39.791 | 272.625 | -3.5691 | 86.148 | -75 | 10.7219 | 223.8285 | -409.2325 | -295.2325 | -93.5835 | 0 | -93.5835 | 66.92 | -93.5835 | 9/29/16:00
9 | 29 | 1900-01-16 | 18.9 | 105 | 514 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 105 | 0 | 0 | 39.791 | 272.6667 | -3.5853 | 86.148 | -75 | 10.7356 | 238.8319 | -224.5773 | -119.5773 | -37.9039 | 0 | -37.9039 | 66.02 | -37.9039 | 9/29/17:00
9 | 29 | 1900-01-17 | 18.3 | 56 | 314 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 56 | 0 | 0 | 39.791 | 272.7083 | -3.6015 | 86.148 | -75 | 10.7493 | 253.8353 | -79.6608 | -23.6608 | -7.5001 | 0 | -7.5001 | 64.94 | -7.5001 | 9/29/18:00
9 | 29 | 1900-01-18 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 272.75 | -3.6177 | 86.148 | -75 | 10.7629 | 268.8387 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 9/29/19:00
9 | 29 | 1900-01-19 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 272.7917 | -3.6339 | 86.148 | -75 | 10.7766 | 283.8421 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 9/29/20:00
9 | 29 | 1900-01-20 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 272.8333 | -3.65 | 86.148 | -75 | 10.7902 | 298.8456 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/29/21:00
9 | 29 | 1900-01-21 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 272.875 | -3.6662 | 86.148 | -75 | 10.8039 | 313.849 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 9/29/22:00
9 | 29 | 1900-01-22 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 272.9167 | -3.6824 | 86.148 | -75 | 10.8175 | 328.8524 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 9/29/23:00
9 | 29 | 1900-01-23 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 272.9583 | -3.6986 | 86.148 | -75 | 10.8311 | 343.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/29/24:00
9 | 30 | 1899-12-31 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 273 | -3.7147 | 86.148 | -75 | 10.8447 | -1.1408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/30/1:00
9 | 30 | 1900-01-01 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 273.0417 | -3.7309 | 86.148 | -75 | 10.8583 | 13.8626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/30/2:00
9 | 30 | 1900-01-02 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 273.0833 | -3.7471 | 86.148 | -75 | 10.8718 | 28.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/30/3:00
9 | 30 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 273.125 | -3.7632 | 86.148 | -75 | 10.8854 | 43.8694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/30/4:00
9 | 30 | 1900-01-04 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 273.1667 | -3.7794 | 86.148 | -75 | 10.899 | 58.8727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/30/5:00
9 | 30 | 1900-01-05 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 273.2083 | -3.7956 | 86.148 | -75 | 10.9125 | 73.8761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/30/6:00
9 | 30 | 1900-01-06 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 273.25 | -3.8117 | 86.148 | -75 | 10.926 | 88.8795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9/30/7:00
9 | 30 | 1900-01-07 | 11.1 | 73 | 184 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 73 | 0 | 0 | 39.791 | 273.2917 | -3.8279 | 86.148 | -75 | 10.9396 | 103.8829 | -41.7089 | 31.2911 | 9.9187 | 9.9187 | 0 | 0 | 0 | 9/30/8:00
9 | 30 | 1900-01-08 | 13.3 | 106 | 490 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 106 | 0 | 0 | 39.791 | 273.3333 | -3.844 | 86.148 | -75 | 10.9531 | 118.8863 | -202.4952 | -96.4952 | -30.5873 | 0 | -30.5873 | 55.94 | -30.5873 | 9/30/9:00
9 | 30 | 1900-01-09 | 15.6 | 165 | 523 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 165 | 0 | 0 | 39.791 | 273.375 | -3.8602 | 86.148 | -75 | 10.9666 | 133.8896 | -300.5031 | -135.5031 | -42.9521 | 0 | -42.9521 | 60.08 | -42.9521 | 9/30/10:00
9 | 30 | 1900-01-10 | 17.8 | 186 | 577 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 186 | 0 | 0 | 39.791 | 273.4167 | -3.8763 | 86.148 | -75 | 10.9801 | 148.893 | -403.7003 | -217.7003 | -69.0072 | 0 | -69.0072 | 64.04 | -69.0072 | 9/30/11:00
9 | 30 | 1900-01-11 | 18.9 | 204 | 621 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 204 | 0 | 0 | 39.791 | 273.4583 | -3.8925 | 86.148 | -75 | 10.9935 | 163.8964 | -484.3653 | -280.3653 | -88.8709 | 0 | -88.8709 | 66.02 | -88.8709 | 9/30/12:00
9 | 30 | 1900-01-12 | 20 | 224 | 606 | 68 | 0 | 1 | 0 | 68 | 0 | 224 | 0 | 0 | 39.791 | 273.5 | -3.9086 | 86.148 | -75 | 11.007 | 178.8997 | -490.909 | -266.909 | -84.6055 | 0 | -84.6055 | 68 | -84.6055 | 9/30/13:00
9 | 30 | 1900-01-13 | 21.1 | 200 | 646 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 200 | 0 | 0 | 39.791 | 273.5417 | -3.9248 | 86.148 | -75 | 11.0205 | 193.9031 | -509.0022 | -309.0022 | -97.9483 | 0 | -97.9483 | 69.98 | -97.9483 | 9/30/14:00
9 | 30 | 1900-01-14 | 21.7 | 177 | 631 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 177 | 0 | 0 | 39.791 | 273.5833 | -3.9409 | 86.148 | -75 | 11.0339 | 208.9065 | -451.1939 | -274.1939 | -86.9147 | 0 | -86.9147 | 71.06 | -86.9147 | 9/30/15:00
9 | 30 | 1900-01-15 | 22.2 | 129 | 625 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 129 | 0 | 0 | 39.791 | 273.625 | -3.9571 | 86.148 | -75 | 11.0473 | 223.9098 | -372.7588 | -243.7588 | -77.2673 | 0 | -77.2673 | 71.96 | -77.2673 | 9/30/16:00
9 | 30 | 1900-01-16 | 21.7 | 80 | 617 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 80 | 0 | 0 | 39.791 | 273.6667 | -3.9732 | 86.148 | -75 | 11.0608 | 238.9132 | -271.5639 | -191.5639 | -60.7224 | 0 | -60.7224 | 71.06 | -60.7224 | 9/30/17:00
9 | 30 | 1900-01-17 | 20.6 | 50 | 371 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 50 | 0 | 0 | 39.791 | 273.7083 | -3.9894 | 86.148 | -75 | 11.0742 | 253.9165 | -95.3025 | -45.3025 | -14.3601 | 0 | -14.3601 | 69.08 | -14.3601 | 9/30/18:00
9 | 30 | 1900-01-18 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 273.75 | -4.0055 | 86.148 | -75 | 11.0876 | 268.9199 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 9/30/19:00
9 | 30 | 1900-01-19 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 273.7917 | -4.0217 | 86.148 | -75 | 11.101 | 283.9232 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 9/30/20:00
9 | 30 | 1900-01-20 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 273.8333 | -4.0378 | 86.148 | -75 | 11.1144 | 298.9266 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 9/30/21:00
9 | 30 | 1900-01-21 | 15.1 | 0 | 0 | 59.18 | 0 | 1 | 0 | 59.18 | 0 | 0 | 0 | 0 | 39.791 | 273.875 | -4.0539 | 86.148 | -75 | 11.1277 | 313.9299 | 0 | 0 | 0 | 0 | 0 | 59.18 | 0 | 9/30/22:00
9 | 30 | 1900-01-22 | 16.3 | 0 | 0 | 61.34 | 0 | 1 | 0 | 61.34 | 0 | 0 | 0 | 0 | 39.791 | 273.9167 | -4.0701 | 86.148 | -75 | 11.1411 | 328.9333 | 0 | 0 | 0 | 0 | 0 | 61.34 | 0 | 9/30/23:00
9 | 30 | 1900-01-23 | 17.5 | 0 | 0 | 63.5 | 0 | 1 | 0 | 63.5 | 0 | 0 | 0 | 0 | 39.791 | 273.9583 | -4.0862 | 86.148 | -75 | 11.1544 | 343.9366 | 0 | 0 | 0 | 0 | 0 | 63.5 | 0 | 9/30/24:00
10 | 1 | 1899-12-31 | 18.6 | 0 | 0 | 65.48 | 0 | 1 | 0 | 65.48 | 0 | 0 | 0 | 0 | 39.791 | 274 | -4.1023 | 86.148 | -75 | 11.1678 | -1.0601 | 0 | 0 | 0 | 0 | 0 | 65.48 | 0 | 10/1/1:00
10 | 1 | 1900-01-01 | 19.8 | 0 | 0 | 67.64 | 0 | 1 | 0 | 67.64 | 0 | 0 | 0 | 0 | 39.791 | 274.0417 | -4.1185 | 86.148 | -75 | 11.1811 | 13.9433 | 0 | 0 | 0 | 0 | 0 | 67.64 | 0 | 10/1/2:00
10 | 1 | 1900-01-02 | 21 | 0 | 0 | 69.8 | 0 | 1 | 0 | 69.8 | 0 | 0 | 0 | 0 | 39.791 | 274.0833 | -4.1346 | 86.148 | -75 | 11.1944 | 28.9466 | 0 | 0 | 0 | 0 | 0 | 69.8 | 0 | 10/1/3:00
10 | 1 | 1900-01-03 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 274.125 | -4.1507 | 86.148 | -75 | 11.2077 | 43.9499 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 10/1/4:00
10 | 1 | 1900-01-04 | 22.2 | 0 | 0 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 0 | 0 | 0 | 39.791 | 274.1667 | -4.1668 | 86.148 | -75 | 11.221 | 58.9532 | 0 | 0 | 0 | 0 | 0 | 71.96 | 0 | 10/1/5:00
10 | 1 | 1900-01-05 | 21.7 | 0 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 0 | 0 | 0 | 39.791 | 274.2083 | -4.1829 | 86.148 | -75 | 11.2343 | 73.9566 | 0 | 0 | 0 | 0 | 0 | 71.06 | 0 | 10/1/6:00
10 | 1 | 1900-01-06 | 21.7 | 1 | 0 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 1 | 0 | 0 | 39.791 | 274.25 | -4.1991 | 86.148 | -75 | 11.2475 | 88.9599 | 0 | 1 | 0.31698 | 0 | 0.31698 | 71.06 | 0.31698 | 10/1/7:00
10 | 1 | 1900-01-07 | 19.4 | 38 | 3 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 38 | 0 | 0 | 39.791 | 274.2917 | -4.2152 | 86.148 | -75 | 11.2608 | 103.9632 | -0.69585 | 37.3042 | 11.8248 | 0 | 11.8248 | 66.92 | 11.8248 | 10/1/8:00
10 | 1 | 1900-01-08 | 17.2 | 103 | 5 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 103 | 0 | 0 | 39.791 | 274.3333 | -4.2313 | 86.148 | -75 | 11.2741 | 118.9665 | -2.0917 | 100.9083 | 31.9862 | 0 | 31.9862 | 62.96 | 31.9862 | 10/1/9:00
10 | 1 | 1900-01-09 | 17.2 | 186 | 541 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 186 | 0 | 0 | 39.791 | 274.375 | -4.2474 | 86.148 | -75 | 11.2873 | 133.9698 | -313.4596 | -127.4596 | -40.4025 | 0 | -40.4025 | 62.96 | -40.4025 | 10/1/10:00
10 | 1 | 1900-01-10 | 16.7 | 276 | 256 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 276 | 0 | 0 | 39.791 | 274.4167 | -4.2635 | 86.148 | -75 | 11.3005 | 148.9731 | -180.2765 | 95.7235 | 30.3427 | 0 | 30.3427 | 62.06 | 30.3427 | 10/1/11:00
10 | 1 | 1900-01-11 | 17.2 | 187 | 668 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 187 | 0 | 0 | 39.791 | 274.4583 | -4.2796 | 86.148 | -75 | 11.3137 | 163.9764 | -523.8659 | -336.8659 | -106.7806 | 0 | -106.7806 | 62.96 | -106.7806 | 10/1/12:00
10 | 1 | 1900-01-12 | 18.9 | 249 | 552 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 249 | 0 | 0 | 39.791 | 274.5 | -4.2957 | 86.148 | -75 | 11.3269 | 178.9797 | -449.3512 | -200.3512 | -63.5078 | 0 | -63.5078 | 66.02 | -63.5078 | 10/1/13:00
10 | 1 | 1900-01-13 | 20 | 214 | 668 | 68 | 0 | 1 | 0 | 68 | 0 | 214 | 0 | 0 | 39.791 | 274.5417 | -4.3118 | 86.148 | -75 | 11.3401 | 193.983 | -528.8034 | -314.8034 | -99.7872 | 0 | -99.7872 | 68 | -99.7872 | 10/1/14:00
10 | 1 | 1900-01-14 | 20 | 221 | 560 | 68 | 0 | 1 | 0 | 68 | 0 | 221 | 0 | 0 | 39.791 | 274.5833 | -4.3279 | 86.148 | -75 | 11.3533 | 208.9863 | -402.3673 | -181.3673 | -57.4903 | 0 | -57.4903 | 68 | -57.4903 | 10/1/15:00
10 | 1 | 1900-01-15 | 20 | 117 | 591 | 68 | 0 | 1 | 0 | 68 | 0 | 117 | 0 | 0 | 39.791 | 274.625 | -4.3441 | 86.148 | -75 | 11.3665 | 223.9896 | -354.431 | -237.431 | -75.2615 | 0 | -75.2615 | 68 | -75.2615 | 10/1/16:00
10 | 1 | 1900-01-16 | 20 | 93 | 526 | 68 | 0 | 1 | 0 | 68 | 0 | 93 | 0 | 0 | 39.791 | 274.6667 | -4.3602 | 86.148 | -75 | 11.3796 | 238.9929 | -233.1961 | -140.1961 | -44.4397 | 0 | -44.4397 | 68 | -44.4397 | 10/1/17:00
10 | 1 | 1900-01-17 | 18.9 | 51 | 287 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 51 | 0 | 0 | 39.791 | 274.7083 | -4.3763 | 86.148 | -75 | 11.3928 | 253.9962 | -74.6377 | -23.6377 | -7.4927 | 0 | -7.4927 | 66.02 | -7.4927 | 10/1/18:00
10 | 1 | 1900-01-18 | 15.6 | 10 | 15 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 10 | 0 | 0 | 39.791 | 274.75 | -4.3923 | 86.148 | -75 | 11.4059 | 268.9995 | -0.93588 | 9.0641 | 2.8732 | 0 | 2.8732 | 60.08 | 2.8732 | 10/1/19:00
10 | 1 | 1900-01-19 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 274.7917 | -4.4084 | 86.148 | -75 | 11.419 | 284.0028 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/1/20:00
10 | 1 | 1900-01-20 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 274.8333 | -4.4245 | 86.148 | -75 | 11.4321 | 299.006 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 10/1/21:00
10 | 1 | 1900-01-21 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 274.875 | -4.4406 | 86.148 | -75 | 11.4452 | 314.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/1/22:00
10 | 1 | 1900-01-22 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 274.9167 | -4.4567 | 86.148 | -75 | 11.4583 | 329.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/1/23:00
10 | 1 | 1900-01-23 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 274.9583 | -4.4728 | 86.148 | -75 | 11.4714 | 344.0158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/1/24:00
10 | 2 | 1899-12-31 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275 | -4.4889 | 86.148 | -75 | 11.4844 | -0.98089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/1:00
10 | 2 | 1900-01-01 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.0417 | -4.505 | 86.148 | -75 | 11.4975 | 14.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/2:00
10 | 2 | 1900-01-02 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.0833 | -4.521 | 86.148 | -75 | 11.5105 | 29.0256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/3:00
10 | 2 | 1900-01-03 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.125 | -4.5371 | 86.148 | -75 | 11.5236 | 44.0289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/4:00
10 | 2 | 1900-01-04 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.1667 | -4.5532 | 86.148 | -75 | 11.5366 | 59.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/5:00
10 | 2 | 1900-01-05 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.2083 | -4.5693 | 86.148 | -75 | 11.5496 | 74.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/6:00
10 | 2 | 1900-01-06 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.25 | -4.5854 | 86.148 | -75 | 11.5626 | 89.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/7:00
10 | 2 | 1900-01-07 | 4.4 | 44 | 3 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 44 | 0 | 0 | 39.791 | 275.2917 | -4.6014 | 86.148 | -75 | 11.5755 | 104.0419 | -0.71153 | 43.2885 | 13.7217 | 13.7217 | 0 | 0 | 0 | 10/2/8:00
10 | 2 | 1900-01-08 | 5 | 151 | 126 | 41 | 1 | 0 | 41 | 0 | 0 | 151 | 0 | 0 | 39.791 | 275.3333 | -4.6175 | 86.148 | -75 | 11.5885 | 119.0451 | -53.3433 | 97.6567 | 30.9555 | 30.9555 | 0 | 0 | 0 | 10/2/9:00
10 | 2 | 1900-01-09 | 6.1 | 252 | 226 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 252 | 0 | 0 | 39.791 | 275.375 | -4.6336 | 86.148 | -75 | 11.6015 | 134.0484 | -132.0258 | 119.9742 | 38.0297 | 38.0297 | 0 | 0 | 0 | 10/2/10:00
10 | 2 | 1900-01-10 | 7.2 | 161 | 708 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 161 | 0 | 0 | 39.791 | 275.4167 | -4.6496 | 86.148 | -75 | 11.6144 | 149.0516 | -501.7597 | -340.7597 | -108.0149 | -108.0149 | 0 | 0 | 0 | 10/2/11:00
10 | 2 | 1900-01-11 | 10 | 210 | 478 | 50 | 1 | 0 | 50 | 0 | 0 | 210 | 0 | 0 | 39.791 | 275.4583 | -4.6657 | 86.148 | -75 | 11.6273 | 164.0548 | -376.8696 | -166.8696 | -52.8947 | -52.8947 | 0 | 0 | 0 | 10/2/12:00
10 | 2 | 1900-01-12 | 11.1 | 214 | 526 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 214 | 0 | 0 | 39.791 | 275.5 | -4.6818 | 86.148 | -75 | 11.6403 | 179.0581 | -430.2435 | -216.2435 | -68.5454 | -68.5454 | 0 | 0 | 0 | 10/2/13:00
10 | 2 | 1900-01-13 | 11.7 | 257 | 509 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 257 | 0 | 0 | 39.791 | 275.5417 | -4.6978 | 86.148 | -75 | 11.6532 | 194.0613 | -404.7934 | -147.7934 | -46.8479 | -46.8479 | 0 | 0 | 0 | 10/2/14:00
10 | 2 | 1900-01-14 | 11.1 | 252 | 264 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 252 | 0 | 0 | 39.791 | 275.5833 | -4.7139 | 86.148 | -75 | 11.6661 | 209.0645 | -190.5938 | 61.4062 | 19.4647 | 19.4647 | 0 | 0 | 0 | 10/2/15:00
10 | 2 | 1900-01-15 | 11.1 | 171 | 133 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 171 | 0 | 0 | 39.791 | 275.625 | -4.7299 | 86.148 | -75 | 11.6789 | 224.0677 | -80.1977 | 90.8023 | 28.7827 | 28.7827 | 0 | 0 | 0 | 10/2/16:00
10 | 2 | 1900-01-16 | 12.2 | 108 | 534 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 108 | 0 | 0 | 39.791 | 275.6667 | -4.746 | 86.148 | -75 | 11.6918 | 239.071 | -238.4462 | -130.4462 | -41.3492 | -41.3492 | 0 | 0 | 0 | 10/2/17:00
10 | 2 | 1900-01-17 | 11.1 | 43 | 425 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 43 | 0 | 0 | 39.791 | 275.7083 | -4.762 | 86.148 | -75 | 11.7047 | 254.0742 | -111.8776 | -68.8776 | -21.833 | -21.833 | 0 | 0 | 0 | 10/2/18:00
10 | 2 | 1900-01-18 | 7.2 | 12 | 49 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 12 | 0 | 0 | 39.791 | 275.75 | -4.7781 | 86.148 | -75 | 11.7175 | 269.0774 | -3.2163 | 8.7837 | 2.7843 | 2.7843 | 0 | 0 | 0 | 10/2/19:00
10 | 2 | 1900-01-19 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.7917 | -4.7941 | 86.148 | -75 | 11.7303 | 284.0806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/20:00
10 | 2 | 1900-01-20 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.8333 | -4.8102 | 86.148 | -75 | 11.7432 | 299.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/21:00
10 | 2 | 1900-01-21 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.875 | -4.8262 | 86.148 | -75 | 11.756 | 314.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/22:00
10 | 2 | 1900-01-22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.9167 | -4.8422 | 86.148 | -75 | 11.7688 | 329.0902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/23:00
10 | 2 | 1900-01-23 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 275.9583 | -4.8583 | 86.148 | -75 | 11.7816 | 344.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/2/24:00
10 | 3 | 1899-12-31 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276 | -4.8743 | 86.148 | -75 | 11.7943 | -0.90342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/1:00
10 | 3 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.0417 | -4.8904 | 86.148 | -75 | 11.8071 | 14.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/2:00
10 | 3 | 1900-01-02 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.0833 | -4.9064 | 86.148 | -75 | 11.8198 | 29.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/3:00
10 | 3 | 1900-01-03 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.125 | -4.9224 | 86.148 | -75 | 11.8326 | 44.1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/4:00
10 | 3 | 1900-01-04 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.1667 | -4.9384 | 86.148 | -75 | 11.8453 | 59.1093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/5:00
10 | 3 | 1900-01-05 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.2083 | -4.9545 | 86.148 | -75 | 11.858 | 74.1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/6:00
10 | 3 | 1900-01-06 | -1.7 | 5 | 14 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 5 | 0 | 0 | 39.791 | 276.25 | -4.9705 | 86.148 | -75 | 11.8707 | 89.1157 | -0.6109 | 4.3891 | 1.3913 | 1.3913 | 0 | 0 | 0 | 10/3/7:00
10 | 3 | 1900-01-07 | 0 | 38 | 360 | 32 | 1 | 0 | 32 | 0 | 0 | 38 | 0 | 0 | 39.791 | 276.2917 | -4.9865 | 86.148 | -75 | 11.8834 | 104.1188 | -87.2475 | -49.2475 | -15.6106 | -15.6106 | 0 | 0 | 0 | 10/3/8:00
10 | 3 | 1900-01-08 | 4.4 | 64 | 646 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 64 | 0 | 0 | 39.791 | 276.3333 | -5.0025 | 86.148 | -75 | 11.8961 | 119.122 | -276.7029 | -212.7029 | -67.4231 | -67.4231 | 0 | 0 | 0 | 10/3/9:00
10 | 3 | 1900-01-09 | 7.2 | 85 | 781 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 85 | 0 | 0 | 39.791 | 276.375 | -5.0185 | 86.148 | -75 | 11.9087 | 134.1252 | -459.9348 | -374.9348 | -118.8478 | -118.8478 | 0 | 0 | 0 | 10/3/10:00
10 | 3 | 1900-01-10 | 10 | 100 | 841 | 50 | 1 | 0 | 50 | 0 | 0 | 100 | 0 | 0 | 39.791 | 276.4167 | -5.0346 | 86.148 | -75 | 11.9214 | 149.1283 | -599.7485 | -499.7485 | -158.4115 | -158.4115 | 0 | 0 | 0 | 10/3/11:00
10 | 3 | 1900-01-11 | 12.2 | 128 | 839 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 128 | 0 | 0 | 39.791 | 276.4583 | -5.0506 | 86.148 | -75 | 11.934 | 164.1315 | -664.9697 | -536.9697 | -170.21 | -170.21 | 0 | 0 | 0 | 10/3/12:00
10 | 3 | 1900-01-12 | 13.3 | 149 | 787 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 149 | 0 | 0 | 39.791 | 276.5 | -5.0666 | 86.148 | -75 | 11.9466 | 179.1347 | -646.7677 | -497.7677 | -157.7837 | 0 | -157.7837 | 55.94 | -157.7837 | 10/3/13:00
10 | 3 | 1900-01-13 | 14.4 | 164 | 798 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 164 | 0 | 0 | 39.791 | 276.5417 | -5.0826 | 86.148 | -75 | 11.9592 | 194.1378 | -637.505 | -473.505 | -150.0928 | 0 | -150.0928 | 57.92 | -150.0928 | 10/3/14:00
10 | 3 | 1900-01-14 | 15 | 174 | 709 | 59 | 0 | 1 | 0 | 59 | 0 | 174 | 0 | 0 | 39.791 | 276.5833 | -5.0986 | 86.148 | -75 | 11.9718 | 209.141 | -514.2701 | -340.2701 | -107.8597 | 0 | -107.8597 | 59 | -107.8597 | 10/3/15:00
10 | 3 | 1900-01-15 | 15.6 | 165 | 575 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 165 | 0 | 0 | 39.791 | 276.625 | -5.1146 | 86.148 | -75 | 11.9844 | 224.1441 | -348.59 | -183.59 | -58.1948 | 0 | -58.1948 | 60.08 | -58.1948 | 10/3/16:00
10 | 3 | 1900-01-16 | 15 | 131 | 247 | 59 | 0 | 1 | 0 | 59 | 0 | 131 | 0 | 0 | 39.791 | 276.6667 | -5.1306 | 86.148 | -75 | 11.997 | 239.1472 | -111.0774 | 19.9226 | 6.3151 | 0 | 6.3151 | 59 | 6.3151 | 10/3/17:00
10 | 3 | 1900-01-17 | 13.3 | 60 | 242 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 60 | 0 | 0 | 39.791 | 276.7083 | -5.1466 | 86.148 | -75 | 12.0095 | 254.1504 | -64.4736 | -4.4736 | -1.418 | 0 | -1.418 | 55.94 | -1.418 | 10/3/18:00
10 | 3 | 1900-01-18 | 10.6 | 12 | 10 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 12 | 0 | 0 | 39.791 | 276.75 | -5.1626 | 86.148 | -75 | 12.0221 | 269.1535 | -0.68893 | 11.3111 | 3.5854 | 3.5854 | 0 | 0 | 0 | 10/3/19:00
10 | 3 | 1900-01-19 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.7917 | -5.1786 | 86.148 | -75 | 12.0346 | 284.1567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/20:00
10 | 3 | 1900-01-20 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.8333 | -5.1946 | 86.148 | -75 | 12.0471 | 299.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/21:00
10 | 3 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.875 | -5.2106 | 86.148 | -75 | 12.0596 | 314.1629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/22:00
10 | 3 | 1900-01-22 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.9167 | -5.2266 | 86.148 | -75 | 12.0721 | 329.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/23:00
10 | 3 | 1900-01-23 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 276.9583 | -5.2425 | 86.148 | -75 | 12.0846 | 344.1691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/3/24:00
10 | 4 | 1899-12-31 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 277 | -5.2585 | 86.148 | -75 | 12.0971 | -0.82773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/4/1:00
10 | 4 | 1900-01-01 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 277.0417 | -5.2745 | 86.148 | -75 | 12.1095 | 14.1754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/4/2:00
10 | 4 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 277.0833 | -5.2905 | 86.148 | -75 | 12.122 | 29.1785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/4/3:00
10 | 4 | 1900-01-03 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 277.125 | -5.3065 | 86.148 | -75 | 12.1344 | 44.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/4/4:00
10 | 4 | 1900-01-04 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 277.1667 | -5.3224 | 86.148 | -75 | 12.1468 | 59.1847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/4/5:00
10 | 4 | 1900-01-05 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 277.2083 | -5.3384 | 86.148 | -75 | 12.1592 | 74.1878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/4/6:00
10 | 4 | 1900-01-06 | 7.2 | 2 | 3 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 2 | 0 | 0 | 39.791 | 277.25 | -5.3544 | 86.148 | -75 | 12.1716 | 89.1909 | -0.14675 | 1.8532 | 0.58745 | 0.58745 | 0 | 0 | 0 | 10/4/7:00
10 | 4 | 1900-01-07 | 8.3 | 59 | 70 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 59 | 0 | 0 | 39.791 | 277.2917 | -5.3703 | 86.148 | -75 | 12.184 | 104.194 | -17.3239 | 41.6761 | 13.2106 | 13.2106 | 0 | 0 | 0 | 10/4/8:00
10 | 4 | 1900-01-08 | 11.1 | 86 | 1 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 86 | 0 | 0 | 39.791 | 277.3333 | -5.3863 | 86.148 | -75 | 12.1963 | 119.1971 | -0.43325 | 85.5667 | 27.1232 | 27.1232 | 0 | 0 | 0 | 10/4/9:00
10 | 4 | 1900-01-09 | 12.8 | 186 | 10 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 186 | 0 | 0 | 39.791 | 277.375 | -5.4023 | 86.148 | -75 | 12.2087 | 134.2002 | -5.9357 | 180.0643 | 57.0773 | 0 | 57.0773 | 55.04 | 57.0773 | 10/4/10:00
10 | 4 | 1900-01-10 | 13.9 | 258 | 10 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 258 | 0 | 0 | 39.791 | 277.4167 | -5.4182 | 86.148 | -75 | 12.221 | 149.2033 | -7.1752 | 250.8248 | 79.5071 | 0 | 79.5071 | 57.02 | 79.5071 | 10/4/11:00
10 | 4 | 1900-01-11 | 15.6 | 315 | 18 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 315 | 0 | 0 | 39.791 | 277.4583 | -5.4342 | 86.148 | -75 | 12.2333 | 164.2063 | -14.3399 | 300.6601 | 95.304 | 0 | 95.304 | 60.08 | 95.304 | 10/4/12:00
10 | 4 | 1900-01-12 | 16.7 | 325 | 10 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 325 | 0 | 0 | 39.791 | 277.5 | -5.4501 | 86.148 | -75 | 12.2456 | 179.2094 | -8.2562 | 316.7438 | 100.4022 | 0 | 100.4022 | 62.06 | 100.4022 | 10/4/13:00
10 | 4 | 1900-01-13 | 17.2 | 296 | 4 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 296 | 0 | 0 | 39.791 | 277.5417 | -5.4661 | 86.148 | -75 | 12.2579 | 194.2125 | -3.2098 | 292.7902 | 92.8094 | 0 | 92.8094 | 62.96 | 92.8094 | 10/4/14:00
10 | 4 | 1900-01-14 | 18.3 | 305 | 131 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 305 | 0 | 0 | 39.791 | 277.5833 | -5.482 | 86.148 | -75 | 12.2702 | 209.2156 | -95.4611 | 209.5389 | 66.4202 | 0 | 66.4202 | 64.94 | 66.4202 | 10/4/15:00
10 | 4 | 1900-01-15 | 18.3 | 247 | 6 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 247 | 0 | 0 | 39.791 | 277.625 | -5.498 | 86.148 | -75 | 12.2825 | 224.2186 | -3.6568 | 243.3432 | 77.1355 | 0 | 77.1355 | 64.94 | 77.1355 | 10/4/16:00
10 | 4 | 1900-01-16 | 20 | 135 | 35 | 68 | 0 | 1 | 0 | 68 | 0 | 135 | 0 | 0 | 39.791 | 277.6667 | -5.5139 | 86.148 | -75 | 12.2947 | 239.2217 | -15.8505 | 119.1495 | 37.7683 | 0 | 37.7683 | 68 | 37.7683 | 10/4/17:00
10 | 4 | 1900-01-17 | 21.1 | 49 | 6 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 49 | 0 | 0 | 39.791 | 277.7083 | -5.5299 | 86.148 | -75 | 12.307 | 254.2247 | -1.6176 | 47.3824 | 15.0194 | 0 | 15.0194 | 69.98 | 15.0194 | 10/4/18:00
10 | 4 | 1900-01-18 | 20 | 10 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 10 | 0 | 0 | 39.791 | 277.75 | -5.5458 | 86.148 | -75 | 12.3192 | 269.2278 | 0 | 10 | 3.1698 | 0 | 3.1698 | 68 | 3.1698 | 10/4/19:00
10 | 4 | 1900-01-19 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 277.7917 | -5.5618 | 86.148 | -75 | 12.3314 | 284.2309 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 10/4/20:00
10 | 4 | 1900-01-20 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 277.8333 | -5.5777 | 86.148 | -75 | 12.3436 | 299.2339 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 10/4/21:00
10 | 4 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 277.875 | -5.5936 | 86.148 | -75 | 12.3558 | 314.237 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 10/4/22:00
10 | 4 | 1900-01-22 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 277.9167 | -5.6096 | 86.148 | -75 | 12.368 | 329.24 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 10/4/23:00
10 | 4 | 1900-01-23 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 277.9583 | -5.6255 | 86.148 | -75 | 12.3801 | 344.243 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 10/4/24:00
10 | 5 | 1899-12-31 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 278 | -5.6414 | 86.148 | -75 | 12.3923 | -0.75393 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 10/5/1:00
10 | 5 | 1900-01-01 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 278.0417 | -5.6573 | 86.148 | -75 | 12.4044 | 14.2491 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 10/5/2:00
10 | 5 | 1900-01-02 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 278.0833 | -5.6733 | 86.148 | -75 | 12.4165 | 29.2521 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 10/5/3:00
10 | 5 | 1900-01-03 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 278.125 | -5.6892 | 86.148 | -75 | 12.4286 | 44.2552 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 10/5/4:00
10 | 5 | 1900-01-04 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 278.1667 | -5.7051 | 86.148 | -75 | 12.4407 | 59.2582 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 10/5/5:00
10 | 5 | 1900-01-05 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 278.2083 | -5.721 | 86.148 | -75 | 12.4528 | 74.2612 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 10/5/6:00
10 | 5 | 1900-01-06 | 15 | 5 | 2 | 59 | 0 | 1 | 0 | 59 | 0 | 5 | 0 | 0 | 39.791 | 278.25 | -5.7369 | 86.148 | -75 | 12.4649 | 89.2642 | -0.10831 | 4.8917 | 1.5506 | 0 | 1.5506 | 59 | 1.5506 | 10/5/7:00
10 | 5 | 1900-01-07 | 15.6 | 50 | 246 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 50 | 0 | 0 | 39.791 | 278.2917 | -5.7528 | 86.148 | -75 | 12.4769 | 104.2672 | -62.13 | -12.13 | -3.845 | 0 | -3.845 | 60.08 | -3.845 | 10/5/8:00
10 | 5 | 1900-01-08 | 18.3 | 86 | 421 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 86 | 0 | 0 | 39.791 | 278.3333 | -5.7687 | 86.148 | -75 | 12.489 | 119.2702 | -184.4444 | -98.4444 | -31.2052 | 0 | -31.2052 | 64.94 | -31.2052 | 10/5/9:00
10 | 5 | 1900-01-09 | 21.1 | 166 | 386 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 166 | 0 | 0 | 39.791 | 278.375 | -5.7846 | 86.148 | -75 | 12.501 | 134.2732 | -230.8924 | -64.8924 | -20.5698 | 0 | -20.5698 | 69.98 | -20.5698 | 10/5/10:00
10 | 5 | 1900-01-10 | 23.3 | 316 | 158 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 316 | 0 | 0 | 39.791 | 278.4167 | -5.8005 | 86.148 | -75 | 12.513 | 149.2762 | -114.0496 | 201.9504 | 64.0148 | 0 | 64.0148 | 73.94 | 64.0148 | 10/5/11:00
10 | 5 | 1900-01-11 | 25 | 209 | 618 | 77 | 0 | 1 | 0 | 77 | 0 | 209 | 0 | 0 | 39.791 | 278.4583 | -5.8164 | 86.148 | -75 | 12.525 | 164.2792 | -494.8271 | -285.8271 | -90.6022 | 0 | -90.6022 | 77 | -90.6022 | 10/5/12:00
10 | 5 | 1900-01-12 | 25.6 | 146 | 757 | 78.08 | 0 | 1 | 0 | 78.08 | 0 | 146 | 0 | 0 | 39.791 | 278.5 | -5.8323 | 86.148 | -75 | 12.537 | 179.2822 | -627.8412 | -481.8412 | -152.7352 | 0 | -152.7352 | 78.08 | -152.7352 | 10/5/13:00
10 | 5 | 1900-01-13 | 26.1 | 153 | 686 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 153 | 0 | 0 | 39.791 | 278.5417 | -5.8482 | 86.148 | -75 | 12.5489 | 194.2852 | -552.8888 | -399.8888 | -126.7578 | 0 | -126.7578 | 78.98 | -126.7578 | 10/5/14:00
10 | 5 | 1900-01-14 | 26.1 | 129 | 718 | 78.98 | 0 | 1 | 0 | 78.98 | 0 | 129 | 0 | 0 | 39.791 | 278.5833 | -5.8641 | 86.148 | -75 | 12.5609 | 209.2882 | -525.606 | -396.606 | -125.7172 | 0 | -125.7172 | 78.98 | -125.7172 | 10/5/15:00
10 | 5 | 1900-01-15 | 27.2 | 114 | 665 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 114 | 0 | 0 | 39.791 | 278.625 | -5.88 | 86.148 | -75 | 12.5728 | 224.2912 | -407.4317 | -293.4317 | -93.0127 | 0 | -93.0127 | 80.96 | -93.0127 | 10/5/16:00
10 | 5 | 1900-01-16 | 27.2 | 93 | 337 | 80.96 | 0 | 1 | 0 | 80.96 | 0 | 93 | 0 | 0 | 39.791 | 278.6667 | -5.8959 | 86.148 | -75 | 12.5847 | 239.2942 | -153.6804 | -60.6804 | -19.2346 | 0 | -19.2346 | 80.96 | -19.2346 | 10/5/17:00
10 | 5 | 1900-01-17 | 25 | 64 | 143 | 77 | 0 | 1 | 0 | 77 | 0 | 64 | 0 | 0 | 39.791 | 278.7083 | -5.9118 | 86.148 | -75 | 12.5967 | 254.2972 | -39.0065 | 24.9935 | 7.9225 | 0 | 7.9225 | 77 | 7.9225 | 10/5/18:00
10 | 5 | 1900-01-18 | 23.9 | 8 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 8 | 0 | 0 | 39.791 | 278.75 | -5.9276 | 86.148 | -75 | 12.6085 | 269.3001 | 0 | 8 | 2.5359 | 0 | 2.5359 | 75.02 | 2.5359 | 10/5/19:00
10 | 5 | 1900-01-19 | 24.4 | 0 | 0 | 75.92 | 0 | 1 | 0 | 75.92 | 0 | 0 | 0 | 0 | 39.791 | 278.7917 | -5.9435 | 86.148 | -75 | 12.6204 | 284.3031 | 0 | 0 | 0 | 0 | 0 | 75.92 | 0 | 10/5/20:00
10 | 5 | 1900-01-20 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 278.8333 | -5.9594 | 86.148 | -75 | 12.6323 | 299.3061 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 10/5/21:00
10 | 5 | 1900-01-21 | 23.9 | 0 | 0 | 75.02 | 0 | 1 | 0 | 75.02 | 0 | 0 | 0 | 0 | 39.791 | 278.875 | -5.9753 | 86.148 | -75 | 12.6441 | 314.309 | 0 | 0 | 0 | 0 | 0 | 75.02 | 0 | 10/5/22:00
10 | 5 | 1900-01-22 | 22.8 | 0 | 0 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 0 | 0 | 0 | 39.791 | 278.9167 | -5.9911 | 86.148 | -75 | 12.656 | 329.312 | 0 | 0 | 0 | 0 | 0 | 73.04 | 0 | 10/5/23:00
10 | 5 | 1900-01-23 | 21.1 | 0 | 0 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 0 | 0 | 0 | 39.791 | 278.9583 | -6.007 | 86.148 | -75 | 12.6678 | 344.315 | 0 | 0 | 0 | 0 | 0 | 69.98 | 0 | 10/5/24:00
10 | 6 | 1899-12-31 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 279 | -6.0229 | 86.148 | -75 | 12.6796 | -0.68209 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 10/6/1:00
10 | 6 | 1900-01-01 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 279.0417 | -6.0387 | 86.148 | -75 | 12.6914 | 14.3209 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 10/6/2:00
10 | 6 | 1900-01-02 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 279.0833 | -6.0546 | 86.148 | -75 | 12.7032 | 29.3238 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 10/6/3:00
10 | 6 | 1900-01-03 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 279.125 | -6.0704 | 86.148 | -75 | 12.715 | 44.3267 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 10/6/4:00
10 | 6 | 1900-01-04 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 279.1667 | -6.0863 | 86.148 | -75 | 12.7267 | 59.3297 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 10/6/5:00
10 | 6 | 1900-01-05 | 20.6 | 0 | 0 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 0 | 0 | 0 | 39.791 | 279.2083 | -6.1021 | 86.148 | -75 | 12.7385 | 74.3326 | 0 | 0 | 0 | 0 | 0 | 69.08 | 0 | 10/6/6:00
10 | 6 | 1900-01-06 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 279.25 | -6.118 | 86.148 | -75 | 12.7502 | 89.3355 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 10/6/7:00
10 | 6 | 1900-01-07 | 16.7 | 38 | 3 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 38 | 0 | 0 | 39.791 | 279.2917 | -6.1338 | 86.148 | -75 | 12.7619 | 104.3385 | -0.77275 | 37.2272 | 11.8004 | 0 | 11.8004 | 62.06 | 11.8004 | 10/6/8:00
10 | 6 | 1900-01-08 | 16.7 | 102 | 9 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 102 | 0 | 0 | 39.791 | 279.3333 | -6.1497 | 86.148 | -75 | 12.7736 | 119.3414 | -3.9862 | 98.0138 | 31.0687 | 0 | 31.0687 | 62.06 | 31.0687 | 10/6/9:00
10 | 6 | 1900-01-09 | 15.6 | 182 | 7 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 182 | 0 | 0 | 39.791 | 279.375 | -6.1655 | 86.148 | -75 | 12.7853 | 134.3443 | -4.2189 | 177.7811 | 56.3535 | 0 | 56.3535 | 60.08 | 56.3535 | 10/6/10:00
10 | 6 | 1900-01-10 | 16.7 | 178 | 456 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 178 | 0 | 0 | 39.791 | 279.4167 | -6.1814 | 86.148 | -75 | 12.7969 | 149.3472 | -331.0962 | -153.0962 | -48.5288 | 0 | -48.5288 | 62.06 | -48.5288 | 10/6/11:00
10 | 6 | 1900-01-11 | 16.7 | 232 | 173 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 232 | 0 | 0 | 39.791 | 279.4583 | -6.1972 | 86.148 | -75 | 12.8086 | 164.3501 | -139.2066 | 92.7934 | 29.4139 | 0 | 29.4139 | 62.06 | 29.4139 | 10/6/12:00
10 | 6 | 1900-01-12 | 16.1 | 347 | 29 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 347 | 0 | 0 | 39.791 | 279.5 | -6.213 | 86.148 | -75 | 12.8202 | 179.3531 | -24.1595 | 322.8405 | 102.3348 | 0 | 102.3348 | 60.98 | 102.3348 | 10/6/13:00
10 | 6 | 1900-01-13 | 16.7 | 291 | 8 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 291 | 0 | 0 | 39.791 | 279.5417 | -6.2289 | 86.148 | -75 | 12.8319 | 194.356 | -6.4755 | 284.5245 | 90.1893 | 0 | 90.1893 | 62.06 | 90.1893 | 10/6/14:00
10 | 6 | 1900-01-14 | 17.8 | 246 | 182 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 246 | 0 | 0 | 39.791 | 279.5833 | -6.2447 | 86.148 | -75 | 12.8435 | 209.3589 | -133.8316 | 112.1684 | 35.5554 | 0 | 35.5554 | 64.04 | 35.5554 | 10/6/15:00
10 | 6 | 1900-01-15 | 18.3 | 173 | 470 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 173 | 0 | 0 | 39.791 | 279.625 | -6.2605 | 86.148 | -75 | 12.8551 | 224.3618 | -289.4552 | -116.4552 | -36.9143 | 0 | -36.9143 | 64.94 | -36.9143 | 10/6/16:00
10 | 6 | 1900-01-16 | 17.8 | 97 | 221 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 97 | 0 | 0 | 39.791 | 279.6667 | -6.2763 | 86.148 | -75 | 12.8666 | 239.3647 | -101.4757 | -4.4757 | -1.4187 | 0 | -1.4187 | 64.04 | -1.4187 | 10/6/17:00
10 | 6 | 1900-01-17 | 16.7 | 36 | 389 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 36 | 0 | 0 | 39.791 | 279.7083 | -6.2921 | 86.148 | -75 | 12.8782 | 254.3676 | -107.3434 | -71.3434 | -22.6146 | 0 | -22.6146 | 62.06 | -22.6146 | 10/6/18:00
10 | 6 | 1900-01-18 | 15 | 8 | 32 | 59 | 0 | 1 | 0 | 59 | 0 | 8 | 0 | 0 | 39.791 | 279.75 | -6.308 | 86.148 | -75 | 12.8898 | 269.3704 | -2.5187 | 5.4813 | 1.7375 | 0 | 1.7375 | 59 | 1.7375 | 10/6/19:00
10 | 6 | 1900-01-19 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 279.7917 | -6.3238 | 86.148 | -75 | 12.9013 | 284.3733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/6/20:00
10 | 6 | 1900-01-20 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 279.8333 | -6.3396 | 86.148 | -75 | 12.9128 | 299.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/6/21:00
10 | 6 | 1900-01-21 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 279.875 | -6.3554 | 86.148 | -75 | 12.9243 | 314.3791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/6/22:00
10 | 6 | 1900-01-22 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 279.9167 | -6.3712 | 86.148 | -75 | 12.9358 | 329.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/6/23:00
10 | 6 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 279.9583 | -6.387 | 86.148 | -75 | 12.9473 | 344.3848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/6/24:00
10 | 7 | 1899-12-31 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280 | -6.4028 | 86.148 | -75 | 12.9588 | -0.61231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/1:00
10 | 7 | 1900-01-01 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.0417 | -6.4186 | 86.148 | -75 | 12.9702 | 14.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/2:00
10 | 7 | 1900-01-02 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.0833 | -6.4344 | 86.148 | -75 | 12.9816 | 29.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/3:00
10 | 7 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.125 | -6.4502 | 86.148 | -75 | 12.993 | 44.3963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/4:00
10 | 7 | 1900-01-04 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.1667 | -6.466 | 86.148 | -75 | 13.0044 | 59.3991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/5:00
10 | 7 | 1900-01-05 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.2083 | -6.4817 | 86.148 | -75 | 13.0158 | 74.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/6:00
10 | 7 | 1900-01-06 | 5 | 3 | 7 | 41 | 1 | 0 | 41 | 0 | 0 | 3 | 0 | 0 | 39.791 | 280.25 | -6.4975 | 86.148 | -75 | 13.0272 | 89.4048 | -0.45143 | 2.5486 | 0.80785 | 0.80785 | 0 | 0 | 0 | 10/7/7:00
10 | 7 | 1900-01-07 | 6.1 | 36 | 321 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 36 | 0 | 0 | 39.791 | 280.2917 | -6.5133 | 86.148 | -75 | 13.0386 | 104.4076 | -84.2789 | -48.2789 | -15.3036 | -15.3036 | 0 | 0 | 0 | 10/7/8:00
10 | 7 | 1900-01-08 | 7.2 | 63 | 629 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 63 | 0 | 0 | 39.791 | 280.3333 | -6.5291 | 86.148 | -75 | 13.0499 | 119.4105 | -281.5714 | -218.5714 | -69.2833 | -69.2833 | 0 | 0 | 0 | 10/7/9:00
10 | 7 | 1900-01-09 | 10 | 89 | 747 | 50 | 1 | 0 | 50 | 0 | 0 | 89 | 0 | 0 | 39.791 | 280.375 | -6.5449 | 86.148 | -75 | 13.0612 | 134.4133 | -453.5633 | -364.5633 | -115.5602 | -115.5602 | 0 | 0 | 0 | 10/7/10:00
10 | 7 | 1900-01-10 | 11.7 | 245 | 366 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 245 | 0 | 0 | 39.791 | 280.4167 | -6.5606 | 86.148 | -75 | 13.0725 | 149.4161 | -267.2826 | -22.2826 | -7.0632 | -7.0632 | 0 | 0 | 0 | 10/7/11:00
10 | 7 | 1900-01-11 | 13.3 | 263 | 511 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 263 | 0 | 0 | 39.791 | 280.4583 | -6.5764 | 86.148 | -75 | 13.0838 | 164.419 | -413.1811 | -150.1811 | -47.6048 | 0 | -47.6048 | 55.94 | -47.6048 | 10/7/12:00
10 | 7 | 1900-01-12 | 15 | 116 | 786 | 59 | 0 | 1 | 0 | 59 | 0 | 116 | 0 | 0 | 39.791 | 280.5 | -6.5922 | 86.148 | -75 | 13.0951 | 179.4218 | -657.6749 | -541.6749 | -171.7015 | 0 | -171.7015 | 59 | -171.7015 | 10/7/13:00
10 | 7 | 1900-01-13 | 15.6 | 131 | 771 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 131 | 0 | 0 | 39.791 | 280.5417 | -6.6079 | 86.148 | -75 | 13.1064 | 194.4246 | -626.7186 | -495.7186 | -157.1341 | 0 | -157.1341 | 60.08 | -157.1341 | 10/7/14:00
10 | 7 | 1900-01-14 | 16.1 | 146 | 721 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 146 | 0 | 0 | 39.791 | 280.5833 | -6.6237 | 86.148 | -75 | 13.1176 | 209.4274 | -532.5309 | -386.5309 | -122.5235 | 0 | -122.5235 | 60.98 | -122.5235 | 10/7/15:00
10 | 7 | 1900-01-15 | 16.1 | 119 | 656 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 119 | 0 | 0 | 39.791 | 280.625 | -6.6394 | 86.148 | -75 | 13.1289 | 224.4302 | -406.0784 | -287.0784 | -90.9988 | 0 | -90.9988 | 60.98 | -90.9988 | 10/7/16:00
10 | 7 | 1900-01-16 | 15 | 76 | 573 | 59 | 0 | 1 | 0 | 59 | 0 | 76 | 0 | 0 | 39.791 | 280.6667 | -6.6552 | 86.148 | -75 | 13.1401 | 239.433 | -264.8955 | -188.8955 | -59.8766 | 0 | -59.8766 | 59 | -59.8766 | 10/7/17:00
10 | 7 | 1900-01-17 | 13.3 | 44 | 335 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 44 | 0 | 0 | 39.791 | 280.7083 | -6.6709 | 86.148 | -75 | 13.1513 | 254.4358 | -93.5054 | -49.5054 | -15.6924 | 0 | -15.6924 | 55.94 | -15.6924 | 10/7/18:00
10 | 7 | 1900-01-18 | 10 | 7 | 10 | 50 | 1 | 0 | 50 | 0 | 0 | 7 | 0 | 0 | 39.791 | 280.75 | -6.6867 | 86.148 | -75 | 13.1625 | 269.4386 | -0.81997 | 6.18 | 1.959 | 1.959 | 0 | 0 | 0 | 10/7/19:00
10 | 7 | 1900-01-19 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.7917 | -6.7024 | 86.148 | -75 | 13.1737 | 284.4414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/20:00
10 | 7 | 1900-01-20 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.8333 | -6.7182 | 86.148 | -75 | 13.1848 | 299.4442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/21:00
10 | 7 | 1900-01-21 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.875 | -6.7339 | 86.148 | -75 | 13.196 | 314.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/22:00
10 | 7 | 1900-01-22 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.9167 | -6.7496 | 86.148 | -75 | 13.2071 | 329.4498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/23:00
10 | 7 | 1900-01-23 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 280.9583 | -6.7654 | 86.148 | -75 | 13.2182 | 344.4526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/7/24:00
10 | 8 | 1899-12-31 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281 | -6.7811 | 86.148 | -75 | 13.2293 | -0.54467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/1:00
10 | 8 | 1900-01-01 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.0417 | -6.7968 | 86.148 | -75 | 13.2404 | 14.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/2:00
10 | 8 | 1900-01-02 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.0833 | -6.8126 | 86.148 | -75 | 13.2515 | 29.4609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/3:00
10 | 8 | 1900-01-03 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.125 | -6.8283 | 86.148 | -75 | 13.2625 | 44.4636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/4:00
10 | 8 | 1900-01-04 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.1667 | -6.844 | 86.148 | -75 | 13.2736 | 59.4664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/5:00
10 | 8 | 1900-01-05 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.2083 | -6.8597 | 86.148 | -75 | 13.2846 | 74.4691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/6:00
10 | 8 | 1900-01-06 | 1.7 | 2 | 15 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 2 | 0 | 0 | 39.791 | 281.25 | -6.8754 | 86.148 | -75 | 13.2956 | 89.4719 | -1.0437 | 0.95627 | 0.30312 | 0.30312 | 0 | 0 | 0 | 10/8/7:00
10 | 8 | 1900-01-07 | 2.8 | 31 | 393 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 31 | 0 | 0 | 39.791 | 281.2917 | -6.8911 | 86.148 | -75 | 13.3066 | 104.4746 | -105.1114 | -74.1114 | -23.492 | -23.492 | 0 | 0 | 0 | 10/8/8:00
10 | 8 | 1900-01-08 | 6.1 | 52 | 683 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 52 | 0 | 0 | 39.791 | 281.3333 | -6.9068 | 86.148 | -75 | 13.3175 | 119.4774 | -308.9376 | -256.9376 | -81.4447 | -81.4447 | 0 | 0 | 0 | 10/8/9:00
10 | 8 | 1900-01-09 | 8.3 | 69 | 806 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 69 | 0 | 0 | 39.791 | 281.375 | -6.9225 | 86.148 | -75 | 13.3285 | 134.4801 | -492.9405 | -423.9405 | -134.3817 | -134.3817 | 0 | 0 | 0 | 10/8/10:00
10 | 8 | 1900-01-10 | 10 | 86 | 859 | 50 | 1 | 0 | 50 | 0 | 0 | 86 | 0 | 0 | 39.791 | 281.4167 | -6.9382 | 86.148 | -75 | 13.3394 | 149.4829 | -630.8566 | -544.8566 | -172.71 | -172.71 | 0 | 0 | 0 | 10/8/11:00
10 | 8 | 1900-01-11 | 11.7 | 89 | 903 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 89 | 0 | 0 | 39.791 | 281.4583 | -6.9539 | 86.148 | -75 | 13.3504 | 164.4856 | -733.6192 | -644.6192 | -204.333 | -204.333 | 0 | 0 | 0 | 10/8/12:00
10 | 8 | 1900-01-12 | 13.3 | 92 | 913 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 92 | 0 | 0 | 39.791 | 281.5 | -6.9696 | 86.148 | -75 | 13.3613 | 179.4883 | -767.2249 | -675.2249 | -214.0345 | 0 | -214.0345 | 55.94 | -214.0345 | 10/8/13:00
10 | 8 | 1900-01-13 | 15 | 90 | 910 | 59 | 0 | 1 | 0 | 59 | 0 | 90 | 0 | 0 | 39.791 | 281.5417 | -6.9853 | 86.148 | -75 | 13.3722 | 194.491 | -742.787 | -652.787 | -206.9221 | 0 | -206.9221 | 59 | -206.9221 | 10/8/14:00
10 | 8 | 1900-01-14 | 15.6 | 83 | 880 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 83 | 0 | 0 | 39.791 | 281.5833 | -7.001 | 86.148 | -75 | 13.3831 | 209.4938 | -652.8087 | -569.8087 | -180.6194 | 0 | -180.6194 | 60.08 | -180.6194 | 10/8/15:00
10 | 8 | 1900-01-15 | 16.7 | 70 | 824 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 70 | 0 | 0 | 39.791 | 281.625 | -7.0167 | 86.148 | -75 | 13.3939 | 224.4965 | -512.6586 | -442.6586 | -140.315 | 0 | -140.315 | 62.06 | -140.315 | 10/8/16:00
10 | 8 | 1900-01-16 | 16.1 | 53 | 708 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 53 | 0 | 0 | 39.791 | 281.6667 | -7.0324 | 86.148 | -75 | 13.4048 | 239.4992 | -329.5128 | -276.5128 | -87.6497 | 0 | -87.6497 | 60.98 | -87.6497 | 10/8/17:00
10 | 8 | 1900-01-17 | 14.4 | 36 | 413 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 36 | 0 | 0 | 39.791 | 281.7083 | -7.048 | 86.148 | -75 | 13.4156 | 254.5019 | -116.5871 | -80.5871 | -25.5447 | 0 | -25.5447 | 57.92 | -25.5447 | 10/8/18:00
10 | 8 | 1900-01-18 | 11.1 | 6 | 24 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 6 | 0 | 0 | 39.791 | 281.75 | -7.0637 | 86.148 | -75 | 13.4264 | 269.5046 | -2.0471 | 3.9529 | 1.253 | 1.253 | 0 | 0 | 0 | 10/8/19:00
10 | 8 | 1900-01-19 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.7917 | -7.0794 | 86.148 | -75 | 13.4372 | 284.5073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/20:00
10 | 8 | 1900-01-20 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.8333 | -7.095 | 86.148 | -75 | 13.448 | 299.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/21:00
10 | 8 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.875 | -7.1107 | 86.148 | -75 | 13.4588 | 314.5127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/22:00
10 | 8 | 1900-01-22 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.9167 | -7.1264 | 86.148 | -75 | 13.4695 | 329.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/23:00
10 | 8 | 1900-01-23 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 281.9583 | -7.142 | 86.148 | -75 | 13.4803 | 344.5181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/8/24:00
10 | 9 | 1899-12-31 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 282 | -7.1577 | 86.148 | -75 | 13.491 | -0.47925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/9/1:00
10 | 9 | 1900-01-01 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 282.0417 | -7.1733 | 86.148 | -75 | 13.5017 | 14.5234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/9/2:00
10 | 9 | 1900-01-02 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 282.0833 | -7.189 | 86.148 | -75 | 13.5124 | 29.5261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/9/3:00
10 | 9 | 1900-01-03 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 282.125 | -7.2046 | 86.148 | -75 | 13.5231 | 44.5288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/9/4:00
10 | 9 | 1900-01-04 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 282.1667 | -7.2203 | 86.148 | -75 | 13.5337 | 59.5314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/9/5:00
10 | 9 | 1900-01-05 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 282.2083 | -7.2359 | 86.148 | -75 | 13.5444 | 74.5341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/9/6:00
10 | 9 | 1900-01-06 | 7.2 | 1 | 2 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 1 | 0 | 0 | 39.791 | 282.25 | -7.2516 | 86.148 | -75 | 13.555 | 89.5367 | -0.14924 | 0.85076 | 0.26968 | 0.26968 | 0 | 0 | 0 | 10/9/7:00
10 | 9 | 1900-01-07 | 7.8 | 52 | 4 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 52 | 0 | 0 | 39.791 | 282.2917 | -7.2672 | 86.148 | -75 | 13.5656 | 104.5394 | -1.0892 | 50.9108 | 16.1378 | 16.1378 | 0 | 0 | 0 | 10/9/8:00
10 | 9 | 1900-01-08 | 9.4 | 116 | 275 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 116 | 0 | 0 | 39.791 | 282.3333 | -7.2828 | 86.148 | -75 | 13.5762 | 119.542 | -125.6569 | -9.6569 | -3.0611 | -3.0611 | 0 | 0 | 0 | 10/9/9:00
10 | 9 | 1900-01-09 | 10.6 | 156 | 470 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 156 | 0 | 0 | 39.791 | 282.375 | -7.2984 | 86.148 | -75 | 13.5868 | 134.5447 | -289.4873 | -133.4873 | -42.3132 | -42.3132 | 0 | 0 | 0 | 10/9/10:00
10 | 9 | 1900-01-10 | 12.8 | 148 | 625 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 148 | 0 | 0 | 39.791 | 282.4167 | -7.3141 | 86.148 | -75 | 13.5973 | 149.5473 | -461.5438 | -313.5438 | -99.3879 | 0 | -99.3879 | 55.04 | -99.3879 | 10/9/11:00
10 | 9 | 1900-01-11 | 14.4 | 118 | 788 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 118 | 0 | 0 | 39.791 | 282.4583 | -7.3297 | 86.148 | -75 | 13.6079 | 164.55 | -643.1766 | -525.1766 | -166.4718 | 0 | -166.4718 | 57.92 | -166.4718 | 10/9/12:00
10 | 9 | 1900-01-12 | 16.1 | 113 | 862 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 113 | 0 | 0 | 39.791 | 282.5 | -7.3453 | 86.148 | -75 | 13.6184 | 179.5526 | -727.422 | -614.422 | -194.761 | 0 | -194.761 | 60.98 | -194.761 | 10/9/13:00
10 | 9 | 1900-01-13 | 17.8 | 111 | 854 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 111 | 0 | 0 | 39.791 | 282.5417 | -7.3609 | 86.148 | -75 | 13.6289 | 194.5552 | -699.9291 | -588.9291 | -186.6802 | 0 | -186.6802 | 64.04 | -186.6802 | 10/9/14:00
10 | 9 | 1900-01-14 | 18.3 | 109 | 764 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 109 | 0 | 0 | 39.791 | 282.5833 | -7.3765 | 86.148 | -75 | 13.6394 | 209.5578 | -569.1962 | -460.1962 | -145.8741 | 0 | -145.8741 | 64.94 | -145.8741 | 10/9/15:00
10 | 9 | 1900-01-15 | 18.3 | 128 | 615 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 128 | 0 | 0 | 39.791 | 282.625 | -7.3921 | 86.148 | -75 | 13.6499 | 224.5605 | -384.5423 | -256.5423 | -81.3194 | 0 | -81.3194 | 64.94 | -81.3194 | 10/9/16:00
10 | 9 | 1900-01-16 | 17.8 | 148 | 82 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 148 | 0 | 0 | 39.791 | 282.6667 | -7.4077 | 86.148 | -75 | 13.6603 | 239.5631 | -38.4186 | 109.5814 | 34.7354 | 0 | 34.7354 | 64.04 | 34.7354 | 10/9/17:00
10 | 9 | 1900-01-17 | 16.7 | 27 | 28 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 27 | 0 | 0 | 39.791 | 282.7083 | -7.4233 | 86.148 | -75 | 13.6708 | 254.5657 | -7.993 | 19.007 | 6.0249 | 0 | 6.0249 | 62.06 | 6.0249 | 10/9/18:00
10 | 9 | 1900-01-18 | 15.6 | 1 | 1 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 1 | 0 | 0 | 39.791 | 282.75 | -7.4389 | 86.148 | -75 | 13.6812 | 269.5683 | -0.0886 | 0.9114 | 0.2889 | 0 | 0.2889 | 60.08 | 0.2889 | 10/9/19:00
10 | 9 | 1900-01-19 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 282.7917 | -7.4545 | 86.148 | -75 | 13.6916 | 284.5709 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/9/20:00
10 | 9 | 1900-01-20 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 282.8333 | -7.4701 | 86.148 | -75 | 13.702 | 299.5735 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/9/21:00
10 | 9 | 1900-01-21 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 282.875 | -7.4857 | 86.148 | -75 | 13.7124 | 314.5761 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/9/22:00
10 | 9 | 1900-01-22 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 282.9167 | -7.5013 | 86.148 | -75 | 13.7228 | 329.5787 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/9/23:00
10 | 9 | 1900-01-23 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 282.9583 | -7.5169 | 86.148 | -75 | 13.7331 | 344.5813 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/9/24:00
10 | 10 | 1899-12-31 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 283 | -7.5324 | 86.148 | -75 | 13.7434 | -0.41614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/10/1:00
10 | 10 | 1900-01-01 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 283.0417 | -7.548 | 86.148 | -75 | 13.7538 | 14.5864 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/10/2:00
10 | 10 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 283.0833 | -7.5636 | 86.148 | -75 | 13.7641 | 29.589 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/10/3:00
10 | 10 | 1900-01-03 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 283.125 | -7.5792 | 86.148 | -75 | 13.7743 | 44.5916 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/10/4:00
10 | 10 | 1900-01-04 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 283.1667 | -7.5947 | 86.148 | -75 | 13.7846 | 59.5942 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/10/5:00
10 | 10 | 1900-01-05 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 283.2083 | -7.6103 | 86.148 | -75 | 13.7949 | 74.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/10/6:00
10 | 10 | 1900-01-06 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 283.25 | -7.6258 | 86.148 | -75 | 13.8051 | 89.5993 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/10/7:00
10 | 10 | 1900-01-07 | 12.8 | 40 | 7 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 40 | 0 | 0 | 39.791 | 283.2917 | -7.6414 | 86.148 | -75 | 13.8153 | 104.6018 | -1.9396 | 38.0604 | 12.0645 | 0 | 12.0645 | 55.04 | 12.0645 | 10/10/8:00
10 | 10 | 1900-01-08 | 12.8 | 99 | 7 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 99 | 0 | 0 | 39.791 | 283.3333 | -7.6569 | 86.148 | -75 | 13.8255 | 119.6044 | -3.2303 | 95.7697 | 30.3573 | 0 | 30.3573 | 55.04 | 30.3573 | 10/10/9:00
10 | 10 | 1900-01-09 | 13.3 | 189 | 5 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 189 | 0 | 0 | 39.791 | 283.375 | -7.6725 | 86.148 | -75 | 13.8357 | 134.6069 | -3.101 | 185.899 | 58.9267 | 0 | 58.9267 | 55.94 | 58.9267 | 10/10/10:00
10 | 10 | 1900-01-10 | 14.4 | 240 | 8 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 240 | 0 | 0 | 39.791 | 283.4167 | -7.688 | 86.148 | -75 | 13.8458 | 149.6095 | -5.9397 | 234.0603 | 74.193 | 0 | 74.193 | 57.92 | 74.193 | 10/10/11:00
10 | 10 | 1900-01-11 | 15.6 | 306 | 8 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 306 | 0 | 0 | 39.791 | 283.4583 | -7.7036 | 86.148 | -75 | 13.856 | 164.612 | -6.5595 | 299.4405 | 94.9174 | 0 | 94.9174 | 60.08 | 94.9174 | 10/10/12:00
10 | 10 | 1900-01-12 | 16.1 | 363 | 6 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 363 | 0 | 0 | 39.791 | 283.5 | -7.7191 | 86.148 | -75 | 13.8661 | 179.6145 | -5.0842 | 357.9158 | 113.4531 | 0 | 113.4531 | 60.98 | 113.4531 | 10/10/13:00
10 | 10 | 1900-01-13 | 16.1 | 173 | 3 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 173 | 0 | 0 | 39.791 | 283.5417 | -7.7346 | 86.148 | -75 | 13.8762 | 194.6171 | -2.4686 | 170.5314 | 54.0555 | 0 | 54.0555 | 60.98 | 54.0555 | 10/10/14:00
10 | 10 | 1900-01-14 | 16.1 | 291 | 1 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 291 | 0 | 0 | 39.791 | 283.5833 | -7.7502 | 86.148 | -75 | 13.8863 | 209.6196 | -0.74818 | 290.2518 | 92.0048 | 0 | 92.0048 | 60.98 | 92.0048 | 10/10/15:00
10 | 10 | 1900-01-15 | 16.7 | 221 | 1 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 221 | 0 | 0 | 39.791 | 283.625 | -7.7657 | 86.148 | -75 | 13.8964 | 224.6221 | -0.62836 | 220.3716 | 69.854 | 0 | 69.854 | 62.06 | 69.854 | 10/10/16:00
10 | 10 | 1900-01-16 | 16.7 | 121 | 1 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 121 | 0 | 0 | 39.791 | 283.6667 | -7.7812 | 86.148 | -75 | 13.9065 | 239.6246 | -0.47161 | 120.5284 | 38.2054 | 0 | 38.2054 | 62.06 | 38.2054 | 10/10/17:00
10 | 10 | 1900-01-17 | 16.1 | 45 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 45 | 0 | 0 | 39.791 | 283.7083 | -7.7967 | 86.148 | -75 | 13.9165 | 254.6271 | 0 | 45 | 14.2642 | 0 | 14.2642 | 60.98 | 14.2642 | 10/10/18:00
10 | 10 | 1900-01-18 | 15 | 6 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 6 | 0 | 0 | 39.791 | 283.75 | -7.8123 | 86.148 | -75 | 13.9266 | 269.6296 | 0 | 6 | 1.9019 | 0 | 1.9019 | 59 | 1.9019 | 10/10/19:00
10 | 10 | 1900-01-19 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 283.7917 | -7.8278 | 86.148 | -75 | 13.9366 | 284.6321 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/10/20:00
10 | 10 | 1900-01-20 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 283.8333 | -7.8433 | 86.148 | -75 | 13.9466 | 299.6346 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/10/21:00
10 | 10 | 1900-01-21 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 283.875 | -7.8588 | 86.148 | -75 | 13.9565 | 314.6371 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/10/22:00
10 | 10 | 1900-01-22 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 283.9167 | -7.8743 | 86.148 | -75 | 13.9665 | 329.6396 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 10/10/23:00
10 | 10 | 1900-01-23 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 283.9583 | -7.8898 | 86.148 | -75 | 13.9764 | 344.6421 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/10/24:00
10 | 11 | 1899-12-31 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 284 | -7.9053 | 86.148 | -75 | 13.9864 | -0.35541 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/11/1:00
10 | 11 | 1900-01-01 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 284.0417 | -7.9208 | 86.148 | -75 | 13.9963 | 14.6471 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/11/2:00
10 | 11 | 1900-01-02 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 284.0833 | -7.9363 | 86.148 | -75 | 14.0062 | 29.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/11/3:00
10 | 11 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 284.125 | -7.9518 | 86.148 | -75 | 14.0161 | 44.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/11/4:00
10 | 11 | 1900-01-04 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 284.1667 | -7.9672 | 86.148 | -75 | 14.0259 | 59.6545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/11/5:00
10 | 11 | 1900-01-05 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 284.2083 | -7.9827 | 86.148 | -75 | 14.0358 | 74.6569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/11/6:00
10 | 11 | 1900-01-06 | 10.6 | 3 | 6 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 3 | 0 | 0 | 39.791 | 284.25 | -7.9982 | 86.148 | -75 | 14.0456 | 89.6594 | -0.50716 | 2.4928 | 0.79019 | 0.79019 | 0 | 0 | 0 | 10/11/7:00
10 | 11 | 1900-01-07 | 10.6 | 29 | 389 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 29 | 0 | 0 | 39.791 | 284.2917 | -8.0137 | 86.148 | -75 | 14.0554 | 104.6618 | -109.624 | -80.624 | -25.5564 | -25.5564 | 0 | 0 | 0 | 10/11/8:00
10 | 11 | 1900-01-08 | 12.2 | 45 | 699 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 45 | 0 | 0 | 39.791 | 284.3333 | -8.0291 | 86.148 | -75 | 14.0652 | 119.6643 | -325.6991 | -280.6991 | -88.9767 | -88.9767 | 0 | 0 | 0 | 10/11/9:00
10 | 11 | 1900-01-09 | 13.3 | 60 | 820 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 60 | 0 | 0 | 39.791 | 284.375 | -8.0446 | 86.148 | -75 | 14.075 | 134.6667 | -512.0138 | -452.0138 | -143.2805 | 0 | -143.2805 | 55.94 | -143.2805 | 10/11/10:00
10 | 11 | 1900-01-10 | 15 | 72 | 881 | 59 | 0 | 1 | 0 | 59 | 0 | 72 | 0 | 0 | 39.791 | 284.4167 | -8.06 | 86.148 | -75 | 14.0847 | 149.6692 | -657.572 | -585.572 | -185.6161 | 0 | -185.6161 | 59 | -185.6161 | 10/11/11:00
10 | 11 | 1900-01-11 | 16.1 | 78 | 904 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 78 | 0 | 0 | 39.791 | 284.4583 | -8.0755 | 86.148 | -75 | 14.0944 | 164.6716 | -744.5398 | -666.5398 | -211.2815 | 0 | -211.2815 | 60.98 | -211.2815 | 10/11/12:00
10 | 11 | 1900-01-12 | 18.3 | 81 | 918 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 81 | 0 | 0 | 39.791 | 284.5 | -8.091 | 86.148 | -75 | 14.1042 | 179.674 | -781.0329 | -700.0329 | -221.8982 | 0 | -221.8982 | 64.94 | -221.8982 | 10/11/13:00
10 | 11 | 1900-01-13 | 18.9 | 79 | 912 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 79 | 0 | 0 | 39.791 | 284.5417 | -8.1064 | 86.148 | -75 | 14.1139 | 194.6765 | -753.4323 | -674.4323 | -213.7833 | 0 | -213.7833 | 66.02 | -213.7833 | 10/11/14:00
10 | 11 | 1900-01-14 | 19.4 | 72 | 890 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 72 | 0 | 0 | 39.791 | 284.5833 | -8.1218 | 86.148 | -75 | 14.1236 | 209.6789 | -668.6603 | -596.6603 | -189.1309 | 0 | -189.1309 | 66.92 | -189.1309 | 10/11/15:00
10 | 11 | 1900-01-15 | 19.4 | 61 | 836 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 61 | 0 | 0 | 39.791 | 284.625 | -8.1373 | 86.148 | -75 | 14.1332 | 224.6813 | -527.8756 | -466.8756 | -147.9914 | 0 | -147.9914 | 66.92 | -147.9914 | 10/11/16:00
10 | 11 | 1900-01-16 | 18.9 | 46 | 721 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 46 | 0 | 0 | 39.791 | 284.6667 | -8.1527 | 86.148 | -75 | 14.1429 | 239.6837 | -342.2572 | -296.2572 | -93.9084 | 0 | -93.9084 | 66.02 | -93.9084 | 10/11/17:00
10 | 11 | 1900-01-17 | 17.2 | 28 | 442 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 28 | 0 | 0 | 39.791 | 284.7083 | -8.1682 | 86.148 | -75 | 14.1525 | 254.6861 | -128.978 | -100.978 | -32.0083 | 0 | -32.0083 | 62.96 | -32.0083 | 10/11/18:00
10 | 11 | 1900-01-18 | 13.3 | 4 | 23 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 4 | 0 | 0 | 39.791 | 284.75 | -8.1836 | 86.148 | -75 | 14.1621 | 269.6885 | -2.1904 | 1.8096 | 0.57362 | 0 | 0.57362 | 55.94 | 0.57362 | 10/11/19:00
10 | 11 | 1900-01-19 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 284.7917 | -8.199 | 86.148 | -75 | 14.1717 | 284.6909 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/11/20:00
10 | 11 | 1900-01-20 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 284.8333 | -8.2144 | 86.148 | -75 | 14.1813 | 299.6933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/11/21:00
10 | 11 | 1900-01-21 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 284.875 | -8.2299 | 86.148 | -75 | 14.1909 | 314.6957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/11/22:00
10 | 11 | 1900-01-22 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 284.9167 | -8.2453 | 86.148 | -75 | 14.2004 | 329.6981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/11/23:00
10 | 11 | 1900-01-23 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 284.9583 | -8.2607 | 86.148 | -75 | 14.21 | 344.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/11/24:00
10 | 12 | 1899-12-31 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 285 | -8.2761 | 86.148 | -75 | 14.2195 | -0.29713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/12/1:00
10 | 12 | 1900-01-01 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 285.0417 | -8.2915 | 86.148 | -75 | 14.229 | 14.7052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/12/2:00
10 | 12 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 285.0833 | -8.3069 | 86.148 | -75 | 14.2384 | 29.7076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/12/3:00
10 | 12 | 1900-01-03 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 285.125 | -8.3223 | 86.148 | -75 | 14.2479 | 44.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/12/4:00
10 | 12 | 1900-01-04 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 285.1667 | -8.3377 | 86.148 | -75 | 14.2573 | 59.7123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/12/5:00
10 | 12 | 1900-01-05 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 285.2083 | -8.3531 | 86.148 | -75 | 14.2668 | 74.7147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/12/6:00
10 | 12 | 1900-01-06 | 8.3 | 1 | 2 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 1 | 0 | 0 | 39.791 | 285.25 | -8.3685 | 86.148 | -75 | 14.2762 | 89.717 | -0.17878 | 0.82122 | 0.26031 | 0.26031 | 0 | 0 | 0 | 10/12/7:00
10 | 12 | 1900-01-07 | 8.9 | 46 | 110 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 46 | 0 | 0 | 39.791 | 285.2917 | -8.3839 | 86.148 | -75 | 14.2856 | 104.7194 | -31.5108 | 14.4892 | 4.5928 | 4.5928 | 0 | 0 | 0 | 10/12/8:00
10 | 12 | 1900-01-08 | 10 | 85 | 39 | 50 | 1 | 0 | 50 | 0 | 0 | 85 | 0 | 0 | 39.791 | 285.3333 | -8.3992 | 86.148 | -75 | 14.2949 | 119.7217 | -18.3438 | 66.6562 | 21.1289 | 21.1289 | 0 | 0 | 0 | 10/12/9:00
10 | 12 | 1900-01-09 | 11.7 | 161 | 71 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 161 | 0 | 0 | 39.791 | 285.375 | -8.4146 | 86.148 | -75 | 14.3043 | 134.7241 | -44.6263 | 116.3737 | 36.8884 | 36.8884 | 0 | 0 | 0 | 10/12/10:00
10 | 12 | 1900-01-10 | 13.9 | 183 | 415 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 183 | 0 | 0 | 39.791 | 285.4167 | -8.43 | 86.148 | -75 | 14.3136 | 149.7264 | -311.3542 | -128.3542 | -40.6861 | 0 | -40.6861 | 57.02 | -40.6861 | 10/12/11:00
10 | 12 | 1900-01-11 | 16.7 | 119 | 803 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 119 | 0 | 0 | 39.791 | 285.4583 | -8.4454 | 86.148 | -75 | 14.3229 | 164.7287 | -664.2472 | -545.2472 | -172.8338 | 0 | -172.8338 | 62.06 | -172.8338 | 10/12/12:00
10 | 12 | 1900-01-12 | 18.3 | 183 | 663 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 183 | 0 | 0 | 39.791 | 285.5 | -8.4607 | 86.148 | -75 | 14.3322 | 179.7311 | -566.3186 | -383.3186 | -121.5053 | 0 | -121.5053 | 64.94 | -121.5053 | 10/12/13:00
10 | 12 | 1900-01-13 | 20 | 99 | 808 | 68 | 0 | 1 | 0 | 68 | 0 | 99 | 0 | 0 | 39.791 | 285.5417 | -8.4761 | 86.148 | -75 | 14.3415 | 194.7334 | -670.1026 | -571.1026 | -181.0295 | 0 | -181.0295 | 68 | -181.0295 | 10/12/14:00
10 | 12 | 1900-01-14 | 21.1 | 92 | 783 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 92 | 0 | 0 | 39.791 | 285.5833 | -8.4914 | 86.148 | -75 | 14.3508 | 209.7357 | -590.6899 | -498.6899 | -158.076 | 0 | -158.076 | 69.98 | -158.076 | 10/12/15:00
10 | 12 | 1900-01-15 | 21.7 | 82 | 716 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 82 | 0 | 0 | 39.791 | 285.625 | -8.5068 | 86.148 | -75 | 14.36 | 224.738 | -454.2841 | -372.2841 | -118.0076 | 0 | -118.0076 | 71.06 | -118.0076 | 10/12/16:00
10 | 12 | 1900-01-16 | 20.6 | 63 | 588 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 63 | 0 | 0 | 39.791 | 285.6667 | -8.5221 | 86.148 | -75 | 14.3693 | 239.7403 | -280.9287 | -217.9287 | -69.0796 | 0 | -69.0796 | 69.08 | -69.0796 | 10/12/17:00
10 | 12 | 1900-01-17 | 18.3 | 32 | 345 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 32 | 0 | 0 | 39.791 | 285.7083 | -8.5375 | 86.148 | -75 | 14.3785 | 254.7426 | -101.7662 | -69.7662 | -22.1147 | 0 | -22.1147 | 64.94 | -22.1147 | 10/12/18:00
10 | 12 | 1900-01-18 | 16.7 | 0 | 6 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 285.75 | -8.5528 | 86.148 | -75 | 14.3877 | 269.7449 | -0.59138 | -0.59138 | -0.18746 | 0 | -0.18746 | 62.06 | -0.18746 | 10/12/19:00
10 | 12 | 1900-01-19 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 285.7917 | -8.5682 | 86.148 | -75 | 14.3968 | 284.7472 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/12/20:00
10 | 12 | 1900-01-20 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 285.8333 | -8.5835 | 86.148 | -75 | 14.406 | 299.7495 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/12/21:00
10 | 12 | 1900-01-21 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 285.875 | -8.5988 | 86.148 | -75 | 14.4151 | 314.7518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/12/22:00
10 | 12 | 1900-01-22 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 285.9167 | -8.6142 | 86.148 | -75 | 14.4242 | 329.7541 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/12/23:00
10 | 12 | 1900-01-23 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 285.9583 | -8.6295 | 86.148 | -75 | 14.4333 | 344.7563 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/12/24:00
10 | 13 | 1899-12-31 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 286 | -8.6448 | 86.148 | -75 | 14.4424 | -0.24139 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/13/1:00
10 | 13 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 286.0417 | -8.6601 | 86.148 | -75 | 14.4515 | 14.7609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/13/2:00
10 | 13 | 1900-01-02 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 286.0833 | -8.6754 | 86.148 | -75 | 14.4605 | 29.7631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/13/3:00
10 | 13 | 1900-01-03 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 286.125 | -8.6907 | 86.148 | -75 | 14.4696 | 44.7654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/13/4:00
10 | 13 | 1900-01-04 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 286.1667 | -8.706 | 86.148 | -75 | 14.4786 | 59.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/13/5:00
10 | 13 | 1900-01-05 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 286.2083 | -8.7213 | 86.148 | -75 | 14.4876 | 74.7699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/13/6:00
10 | 13 | 1900-01-06 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 286.25 | -8.7366 | 86.148 | -75 | 14.4966 | 89.7721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/13/7:00
10 | 13 | 1900-01-07 | 10.6 | 51 | 17 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 51 | 0 | 0 | 39.791 | 286.2917 | -8.7519 | 86.148 | -75 | 14.5055 | 104.7744 | -4.9478 | 46.0522 | 14.5978 | 14.5978 | 0 | 0 | 0 | 10/13/8:00
10 | 13 | 1900-01-08 | 11.7 | 127 | 217 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 127 | 0 | 0 | 39.791 | 286.3333 | -8.7672 | 86.148 | -75 | 14.5144 | 119.7766 | -103.0063 | 23.9937 | 7.6056 | 7.6056 | 0 | 0 | 0 | 10/13/9:00
10 | 13 | 1900-01-09 | 13.9 | 181 | 443 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 181 | 0 | 0 | 39.791 | 286.375 | -8.7825 | 86.148 | -75 | 14.5234 | 134.7788 | -280.2411 | -99.2411 | -31.4577 | 0 | -31.4577 | 57.02 | -31.4577 | 10/13/10:00
10 | 13 | 1900-01-10 | 16.7 | 230 | 435 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 230 | 0 | 0 | 39.791 | 286.4167 | -8.7978 | 86.148 | -75 | 14.5323 | 149.7811 | -328.0073 | -98.0073 | -31.0666 | 0 | -31.0666 | 62.06 | -31.0666 | 10/13/11:00
10 | 13 | 1900-01-11 | 19.4 | 297 | 408 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 297 | 0 | 0 | 39.791 | 286.4583 | -8.813 | 86.148 | -75 | 14.5412 | 164.7833 | -338.9435 | -41.9435 | -13.2954 | 0 | -13.2954 | 66.92 | -13.2954 | 10/13/12:00
10 | 13 | 1900-01-12 | 21.7 | 352 | 375 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 352 | 0 | 0 | 39.791 | 286.5 | -8.8283 | 86.148 | -75 | 14.55 | 179.7855 | -321.5615 | 30.4385 | 9.6485 | 0 | 9.6485 | 71.06 | 9.6485 | 10/13/13:00
10 | 13 | 1900-01-13 | 22.2 | 302 | 81 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 302 | 0 | 0 | 39.791 | 286.5417 | -8.8436 | 86.148 | -75 | 14.5589 | 194.7877 | -67.4318 | 234.5682 | 74.354 | 0 | 74.354 | 71.96 | 74.354 | 10/13/14:00
10 | 13 | 1900-01-14 | 22.8 | 212 | 529 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 212 | 0 | 0 | 39.791 | 286.5833 | -8.8588 | 86.148 | -75 | 14.5677 | 209.7899 | -400.6901 | -188.6901 | -59.8115 | 0 | -59.8115 | 73.04 | -59.8115 | 10/13/15:00
10 | 13 | 1900-01-15 | 22.8 | 193 | 313 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 193 | 0 | 0 | 39.791 | 286.625 | -8.8741 | 86.148 | -75 | 14.5765 | 224.7921 | -199.5366 | -6.5366 | -2.072 | 0 | -2.072 | 73.04 | -2.072 | 10/13/16:00
10 | 13 | 1900-01-16 | 21.7 | 129 | 216 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 129 | 0 | 0 | 39.791 | 286.6667 | -8.8894 | 86.148 | -75 | 14.5853 | 239.7943 | -103.8594 | 25.1406 | 7.9691 | 0 | 7.9691 | 71.06 | 7.9691 | 10/13/17:00
10 | 13 | 1900-01-17 | 19.4 | 47 | 20 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 47 | 0 | 0 | 39.791 | 286.7083 | -8.9046 | 86.148 | -75 | 14.5941 | 254.7965 | -5.9628 | 41.0372 | 13.0081 | 0 | 13.0081 | 66.92 | 13.0081 | 10/13/18:00
10 | 13 | 1900-01-18 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 286.75 | -8.9199 | 86.148 | -75 | 14.6028 | 269.7987 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 10/13/19:00
10 | 13 | 1900-01-19 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 286.7917 | -8.9351 | 86.148 | -75 | 14.6116 | 284.8009 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 10/13/20:00
10 | 13 | 1900-01-20 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 286.8333 | -8.9503 | 86.148 | -75 | 14.6203 | 299.8031 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 10/13/21:00
10 | 13 | 1900-01-21 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 286.875 | -8.9656 | 86.148 | -75 | 14.629 | 314.8052 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 10/13/22:00
10 | 13 | 1900-01-22 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 286.9167 | -8.9808 | 86.148 | -75 | 14.6377 | 329.8074 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/13/23:00
10 | 13 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 286.9583 | -8.996 | 86.148 | -75 | 14.6463 | 344.8096 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/13/24:00
10 | 14 | 1899-12-31 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 287 | -9.0113 | 86.148 | -75 | 14.655 | -0.18826 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/14/1:00
10 | 14 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 287.0417 | -9.0265 | 86.148 | -75 | 14.6636 | 14.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/14/2:00
10 | 14 | 1900-01-02 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 287.0833 | -9.0417 | 86.148 | -75 | 14.6722 | 29.8161 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/14/3:00
10 | 14 | 1900-01-03 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 287.125 | -9.0569 | 86.148 | -75 | 14.6808 | 44.8182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/14/4:00
10 | 14 | 1900-01-04 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 287.1667 | -9.0721 | 86.148 | -75 | 14.6894 | 59.8203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/14/5:00
10 | 14 | 1900-01-05 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 287.2083 | -9.0873 | 86.148 | -75 | 14.6979 | 74.8225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/14/6:00
10 | 14 | 1900-01-06 | 11.1 | 2 | 1 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 2 | 0 | 0 | 39.791 | 287.25 | -9.1025 | 86.148 | -75 | 14.7065 | 89.8246 | -0.098925 | 1.9011 | 0.60261 | 0.60261 | 0 | 0 | 0 | 10/14/7:00
10 | 14 | 1900-01-07 | 12.2 | 39 | 57 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 39 | 0 | 0 | 39.791 | 287.2917 | -9.1177 | 86.148 | -75 | 14.715 | 104.8267 | -16.8468 | 22.1532 | 7.0222 | 7.0222 | 0 | 0 | 0 | 10/14/8:00
10 | 14 | 1900-01-08 | 12.8 | 119 | 33 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 119 | 0 | 0 | 39.791 | 287.3333 | -9.1329 | 86.148 | -75 | 14.7235 | 119.8289 | -15.805 | 103.195 | 32.711 | 0 | 32.711 | 55.04 | 32.711 | 10/14/9:00
10 | 14 | 1900-01-09 | 13.9 | 196 | 3 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 196 | 0 | 0 | 39.791 | 287.375 | -9.1481 | 86.148 | -75 | 14.7319 | 134.831 | -1.9098 | 194.0902 | 61.5232 | 0 | 61.5232 | 57.02 | 61.5232 | 10/14/10:00
10 | 14 | 1900-01-10 | 15.6 | 211 | 6 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 211 | 0 | 0 | 39.791 | 287.4167 | -9.1633 | 86.148 | -75 | 14.7404 | 149.8331 | -4.5465 | 206.4535 | 65.4421 | 0 | 65.4421 | 60.08 | 65.4421 | 10/14/11:00
10 | 14 | 1900-01-11 | 17.2 | 246 | 10 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 246 | 0 | 0 | 39.791 | 287.4583 | -9.1785 | 86.148 | -75 | 14.7488 | 164.8352 | -8.3422 | 237.6578 | 75.3334 | 0 | 75.3334 | 62.96 | 75.3334 | 10/14/12:00
10 | 14 | 1900-01-12 | 17.2 | 177 | 9 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 177 | 0 | 0 | 39.791 | 287.5 | -9.1936 | 86.148 | -75 | 14.7573 | 179.8373 | -7.7469 | 169.2531 | 53.6503 | 0 | 53.6503 | 62.96 | 53.6503 | 10/14/13:00
10 | 14 | 1900-01-13 | 16.1 | 182 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 182 | 0 | 0 | 39.791 | 287.5417 | -9.2088 | 86.148 | -75 | 14.7657 | 194.8394 | 0 | 182 | 57.6908 | 0 | 57.6908 | 60.98 | 57.6908 | 10/14/14:00
10 | 14 | 1900-01-14 | 14.4 | 143 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 143 | 0 | 0 | 39.791 | 287.5833 | -9.224 | 86.148 | -75 | 14.774 | 209.8415 | 0 | 143 | 45.3285 | 0 | 45.3285 | 57.92 | 45.3285 | 10/14/15:00
10 | 14 | 1900-01-15 | 13.9 | 142 | 1 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 142 | 0 | 0 | 39.791 | 287.625 | -9.2391 | 86.148 | -75 | 14.7824 | 224.8436 | -0.6405 | 141.3595 | 44.8085 | 0 | 44.8085 | 57.02 | 44.8085 | 10/14/16:00
10 | 14 | 1900-01-16 | 13.9 | 74 | 1 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 74 | 0 | 0 | 39.791 | 287.6667 | -9.2543 | 86.148 | -75 | 14.7907 | 239.8457 | -0.48388 | 73.5161 | 23.3033 | 0 | 23.3033 | 57.02 | 23.3033 | 10/14/17:00
10 | 14 | 1900-01-17 | 13.9 | 25 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 25 | 0 | 0 | 39.791 | 287.7083 | -9.2695 | 86.148 | -75 | 14.7991 | 254.8478 | 0 | 25 | 7.9246 | 0 | 7.9246 | 57.02 | 7.9246 | 10/14/18:00
10 | 14 | 1900-01-18 | 12.8 | 1 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 1 | 0 | 0 | 39.791 | 287.75 | -9.2846 | 86.148 | -75 | 14.8074 | 269.8498 | 0 | 1 | 0.31698 | 0 | 0.31698 | 55.04 | 0.31698 | 10/14/19:00
10 | 14 | 1900-01-19 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 287.7917 | -9.2997 | 86.148 | -75 | 14.8157 | 284.8519 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/14/20:00
10 | 14 | 1900-01-20 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 287.8333 | -9.3149 | 86.148 | -75 | 14.8239 | 299.854 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/14/21:00
10 | 14 | 1900-01-21 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 287.875 | -9.33 | 86.148 | -75 | 14.8322 | 314.856 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/14/22:00
10 | 14 | 1900-01-22 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 287.9167 | -9.3452 | 86.148 | -75 | 14.8404 | 329.8581 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/14/23:00
10 | 14 | 1900-01-23 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 287.9583 | -9.3603 | 86.148 | -75 | 14.8486 | 344.8602 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/14/24:00
10 | 15 | 1899-12-31 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 288 | -9.3754 | 86.148 | -75 | 14.8568 | -0.13779 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/15/1:00
10 | 15 | 1900-01-01 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 288.0417 | -9.3905 | 86.148 | -75 | 14.865 | 14.8643 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/15/2:00
10 | 15 | 1900-01-02 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 288.0833 | -9.4057 | 86.148 | -75 | 14.8732 | 29.8663 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/15/3:00
10 | 15 | 1900-01-03 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 288.125 | -9.4208 | 86.148 | -75 | 14.8813 | 44.8683 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/15/4:00
10 | 15 | 1900-01-04 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 288.1667 | -9.4359 | 86.148 | -75 | 14.8894 | 59.8704 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/15/5:00
10 | 15 | 1900-01-05 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 288.2083 | -9.451 | 86.148 | -75 | 14.8975 | 74.8724 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/15/6:00
10 | 15 | 1900-01-06 | 13.3 | 1 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 1 | 0 | 0 | 39.791 | 288.25 | -9.4661 | 86.148 | -75 | 14.9056 | 89.8744 | 0 | 1 | 0.31698 | 0 | 0.31698 | 55.94 | 0.31698 | 10/15/7:00
10 | 15 | 1900-01-07 | 13.3 | 21 | 1 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 21 | 0 | 0 | 39.791 | 288.2917 | -9.4812 | 86.148 | -75 | 14.9137 | 104.8764 | -0.3 | 20.7 | 6.5615 | 0 | 6.5615 | 55.94 | 6.5615 | 10/15/8:00
10 | 15 | 1900-01-08 | 13.9 | 115 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 115 | 0 | 0 | 39.791 | 288.3333 | -9.4963 | 86.148 | -75 | 14.9217 | 119.8784 | 0 | 115 | 36.453 | 0 | 36.453 | 57.02 | 36.453 | 10/15/9:00
10 | 15 | 1900-01-09 | 14.4 | 196 | 1 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 196 | 0 | 0 | 39.791 | 288.375 | -9.5114 | 86.148 | -75 | 14.9297 | 134.8804 | -0.64049 | 195.3595 | 61.9256 | 0 | 61.9256 | 57.92 | 61.9256 | 10/15/10:00
10 | 15 | 1900-01-10 | 15 | 286 | 1 | 59 | 0 | 1 | 0 | 59 | 0 | 286 | 0 | 0 | 39.791 | 288.4167 | -9.5264 | 86.148 | -75 | 14.9377 | 149.8824 | -0.7614 | 285.2386 | 90.4157 | 0 | 90.4157 | 59 | 90.4157 | 10/15/11:00
10 | 15 | 1900-01-11 | 15 | 307 | 1 | 59 | 0 | 1 | 0 | 59 | 0 | 307 | 0 | 0 | 39.791 | 288.4583 | -9.5415 | 86.148 | -75 | 14.9457 | 164.8844 | -0.83762 | 306.1624 | 97.0481 | 0 | 97.0481 | 59 | 97.0481 | 10/15/12:00
10 | 15 | 1900-01-12 | 15 | 208 | 1 | 59 | 0 | 1 | 0 | 59 | 0 | 208 | 0 | 0 | 39.791 | 288.5 | -9.5566 | 86.148 | -75 | 14.9537 | 179.8864 | -0.86397 | 207.136 | 65.6585 | 0 | 65.6585 | 59 | 65.6585 | 10/15/13:00
10 | 15 | 1900-01-13 | 16.1 | 299 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 299 | 0 | 0 | 39.791 | 288.5417 | -9.5717 | 86.148 | -75 | 14.9616 | 194.8884 | 0 | 299 | 94.7778 | 0 | 94.7778 | 60.98 | 94.7778 | 10/15/14:00
10 | 15 | 1900-01-14 | 17.2 | 266 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 266 | 0 | 0 | 39.791 | 288.5833 | -9.5867 | 86.148 | -75 | 14.9695 | 209.8904 | 0 | 266 | 84.3174 | 0 | 84.3174 | 62.96 | 84.3174 | 10/15/15:00
10 | 15 | 1900-01-15 | 17.8 | 201 | 253 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 201 | 0 | 0 | 39.791 | 288.625 | -9.6018 | 86.148 | -75 | 14.9774 | 224.8924 | -162.7987 | 38.2013 | 12.1091 | 0 | 12.1091 | 64.04 | 12.1091 | 10/15/16:00
10 | 15 | 1900-01-16 | 17.8 | 93 | 3 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 93 | 0 | 0 | 39.791 | 288.6667 | -9.6168 | 86.148 | -75 | 14.9853 | 239.8943 | -1.4608 | 91.5392 | 29.0163 | 0 | 29.0163 | 64.04 | 29.0163 | 10/15/17:00
10 | 15 | 1900-01-17 | 16.7 | 42 | 18 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 42 | 0 | 0 | 39.791 | 288.7083 | -9.6319 | 86.148 | -75 | 14.9932 | 254.8963 | -5.4805 | 36.5195 | 11.576 | 0 | 11.576 | 62.06 | 11.576 | 10/15/18:00
10 | 15 | 1900-01-18 | 16.7 | 1 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 1 | 0 | 0 | 39.791 | 288.75 | -9.6469 | 86.148 | -75 | 15.001 | 269.8983 | 0 | 1 | 0.31698 | 0 | 0.31698 | 62.06 | 0.31698 | 10/15/19:00
10 | 15 | 1900-01-19 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 288.7917 | -9.662 | 86.148 | -75 | 15.0089 | 284.9002 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 10/15/20:00
10 | 15 | 1900-01-20 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 288.8333 | -9.677 | 86.148 | -75 | 15.0167 | 299.9022 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 10/15/21:00
10 | 15 | 1900-01-21 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 288.875 | -9.6921 | 86.148 | -75 | 15.0245 | 314.9041 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 10/15/22:00
10 | 15 | 1900-01-22 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 288.9167 | -9.7071 | 86.148 | -75 | 15.0322 | 329.9061 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 10/15/23:00
10 | 15 | 1900-01-23 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 288.9583 | -9.7221 | 86.148 | -75 | 15.04 | 344.908 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 10/15/24:00
10 | 16 | 1899-12-31 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 289 | -9.7371 | 86.148 | -75 | 15.0477 | -0.090068 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 10/16/1:00
10 | 16 | 1900-01-01 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 289.0417 | -9.7522 | 86.148 | -75 | 15.0554 | 14.9119 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/16/2:00
10 | 16 | 1900-01-02 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 289.0833 | -9.7672 | 86.148 | -75 | 15.0631 | 29.9138 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/16/3:00
10 | 16 | 1900-01-03 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 289.125 | -9.7822 | 86.148 | -75 | 15.0708 | 44.9157 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/16/4:00
10 | 16 | 1900-01-04 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 289.1667 | -9.7972 | 86.148 | -75 | 15.0785 | 59.9176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/16/5:00
10 | 16 | 1900-01-05 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 289.2083 | -9.8122 | 86.148 | -75 | 15.0861 | 74.9195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/16/6:00
10 | 16 | 1900-01-06 | 9.4 | 1 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 1 | 0 | 0 | 39.791 | 289.25 | -9.8272 | 86.148 | -75 | 15.0937 | 89.9214 | -0.10819 | 0.89181 | 0.28269 | 0.28269 | 0 | 0 | 0 | 10/16/7:00
10 | 16 | 1900-01-07 | 9.4 | 28 | 309 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 28 | 0 | 0 | 39.791 | 289.2917 | -9.8422 | 86.148 | -75 | 15.1013 | 104.9233 | -94.0482 | -66.0482 | -20.9361 | -20.9361 | 0 | 0 | 0 | 10/16/8:00
10 | 16 | 1900-01-08 | 11.1 | 46 | 664 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 46 | 0 | 0 | 39.791 | 289.3333 | -9.8572 | 86.148 | -75 | 15.1089 | 119.9252 | -323.5179 | -277.5179 | -87.9683 | -87.9683 | 0 | 0 | 0 | 10/16/9:00
10 | 16 | 1900-01-09 | 12.8 | 62 | 803 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 62 | 0 | 0 | 39.791 | 289.375 | -9.8721 | 86.148 | -75 | 15.1164 | 134.9271 | -517.3963 | -455.3963 | -144.3527 | 0 | -144.3527 | 55.04 | -144.3527 | 10/16/10:00
10 | 16 | 1900-01-10 | 14.4 | 74 | 866 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 74 | 0 | 0 | 39.791 | 289.4167 | -9.8871 | 86.148 | -75 | 15.124 | 149.929 | -662.4713 | -588.4713 | -186.5351 | 0 | -186.5351 | 57.92 | -186.5351 | 10/16/11:00
10 | 16 | 1900-01-11 | 15.6 | 86 | 889 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 86 | 0 | 0 | 39.791 | 289.4583 | -9.9021 | 86.148 | -75 | 15.1315 | 164.9309 | -747.6173 | -661.6173 | -209.7211 | 0 | -209.7211 | 60.08 | -209.7211 | 10/16/12:00
10 | 16 | 1900-01-12 | 16.1 | 107 | 884 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 107 | 0 | 0 | 39.791 | 289.5 | -9.9171 | 86.148 | -75 | 15.139 | 179.9327 | -766.5366 | -659.5366 | -209.0616 | 0 | -209.0616 | 60.98 | -209.0616 | 10/16/13:00
10 | 16 | 1900-01-13 | 20.6 | 156 | 736 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 156 | 0 | 0 | 39.791 | 289.5417 | -9.932 | 86.148 | -75 | 15.1465 | 194.9346 | -619.4815 | -463.4815 | -146.9156 | 0 | -146.9156 | 69.08 | -146.9156 | 10/16/14:00
10 | 16 | 1900-01-14 | 18.9 | 113 | 742 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 113 | 0 | 0 | 39.791 | 289.5833 | -9.947 | 86.148 | -75 | 15.1539 | 209.9365 | -568.6733 | -455.6733 | -144.4405 | 0 | -144.4405 | 66.02 | -144.4405 | 10/16/15:00
10 | 16 | 1900-01-15 | 18.9 | 120 | 639 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 120 | 0 | 0 | 39.791 | 289.625 | -9.9619 | 86.148 | -75 | 15.1614 | 224.9383 | -413.0672 | -293.0672 | -92.8972 | 0 | -92.8972 | 66.02 | -92.8972 | 10/16/16:00
10 | 16 | 1900-01-16 | 18.3 | 70 | 527 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 70 | 0 | 0 | 39.791 | 289.6667 | -9.9769 | 86.148 | -75 | 15.1688 | 239.9402 | -258.2009 | -188.2009 | -59.6564 | 0 | -59.6564 | 64.94 | -59.6564 | 10/16/17:00
10 | 16 | 1900-01-17 | 15.6 | 38 | 142 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 38 | 0 | 0 | 39.791 | 289.7083 | -9.9918 | 86.148 | -75 | 15.1762 | 254.942 | -43.6847 | -5.6847 | -1.8019 | 0 | -1.8019 | 60.08 | -1.8019 | 10/16/18:00
10 | 16 | 1900-01-18 | 14.4 | 1 | 3 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 1 | 0 | 0 | 39.791 | 289.75 | -10.0068 | 86.148 | -75 | 15.1836 | 269.9439 | -0.33585 | 0.66415 | 0.21053 | 0 | 0.21053 | 57.92 | 0.21053 | 10/16/19:00
10 | 16 | 1900-01-19 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 289.7917 | -10.0217 | 86.148 | -75 | 15.1909 | 284.9457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/16/20:00
10 | 16 | 1900-01-20 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 289.8333 | -10.0367 | 86.148 | -75 | 15.1983 | 299.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/16/21:00
10 | 16 | 1900-01-21 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 289.875 | -10.0516 | 86.148 | -75 | 15.2056 | 314.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/16/22:00
10 | 16 | 1900-01-22 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 289.9167 | -10.0665 | 86.148 | -75 | 15.2129 | 329.9512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/16/23:00
10 | 16 | 1900-01-23 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 289.9583 | -10.0814 | 86.148 | -75 | 15.2202 | 344.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/16/24:00
10 | 17 | 1899-12-31 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 290 | -10.0963 | 86.148 | -75 | 15.2274 | -0.045145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/17/1:00
10 | 17 | 1900-01-01 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 290.0417 | -10.1113 | 86.148 | -75 | 15.2347 | 14.9567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/17/2:00
10 | 17 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 290.0833 | -10.1262 | 86.148 | -75 | 15.2419 | 29.9585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/17/3:00
10 | 17 | 1900-01-03 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 290.125 | -10.1411 | 86.148 | -75 | 15.2491 | 44.9603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/17/4:00
10 | 17 | 1900-01-04 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 290.1667 | -10.156 | 86.148 | -75 | 15.2563 | 59.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/17/5:00
10 | 17 | 1900-01-05 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 290.2083 | -10.1708 | 86.148 | -75 | 15.2634 | 74.9639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/17/6:00
10 | 17 | 1900-01-06 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 290.25 | -10.1857 | 86.148 | -75 | 15.2706 | 89.9656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/17/7:00
10 | 17 | 1900-01-07 | 11.1 | 19 | 1 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 19 | 0 | 0 | 39.791 | 290.2917 | -10.2006 | 86.148 | -75 | 15.2777 | 104.9674 | -0.30865 | 18.6913 | 5.9248 | 5.9248 | 0 | 0 | 0 | 10/17/8:00
10 | 17 | 1900-01-08 | 11.7 | 79 | 5 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 79 | 0 | 0 | 39.791 | 290.3333 | -10.2155 | 86.148 | -75 | 15.2848 | 119.9692 | -2.4563 | 76.5437 | 24.263 | 24.263 | 0 | 0 | 0 | 10/17/9:00
10 | 17 | 1900-01-09 | 12.2 | 132 | 9 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 132 | 0 | 0 | 39.791 | 290.375 | -10.2304 | 86.148 | -75 | 15.2919 | 134.971 | -5.8328 | 126.1672 | 39.9928 | 39.9928 | 0 | 0 | 0 | 10/17/10:00
10 | 17 | 1900-01-10 | 13.3 | 229 | 11 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 229 | 0 | 0 | 39.791 | 290.4167 | -10.2452 | 86.148 | -75 | 15.2989 | 149.9727 | -8.4533 | 220.5467 | 69.9095 | 0 | 69.9095 | 55.94 | 69.9095 | 10/17/11:00
10 | 17 | 1900-01-11 | 13.3 | 179 | 8 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 179 | 0 | 0 | 39.791 | 290.4583 | -10.2601 | 86.148 | -75 | 15.306 | 164.9745 | -6.7539 | 172.2461 | 54.599 | 0 | 54.599 | 55.94 | 54.599 | 10/17/12:00
10 | 17 | 1900-01-12 | 15 | 294 | 2 | 59 | 0 | 1 | 0 | 59 | 0 | 294 | 0 | 0 | 39.791 | 290.5 | -10.275 | 86.148 | -75 | 15.313 | 179.9762 | -1.7404 | 292.2596 | 92.6412 | 0 | 92.6412 | 59 | 92.6412 | 10/17/13:00
10 | 17 | 1900-01-13 | 16.7 | 309 | 6 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 309 | 0 | 0 | 39.791 | 290.5417 | -10.2898 | 86.148 | -75 | 15.32 | 194.978 | -5.068 | 303.932 | 96.3411 | 0 | 96.3411 | 62.06 | 96.3411 | 10/17/14:00
10 | 17 | 1900-01-14 | 19.4 | 235 | 1 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 235 | 0 | 0 | 39.791 | 290.5833 | -10.3047 | 86.148 | -75 | 15.327 | 209.9797 | -0.76932 | 234.2307 | 74.247 | 0 | 74.247 | 66.92 | 74.247 | 10/17/15:00
10 | 17 | 1900-01-15 | 20.6 | 188 | 3 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 188 | 0 | 0 | 39.791 | 290.625 | -10.3195 | 86.148 | -75 | 15.3339 | 224.9815 | -1.9481 | 186.0519 | 58.9752 | 0 | 58.9752 | 69.08 | 58.9752 | 10/17/16:00
10 | 17 | 1900-01-16 | 17.2 | 70 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 70 | 0 | 0 | 39.791 | 290.6667 | -10.3344 | 86.148 | -75 | 15.3409 | 239.9832 | 0 | 70 | 22.1888 | 0 | 22.1888 | 62.96 | 22.1888 | 10/17/17:00
10 | 17 | 1900-01-17 | 16.7 | 20 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 20 | 0 | 0 | 39.791 | 290.7083 | -10.3492 | 86.148 | -75 | 15.3478 | 254.9849 | 0 | 20 | 6.3397 | 0 | 6.3397 | 62.06 | 6.3397 | 10/17/18:00
10 | 17 | 1900-01-18 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 290.75 | -10.364 | 86.148 | -75 | 15.3547 | 269.9867 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 10/17/19:00
10 | 17 | 1900-01-19 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 290.7917 | -10.3789 | 86.148 | -75 | 15.3616 | 284.9884 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 10/17/20:00
10 | 17 | 1900-01-20 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 290.8333 | -10.3937 | 86.148 | -75 | 15.3684 | 299.9901 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 10/17/21:00
10 | 17 | 1900-01-21 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 290.875 | -10.4085 | 86.148 | -75 | 15.3753 | 314.9918 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 10/17/22:00
10 | 17 | 1900-01-22 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 290.9167 | -10.4233 | 86.148 | -75 | 15.3821 | 329.9935 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 10/17/23:00
10 | 17 | 1900-01-23 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 290.9583 | -10.4381 | 86.148 | -75 | 15.3889 | 344.9952 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 10/17/24:00
10 | 18 | 1899-12-31 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 291 | -10.4529 | 86.148 | -75 | 15.3957 | -0.0030854 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 10/18/1:00
10 | 18 | 1900-01-01 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 291.0417 | -10.4677 | 86.148 | -75 | 15.4024 | 14.9986 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 10/18/2:00
10 | 18 | 1900-01-02 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 291.0833 | -10.4825 | 86.148 | -75 | 15.4092 | 30.0003 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/18/3:00
10 | 18 | 1900-01-03 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.125 | -10.4973 | 86.148 | -75 | 15.4159 | 45.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/4:00
10 | 18 | 1900-01-04 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.1667 | -10.5121 | 86.148 | -75 | 15.4226 | 60.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/5:00
10 | 18 | 1900-01-05 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.2083 | -10.5269 | 86.148 | -75 | 15.4292 | 75.0053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/6:00
10 | 18 | 1900-01-06 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.25 | -10.5416 | 86.148 | -75 | 15.4359 | 90.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/7:00
10 | 18 | 1900-01-07 | 9.4 | 37 | 18 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 37 | 0 | 0 | 39.791 | 291.2917 | -10.5564 | 86.148 | -75 | 15.4425 | 105.0086 | -5.6316 | 31.3684 | 9.9432 | 9.9432 | 0 | 0 | 0 | 10/18/8:00
10 | 18 | 1900-01-08 | 10.6 | 93 | 7 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 93 | 0 | 0 | 39.791 | 291.3333 | -10.5712 | 86.148 | -75 | 15.4492 | 120.0103 | -3.4664 | 89.5336 | 28.3806 | 28.3806 | 0 | 0 | 0 | 10/18/9:00
10 | 18 | 1900-01-09 | 11.1 | 130 | 2 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 130 | 0 | 0 | 39.791 | 291.375 | -10.5859 | 86.148 | -75 | 15.4557 | 135.0119 | -1.3035 | 128.6965 | 40.7945 | 40.7945 | 0 | 0 | 0 | 10/18/10:00
10 | 18 | 1900-01-10 | 9.4 | 243 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 243 | 0 | 0 | 39.791 | 291.4167 | -10.6007 | 86.148 | -75 | 15.4623 | 150.0136 | -0.77191 | 242.2281 | 76.7821 | 76.7821 | 0 | 0 | 0 | 10/18/11:00
10 | 18 | 1900-01-11 | 11.7 | 237 | 374 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 237 | 0 | 0 | 39.791 | 291.4583 | -10.6154 | 86.148 | -75 | 15.4689 | 165.0152 | -316.9456 | -79.9456 | -25.3413 | -25.3413 | 0 | 0 | 0 | 10/18/12:00
10 | 18 | 1900-01-12 | 9.4 | 290 | 8 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 290 | 0 | 0 | 39.791 | 291.5 | -10.6302 | 86.148 | -75 | 15.4754 | 180.0169 | -6.986 | 283.014 | 89.7105 | 89.7105 | 0 | 0 | 0 | 10/18/13:00
10 | 18 | 1900-01-13 | 10 | 159 | 5 | 50 | 1 | 0 | 50 | 0 | 0 | 159 | 0 | 0 | 39.791 | 291.5417 | -10.6449 | 86.148 | -75 | 15.4819 | 195.0185 | -4.2379 | 154.7621 | 49.0569 | 49.0569 | 0 | 0 | 0 | 10/18/14:00
10 | 18 | 1900-01-14 | 10 | 146 | 167 | 50 | 1 | 0 | 50 | 0 | 0 | 146 | 0 | 0 | 39.791 | 291.5833 | -10.6597 | 86.148 | -75 | 15.4884 | 210.0201 | -128.9584 | 17.0416 | 5.4019 | 5.4019 | 0 | 0 | 0 | 10/18/15:00
10 | 18 | 1900-01-15 | 7.8 | 95 | 17 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 95 | 0 | 0 | 39.791 | 291.625 | -10.6744 | 86.148 | -75 | 15.4949 | 225.0217 | -11.0886 | 83.9114 | 26.5985 | 26.5985 | 0 | 0 | 0 | 10/18/16:00
10 | 18 | 1900-01-16 | 8.3 | 79 | 7 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 79 | 0 | 0 | 39.791 | 291.6667 | -10.6891 | 86.148 | -75 | 15.5013 | 240.0233 | -3.4718 | 75.5282 | 23.9411 | 23.9411 | 0 | 0 | 0 | 10/18/17:00
10 | 18 | 1900-01-17 | 7.2 | 35 | 6 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 35 | 0 | 0 | 39.791 | 291.7083 | -10.7038 | 86.148 | -75 | 15.5078 | 255.0249 | -1.8838 | 33.1162 | 10.4973 | 10.4973 | 0 | 0 | 0 | 10/18/18:00
10 | 18 | 1900-01-18 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.75 | -10.7186 | 86.148 | -75 | 15.5142 | 270.0265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/19:00
10 | 18 | 1900-01-19 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.7917 | -10.7333 | 86.148 | -75 | 15.5206 | 285.0281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/20:00
10 | 18 | 1900-01-20 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.8333 | -10.748 | 86.148 | -75 | 15.5269 | 300.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/21:00
10 | 18 | 1900-01-21 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.875 | -10.7627 | 86.148 | -75 | 15.5333 | 315.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/22:00
10 | 18 | 1900-01-22 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.9167 | -10.7774 | 86.148 | -75 | 15.5396 | 330.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/23:00
10 | 18 | 1900-01-23 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 291.9583 | -10.7921 | 86.148 | -75 | 15.5459 | 345.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/18/24:00
10 | 19 | 1899-12-31 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292 | -10.8068 | 86.148 | -75 | 15.5522 | 0.036054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/1:00
10 | 19 | 1900-01-01 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.0417 | -10.8214 | 86.148 | -75 | 15.5585 | 15.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/2:00
10 | 19 | 1900-01-02 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.0833 | -10.8361 | 86.148 | -75 | 15.5647 | 30.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/3:00
10 | 19 | 1900-01-03 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.125 | -10.8508 | 86.148 | -75 | 15.571 | 45.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/4:00
10 | 19 | 1900-01-04 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.1667 | -10.8655 | 86.148 | -75 | 15.5772 | 60.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/5:00
10 | 19 | 1900-01-05 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.2083 | -10.8801 | 86.148 | -75 | 15.5833 | 75.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/6:00
10 | 19 | 1900-01-06 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.25 | -10.8948 | 86.148 | -75 | 15.5895 | 90.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/7:00
10 | 19 | 1900-01-07 | 1.7 | 25 | 279 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 25 | 0 | 0 | 39.791 | 292.2917 | -10.9094 | 86.148 | -75 | 15.5956 | 105.0469 | -88.4423 | -63.4423 | -20.1101 | -20.1101 | 0 | 0 | 0 | 10/19/8:00
10 | 19 | 1900-01-08 | 3.3 | 49 | 643 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 49 | 0 | 0 | 39.791 | 292.3333 | -10.9241 | 86.148 | -75 | 15.6018 | 120.0484 | -320.8992 | -271.8992 | -86.1873 | -86.1873 | 0 | 0 | 0 | 10/19/9:00
10 | 19 | 1900-01-09 | 5.6 | 66 | 791 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 66 | 0 | 0 | 39.791 | 292.375 | -10.9387 | 86.148 | -75 | 15.6079 | 135.05 | -518.3949 | -452.3949 | -143.4013 | -143.4013 | 0 | 0 | 0 | 10/19/10:00
10 | 19 | 1900-01-10 | 6.7 | 79 | 861 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 79 | 0 | 0 | 39.791 | 292.4167 | -10.9534 | 86.148 | -75 | 15.6139 | 150.0515 | -667.4991 | -588.4991 | -186.5439 | -186.5439 | 0 | 0 | 0 | 10/19/11:00
10 | 19 | 1900-01-11 | 8.3 | 87 | 887 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 87 | 0 | 0 | 39.791 | 292.4583 | -10.968 | 86.148 | -75 | 15.62 | 165.053 | -754.4731 | -667.4731 | -211.5773 | -211.5773 | 0 | 0 | 0 | 10/19/12:00
10 | 19 | 1900-01-12 | 9.4 | 90 | 907 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 90 | 0 | 0 | 39.791 | 292.5 | -10.9826 | 86.148 | -75 | 15.626 | 180.0545 | -794.746 | -704.746 | -223.3922 | -223.3922 | 0 | 0 | 0 | 10/19/13:00
10 | 19 | 1900-01-13 | 10.6 | 87 | 897 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 87 | 0 | 0 | 39.791 | 292.5417 | -10.9973 | 86.148 | -75 | 15.6321 | 195.056 | -762.8688 | -675.8688 | -214.2386 | -214.2386 | 0 | 0 | 0 | 10/19/14:00
10 | 19 | 1900-01-14 | 11.1 | 79 | 861 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 79 | 0 | 0 | 39.791 | 292.5833 | -11.0119 | 86.148 | -75 | 15.6381 | 210.0575 | -667.3222 | -588.3222 | -186.4878 | -186.4878 | 0 | 0 | 0 | 10/19/15:00
10 | 19 | 1900-01-15 | 11.1 | 66 | 792 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 66 | 0 | 0 | 39.791 | 292.625 | -11.0265 | 86.148 | -75 | 15.644 | 225.059 | -518.8833 | -452.8833 | -143.5561 | -143.5561 | 0 | 0 | 0 | 10/19/16:00
10 | 19 | 1900-01-16 | 10.6 | 48 | 652 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 48 | 0 | 0 | 39.791 | 292.6667 | -11.0411 | 86.148 | -75 | 15.65 | 240.0605 | -325.32 | -277.32 | -87.9056 | -87.9056 | 0 | 0 | 0 | 10/19/17:00
10 | 19 | 1900-01-17 | 8.9 | 26 | 292 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 26 | 0 | 0 | 39.791 | 292.7083 | -11.0557 | 86.148 | -75 | 15.6559 | 255.062 | -92.599 | -66.599 | -21.1107 | -21.1107 | 0 | 0 | 0 | 10/19/18:00
10 | 19 | 1900-01-18 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.75 | -11.0703 | 86.148 | -75 | 15.6618 | 270.0635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/19:00
10 | 19 | 1900-01-19 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.7917 | -11.0849 | 86.148 | -75 | 15.6677 | 285.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/20:00
10 | 19 | 1900-01-20 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.8333 | -11.0995 | 86.148 | -75 | 15.6736 | 300.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/21:00
10 | 19 | 1900-01-21 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.875 | -11.1141 | 86.148 | -75 | 15.6794 | 315.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/22:00
10 | 19 | 1900-01-22 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.9167 | -11.1286 | 86.148 | -75 | 15.6853 | 330.0693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/23:00
10 | 19 | 1900-01-23 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 292.9583 | -11.1432 | 86.148 | -75 | 15.6911 | 345.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/19/24:00
10 | 20 | 1899-12-31 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 293 | -11.1578 | 86.148 | -75 | 15.6969 | 0.072218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/20/1:00
10 | 20 | 1900-01-01 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 293.0417 | -11.1723 | 86.148 | -75 | 15.7026 | 15.0737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/20/2:00
10 | 20 | 1900-01-02 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 293.0833 | -11.1869 | 86.148 | -75 | 15.7084 | 30.0751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/20/3:00
10 | 20 | 1900-01-03 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 293.125 | -11.2015 | 86.148 | -75 | 15.7141 | 45.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/20/4:00
10 | 20 | 1900-01-04 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 293.1667 | -11.216 | 86.148 | -75 | 15.7198 | 60.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/20/5:00
10 | 20 | 1900-01-05 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 293.2083 | -11.2306 | 86.148 | -75 | 15.7255 | 75.0794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/20/6:00
10 | 20 | 1900-01-06 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 293.25 | -11.2451 | 86.148 | -75 | 15.7312 | 90.0808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/20/7:00
10 | 20 | 1900-01-07 | 6.1 | 31 | 131 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 31 | 0 | 0 | 39.791 | 293.2917 | -11.2596 | 86.148 | -75 | 15.7368 | 105.0822 | -42.0575 | -11.0575 | -3.505 | -3.505 | 0 | 0 | 0 | 10/20/8:00
10 | 20 | 1900-01-08 | 8.3 | 69 | 485 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 69 | 0 | 0 | 39.791 | 293.3333 | -11.2741 | 86.148 | -75 | 15.7424 | 120.0836 | -243.8824 | -174.8824 | -55.4347 | -55.4347 | 0 | 0 | 0 | 10/20/9:00
10 | 20 | 1900-01-09 | 12.2 | 97 | 657 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 97 | 0 | 0 | 39.791 | 293.375 | -11.2887 | 86.148 | -75 | 15.748 | 135.085 | -432.8889 | -335.8889 | -106.4709 | -106.4709 | 0 | 0 | 0 | 10/20/10:00
10 | 20 | 1900-01-10 | 16.1 | 117 | 742 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 117 | 0 | 0 | 39.791 | 293.4167 | -11.3032 | 86.148 | -75 | 15.7536 | 150.0864 | -577.6757 | -460.6757 | -146.0262 | 0 | -146.0262 | 60.98 | -146.0262 | 10/20/11:00
10 | 20 | 1900-01-11 | 18.3 | 129 | 781 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 129 | 0 | 0 | 39.791 | 293.4583 | -11.3177 | 86.148 | -75 | 15.7591 | 165.0878 | -666.7119 | -537.7119 | -170.4453 | 0 | -170.4453 | 64.94 | -170.4453 | 10/20/12:00
10 | 20 | 1900-01-12 | 20.6 | 133 | 793 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 133 | 0 | 0 | 39.791 | 293.5 | -11.3322 | 86.148 | -75 | 15.7647 | 180.0892 | -697.1732 | -564.1732 | -178.833 | 0 | -178.833 | 69.08 | -178.833 | 10/20/13:00
10 | 20 | 1900-01-13 | 21.1 | 129 | 781 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 129 | 0 | 0 | 39.791 | 293.5417 | -11.3467 | 86.148 | -75 | 15.7702 | 195.0905 | -666.4283 | -537.4283 | -170.3554 | 0 | -170.3554 | 69.98 | -170.3554 | 10/20/14:00
10 | 20 | 1900-01-14 | 21.1 | 117 | 739 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 117 | 0 | 0 | 39.791 | 293.5833 | -11.3612 | 86.148 | -75 | 15.7757 | 210.0919 | -574.8454 | -457.8454 | -145.129 | 0 | -145.129 | 69.98 | -145.129 | 10/20/15:00
10 | 20 | 1900-01-15 | 21.1 | 96 | 653 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 96 | 0 | 0 | 39.791 | 293.625 | -11.3757 | 86.148 | -75 | 15.7811 | 225.0933 | -429.6872 | -333.6872 | -105.773 | 0 | -105.773 | 69.98 | -105.773 | 10/20/16:00
10 | 20 | 1900-01-16 | 20 | 69 | 478 | 68 | 0 | 1 | 0 | 68 | 0 | 69 | 0 | 0 | 39.791 | 293.6667 | -11.3902 | 86.148 | -75 | 15.7866 | 240.0946 | -239.9265 | -170.9265 | -54.1807 | 0 | -54.1807 | 68 | -54.1807 | 10/20/17:00
10 | 20 | 1900-01-17 | 18.3 | 31 | 126 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 31 | 0 | 0 | 39.791 | 293.7083 | -11.4047 | 86.148 | -75 | 15.792 | 255.096 | -40.3548 | -9.3548 | -2.9653 | 0 | -2.9653 | 64.94 | -2.9653 | 10/20/18:00
10 | 20 | 1900-01-18 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 293.75 | -11.4191 | 86.148 | -75 | 15.7974 | 270.0974 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 10/20/19:00
10 | 20 | 1900-01-19 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 293.7917 | -11.4336 | 86.148 | -75 | 15.8028 | 285.0987 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/20/20:00
10 | 20 | 1900-01-20 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 293.8333 | -11.4481 | 86.148 | -75 | 15.8082 | 300.1 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/20/21:00
10 | 20 | 1900-01-21 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 293.875 | -11.4625 | 86.148 | -75 | 15.8135 | 315.1014 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/20/22:00
10 | 20 | 1900-01-22 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 293.9167 | -11.477 | 86.148 | -75 | 15.8188 | 330.1027 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/20/23:00
10 | 20 | 1900-01-23 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 293.9583 | -11.4914 | 86.148 | -75 | 15.8241 | 345.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/20/24:00
10 | 21 | 1899-12-31 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294 | -11.5059 | 86.148 | -75 | 15.8294 | 0.10536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/1:00
10 | 21 | 1900-01-01 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.0417 | -11.5203 | 86.148 | -75 | 15.8347 | 15.1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/2:00
10 | 21 | 1900-01-02 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.0833 | -11.5348 | 86.148 | -75 | 15.8399 | 30.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/3:00
10 | 21 | 1900-01-03 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.125 | -11.5492 | 86.148 | -75 | 15.8451 | 45.1093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/4:00
10 | 21 | 1900-01-04 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.1667 | -11.5636 | 86.148 | -75 | 15.8503 | 60.1106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/5:00
10 | 21 | 1900-01-05 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.2083 | -11.578 | 86.148 | -75 | 15.8555 | 75.1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/6:00
10 | 21 | 1900-01-06 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.25 | -11.5924 | 86.148 | -75 | 15.8606 | 90.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/7:00
10 | 21 | 1900-01-07 | 9.4 | 27 | 19 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 27 | 0 | 0 | 39.791 | 294.2917 | -11.6068 | 86.148 | -75 | 15.8658 | 105.1144 | -6.1754 | 20.8246 | 6.601 | 6.601 | 0 | 0 | 0 | 10/21/8:00
10 | 21 | 1900-01-08 | 12.8 | 93 | 86 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 93 | 0 | 0 | 39.791 | 294.3333 | -11.6212 | 86.148 | -75 | 15.8709 | 120.1157 | -43.5635 | 49.4365 | 15.6705 | 0 | 15.6705 | 55.04 | 15.6705 | 10/21/9:00
10 | 21 | 1900-01-09 | 14.4 | 164 | 286 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 164 | 0 | 0 | 39.791 | 294.375 | -11.6356 | 86.148 | -75 | 15.876 | 135.117 | -189.4256 | -25.4256 | -8.0595 | 0 | -8.0595 | 57.92 | -8.0595 | 10/21/10:00
10 | 21 | 1900-01-10 | 16.7 | 142 | 657 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 142 | 0 | 0 | 39.791 | 294.4167 | -11.65 | 86.148 | -75 | 15.881 | 150.1183 | -513.6044 | -371.6044 | -117.7921 | 0 | -117.7921 | 62.06 | -117.7921 | 10/21/11:00
10 | 21 | 1900-01-11 | 18.9 | 157 | 705 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 157 | 0 | 0 | 39.791 | 294.4583 | -11.6644 | 86.148 | -75 | 15.8861 | 165.1195 | -603.9535 | -446.9535 | -141.6764 | 0 | -141.6764 | 66.02 | -141.6764 | 10/21/12:00
10 | 21 | 1900-01-12 | 20.6 | 193 | 687 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 193 | 0 | 0 | 39.791 | 294.5 | -11.6788 | 86.148 | -75 | 15.8911 | 180.1208 | -605.9511 | -412.9511 | -130.8983 | 0 | -130.8983 | 69.08 | -130.8983 | 10/21/13:00
10 | 21 | 1900-01-13 | 21.7 | 179 | 681 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 179 | 0 | 0 | 39.791 | 294.5417 | -11.6932 | 86.148 | -75 | 15.8961 | 195.122 | -582.997 | -403.997 | -128.06 | 0 | -128.06 | 71.06 | -128.06 | 10/21/14:00
10 | 21 | 1900-01-14 | 22.2 | 141 | 656 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 141 | 0 | 0 | 39.791 | 294.5833 | -11.7075 | 86.148 | -75 | 15.9011 | 210.1233 | -512.1062 | -371.1062 | -117.6342 | 0 | -117.6342 | 71.96 | -117.6342 | 10/21/15:00
10 | 21 | 1900-01-15 | 21.1 | 143 | 106 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 143 | 0 | 0 | 39.791 | 294.625 | -11.7219 | 86.148 | -75 | 15.906 | 225.1245 | -70.0514 | 72.9486 | 23.1234 | 0 | 23.1234 | 69.98 | 23.1234 | 10/21/16:00
10 | 21 | 1900-01-16 | 20.6 | 91 | 212 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 91 | 0 | 0 | 39.791 | 294.6667 | -11.7363 | 86.148 | -75 | 15.911 | 240.1257 | -107.0404 | -16.0404 | -5.0845 | 0 | -5.0845 | 69.08 | -5.0845 | 10/21/17:00
10 | 21 | 1900-01-17 | 17.8 | 34 | 26 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 34 | 0 | 0 | 39.791 | 294.7083 | -11.7506 | 86.148 | -75 | 15.9159 | 255.127 | -8.4092 | 25.5908 | 8.1118 | 0 | 8.1118 | 64.04 | 8.1118 | 10/21/18:00
10 | 21 | 1900-01-18 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 294.75 | -11.765 | 86.148 | -75 | 15.9208 | 270.1282 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/21/19:00
10 | 21 | 1900-01-19 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 294.7917 | -11.7793 | 86.148 | -75 | 15.9256 | 285.1294 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/21/20:00
10 | 21 | 1900-01-20 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.8333 | -11.7936 | 86.148 | -75 | 15.9305 | 300.1306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/21:00
10 | 21 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.875 | -11.808 | 86.148 | -75 | 15.9353 | 315.1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/22:00
10 | 21 | 1900-01-22 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.9167 | -11.8223 | 86.148 | -75 | 15.9401 | 330.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/23:00
10 | 21 | 1900-01-23 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 294.9583 | -11.8366 | 86.148 | -75 | 15.9449 | 345.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/21/24:00
10 | 22 | 1899-12-31 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295 | -11.8509 | 86.148 | -75 | 15.9497 | 0.13542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/1:00
10 | 22 | 1900-01-01 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.0417 | -11.8653 | 86.148 | -75 | 15.9544 | 15.1366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/2:00
10 | 22 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.0833 | -11.8796 | 86.148 | -75 | 15.9591 | 30.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/3:00
10 | 22 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.125 | -11.8939 | 86.148 | -75 | 15.9638 | 45.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/4:00
10 | 22 | 1900-01-04 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.1667 | -11.9082 | 86.148 | -75 | 15.9685 | 60.1401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/5:00
10 | 22 | 1900-01-05 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.2083 | -11.9224 | 86.148 | -75 | 15.9732 | 75.1413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/6:00
10 | 22 | 1900-01-06 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.25 | -11.9367 | 86.148 | -75 | 15.9778 | 90.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/7:00
10 | 22 | 1900-01-07 | 7.2 | 22 | 4 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 22 | 0 | 0 | 39.791 | 295.2917 | -11.951 | 86.148 | -75 | 15.9824 | 105.1436 | -1.3156 | 20.6844 | 6.5566 | 6.5566 | 0 | 0 | 0 | 10/22/8:00
10 | 22 | 1900-01-08 | 7.2 | 48 | 1 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 48 | 0 | 0 | 39.791 | 295.3333 | -11.9653 | 86.148 | -75 | 15.987 | 120.1447 | -0.51017 | 47.4898 | 15.0534 | 15.0534 | 0 | 0 | 0 | 10/22/9:00
10 | 22 | 1900-01-09 | 6.7 | 120 | 10 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 120 | 0 | 0 | 39.791 | 295.375 | -11.9795 | 86.148 | -75 | 15.9916 | 135.1459 | -6.6569 | 113.3431 | 35.9278 | 35.9278 | 0 | 0 | 0 | 10/22/10:00
10 | 22 | 1900-01-10 | 6.7 | 115 | 10 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 115 | 0 | 0 | 39.791 | 295.4167 | -11.9938 | 86.148 | -75 | 15.9961 | 150.147 | -7.8487 | 107.1513 | 33.9651 | 33.9651 | 0 | 0 | 0 | 10/22/11:00
10 | 22 | 1900-01-11 | 7.2 | 143 | 2 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 143 | 0 | 0 | 39.791 | 295.4583 | -12.0081 | 86.148 | -75 | 16.0006 | 165.1482 | -1.7192 | 141.2808 | 44.7835 | 44.7835 | 0 | 0 | 0 | 10/22/12:00
10 | 22 | 1900-01-12 | 7.2 | 181 | 7 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 181 | 0 | 0 | 39.791 | 295.5 | -12.0223 | 86.148 | -75 | 16.0051 | 180.1493 | -6.1938 | 174.8062 | 55.4105 | 55.4105 | 0 | 0 | 0 | 10/22/13:00
10 | 22 | 1900-01-13 | 7.2 | 200 | 2 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 200 | 0 | 0 | 39.791 | 295.5417 | -12.0366 | 86.148 | -75 | 16.0096 | 195.1504 | -1.7177 | 198.2823 | 62.852 | 62.852 | 0 | 0 | 0 | 10/22/14:00
10 | 22 | 1900-01-14 | 7.2 | 174 | 3 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 174 | 0 | 0 | 39.791 | 295.5833 | -12.0508 | 86.148 | -75 | 16.0141 | 210.1515 | -2.3502 | 171.6498 | 54.41 | 54.41 | 0 | 0 | 0 | 10/22/15:00
10 | 22 | 1900-01-15 | 7.2 | 116 | 1 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 116 | 0 | 0 | 39.791 | 295.625 | -12.065 | 86.148 | -75 | 16.0185 | 225.1526 | -0.66368 | 115.3363 | 36.5596 | 36.5596 | 0 | 0 | 0 | 10/22/16:00
10 | 22 | 1900-01-16 | 7.2 | 68 | 1 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 68 | 0 | 0 | 39.791 | 295.6667 | -12.0793 | 86.148 | -75 | 16.0229 | 240.1537 | -0.50787 | 67.4921 | 21.3938 | 21.3938 | 0 | 0 | 0 | 10/22/17:00
10 | 22 | 1900-01-17 | 6.7 | 19 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 19 | 0 | 0 | 39.791 | 295.7083 | -12.0935 | 86.148 | -75 | 16.0273 | 255.1548 | 0 | 19 | 6.0227 | 6.0227 | 0 | 0 | 0 | 10/22/18:00
10 | 22 | 1900-01-18 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.75 | -12.1077 | 86.148 | -75 | 16.0317 | 270.1559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/19:00
10 | 22 | 1900-01-19 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.7917 | -12.1219 | 86.148 | -75 | 16.036 | 285.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/20:00
10 | 22 | 1900-01-20 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.8333 | -12.1361 | 86.148 | -75 | 16.0403 | 300.1581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/21:00
10 | 22 | 1900-01-21 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.875 | -12.1503 | 86.148 | -75 | 16.0447 | 315.1592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/22:00
10 | 22 | 1900-01-22 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.9167 | -12.1645 | 86.148 | -75 | 16.0489 | 330.1602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/23:00
10 | 22 | 1900-01-23 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 295.9583 | -12.1787 | 86.148 | -75 | 16.0532 | 345.1613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/22/24:00
10 | 23 | 1899-12-31 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296 | -12.1929 | 86.148 | -75 | 16.0574 | 0.16236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/1:00
10 | 23 | 1900-01-01 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.0417 | -12.2071 | 86.148 | -75 | 16.0617 | 15.1634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/2:00
10 | 23 | 1900-01-02 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.0833 | -12.2212 | 86.148 | -75 | 16.0658 | 30.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/3:00
10 | 23 | 1900-01-03 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.125 | -12.2354 | 86.148 | -75 | 16.07 | 45.1655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/4:00
10 | 23 | 1900-01-04 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.1667 | -12.2496 | 86.148 | -75 | 16.0742 | 60.1665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/5:00
10 | 23 | 1900-01-05 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.2083 | -12.2637 | 86.148 | -75 | 16.0783 | 75.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/6:00
10 | 23 | 1900-01-06 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.25 | -12.2779 | 86.148 | -75 | 16.0824 | 90.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/7:00
10 | 23 | 1900-01-07 | 0.6 | 27 | 150 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 27 | 0 | 0 | 39.791 | 296.2917 | -12.292 | 86.148 | -75 | 16.0865 | 105.1696 | -49.9064 | -22.9064 | -7.2609 | -7.2609 | 0 | 0 | 0 | 10/23/8:00
10 | 23 | 1900-01-08 | 1.7 | 59 | 528 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 59 | 0 | 0 | 39.791 | 296.3333 | -12.3061 | 86.148 | -75 | 16.0906 | 120.1706 | -271.2352 | -212.2352 | -67.2749 | -67.2749 | 0 | 0 | 0 | 10/23/9:00
10 | 23 | 1900-01-09 | 2.2 | 115 | 589 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 115 | 0 | 0 | 39.791 | 296.375 | -12.3203 | 86.148 | -75 | 16.0946 | 135.1716 | -394.0192 | -279.0192 | -88.4442 | -88.4442 | 0 | 0 | 0 | 10/23/10:00
10 | 23 | 1900-01-10 | 2.8 | 165 | 461 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 165 | 0 | 0 | 39.791 | 296.4167 | -12.3344 | 86.148 | -75 | 16.0986 | 150.1727 | -363.2314 | -198.2314 | -62.8359 | -62.8359 | 0 | 0 | 0 | 10/23/11:00
10 | 23 | 1900-01-11 | 2.8 | 213 | 447 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 213 | 0 | 0 | 39.791 | 296.4583 | -12.3485 | 86.148 | -75 | 16.1026 | 165.1737 | -385.53 | -172.53 | -54.689 | -54.689 | 0 | 0 | 0 | 10/23/12:00
10 | 23 | 1900-01-12 | 2.8 | 332 | 177 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 332 | 0 | 0 | 39.791 | 296.5 | -12.3626 | 86.148 | -75 | 16.1066 | 180.1746 | -157.1024 | 174.8976 | 55.4395 | 55.4395 | 0 | 0 | 0 | 10/23/13:00
10 | 23 | 1900-01-13 | 2.2 | 249 | 3 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 249 | 0 | 0 | 39.791 | 296.5417 | -12.3767 | 86.148 | -75 | 16.1105 | 195.1756 | -2.5846 | 246.4154 | 78.1094 | 78.1094 | 0 | 0 | 0 | 10/23/14:00
10 | 23 | 1900-01-14 | 2.2 | 229 | 14 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 229 | 0 | 0 | 39.791 | 296.5833 | -12.3909 | 86.148 | -75 | 16.1145 | 210.1766 | -11.0055 | 217.9945 | 69.1004 | 69.1004 | 0 | 0 | 0 | 10/23/15:00
10 | 23 | 1900-01-15 | 2.2 | 140 | 14 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 140 | 0 | 0 | 39.791 | 296.625 | -12.405 | 86.148 | -75 | 16.1184 | 225.1776 | -9.3307 | 130.6693 | 41.4199 | 41.4199 | 0 | 0 | 0 | 10/23/16:00
10 | 23 | 1900-01-16 | 1.7 | 66 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 66 | 0 | 0 | 39.791 | 296.6667 | -12.419 | 86.148 | -75 | 16.1223 | 240.1786 | 0 | 66 | 20.9208 | 20.9208 | 0 | 0 | 0 | 10/23/17:00
10 | 23 | 1900-01-17 | 1.1 | 28 | 2 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 28 | 0 | 0 | 39.791 | 296.7083 | -12.4331 | 86.148 | -75 | 16.1261 | 255.1795 | -0.65945 | 27.3405 | 8.6665 | 8.6665 | 0 | 0 | 0 | 10/23/18:00
10 | 23 | 1900-01-18 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.75 | -12.4472 | 86.148 | -75 | 16.13 | 270.1805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/19:00
10 | 23 | 1900-01-19 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.7917 | -12.4613 | 86.148 | -75 | 16.1338 | 285.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/20:00
10 | 23 | 1900-01-20 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.8333 | -12.4754 | 86.148 | -75 | 16.1376 | 300.1824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/21:00
10 | 23 | 1900-01-21 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.875 | -12.4894 | 86.148 | -75 | 16.1414 | 315.1833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/22:00
10 | 23 | 1900-01-22 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.9167 | -12.5035 | 86.148 | -75 | 16.1451 | 330.1843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/23:00
10 | 23 | 1900-01-23 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 296.9583 | -12.5175 | 86.148 | -75 | 16.1488 | 345.1852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/23/24:00
10 | 24 | 1899-12-31 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297 | -12.5316 | 86.148 | -75 | 16.1526 | 0.18614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/1:00
10 | 24 | 1900-01-01 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.0417 | -12.5456 | 86.148 | -75 | 16.1562 | 15.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/2:00
10 | 24 | 1900-01-02 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.0833 | -12.5597 | 86.148 | -75 | 16.1599 | 30.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/3:00
10 | 24 | 1900-01-03 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.125 | -12.5737 | 86.148 | -75 | 16.1635 | 45.1889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/4:00
10 | 24 | 1900-01-04 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.1667 | -12.5877 | 86.148 | -75 | 16.1672 | 60.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/5:00
10 | 24 | 1900-01-05 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.2083 | -12.6017 | 86.148 | -75 | 16.1708 | 75.1907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/6:00
10 | 24 | 1900-01-06 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.25 | -12.6157 | 86.148 | -75 | 16.1743 | 90.1916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/7:00
10 | 24 | 1900-01-07 | -5.6 | 26 | 185 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 26 | 0 | 0 | 39.791 | 297.2917 | -12.6297 | 86.148 | -75 | 16.1779 | 105.1925 | -62.2388 | -36.2388 | -11.4871 | -11.4871 | 0 | 0 | 0 | 10/24/8:00
10 | 24 | 1900-01-08 | -2.8 | 53 | 571 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 53 | 0 | 0 | 39.791 | 297.3333 | -12.6437 | 86.148 | -75 | 16.1814 | 120.1934 | -295.2929 | -242.2929 | -76.8026 | -76.8026 | 0 | 0 | 0 | 10/24/9:00
10 | 24 | 1900-01-09 | 0 | 74 | 737 | 32 | 1 | 0 | 32 | 0 | 0 | 74 | 0 | 0 | 39.791 | 297.375 | -12.6577 | 86.148 | -75 | 16.1849 | 135.1942 | -495.38 | -421.38 | -133.5701 | -133.5701 | 0 | 0 | 0 | 10/24/10:00
10 | 24 | 1900-01-10 | 2.2 | 89 | 824 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 89 | 0 | 0 | 39.791 | 297.4167 | -12.6717 | 86.148 | -75 | 16.1884 | 150.1951 | -651.698 | -562.698 | -178.3654 | -178.3654 | 0 | 0 | 0 | 10/24/11:00
10 | 24 | 1900-01-11 | 3.3 | 99 | 864 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 99 | 0 | 0 | 39.791 | 297.4583 | -12.6857 | 86.148 | -75 | 16.1919 | 165.196 | -747.6081 | -648.6081 | -205.5974 | -205.5974 | 0 | 0 | 0 | 10/24/12:00
10 | 24 | 1900-01-12 | 4.4 | 101 | 871 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 101 | 0 | 0 | 39.791 | 297.5 | -12.6997 | 86.148 | -75 | 16.1953 | 180.1968 | -775.4317 | -674.4317 | -213.7831 | -213.7831 | 0 | 0 | 0 | 10/24/13:00
10 | 24 | 1900-01-13 | 5.6 | 98 | 862 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 98 | 0 | 0 | 39.791 | 297.5417 | -12.7137 | 86.148 | -75 | 16.1987 | 195.1977 | -744.9224 | -646.9224 | -205.0631 | -205.0631 | 0 | 0 | 0 | 10/24/14:00
10 | 24 | 1900-01-14 | 6.7 | 89 | 821 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 89 | 0 | 0 | 39.791 | 297.5833 | -12.7276 | 86.148 | -75 | 16.2021 | 210.1985 | -647.5941 | -558.5941 | -177.0646 | -177.0646 | 0 | 0 | 0 | 10/24/15:00
10 | 24 | 1900-01-15 | 6.7 | 77 | 731 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 77 | 0 | 0 | 39.791 | 297.625 | -12.7416 | 86.148 | -75 | 16.2055 | 225.1994 | -489.2253 | -412.2253 | -130.6682 | -130.6682 | 0 | 0 | 0 | 10/24/16:00
10 | 24 | 1900-01-16 | 6.7 | 53 | 571 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 53 | 0 | 0 | 39.791 | 297.6667 | -12.7555 | 86.148 | -75 | 16.2089 | 240.2002 | -293.3482 | -240.3482 | -76.1862 | -76.1862 | 0 | 0 | 0 | 10/24/17:00
10 | 24 | 1900-01-17 | 4.4 | 25 | 175 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 25 | 0 | 0 | 39.791 | 297.7083 | -12.7695 | 86.148 | -75 | 16.2122 | 255.201 | -58.252 | -33.252 | -10.5403 | -10.5403 | 0 | 0 | 0 | 10/24/18:00
10 | 24 | 1900-01-18 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.75 | -12.7834 | 86.148 | -75 | 16.2155 | 270.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/19:00
10 | 24 | 1900-01-19 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.7917 | -12.7974 | 86.148 | -75 | 16.2188 | 285.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/20:00
10 | 24 | 1900-01-20 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.8333 | -12.8113 | 86.148 | -75 | 16.222 | 300.2035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/21:00
10 | 24 | 1900-01-21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.875 | -12.8252 | 86.148 | -75 | 16.2253 | 315.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/22:00
10 | 24 | 1900-01-22 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.9167 | -12.8391 | 86.148 | -75 | 16.2285 | 330.2051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/23:00
10 | 24 | 1900-01-23 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 297.9583 | -12.853 | 86.148 | -75 | 16.2317 | 345.2059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/24/24:00
10 | 25 | 1899-12-31 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298 | -12.8669 | 86.148 | -75 | 16.2349 | 0.20671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/1:00
10 | 25 | 1900-01-01 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.0417 | -12.8808 | 86.148 | -75 | 16.238 | 15.2075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/2:00
10 | 25 | 1900-01-02 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.0833 | -12.8947 | 86.148 | -75 | 16.2411 | 30.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/3:00
10 | 25 | 1900-01-03 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.125 | -12.9086 | 86.148 | -75 | 16.2442 | 45.2091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/4:00
10 | 25 | 1900-01-04 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.1667 | -12.9225 | 86.148 | -75 | 16.2473 | 60.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/5:00
10 | 25 | 1900-01-05 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.2083 | -12.9364 | 86.148 | -75 | 16.2504 | 75.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/6:00
10 | 25 | 1900-01-06 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.25 | -12.9503 | 86.148 | -75 | 16.2534 | 90.2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/7:00
10 | 25 | 1900-01-07 | -1.7 | 27 | 116 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 27 | 0 | 0 | 39.791 | 298.2917 | -12.9641 | 86.148 | -75 | 16.2564 | 105.2121 | -39.4464 | -12.4464 | -3.9453 | -3.9453 | 0 | 0 | 0 | 10/25/8:00
10 | 25 | 1900-01-08 | 0.6 | 66 | 362 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 66 | 0 | 0 | 39.791 | 298.3333 | -12.978 | 86.148 | -75 | 16.2594 | 120.2129 | -188.4251 | -122.4251 | -38.8066 | -38.8066 | 0 | 0 | 0 | 10/25/9:00
10 | 25 | 1900-01-09 | 4.4 | 86 | 630 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 86 | 0 | 0 | 39.791 | 298.375 | -12.9918 | 86.148 | -75 | 16.2624 | 135.2136 | -425.4193 | -339.4193 | -107.59 | -107.59 | 0 | 0 | 0 | 10/25/10:00
10 | 25 | 1900-01-10 | 7.8 | 119 | 679 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 119 | 0 | 0 | 39.791 | 298.4167 | -13.0057 | 86.148 | -75 | 16.2653 | 150.2143 | -538.9861 | -419.9861 | -133.1282 | -133.1282 | 0 | 0 | 0 | 10/25/11:00
10 | 25 | 1900-01-11 | 11.7 | 167 | 655 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 167 | 0 | 0 | 39.791 | 298.4583 | -13.0195 | 86.148 | -75 | 16.2683 | 165.2151 | -568.5553 | -401.5553 | -127.286 | -127.286 | 0 | 0 | 0 | 10/25/12:00
10 | 25 | 1900-01-12 | 13.3 | 210 | 434 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 210 | 0 | 0 | 39.791 | 298.5 | -13.0334 | 86.148 | -75 | 16.2712 | 180.2158 | -387.5245 | -177.5245 | -56.2722 | 0 | -56.2722 | 55.94 | -56.2722 | 10/25/13:00
10 | 25 | 1900-01-13 | 14.4 | 239 | 452 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 239 | 0 | 0 | 39.791 | 298.5417 | -13.0472 | 86.148 | -75 | 16.274 | 195.2165 | -391.7864 | -152.7864 | -48.4306 | 0 | -48.4306 | 57.92 | -48.4306 | 10/25/14:00
10 | 25 | 1900-01-14 | 14.4 | 271 | 198 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 271 | 0 | 0 | 39.791 | 298.5833 | -13.061 | 86.148 | -75 | 16.2769 | 210.2172 | -156.7035 | 114.2965 | 36.23 | 0 | 36.23 | 57.92 | 36.23 | 10/25/15:00
10 | 25 | 1900-01-15 | 14.4 | 184 | 92 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 184 | 0 | 0 | 39.791 | 298.625 | -13.0748 | 86.148 | -75 | 16.2797 | 225.2179 | -61.8247 | 122.1753 | 38.7274 | 0 | 38.7274 | 57.92 | 38.7274 | 10/25/16:00
10 | 25 | 1900-01-16 | 13.9 | 112 | 190 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 112 | 0 | 0 | 39.791 | 298.6667 | -13.0886 | 86.148 | -75 | 16.2825 | 240.2186 | -98.1665 | 13.8335 | 4.385 | 0 | 4.385 | 57.02 | 4.385 | 10/25/17:00
10 | 25 | 1900-01-17 | 13.3 | 16 | 1 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 16 | 0 | 0 | 39.791 | 298.7083 | -13.1024 | 86.148 | -75 | 16.2853 | 255.2193 | -0.33601 | 15.664 | 4.9652 | 0 | 4.9652 | 55.94 | 4.9652 | 10/25/18:00
10 | 25 | 1900-01-18 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.75 | -13.1162 | 86.148 | -75 | 16.2881 | 270.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/19:00
10 | 25 | 1900-01-19 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.7917 | -13.13 | 86.148 | -75 | 16.2908 | 285.2207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/20:00
10 | 25 | 1900-01-20 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.8333 | -13.1438 | 86.148 | -75 | 16.2936 | 300.2214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/21:00
10 | 25 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.875 | -13.1576 | 86.148 | -75 | 16.2963 | 315.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/22:00
10 | 25 | 1900-01-22 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.9167 | -13.1714 | 86.148 | -75 | 16.2989 | 330.2227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/23:00
10 | 25 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 298.9583 | -13.1851 | 86.148 | -75 | 16.3016 | 345.2234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/25/24:00
10 | 26 | 1899-12-31 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299 | -13.1989 | 86.148 | -75 | 16.3042 | 0.22405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/1:00
10 | 26 | 1900-01-01 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.0417 | -13.2126 | 86.148 | -75 | 16.3068 | 15.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/2:00
10 | 26 | 1900-01-02 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.0833 | -13.2264 | 86.148 | -75 | 16.3094 | 30.2254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/3:00
10 | 26 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.125 | -13.2401 | 86.148 | -75 | 16.312 | 45.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/4:00
10 | 26 | 1900-01-04 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.1667 | -13.2539 | 86.148 | -75 | 16.3145 | 60.2266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/5:00
10 | 26 | 1900-01-05 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.2083 | -13.2676 | 86.148 | -75 | 16.317 | 75.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/6:00
10 | 26 | 1900-01-06 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.25 | -13.2813 | 86.148 | -75 | 16.3195 | 90.2279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/7:00
10 | 26 | 1900-01-07 | 10 | 20 | 2 | 50 | 1 | 0 | 50 | 0 | 0 | 20 | 0 | 0 | 39.791 | 299.2917 | -13.295 | 86.148 | -75 | 16.322 | 105.2285 | -0.68719 | 19.3128 | 6.1218 | 6.1218 | 0 | 0 | 0 | 10/26/8:00
10 | 26 | 1900-01-08 | 10.6 | 90 | 7 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 90 | 0 | 0 | 39.791 | 299.3333 | -13.3087 | 86.148 | -75 | 16.3244 | 120.2291 | -3.6665 | 86.3335 | 27.3662 | 27.3662 | 0 | 0 | 0 | 10/26/9:00
10 | 26 | 1900-01-09 | 11.1 | 171 | 2 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 171 | 0 | 0 | 39.791 | 299.375 | -13.3225 | 86.148 | -75 | 16.3269 | 135.2297 | -1.3566 | 169.6434 | 53.774 | 53.774 | 0 | 0 | 0 | 10/26/10:00
10 | 26 | 1900-01-10 | 11.1 | 131 | 8 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 131 | 0 | 0 | 39.791 | 299.4167 | -13.3362 | 86.148 | -75 | 16.3293 | 150.2303 | -6.3729 | 124.6271 | 39.5046 | 39.5046 | 0 | 0 | 0 | 10/26/11:00
10 | 26 | 1900-01-11 | 11.7 | 244 | 6 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 244 | 0 | 0 | 39.791 | 299.4583 | -13.3498 | 86.148 | -75 | 16.3316 | 165.2309 | -5.2241 | 238.7759 | 75.6878 | 75.6878 | 0 | 0 | 0 | 10/26/12:00
10 | 26 | 1900-01-12 | 12.2 | 255 | 5 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 255 | 0 | 0 | 39.791 | 299.5 | -13.3635 | 86.148 | -75 | 16.334 | 180.2315 | -4.4775 | 250.5225 | 79.4113 | 79.4113 | 0 | 0 | 0 | 10/26/13:00
10 | 26 | 1900-01-13 | 12.8 | 266 | 2 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 266 | 0 | 0 | 39.791 | 299.5417 | -13.3772 | 86.148 | -75 | 16.3363 | 195.2321 | -1.7387 | 264.2613 | 83.7662 | 0 | 83.7662 | 55.04 | 83.7662 | 10/26/14:00
10 | 26 | 1900-01-14 | 12.8 | 229 | 1 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 229 | 0 | 0 | 39.791 | 299.5833 | -13.3909 | 86.148 | -75 | 16.3386 | 210.2327 | -0.79404 | 228.206 | 72.3373 | 0 | 72.3373 | 55.04 | 72.3373 | 10/26/15:00
10 | 26 | 1900-01-15 | 12.8 | 199 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 199 | 0 | 0 | 39.791 | 299.625 | -13.4046 | 86.148 | -75 | 16.3409 | 225.2332 | 0 | 199 | 63.0795 | 0 | 63.0795 | 55.04 | 63.0795 | 10/26/16:00
10 | 26 | 1900-01-16 | 12.2 | 58 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 58 | 0 | 0 | 39.791 | 299.6667 | -13.4182 | 86.148 | -75 | 16.3432 | 240.2338 | 0 | 58 | 18.385 | 18.385 | 0 | 0 | 0 | 10/26/17:00
10 | 26 | 1900-01-17 | 11.7 | 16 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 16 | 0 | 0 | 39.791 | 299.7083 | -13.4319 | 86.148 | -75 | 16.3454 | 255.2344 | 0 | 16 | 5.0717 | 5.0717 | 0 | 0 | 0 | 10/26/18:00
10 | 26 | 1900-01-18 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.75 | -13.4455 | 86.148 | -75 | 16.3477 | 270.2349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/19:00
10 | 26 | 1900-01-19 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.7917 | -13.4592 | 86.148 | -75 | 16.3499 | 285.2355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/20:00
10 | 26 | 1900-01-20 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.8333 | -13.4728 | 86.148 | -75 | 16.352 | 300.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/21:00
10 | 26 | 1900-01-21 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.875 | -13.4864 | 86.148 | -75 | 16.3542 | 315.2365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/22:00
10 | 26 | 1900-01-22 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.9167 | -13.5001 | 86.148 | -75 | 16.3563 | 330.2371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/23:00
10 | 26 | 1900-01-23 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 299.9583 | -13.5137 | 86.148 | -75 | 16.3584 | 345.2376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/26/24:00
10 | 27 | 1899-12-31 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300 | -13.5273 | 86.148 | -75 | 16.3605 | 0.23813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/1:00
10 | 27 | 1900-01-01 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.0417 | -13.5409 | 86.148 | -75 | 16.3626 | 15.2386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/2:00
10 | 27 | 1900-01-02 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.0833 | -13.5545 | 86.148 | -75 | 16.3646 | 30.2392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/3:00
10 | 27 | 1900-01-03 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.125 | -13.5681 | 86.148 | -75 | 16.3666 | 45.2397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/4:00
10 | 27 | 1900-01-04 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.1667 | -13.5817 | 86.148 | -75 | 16.3686 | 60.2402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/5:00
10 | 27 | 1900-01-05 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.2083 | -13.5952 | 86.148 | -75 | 16.3706 | 75.2406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/6:00
10 | 27 | 1900-01-06 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.25 | -13.6088 | 86.148 | -75 | 16.3725 | 90.2411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/7:00
10 | 27 | 1900-01-07 | 10 | 14 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 14 | 0 | 0 | 39.791 | 300.2917 | -13.6224 | 86.148 | -75 | 16.3744 | 105.2416 | 0 | 14 | 4.4378 | 4.4378 | 0 | 0 | 0 | 10/27/8:00
10 | 27 | 1900-01-08 | 10 | 58 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 58 | 0 | 0 | 39.791 | 300.3333 | -13.6359 | 86.148 | -75 | 16.3763 | 120.2421 | 0 | 58 | 18.385 | 18.385 | 0 | 0 | 0 | 10/27/9:00
10 | 27 | 1900-01-09 | 10.6 | 104 | 1 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 104 | 0 | 0 | 39.791 | 300.375 | -13.6495 | 86.148 | -75 | 16.3782 | 135.2426 | -0.68124 | 103.3188 | 32.7502 | 32.7502 | 0 | 0 | 0 | 10/27/10:00
10 | 27 | 1900-01-10 | 10.6 | 145 | 2 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 145 | 0 | 0 | 39.791 | 300.4167 | -13.663 | 86.148 | -75 | 16.3801 | 150.243 | -1.5987 | 143.4013 | 45.4557 | 45.4557 | 0 | 0 | 0 | 10/27/11:00
10 | 27 | 1900-01-11 | 10.6 | 167 | 1 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 167 | 0 | 0 | 39.791 | 300.4583 | -13.6766 | 86.148 | -75 | 16.3819 | 165.2435 | -0.87329 | 166.1267 | 52.6593 | 52.6593 | 0 | 0 | 0 | 10/27/12:00
10 | 27 | 1900-01-12 | 10.6 | 177 | 1 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 177 | 0 | 0 | 39.791 | 300.5 | -13.6901 | 86.148 | -75 | 16.3837 | 180.2439 | -0.89801 | 176.102 | 55.8213 | 55.8213 | 0 | 0 | 0 | 10/27/13:00
10 | 27 | 1900-01-13 | 10.6 | 285 | 1 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 285 | 0 | 0 | 39.791 | 300.5417 | -13.7037 | 86.148 | -75 | 16.3855 | 195.2444 | -0.87186 | 284.1281 | 90.0637 | 90.0637 | 0 | 0 | 0 | 10/27/14:00
10 | 27 | 1900-01-14 | 10.6 | 222 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 222 | 0 | 0 | 39.791 | 300.5833 | -13.7172 | 86.148 | -75 | 16.3873 | 210.2448 | 0 | 222 | 70.3701 | 70.3701 | 0 | 0 | 0 | 10/27/15:00
10 | 27 | 1900-01-15 | 11.1 | 185 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 185 | 0 | 0 | 39.791 | 300.625 | -13.7307 | 86.148 | -75 | 16.389 | 225.2452 | 0 | 185 | 58.6418 | 58.6418 | 0 | 0 | 0 | 10/27/16:00
10 | 27 | 1900-01-16 | 11.1 | 102 | 1 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 102 | 0 | 0 | 39.791 | 300.6667 | -13.7442 | 86.148 | -75 | 16.3907 | 240.2457 | -0.52247 | 101.4775 | 32.1666 | 32.1666 | 0 | 0 | 0 | 10/27/17:00
10 | 27 | 1900-01-17 | 10.6 | 26 | 21 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 26 | 0 | 0 | 39.791 | 300.7083 | -13.7577 | 86.148 | -75 | 16.3924 | 255.2461 | -7.1876 | 18.8124 | 5.9632 | 5.9632 | 0 | 0 | 0 | 10/27/18:00
10 | 27 | 1900-01-18 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.75 | -13.7712 | 86.148 | -75 | 16.3941 | 270.2465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/19:00
10 | 27 | 1900-01-19 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.7917 | -13.7847 | 86.148 | -75 | 16.3957 | 285.2469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/20:00
10 | 27 | 1900-01-20 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.8333 | -13.7982 | 86.148 | -75 | 16.3973 | 300.2473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/21:00
10 | 27 | 1900-01-21 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.875 | -13.8117 | 86.148 | -75 | 16.3989 | 315.2477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/22:00
10 | 27 | 1900-01-22 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.9167 | -13.8251 | 86.148 | -75 | 16.4005 | 330.2481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/23:00
10 | 27 | 1900-01-23 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 300.9583 | -13.8386 | 86.148 | -75 | 16.4021 | 345.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/27/24:00
10 | 28 | 1899-12-31 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301 | -13.852 | 86.148 | -75 | 16.4036 | 0.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/1:00
10 | 28 | 1900-01-01 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.0417 | -13.8655 | 86.148 | -75 | 16.4051 | 15.2493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/2:00
10 | 28 | 1900-01-02 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.0833 | -13.8789 | 86.148 | -75 | 16.4066 | 30.2496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/3:00
10 | 28 | 1900-01-03 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.125 | -13.8924 | 86.148 | -75 | 16.408 | 45.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/4:00
10 | 28 | 1900-01-04 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.1667 | -13.9058 | 86.148 | -75 | 16.4095 | 60.2504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/5:00
10 | 28 | 1900-01-05 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.2083 | -13.9192 | 86.148 | -75 | 16.4109 | 75.2507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/6:00
10 | 28 | 1900-01-06 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.25 | -13.9327 | 86.148 | -75 | 16.4123 | 90.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/7:00
10 | 28 | 1900-01-07 | 0.6 | 19 | 204 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 19 | 0 | 0 | 39.791 | 301.2917 | -13.9461 | 86.148 | -75 | 16.4137 | 105.2514 | -71.484 | -52.484 | -16.6365 | -16.6365 | 0 | 0 | 0 | 10/28/8:00
10 | 28 | 1900-01-08 | 3.9 | 56 | 485 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 56 | 0 | 0 | 39.791 | 301.3333 | -13.9595 | 86.148 | -75 | 16.415 | 120.2518 | -257.0828 | -201.0828 | -63.7397 | -63.7397 | 0 | 0 | 0 | 10/28/9:00
10 | 28 | 1900-01-09 | 7.8 | 87 | 514 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 87 | 0 | 0 | 39.791 | 301.375 | -13.9729 | 86.148 | -75 | 16.4163 | 135.2521 | -351.6277 | -264.6277 | -83.8823 | -83.8823 | 0 | 0 | 0 | 10/28/10:00
10 | 28 | 1900-01-10 | 12.2 | 125 | 681 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 125 | 0 | 0 | 39.791 | 301.4167 | -13.9863 | 86.148 | -75 | 16.4176 | 150.2524 | -546.1803 | -421.1803 | -133.5068 | -133.5068 | 0 | 0 | 0 | 10/28/11:00
10 | 28 | 1900-01-11 | 15 | 158 | 642 | 59 | 0 | 1 | 0 | 59 | 0 | 158 | 0 | 0 | 39.791 | 301.4583 | -13.9996 | 86.148 | -75 | 16.4189 | 165.2527 | -562.2792 | -404.2792 | -128.1494 | 0 | -128.1494 | 59 | -128.1494 | 10/28/12:00
10 | 28 | 1900-01-12 | 17.2 | 144 | 724 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 144 | 0 | 0 | 39.791 | 301.5 | -14.013 | 86.148 | -75 | 16.4202 | 180.253 | -651.9466 | -507.9466 | -161.0102 | 0 | -161.0102 | 62.96 | -161.0102 | 10/28/13:00
10 | 28 | 1900-01-13 | 17.8 | 191 | 572 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 191 | 0 | 0 | 39.791 | 301.5417 | -14.0264 | 86.148 | -75 | 16.4214 | 195.2533 | -500.1144 | -309.1144 | -97.9839 | 0 | -97.9839 | 64.04 | -97.9839 | 10/28/14:00
10 | 28 | 1900-01-14 | 17.8 | 188 | 335 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 188 | 0 | 0 | 39.791 | 301.5833 | -14.0398 | 86.148 | -75 | 16.4226 | 210.2536 | -267.7199 | -79.7199 | -25.2698 | 0 | -25.2698 | 64.04 | -25.2698 | 10/28/15:00
10 | 28 | 1900-01-15 | 17.8 | 131 | 318 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 131 | 0 | 0 | 39.791 | 301.625 | -14.0531 | 86.148 | -75 | 16.4238 | 225.2539 | -216.2814 | -85.2814 | -27.0327 | 0 | -27.0327 | 64.04 | -27.0327 | 10/28/16:00
10 | 28 | 1900-01-16 | 16.1 | 82 | 123 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 82 | 0 | 0 | 39.791 | 301.6667 | -14.0665 | 86.148 | -75 | 16.4249 | 240.2542 | -64.6183 | 17.3817 | 5.5097 | 0 | 5.5097 | 60.98 | 5.5097 | 10/28/17:00
10 | 28 | 1900-01-17 | 14.4 | 32 | 13 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 32 | 0 | 0 | 39.791 | 301.7083 | -14.0798 | 86.148 | -75 | 16.4261 | 255.2545 | -4.4901 | 27.5099 | 8.7202 | 0 | 8.7202 | 57.92 | 8.7202 | 10/28/18:00
10 | 28 | 1900-01-18 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 301.75 | -14.0932 | 86.148 | -75 | 16.4272 | 270.2548 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/28/19:00
10 | 28 | 1900-01-19 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.7917 | -14.1065 | 86.148 | -75 | 16.4283 | 285.2551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/20:00
10 | 28 | 1900-01-20 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.8333 | -14.1198 | 86.148 | -75 | 16.4294 | 300.2553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/21:00
10 | 28 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.875 | -14.1331 | 86.148 | -75 | 16.4304 | 315.2556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/22:00
10 | 28 | 1900-01-22 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.9167 | -14.1465 | 86.148 | -75 | 16.4314 | 330.2559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/23:00
10 | 28 | 1900-01-23 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 301.9583 | -14.1598 | 86.148 | -75 | 16.4324 | 345.2561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/28/24:00
10 | 29 | 1899-12-31 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302 | -14.1731 | 86.148 | -75 | 16.4334 | 0.25635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/1:00
10 | 29 | 1900-01-01 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302.0417 | -14.1864 | 86.148 | -75 | 16.4343 | 15.2566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/2:00
10 | 29 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302.0833 | -14.1996 | 86.148 | -75 | 16.4353 | 30.2568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/3:00
10 | 29 | 1900-01-03 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302.125 | -14.2129 | 86.148 | -75 | 16.4362 | 45.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/4:00
10 | 29 | 1900-01-04 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302.1667 | -14.2262 | 86.148 | -75 | 16.4371 | 60.2573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/5:00
10 | 29 | 1900-01-05 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302.2083 | -14.2395 | 86.148 | -75 | 16.4379 | 75.2575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/6:00
10 | 29 | 1900-01-06 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302.25 | -14.2527 | 86.148 | -75 | 16.4388 | 90.2577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/7:00
10 | 29 | 1900-01-07 | 6.7 | 25 | 103 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 25 | 0 | 0 | 39.791 | 302.2917 | -14.266 | 86.148 | -75 | 16.4396 | 105.2579 | -36.4294 | -11.4294 | -3.6229 | -3.6229 | 0 | 0 | 0 | 10/29/8:00
10 | 29 | 1900-01-08 | 8.3 | 100 | 248 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 100 | 0 | 0 | 39.791 | 302.3333 | -14.2792 | 86.148 | -75 | 16.4404 | 120.2581 | -132.2027 | -32.2027 | -10.2077 | -10.2077 | 0 | 0 | 0 | 10/29/9:00
10 | 29 | 1900-01-09 | 10 | 127 | 544 | 50 | 1 | 0 | 50 | 0 | 0 | 127 | 0 | 0 | 39.791 | 302.375 | -14.2925 | 86.148 | -75 | 16.4411 | 135.2583 | -373.6604 | -246.6604 | -78.187 | -78.187 | 0 | 0 | 0 | 10/29/10:00
10 | 29 | 1900-01-10 | 12.8 | 146 | 609 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 146 | 0 | 0 | 39.791 | 302.4167 | -14.3057 | 86.148 | -75 | 16.4419 | 150.2585 | -490.0116 | -344.0116 | -109.0457 | 0 | -109.0457 | 55.04 | -109.0457 | 10/29/11:00
10 | 29 | 1900-01-11 | 15 | 189 | 550 | 59 | 0 | 1 | 0 | 59 | 0 | 189 | 0 | 0 | 39.791 | 302.4583 | -14.3189 | 86.148 | -75 | 16.4426 | 165.2586 | -483.0589 | -294.0589 | -93.2115 | 0 | -93.2115 | 59 | -93.2115 | 10/29/12:00
10 | 29 | 1900-01-12 | 17.2 | 195 | 458 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 195 | 0 | 0 | 39.791 | 302.5 | -14.3321 | 86.148 | -75 | 16.4433 | 180.2588 | -413.5221 | -218.5221 | -69.2677 | 0 | -69.2677 | 62.96 | -69.2677 | 10/29/13:00
10 | 29 | 1900-01-13 | 17.8 | 176 | 608 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 176 | 0 | 0 | 39.791 | 302.5417 | -14.3454 | 86.148 | -75 | 16.444 | 195.259 | -533.0636 | -357.0636 | -113.1829 | 0 | -113.1829 | 64.04 | -113.1829 | 10/29/14:00
10 | 29 | 1900-01-14 | 18.9 | 163 | 540 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 163 | 0 | 0 | 39.791 | 302.5833 | -14.3586 | 86.148 | -75 | 16.4446 | 210.2592 | -432.904 | -269.904 | -85.5549 | 0 | -85.5549 | 66.02 | -85.5549 | 10/29/15:00
10 | 29 | 1900-01-15 | 19.4 | 80 | 600 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 80 | 0 | 0 | 39.791 | 302.625 | -14.3718 | 86.148 | -75 | 16.4452 | 225.2593 | -409.6754 | -329.6754 | -104.5013 | 0 | -104.5013 | 66.92 | -104.5013 | 10/29/16:00
10 | 29 | 1900-01-16 | 18.3 | 51 | 506 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 51 | 0 | 0 | 39.791 | 302.6667 | -14.385 | 86.148 | -75 | 16.4458 | 240.2595 | -267.2795 | -216.2795 | -68.5568 | 0 | -68.5568 | 64.94 | -68.5568 | 10/29/17:00
10 | 29 | 1900-01-17 | 15.6 | 22 | 118 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 22 | 0 | 0 | 39.791 | 302.7083 | -14.3981 | 86.148 | -75 | 16.4464 | 255.2596 | -41.1237 | -19.1237 | -6.0619 | 0 | -6.0619 | 60.08 | -6.0619 | 10/29/18:00
10 | 29 | 1900-01-18 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 302.75 | -14.4113 | 86.148 | -75 | 16.447 | 270.2597 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 10/29/19:00
10 | 29 | 1900-01-19 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 302.7917 | -14.4245 | 86.148 | -75 | 16.4475 | 285.2599 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/29/20:00
10 | 29 | 1900-01-20 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 302.8333 | -14.4377 | 86.148 | -75 | 16.448 | 300.26 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/29/21:00
10 | 29 | 1900-01-21 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302.875 | -14.4508 | 86.148 | -75 | 16.4485 | 315.2601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/22:00
10 | 29 | 1900-01-22 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302.9167 | -14.464 | 86.148 | -75 | 16.449 | 330.2602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/23:00
10 | 29 | 1900-01-23 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 302.9583 | -14.4771 | 86.148 | -75 | 16.4494 | 345.2603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/29/24:00
10 | 30 | 1899-12-31 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 303 | -14.4903 | 86.148 | -75 | 16.4498 | 0.26045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/30/1:00
10 | 30 | 1900-01-01 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 303.0417 | -14.5034 | 86.148 | -75 | 16.4502 | 15.2606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/30/2:00
10 | 30 | 1900-01-02 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 303.0833 | -14.5165 | 86.148 | -75 | 16.4506 | 30.2606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/30/3:00
10 | 30 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 303.125 | -14.5296 | 86.148 | -75 | 16.4509 | 45.2607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/30/4:00
10 | 30 | 1900-01-04 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 303.1667 | -14.5427 | 86.148 | -75 | 16.4512 | 60.2608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/30/5:00
10 | 30 | 1900-01-05 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 303.2083 | -14.5558 | 86.148 | -75 | 16.4515 | 75.2609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/30/6:00
10 | 30 | 1900-01-06 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 303.25 | -14.5689 | 86.148 | -75 | 16.4518 | 90.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/30/7:00
10 | 30 | 1900-01-07 | 8.3 | 17 | 231 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 17 | 0 | 0 | 39.791 | 303.2917 | -14.582 | 86.148 | -75 | 16.4521 | 105.261 | -82.4356 | -65.4356 | -20.7419 | -20.7419 | 0 | 0 | 0 | 10/30/8:00
10 | 30 | 1900-01-08 | 10 | 48 | 561 | 50 | 1 | 0 | 50 | 0 | 0 | 48 | 0 | 0 | 39.791 | 303.3333 | -14.5951 | 86.148 | -75 | 16.4523 | 120.2611 | -300.6924 | -252.6924 | -80.0991 | -80.0991 | 0 | 0 | 0 | 10/30/9:00
10 | 30 | 1900-01-09 | 13.3 | 46 | 806 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 46 | 0 | 0 | 39.791 | 303.375 | -14.6082 | 86.148 | -75 | 16.4525 | 135.2611 | -555.7904 | -509.7904 | -161.5947 | 0 | -161.5947 | 55.94 | -161.5947 | 10/30/10:00
10 | 30 | 1900-01-10 | 17.2 | 56 | 874 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 56 | 0 | 0 | 39.791 | 303.4167 | -14.6213 | 86.148 | -75 | 16.4527 | 150.2612 | -705.4312 | -649.4312 | -205.8583 | 0 | -205.8583 | 62.96 | -205.8583 | 10/30/11:00
10 | 30 | 1900-01-11 | 20.6 | 67 | 888 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 67 | 0 | 0 | 39.791 | 303.4583 | -14.6343 | 86.148 | -75 | 16.4528 | 165.2612 | -782.049 | -715.049 | -226.6581 | 0 | -226.6581 | 69.08 | -226.6581 | 10/30/12:00
10 | 30 | 1900-01-12 | 21.7 | 92 | 797 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 92 | 0 | 0 | 39.791 | 303.5 | -14.6474 | 86.148 | -75 | 16.453 | 180.2612 | -721.4745 | -629.4745 | -199.5324 | 0 | -199.5324 | 71.06 | -199.5324 | 10/30/13:00
10 | 30 | 1900-01-13 | 23.3 | 128 | 703 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 128 | 0 | 0 | 39.791 | 303.5417 | -14.6604 | 86.148 | -75 | 16.4531 | 195.2613 | -618.0269 | -490.0269 | -155.33 | 0 | -155.33 | 73.94 | -155.33 | 10/30/14:00
10 | 30 | 1900-01-14 | 23.3 | 139 | 631 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 139 | 0 | 0 | 39.791 | 303.5833 | -14.6735 | 86.148 | -75 | 16.4532 | 210.2613 | -507.4192 | -368.4192 | -116.7824 | 0 | -116.7824 | 73.94 | -116.7824 | 10/30/15:00
10 | 30 | 1900-01-15 | 23.3 | 87 | 548 | 73.94 | 0 | 1 | 0 | 73.94 | 0 | 87 | 0 | 0 | 39.791 | 303.625 | -14.6865 | 86.148 | -75 | 16.4532 | 225.2613 | -375.6165 | -288.6165 | -91.4864 | 0 | -91.4864 | 73.94 | -91.4864 | 10/30/16:00
10 | 30 | 1900-01-16 | 21.7 | 61 | 472 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 61 | 0 | 0 | 39.791 | 303.6667 | -14.6995 | 86.148 | -75 | 16.4533 | 240.2613 | -250.6674 | -189.6674 | -60.1213 | 0 | -60.1213 | 71.06 | -60.1213 | 10/30/17:00
10 | 30 | 1900-01-17 | 18.3 | 18 | 194 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 18 | 0 | 0 | 39.791 | 303.7083 | -14.7125 | 86.148 | -75 | 16.4533 | 255.2613 | -68.213 | -50.213 | -15.9167 | 0 | -15.9167 | 64.94 | -15.9167 | 10/30/18:00
10 | 30 | 1900-01-18 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 303.75 | -14.7256 | 86.148 | -75 | 16.4533 | 270.2613 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 10/30/19:00
10 | 30 | 1900-01-19 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 303.7917 | -14.7386 | 86.148 | -75 | 16.4533 | 285.2613 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 10/30/20:00
10 | 30 | 1900-01-20 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 303.8333 | -14.7516 | 86.148 | -75 | 16.4532 | 300.2613 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 10/30/21:00
10 | 30 | 1900-01-21 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 303.875 | -14.7646 | 86.148 | -75 | 16.4531 | 315.2613 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 10/30/22:00
10 | 30 | 1900-01-22 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 303.9167 | -14.7775 | 86.148 | -75 | 16.453 | 330.2613 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 10/30/23:00
10 | 30 | 1900-01-23 | 12.8 | 0 | 0 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 0 | 0 | 0 | 39.791 | 303.9583 | -14.7905 | 86.148 | -75 | 16.4529 | 345.2612 | 0 | 0 | 0 | 0 | 0 | 55.04 | 0 | 10/30/24:00
10 | 31 | 1899-12-31 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 304 | -14.8035 | 86.148 | -75 | 16.4528 | 0.26119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/31/1:00
10 | 31 | 1900-01-01 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 304.0417 | -14.8165 | 86.148 | -75 | 16.4526 | 15.2612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/31/2:00
10 | 31 | 1900-01-02 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 304.0833 | -14.8294 | 86.148 | -75 | 16.4524 | 30.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/31/3:00
10 | 31 | 1900-01-03 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 304.125 | -14.8424 | 86.148 | -75 | 16.4522 | 45.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/31/4:00
10 | 31 | 1900-01-04 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 304.1667 | -14.8553 | 86.148 | -75 | 16.452 | 60.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/31/5:00
10 | 31 | 1900-01-05 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 304.2083 | -14.8683 | 86.148 | -75 | 16.4517 | 75.2609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/31/6:00
10 | 31 | 1900-01-06 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 304.25 | -14.8812 | 86.148 | -75 | 16.4514 | 90.2609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/31/7:00
10 | 31 | 1900-01-07 | 10 | 27 | 8 | 50 | 1 | 0 | 50 | 0 | 0 | 27 | 0 | 0 | 39.791 | 304.2917 | -14.8941 | 86.148 | -75 | 16.4511 | 105.2608 | -2.8796 | 24.1204 | 7.6457 | 7.6457 | 0 | 0 | 0 | 10/31/8:00
10 | 31 | 1900-01-08 | 11.1 | 102 | 42 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 102 | 0 | 0 | 39.791 | 304.3333 | -14.907 | 86.148 | -75 | 16.4508 | 120.2607 | -22.6305 | 79.3695 | 25.1587 | 25.1587 | 0 | 0 | 0 | 10/31/9:00
10 | 31 | 1900-01-09 | 13.3 | 83 | 608 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 83 | 0 | 0 | 39.791 | 304.375 | -14.9199 | 86.148 | -75 | 16.4504 | 135.2606 | -420.8405 | -337.8405 | -107.0895 | 0 | -107.0895 | 55.94 | -107.0895 | 10/31/10:00
10 | 31 | 1900-01-10 | 16.1 | 115 | 677 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 115 | 0 | 0 | 39.791 | 304.4167 | -14.9328 | 86.148 | -75 | 16.45 | 150.2605 | -548.0755 | -433.0755 | -137.2774 | 0 | -137.2774 | 60.98 | -137.2774 | 10/31/11:00
10 | 31 | 1900-01-11 | 18.9 | 277 | 332 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 277 | 0 | 0 | 39.791 | 304.4583 | -14.9457 | 86.148 | -75 | 16.4496 | 165.2604 | -293.1611 | -16.1611 | -5.1228 | 0 | -5.1228 | 66.02 | -5.1228 | 10/31/12:00
10 | 31 | 1900-01-12 | 21.1 | 288 | 54 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 288 | 0 | 0 | 39.791 | 304.5 | -14.9586 | 86.148 | -75 | 16.4492 | 180.2603 | -49.0068 | 238.9932 | 75.7567 | 0 | 75.7567 | 69.98 | 75.7567 | 10/31/13:00
10 | 31 | 1900-01-13 | 22.2 | 317 | 194 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 317 | 0 | 0 | 39.791 | 304.5417 | -14.9715 | 86.148 | -75 | 16.4487 | 195.2602 | -171.0035 | 145.9965 | 46.2783 | 0 | 46.2783 | 71.96 | 46.2783 | 10/31/14:00
10 | 31 | 1900-01-14 | 22.8 | 222 | 155 | 73.04 | 0 | 1 | 0 | 73.04 | 0 | 222 | 0 | 0 | 39.791 | 304.5833 | -14.9844 | 86.148 | -75 | 16.4483 | 210.2601 | -125.0221 | 96.9779 | 30.7403 | 0 | 30.7403 | 73.04 | 30.7403 | 10/31/15:00
10 | 31 | 1900-01-15 | 22.2 | 150 | 205 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 150 | 0 | 0 | 39.791 | 304.625 | -14.9972 | 86.148 | -75 | 16.4478 | 225.2599 | -141.0498 | 8.9502 | 2.8371 | 0 | 2.8371 | 71.96 | 2.8371 | 10/31/16:00
10 | 31 | 1900-01-16 | 21.1 | 100 | 51 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 100 | 0 | 0 | 39.791 | 304.6667 | -15.0101 | 86.148 | -75 | 16.4473 | 240.2598 | -27.2297 | 72.7703 | 23.0669 | 0 | 23.0669 | 69.98 | 23.0669 | 10/31/17:00
10 | 31 | 1900-01-17 | 19.4 | 23 | 11 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 23 | 0 | 0 | 39.791 | 304.7083 | -15.0229 | 86.148 | -75 | 16.4467 | 255.2597 | -3.9018 | 19.0982 | 6.0538 | 0 | 6.0538 | 66.92 | 6.0538 | 10/31/18:00
10 | 31 | 1900-01-18 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 304.75 | -15.0358 | 86.148 | -75 | 16.4461 | 270.2595 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 10/31/19:00
10 | 31 | 1900-01-19 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 304.7917 | -15.0486 | 86.148 | -75 | 16.4455 | 285.2594 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 10/31/20:00
10 | 31 | 1900-01-20 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 304.8333 | -15.0615 | 86.148 | -75 | 16.4449 | 300.2592 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 10/31/21:00
10 | 31 | 1900-01-21 | 15.3 | 0 | 0 | 59.54 | 0 | 1 | 0 | 59.54 | 0 | 0 | 0 | 0 | 39.791 | 304.875 | -15.0743 | 86.148 | -75 | 16.4443 | 315.2591 | 0 | 0 | 0 | 0 | 0 | 59.54 | 0 | 10/31/22:00
10 | 31 | 1900-01-22 | 12.7 | 0 | 0 | 54.86 | 1 | 0 | 54.86 | 0 | 0 | 0 | 0 | 0 | 39.791 | 304.9167 | -15.0871 | 86.148 | -75 | 16.4436 | 330.2589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/31/23:00
10 | 31 | 1900-01-23 | 10.2 | 0 | 0 | 50.36 | 1 | 0 | 50.36 | 0 | 0 | 0 | 0 | 0 | 39.791 | 304.9583 | -15.0999 | 86.148 | -75 | 16.4429 | 345.2587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10/31/24:00
11 | 1 | 1899-12-31 | 7.6 | 0 | 0 | 45.68 | 1 | 0 | 45.68 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305 | -15.1127 | 86.148 | -75 | 16.4422 | 0.25856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/1:00
11 | 1 | 1900-01-01 | 5.1 | 0 | 0 | 41.18 | 1 | 0 | 41.18 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.0417 | -15.1255 | 86.148 | -75 | 16.4415 | 15.2584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/2:00
11 | 1 | 1900-01-02 | 2.5 | 0 | 0 | 36.5 | 1 | 0 | 36.5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.0833 | -15.1383 | 86.148 | -75 | 16.4407 | 30.2582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/3:00
11 | 1 | 1900-01-03 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.125 | -15.1511 | 86.148 | -75 | 16.44 | 45.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/4:00
11 | 1 | 1900-01-04 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.1667 | -15.1638 | 86.148 | -75 | 16.4392 | 60.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/5:00
11 | 1 | 1900-01-05 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.2083 | -15.1766 | 86.148 | -75 | 16.4383 | 75.2576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/6:00
11 | 1 | 1900-01-06 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.25 | -15.1894 | 86.148 | -75 | 16.4375 | 90.2574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/7:00
11 | 1 | 1900-01-07 | -0.6 | 16 | 242 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 16 | 0 | 0 | 39.791 | 305.2917 | -15.2021 | 86.148 | -75 | 16.4366 | 105.2572 | -87.8331 | -71.8331 | -22.7698 | -22.7698 | 0 | 0 | 0 | 11/1/8:00
11 | 1 | 1900-01-08 | 2.2 | 35 | 650 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 35 | 0 | 0 | 39.791 | 305.3333 | -15.2149 | 86.148 | -75 | 16.4357 | 120.2569 | -352.0137 | -317.0137 | -100.4878 | -100.4878 | 0 | 0 | 0 | 11/1/9:00
11 | 1 | 1900-01-09 | 6.1 | 50 | 798 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 50 | 0 | 0 | 39.791 | 305.375 | -15.2276 | 86.148 | -75 | 16.4348 | 135.2567 | -554.3646 | -504.3646 | -159.8748 | -159.8748 | 0 | 0 | 0 | 11/1/10:00
11 | 1 | 1900-01-10 | 8.9 | 78 | 704 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 78 | 0 | 0 | 39.791 | 305.4167 | -15.2403 | 86.148 | -75 | 16.4338 | 150.2565 | -571.594 | -493.594 | -156.4607 | -156.4607 | 0 | 0 | 0 | 11/1/11:00
11 | 1 | 1900-01-11 | 10.6 | 77 | 812 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 77 | 0 | 0 | 39.791 | 305.4583 | -15.253 | 86.148 | -75 | 16.4329 | 165.2562 | -718.8453 | -641.8453 | -203.4537 | -203.4537 | 0 | 0 | 0 | 11/1/12:00
11 | 1 | 1900-01-12 | 11.7 | 149 | 698 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 149 | 0 | 0 | 39.791 | 305.5 | -15.2658 | 86.148 | -75 | 16.4319 | 180.256 | -635.0202 | -486.0202 | -154.0599 | -154.0599 | 0 | 0 | 0 | 11/1/13:00
11 | 1 | 1900-01-13 | 11.1 | 239 | 272 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 239 | 0 | 0 | 39.791 | 305.5417 | -15.2785 | 86.148 | -75 | 16.4309 | 195.2557 | -240.3801 | -1.3801 | -0.43748 | -0.43748 | 0 | 0 | 0 | 11/1/14:00
11 | 1 | 1900-01-14 | 11.1 | 215 | 367 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 215 | 0 | 0 | 39.791 | 305.5833 | -15.2912 | 86.148 | -75 | 16.4298 | 210.2555 | -296.9046 | -81.9046 | -25.9623 | -25.9623 | 0 | 0 | 0 | 11/1/15:00
11 | 1 | 1900-01-15 | 11.1 | 145 | 329 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 145 | 0 | 0 | 39.791 | 305.625 | -15.3039 | 86.148 | -75 | 16.4288 | 225.2552 | -227.2209 | -82.2209 | -26.0626 | -26.0626 | 0 | 0 | 0 | 11/1/16:00
11 | 1 | 1900-01-16 | 10 | 84 | 58 | 50 | 1 | 0 | 50 | 0 | 0 | 84 | 0 | 0 | 39.791 | 305.6667 | -15.3165 | 86.148 | -75 | 16.4277 | 240.2549 | -31.131 | 52.869 | 16.7586 | 16.7586 | 0 | 0 | 0 | 11/1/17:00
11 | 1 | 1900-01-17 | 7.8 | 30 | 47 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 30 | 0 | 0 | 39.791 | 305.7083 | -15.3292 | 86.148 | -75 | 16.4266 | 255.2546 | -16.8168 | 13.1832 | 4.1788 | 4.1788 | 0 | 0 | 0 | 11/1/18:00
11 | 1 | 1900-01-18 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.75 | -15.3419 | 86.148 | -75 | 16.4254 | 270.2544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/19:00
11 | 1 | 1900-01-19 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.7917 | -15.3546 | 86.148 | -75 | 16.4243 | 285.2541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/20:00
11 | 1 | 1900-01-20 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.8333 | -15.3672 | 86.148 | -75 | 16.4231 | 300.2538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/21:00
11 | 1 | 1900-01-21 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.875 | -15.3799 | 86.148 | -75 | 16.4219 | 315.2535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/22:00
11 | 1 | 1900-01-22 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.9167 | -15.3925 | 86.148 | -75 | 16.4207 | 330.2532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/23:00
11 | 1 | 1900-01-23 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 305.9583 | -15.4051 | 86.148 | -75 | 16.4194 | 345.2529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/1/24:00
11 | 2 | 1899-12-31 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306 | -15.4178 | 86.148 | -75 | 16.4181 | 0.25253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/1:00
11 | 2 | 1900-01-01 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.0417 | -15.4304 | 86.148 | -75 | 16.4168 | 15.2522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/2:00
11 | 2 | 1900-01-02 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.0833 | -15.443 | 86.148 | -75 | 16.4155 | 30.2519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/3:00
11 | 2 | 1900-01-03 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.125 | -15.4556 | 86.148 | -75 | 16.4142 | 45.2515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/4:00
11 | 2 | 1900-01-04 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.1667 | -15.4682 | 86.148 | -75 | 16.4128 | 60.2512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/5:00
11 | 2 | 1900-01-05 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.2083 | -15.4808 | 86.148 | -75 | 16.4114 | 75.2508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/6:00
11 | 2 | 1900-01-06 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.25 | -15.4934 | 86.148 | -75 | 16.41 | 90.2505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/7:00
11 | 2 | 1900-01-07 | 5 | 33 | 16 | 41 | 1 | 0 | 41 | 0 | 0 | 33 | 0 | 0 | 39.791 | 306.2917 | -15.506 | 86.148 | -75 | 16.4085 | 105.2501 | -5.8536 | 27.1464 | 8.6049 | 8.6049 | 0 | 0 | 0 | 11/2/8:00
11 | 2 | 1900-01-08 | 6.1 | 50 | 10 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 50 | 0 | 0 | 39.791 | 306.3333 | -15.5185 | 86.148 | -75 | 16.4071 | 120.2498 | -5.4421 | 44.5579 | 14.1241 | 14.1241 | 0 | 0 | 0 | 11/2/9:00
11 | 2 | 1900-01-09 | 6.7 | 132 | 42 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 132 | 0 | 0 | 39.791 | 306.375 | -15.5311 | 86.148 | -75 | 16.4056 | 135.2494 | -29.2794 | 102.7206 | 32.5606 | 32.5606 | 0 | 0 | 0 | 11/2/10:00
11 | 2 | 1900-01-10 | 6.7 | 186 | 3 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 186 | 0 | 0 | 39.791 | 306.4167 | -15.5436 | 86.148 | -75 | 16.4041 | 150.249 | -2.4426 | 183.5574 | 58.1845 | 58.1845 | 0 | 0 | 0 | 11/2/11:00
11 | 2 | 1900-01-11 | 6.1 | 225 | 3 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 225 | 0 | 0 | 39.791 | 306.4583 | -15.5562 | 86.148 | -75 | 16.4025 | 165.2486 | -2.6624 | 222.3376 | 70.4771 | 70.4771 | 0 | 0 | 0 | 11/2/12:00
11 | 2 | 1900-01-12 | 5 | 264 | 3 | 41 | 1 | 0 | 41 | 0 | 0 | 264 | 0 | 0 | 39.791 | 306.5 | -15.5687 | 86.148 | -75 | 16.401 | 180.2482 | -2.7359 | 261.2641 | 82.8162 | 82.8162 | 0 | 0 | 0 | 11/2/13:00
11 | 2 | 1900-01-13 | 4.4 | 251 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 251 | 0 | 0 | 39.791 | 306.5417 | -15.5812 | 86.148 | -75 | 16.3994 | 195.2479 | -0.886 | 250.114 | 79.2818 | 79.2818 | 0 | 0 | 0 | 11/2/14:00
11 | 2 | 1900-01-14 | 5 | 240 | 3 | 41 | 1 | 0 | 41 | 0 | 0 | 240 | 0 | 0 | 39.791 | 306.5833 | -15.5938 | 86.148 | -75 | 16.3978 | 210.2474 | -2.4341 | 237.5659 | 75.3042 | 75.3042 | 0 | 0 | 0 | 11/2/15:00
11 | 2 | 1900-01-15 | 6.1 | 154 | 1 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 154 | 0 | 0 | 39.791 | 306.625 | -15.6063 | 86.148 | -75 | 16.3962 | 225.247 | -0.69321 | 153.3068 | 48.5956 | 48.5956 | 0 | 0 | 0 | 11/2/16:00
11 | 2 | 1900-01-16 | 5.6 | 86 | 2 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 86 | 0 | 0 | 39.791 | 306.6667 | -15.6188 | 86.148 | -75 | 16.3945 | 240.2466 | -1.0791 | 84.9209 | 26.9184 | 26.9184 | 0 | 0 | 0 | 11/2/17:00
11 | 2 | 1900-01-17 | 4.4 | 21 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 21 | 0 | 0 | 39.791 | 306.7083 | -15.6313 | 86.148 | -75 | 16.3928 | 255.2462 | 0 | 21 | 6.6566 | 6.6566 | 0 | 0 | 0 | 11/2/18:00
11 | 2 | 1900-01-18 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.75 | -15.6438 | 86.148 | -75 | 16.3911 | 270.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/19:00
11 | 2 | 1900-01-19 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.7917 | -15.6563 | 86.148 | -75 | 16.3894 | 285.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/20:00
11 | 2 | 1900-01-20 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.8333 | -15.6688 | 86.148 | -75 | 16.3877 | 300.2449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/21:00
11 | 2 | 1900-01-21 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.875 | -15.6812 | 86.148 | -75 | 16.3859 | 315.2445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/22:00
11 | 2 | 1900-01-22 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.9167 | -15.6937 | 86.148 | -75 | 16.3841 | 330.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/23:00
11 | 2 | 1900-01-23 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 306.9583 | -15.7061 | 86.148 | -75 | 16.3823 | 345.2436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/2/24:00
11 | 3 | 1899-12-31 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307 | -15.7186 | 86.148 | -75 | 16.3804 | 0.24311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/1:00
11 | 3 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.0417 | -15.731 | 86.148 | -75 | 16.3786 | 15.2426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/2:00
11 | 3 | 1900-01-02 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.0833 | -15.7435 | 86.148 | -75 | 16.3767 | 30.2422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/3:00
11 | 3 | 1900-01-03 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.125 | -15.7559 | 86.148 | -75 | 16.3748 | 45.2417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/4:00
11 | 3 | 1900-01-04 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.1667 | -15.7683 | 86.148 | -75 | 16.3728 | 60.2412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/5:00
11 | 3 | 1900-01-05 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.2083 | -15.7807 | 86.148 | -75 | 16.3709 | 75.2407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/6:00
11 | 3 | 1900-01-06 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.25 | -15.7931 | 86.148 | -75 | 16.3689 | 90.2402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/7:00
11 | 3 | 1900-01-07 | -3.3 | 19 | 151 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 19 | 0 | 0 | 39.791 | 307.2917 | -15.8055 | 86.148 | -75 | 16.3669 | 105.2397 | -55.667 | -36.667 | -11.6228 | -11.6228 | 0 | 0 | 0 | 11/3/8:00
11 | 3 | 1900-01-08 | 0 | 41 | 545 | 32 | 1 | 0 | 32 | 0 | 0 | 41 | 0 | 0 | 39.791 | 307.3333 | -15.8179 | 86.148 | -75 | 16.3649 | 120.2392 | -297.9855 | -256.9855 | -81.4599 | -81.4599 | 0 | 0 | 0 | 11/3/9:00
11 | 3 | 1900-01-09 | 2.8 | 75 | 706 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 75 | 0 | 0 | 39.791 | 307.375 | -15.8303 | 86.148 | -75 | 16.3628 | 135.2387 | -493.8317 | -418.8317 | -132.7623 | -132.7623 | 0 | 0 | 0 | 11/3/10:00
11 | 3 | 1900-01-10 | 3.9 | 119 | 557 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 119 | 0 | 0 | 39.791 | 307.4167 | -15.8427 | 86.148 | -75 | 16.3607 | 150.2382 | -454.7399 | -335.7399 | -106.4237 | -106.4237 | 0 | 0 | 0 | 11/3/11:00
11 | 3 | 1900-01-11 | 4.4 | 167 | 641 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 167 | 0 | 0 | 39.791 | 307.4583 | -15.855 | 86.148 | -75 | 16.3586 | 165.2377 | -570.2341 | -403.2341 | -127.8182 | -127.8182 | 0 | 0 | 0 | 11/3/12:00
11 | 3 | 1900-01-12 | 5.6 | 183 | 530 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 183 | 0 | 0 | 39.791 | 307.5 | -15.8674 | 86.148 | -75 | 16.3565 | 180.2371 | -484.4627 | -301.4627 | -95.5584 | -95.5584 | 0 | 0 | 0 | 11/3/13:00
11 | 3 | 1900-01-13 | 6.1 | 165 | 622 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 165 | 0 | 0 | 39.791 | 307.5417 | -15.8797 | 86.148 | -75 | 16.3543 | 195.2366 | -552.4576 | -387.4576 | -122.8173 | -122.8173 | 0 | 0 | 0 | 11/3/14:00
11 | 3 | 1900-01-14 | 6.7 | 179 | 414 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 179 | 0 | 0 | 39.791 | 307.5833 | -15.8921 | 86.148 | -75 | 16.3522 | 210.236 | -336.882 | -157.882 | -50.0458 | -50.0458 | 0 | 0 | 0 | 11/3/15:00
11 | 3 | 1900-01-15 | 5.6 | 142 | 194 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 142 | 0 | 0 | 39.791 | 307.625 | -15.9044 | 86.148 | -75 | 16.35 | 225.2355 | -134.9769 | 7.0231 | 2.2262 | 2.2262 | 0 | 0 | 0 | 11/3/16:00
11 | 3 | 1900-01-16 | 5.6 | 78 | 351 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 78 | 0 | 0 | 39.791 | 307.6667 | -15.9167 | 86.148 | -75 | 16.3478 | 240.2349 | -190.3635 | -112.3635 | -35.6173 | -35.6173 | 0 | 0 | 0 | 11/3/17:00
11 | 3 | 1900-01-17 | 2.8 | 20 | 86 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 20 | 0 | 0 | 39.791 | 307.7083 | -15.9291 | 86.148 | -75 | 16.3455 | 255.2344 | -31.3004 | -11.3004 | -3.582 | -3.582 | 0 | 0 | 0 | 11/3/18:00
11 | 3 | 1900-01-18 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.75 | -15.9414 | 86.148 | -75 | 16.3432 | 270.2338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/19:00
11 | 3 | 1900-01-19 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.7917 | -15.9537 | 86.148 | -75 | 16.341 | 285.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/20:00
11 | 3 | 1900-01-20 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.8333 | -15.966 | 86.148 | -75 | 16.3386 | 300.2327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/21:00
11 | 3 | 1900-01-21 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.875 | -15.9783 | 86.148 | -75 | 16.3363 | 315.2321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/22:00
11 | 3 | 1900-01-22 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.9167 | -15.9905 | 86.148 | -75 | 16.3339 | 330.2315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/23:00
11 | 3 | 1900-01-23 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 307.9583 | -16.0028 | 86.148 | -75 | 16.3316 | 345.2309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/3/24:00
11 | 4 | 1899-12-31 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308 | -16.0151 | 86.148 | -75 | 16.3291 | 0.23029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/1:00
11 | 4 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.0417 | -16.0273 | 86.148 | -75 | 16.3267 | 15.2297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/2:00
11 | 4 | 1900-01-02 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.0833 | -16.0396 | 86.148 | -75 | 16.3243 | 30.2291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/3:00
11 | 4 | 1900-01-03 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.125 | -16.0518 | 86.148 | -75 | 16.3218 | 45.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/4:00
11 | 4 | 1900-01-04 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.1667 | -16.0641 | 86.148 | -75 | 16.3193 | 60.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/5:00
11 | 4 | 1900-01-05 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.2083 | -16.0763 | 86.148 | -75 | 16.3167 | 75.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/6:00
11 | 4 | 1900-01-06 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.25 | -16.0885 | 86.148 | -75 | 16.3142 | 90.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/7:00
11 | 4 | 1900-01-07 | 1.1 | 17 | 2 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 17 | 0 | 0 | 39.791 | 308.2917 | -16.1007 | 86.148 | -75 | 16.3116 | 105.2259 | -0.74274 | 16.2573 | 5.1533 | 5.1533 | 0 | 0 | 0 | 11/4/8:00
11 | 4 | 1900-01-08 | 1.7 | 80 | 149 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 80 | 0 | 0 | 39.791 | 308.3333 | -16.1129 | 86.148 | -75 | 16.309 | 120.2253 | -81.8349 | -1.8349 | -0.58162 | -0.58162 | 0 | 0 | 0 | 11/4/9:00
11 | 4 | 1900-01-09 | 3.9 | 124 | 11 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 124 | 0 | 0 | 39.791 | 308.375 | -16.1251 | 86.148 | -75 | 16.3064 | 135.2246 | -7.7192 | 116.2808 | 36.859 | 36.859 | 0 | 0 | 0 | 11/4/10:00
11 | 4 | 1900-01-10 | 5.6 | 211 | 6 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 211 | 0 | 0 | 39.791 | 308.4167 | -16.1373 | 86.148 | -75 | 16.3038 | 150.2239 | -4.9112 | 206.0888 | 65.3265 | 65.3265 | 0 | 0 | 0 | 11/4/11:00
11 | 4 | 1900-01-11 | 6.7 | 274 | 5 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 274 | 0 | 0 | 39.791 | 308.4583 | -16.1495 | 86.148 | -75 | 16.3011 | 165.2233 | -4.4583 | 269.5417 | 85.44 | 85.44 | 0 | 0 | 0 | 11/4/12:00
11 | 4 | 1900-01-12 | 8.3 | 216 | 77 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 216 | 0 | 0 | 39.791 | 308.5 | -16.1617 | 86.148 | -75 | 16.2984 | 180.2226 | -70.5437 | 145.4563 | 46.1071 | 46.1071 | 0 | 0 | 0 | 11/4/13:00
11 | 4 | 1900-01-13 | 10.6 | 234 | 81 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 234 | 0 | 0 | 39.791 | 308.5417 | -16.1738 | 86.148 | -75 | 16.2957 | 195.2219 | -72.1185 | 161.8815 | 51.3136 | 51.3136 | 0 | 0 | 0 | 11/4/14:00
11 | 4 | 1900-01-14 | 11.7 | 115 | 539 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 115 | 0 | 0 | 39.791 | 308.5833 | -16.186 | 86.148 | -75 | 16.2929 | 210.2212 | -439.8428 | -324.8428 | -102.9695 | -102.9695 | 0 | 0 | 0 | 11/4/15:00
11 | 4 | 1900-01-15 | 11.1 | 119 | 429 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 119 | 0 | 0 | 39.791 | 308.625 | -16.1981 | 86.148 | -75 | 16.2902 | 225.2205 | -299.5621 | -180.5621 | -57.235 | -57.235 | 0 | 0 | 0 | 11/4/16:00
11 | 4 | 1900-01-16 | 11.1 | 66 | 188 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 66 | 0 | 0 | 39.791 | 308.6667 | -16.2103 | 86.148 | -75 | 16.2874 | 240.2198 | -102.4835 | -36.4835 | -11.5646 | -11.5646 | 0 | 0 | 0 | 11/4/17:00
11 | 4 | 1900-01-17 | 8.9 | 14 | 188 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 14 | 0 | 0 | 39.791 | 308.7083 | -16.2224 | 86.148 | -75 | 16.2846 | 255.2191 | -68.9995 | -54.9995 | -17.4339 | -17.4339 | 0 | 0 | 0 | 11/4/18:00
11 | 4 | 1900-01-18 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.75 | -16.2345 | 86.148 | -75 | 16.2817 | 270.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/19:00
11 | 4 | 1900-01-19 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.7917 | -16.2467 | 86.148 | -75 | 16.2789 | 285.2177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/20:00
11 | 4 | 1900-01-20 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.8333 | -16.2588 | 86.148 | -75 | 16.276 | 300.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/21:00
11 | 4 | 1900-01-21 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.875 | -16.2709 | 86.148 | -75 | 16.2731 | 315.2163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/22:00
11 | 4 | 1900-01-22 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.9167 | -16.283 | 86.148 | -75 | 16.2702 | 330.2155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/23:00
11 | 4 | 1900-01-23 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 308.9583 | -16.295 | 86.148 | -75 | 16.2672 | 345.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/4/24:00
11 | 5 | 1899-12-31 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 309 | -16.3071 | 86.148 | -75 | 16.2642 | 0.21406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/5/1:00
11 | 5 | 1900-01-01 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 309.0417 | -16.3192 | 86.148 | -75 | 16.2612 | 15.2133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/5/2:00
11 | 5 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 309.0833 | -16.3313 | 86.148 | -75 | 16.2582 | 30.2126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/5/3:00
11 | 5 | 1900-01-03 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 309.125 | -16.3433 | 86.148 | -75 | 16.2552 | 45.2118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/5/4:00
11 | 5 | 1900-01-04 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 309.1667 | -16.3554 | 86.148 | -75 | 16.2521 | 60.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/5/5:00
11 | 5 | 1900-01-05 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 309.2083 | -16.3674 | 86.148 | -75 | 16.249 | 75.2103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/5/6:00
11 | 5 | 1900-01-06 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 309.25 | -16.3794 | 86.148 | -75 | 16.2459 | 90.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/5/7:00
11 | 5 | 1900-01-07 | 7.8 | 19 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 19 | 0 | 0 | 39.791 | 309.2917 | -16.3915 | 86.148 | -75 | 16.2428 | 105.2087 | 0 | 19 | 6.0227 | 6.0227 | 0 | 0 | 0 | 11/5/8:00
11 | 5 | 1900-01-08 | 11.1 | 54 | 3 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 54 | 0 | 0 | 39.791 | 309.3333 | -16.4035 | 86.148 | -75 | 16.2396 | 120.2079 | -1.6548 | 52.3452 | 16.5925 | 16.5925 | 0 | 0 | 0 | 11/5/9:00
11 | 5 | 1900-01-09 | 12.2 | 93 | 7 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 93 | 0 | 0 | 39.791 | 309.375 | -16.4155 | 86.148 | -75 | 16.2364 | 135.2071 | -4.9275 | 88.0725 | 27.9175 | 27.9175 | 0 | 0 | 0 | 11/5/10:00
11 | 5 | 1900-01-10 | 13.3 | 207 | 6 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 207 | 0 | 0 | 39.791 | 309.4167 | -16.4275 | 86.148 | -75 | 16.2332 | 150.2063 | -4.9235 | 202.0765 | 64.0547 | 0 | 64.0547 | 55.94 | 64.0547 | 11/5/11:00
11 | 5 | 1900-01-11 | 14.4 | 217 | 8 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 217 | 0 | 0 | 39.791 | 309.4583 | -16.4395 | 86.148 | -75 | 16.23 | 165.2055 | -7.1493 | 209.8507 | 66.519 | 0 | 66.519 | 57.92 | 66.519 | 11/5/12:00
11 | 5 | 1900-01-12 | 14.4 | 208 | 5 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 208 | 0 | 0 | 39.791 | 309.5 | -16.4514 | 86.148 | -75 | 16.2267 | 180.2047 | -4.5908 | 203.4092 | 64.4772 | 0 | 64.4772 | 57.92 | 64.4772 | 11/5/13:00
11 | 5 | 1900-01-13 | 15 | 217 | 4 | 59 | 0 | 1 | 0 | 59 | 0 | 217 | 0 | 0 | 39.791 | 309.5417 | -16.4634 | 86.148 | -75 | 16.2234 | 195.2039 | -3.5699 | 213.4301 | 67.6536 | 0 | 67.6536 | 59 | 67.6536 | 11/5/14:00
11 | 5 | 1900-01-14 | 15 | 184 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 184 | 0 | 0 | 39.791 | 309.5833 | -16.4754 | 86.148 | -75 | 16.2201 | 210.203 | 0 | 184 | 58.3248 | 0 | 58.3248 | 59 | 58.3248 | 11/5/15:00
11 | 5 | 1900-01-15 | 15 | 126 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 126 | 0 | 0 | 39.791 | 309.625 | -16.4874 | 86.148 | -75 | 16.2168 | 225.2022 | 0 | 126 | 39.9398 | 0 | 39.9398 | 59 | 39.9398 | 11/5/16:00
11 | 5 | 1900-01-16 | 15.6 | 78 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 78 | 0 | 0 | 39.791 | 309.6667 | -16.4993 | 86.148 | -75 | 16.2134 | 240.2014 | 0 | 78 | 24.7246 | 0 | 24.7246 | 60.08 | 24.7246 | 11/5/17:00
11 | 5 | 1900-01-17 | 16.1 | 20 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 20 | 0 | 0 | 39.791 | 309.7083 | -16.5112 | 86.148 | -75 | 16.21 | 255.2005 | 0 | 20 | 6.3397 | 0 | 6.3397 | 60.98 | 6.3397 | 11/5/18:00
11 | 5 | 1900-01-18 | 17.8 | 0 | 0 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 0 | 0 | 0 | 39.791 | 309.75 | -16.5232 | 86.148 | -75 | 16.2066 | 270.1997 | 0 | 0 | 0 | 0 | 0 | 64.04 | 0 | 11/5/19:00
11 | 5 | 1900-01-19 | 18.3 | 0 | 0 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 0 | 0 | 0 | 39.791 | 309.7917 | -16.5351 | 86.148 | -75 | 16.2032 | 285.1988 | 0 | 0 | 0 | 0 | 0 | 64.94 | 0 | 11/5/20:00
11 | 5 | 1900-01-20 | 18.9 | 0 | 0 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 0 | 0 | 0 | 39.791 | 309.8333 | -16.547 | 86.148 | -75 | 16.1998 | 300.1979 | 0 | 0 | 0 | 0 | 0 | 66.02 | 0 | 11/5/21:00
11 | 5 | 1900-01-21 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 309.875 | -16.5589 | 86.148 | -75 | 16.1963 | 315.1971 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 11/5/22:00
11 | 5 | 1900-01-22 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 309.9167 | -16.5708 | 86.148 | -75 | 16.1928 | 330.1962 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 11/5/23:00
11 | 5 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 309.9583 | -16.5827 | 86.148 | -75 | 16.1893 | 345.1953 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 11/5/24:00
11 | 6 | 1899-12-31 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 310 | -16.5946 | 86.148 | -75 | 16.1858 | 0.19444 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 11/6/1:00
11 | 6 | 1900-01-01 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.0417 | -16.6065 | 86.148 | -75 | 16.1822 | 15.1935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/2:00
11 | 6 | 1900-01-02 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.0833 | -16.6184 | 86.148 | -75 | 16.1786 | 30.1926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/3:00
11 | 6 | 1900-01-03 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.125 | -16.6302 | 86.148 | -75 | 16.175 | 45.1917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/4:00
11 | 6 | 1900-01-04 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.1667 | -16.6421 | 86.148 | -75 | 16.1713 | 60.1908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/5:00
11 | 6 | 1900-01-05 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.2083 | -16.6539 | 86.148 | -75 | 16.1677 | 75.1899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/6:00
11 | 6 | 1900-01-06 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.25 | -16.6658 | 86.148 | -75 | 16.164 | 90.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/7:00
11 | 6 | 1900-01-07 | 7.2 | 21 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 21 | 0 | 0 | 39.791 | 310.2917 | -16.6776 | 86.148 | -75 | 16.1603 | 105.1881 | 0 | 21 | 6.6566 | 6.6566 | 0 | 0 | 0 | 11/6/8:00
11 | 6 | 1900-01-08 | 6.7 | 70 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 70 | 0 | 0 | 39.791 | 310.3333 | -16.6894 | 86.148 | -75 | 16.1566 | 120.1871 | 0 | 70 | 22.1888 | 22.1888 | 0 | 0 | 0 | 11/6/9:00
11 | 6 | 1900-01-09 | 6.7 | 139 | 1 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 139 | 0 | 0 | 39.791 | 310.375 | -16.7013 | 86.148 | -75 | 16.1528 | 135.1862 | -0.70602 | 138.294 | 43.8368 | 43.8368 | 0 | 0 | 0 | 11/6/10:00
11 | 6 | 1900-01-10 | 7.2 | 212 | 1 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 212 | 0 | 0 | 39.791 | 310.4167 | -16.7131 | 86.148 | -75 | 16.149 | 150.1853 | -0.82256 | 211.1774 | 66.9396 | 66.9396 | 0 | 0 | 0 | 11/6/11:00
11 | 6 | 1900-01-11 | 7.8 | 248 | 1 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 248 | 0 | 0 | 39.791 | 310.4583 | -16.7249 | 86.148 | -75 | 16.1452 | 165.1843 | -0.89559 | 247.1044 | 78.3278 | 78.3278 | 0 | 0 | 0 | 11/6/12:00
11 | 6 | 1900-01-12 | 8.3 | 257 | 1 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 257 | 0 | 0 | 39.791 | 310.5 | -16.7367 | 86.148 | -75 | 16.1414 | 180.1834 | -0.92013 | 256.0799 | 81.1728 | 81.1728 | 0 | 0 | 0 | 11/6/13:00
11 | 6 | 1900-01-13 | 10.6 | 128 | 710 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 128 | 0 | 0 | 39.791 | 310.5417 | -16.7484 | 86.148 | -75 | 16.1376 | 195.1824 | -635.1185 | -507.1185 | -160.7477 | -160.7477 | 0 | 0 | 0 | 11/6/14:00
11 | 6 | 1900-01-14 | 11.1 | 100 | 712 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 100 | 0 | 0 | 39.791 | 310.5833 | -16.7602 | 86.148 | -75 | 16.1337 | 210.1814 | -584.2357 | -484.2357 | -153.4943 | -153.4943 | 0 | 0 | 0 | 11/6/15:00
11 | 6 | 1900-01-15 | 11.1 | 80 | 590 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 80 | 0 | 0 | 39.791 | 310.625 | -16.772 | 86.148 | -75 | 16.1298 | 225.1805 | -414.9194 | -334.9194 | -106.1636 | -106.1636 | 0 | 0 | 0 | 11/6/16:00
11 | 6 | 1900-01-16 | 11.7 | 53 | 361 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 53 | 0 | 0 | 39.791 | 310.6667 | -16.7837 | 86.148 | -75 | 16.1259 | 240.1795 | -198.7781 | -145.7781 | -46.2091 | -46.2091 | 0 | 0 | 0 | 11/6/17:00
11 | 6 | 1900-01-17 | 8.9 | 13 | 13 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 13 | 0 | 0 | 39.791 | 310.7083 | -16.7955 | 86.148 | -75 | 16.1219 | 255.1785 | -4.8503 | 8.1497 | 2.5833 | 2.5833 | 0 | 0 | 0 | 11/6/18:00
11 | 6 | 1900-01-18 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.75 | -16.8072 | 86.148 | -75 | 16.118 | 270.1775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/19:00
11 | 6 | 1900-01-19 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.7917 | -16.819 | 86.148 | -75 | 16.114 | 285.1765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/20:00
11 | 6 | 1900-01-20 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.8333 | -16.8307 | 86.148 | -75 | 16.11 | 300.1755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/21:00
11 | 6 | 1900-01-21 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.875 | -16.8424 | 86.148 | -75 | 16.1059 | 315.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/22:00
11 | 6 | 1900-01-22 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.9167 | -16.8541 | 86.148 | -75 | 16.1019 | 330.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/23:00
11 | 6 | 1900-01-23 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 310.9583 | -16.8658 | 86.148 | -75 | 16.0978 | 345.1724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/6/24:00
11 | 7 | 1899-12-31 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311 | -16.8775 | 86.148 | -75 | 16.0937 | 0.17142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/1:00
11 | 7 | 1900-01-01 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.0417 | -16.8892 | 86.148 | -75 | 16.0896 | 15.1704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/2:00
11 | 7 | 1900-01-02 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.0833 | -16.9009 | 86.148 | -75 | 16.0854 | 30.1694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/3:00
11 | 7 | 1900-01-03 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.125 | -16.9125 | 86.148 | -75 | 16.0812 | 45.1683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/4:00
11 | 7 | 1900-01-04 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.1667 | -16.9242 | 86.148 | -75 | 16.077 | 60.1673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/5:00
11 | 7 | 1900-01-05 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.2083 | -16.9358 | 86.148 | -75 | 16.0728 | 75.1662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/6:00
11 | 7 | 1900-01-06 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.25 | -16.9475 | 86.148 | -75 | 16.0686 | 90.1651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/7:00
11 | 7 | 1900-01-07 | 8.3 | 10 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 10 | 0 | 0 | 39.791 | 311.2917 | -16.9591 | 86.148 | -75 | 16.0643 | 105.1641 | 0 | 10 | 3.1698 | 3.1698 | 0 | 0 | 0 | 11/7/8:00
11 | 7 | 1900-01-08 | 8.9 | 34 | 5 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 34 | 0 | 0 | 39.791 | 311.3333 | -16.9707 | 86.148 | -75 | 16.06 | 120.163 | -2.7804 | 31.2196 | 9.8961 | 9.8961 | 0 | 0 | 0 | 11/7/9:00
11 | 7 | 1900-01-09 | 8.9 | 112 | 6 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 112 | 0 | 0 | 39.791 | 311.375 | -16.9824 | 86.148 | -75 | 16.0557 | 135.1619 | -4.2482 | 107.7518 | 34.1554 | 34.1554 | 0 | 0 | 0 | 11/7/10:00
11 | 7 | 1900-01-10 | 10 | 189 | 3 | 50 | 1 | 0 | 50 | 0 | 0 | 189 | 0 | 0 | 39.791 | 311.4167 | -16.994 | 86.148 | -75 | 16.0513 | 150.1608 | -2.4734 | 186.5266 | 59.1257 | 59.1257 | 0 | 0 | 0 | 11/7/11:00
11 | 7 | 1900-01-11 | 10.6 | 219 | 9 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 219 | 0 | 0 | 39.791 | 311.4583 | -17.0056 | 86.148 | -75 | 16.047 | 165.1597 | -8.0771 | 210.9229 | 66.8589 | 66.8589 | 0 | 0 | 0 | 11/7/12:00
11 | 7 | 1900-01-12 | 9.4 | 240 | 8 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 240 | 0 | 0 | 39.791 | 311.5 | -17.0172 | 86.148 | -75 | 16.0426 | 180.1586 | -7.3763 | 232.6237 | 73.7377 | 73.7377 | 0 | 0 | 0 | 11/7/13:00
11 | 7 | 1900-01-13 | 8.9 | 294 | 4 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 294 | 0 | 0 | 39.791 | 311.5417 | -17.0288 | 86.148 | -75 | 16.0382 | 195.1575 | -3.5862 | 290.4138 | 92.0561 | 92.0561 | 0 | 0 | 0 | 11/7/14:00
11 | 7 | 1900-01-14 | 9.4 | 187 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 187 | 0 | 0 | 39.791 | 311.5833 | -17.0403 | 86.148 | -75 | 16.0337 | 210.1564 | -0.82277 | 186.1772 | 59.0149 | 59.0149 | 0 | 0 | 0 | 11/7/15:00
11 | 7 | 1900-01-15 | 9.4 | 139 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 139 | 0 | 0 | 39.791 | 311.625 | -17.0519 | 86.148 | -75 | 16.0293 | 225.1553 | -0.7057 | 138.2943 | 43.8369 | 43.8369 | 0 | 0 | 0 | 11/7/16:00
11 | 7 | 1900-01-16 | 8.3 | 74 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 74 | 0 | 0 | 39.791 | 311.6667 | -17.0635 | 86.148 | -75 | 16.0248 | 240.1542 | 0 | 74 | 23.4567 | 23.4567 | 0 | 0 | 0 | 11/7/17:00
11 | 7 | 1900-01-17 | 7.8 | 16 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 16 | 0 | 0 | 39.791 | 311.7083 | -17.075 | 86.148 | -75 | 16.0203 | 255.1531 | 0 | 16 | 5.0717 | 5.0717 | 0 | 0 | 0 | 11/7/18:00
11 | 7 | 1900-01-18 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.75 | -17.0866 | 86.148 | -75 | 16.0158 | 270.1519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/19:00
11 | 7 | 1900-01-19 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.7917 | -17.0981 | 86.148 | -75 | 16.0112 | 285.1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/20:00
11 | 7 | 1900-01-20 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.8333 | -17.1096 | 86.148 | -75 | 16.0066 | 300.1497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/21:00
11 | 7 | 1900-01-21 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.875 | -17.1211 | 86.148 | -75 | 16.002 | 315.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/22:00
11 | 7 | 1900-01-22 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.9167 | -17.1326 | 86.148 | -75 | 15.9974 | 330.1474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/23:00
11 | 7 | 1900-01-23 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 311.9583 | -17.1441 | 86.148 | -75 | 15.9928 | 345.1462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/7/24:00
11 | 8 | 1899-12-31 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312 | -17.1556 | 86.148 | -75 | 15.9881 | 0.14503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/1:00
11 | 8 | 1900-01-01 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.0417 | -17.1671 | 86.148 | -75 | 15.9834 | 15.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/2:00
11 | 8 | 1900-01-02 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.0833 | -17.1786 | 86.148 | -75 | 15.9787 | 30.1427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/3:00
11 | 8 | 1900-01-03 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.125 | -17.1901 | 86.148 | -75 | 15.974 | 45.1415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/4:00
11 | 8 | 1900-01-04 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.1667 | -17.2015 | 86.148 | -75 | 15.9692 | 60.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/5:00
11 | 8 | 1900-01-05 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.2083 | -17.213 | 86.148 | -75 | 15.9644 | 75.1391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/6:00
11 | 8 | 1900-01-06 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.25 | -17.2244 | 86.148 | -75 | 15.9596 | 90.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/7:00
11 | 8 | 1900-01-07 | 7.2 | 17 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 17 | 0 | 0 | 39.791 | 312.2917 | -17.2359 | 86.148 | -75 | 15.9548 | 105.1367 | 0 | 17 | 5.3887 | 5.3887 | 0 | 0 | 0 | 11/8/8:00
11 | 8 | 1900-01-08 | 7.8 | 69 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 69 | 0 | 0 | 39.791 | 312.3333 | -17.2473 | 86.148 | -75 | 15.9499 | 120.1355 | 0 | 69 | 21.8718 | 21.8718 | 0 | 0 | 0 | 11/8/9:00
11 | 8 | 1900-01-09 | 8.3 | 148 | 1 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 148 | 0 | 0 | 39.791 | 312.375 | -17.2587 | 86.148 | -75 | 15.945 | 135.1343 | -0.70996 | 147.29 | 46.6884 | 46.6884 | 0 | 0 | 0 | 11/8/10:00
11 | 8 | 1900-01-10 | 8.9 | 214 | 1 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 214 | 0 | 0 | 39.791 | 312.4167 | -17.2701 | 86.148 | -75 | 15.9401 | 150.133 | -0.82629 | 213.1737 | 67.5723 | 67.5723 | 0 | 0 | 0 | 11/8/11:00
11 | 8 | 1900-01-11 | 9.4 | 273 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 273 | 0 | 0 | 39.791 | 312.4583 | -17.2815 | 86.148 | -75 | 15.9352 | 165.1318 | -0.89925 | 272.1007 | 86.2512 | 86.2512 | 0 | 0 | 0 | 11/8/12:00
11 | 8 | 1900-01-12 | 9.4 | 166 | 1 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 166 | 0 | 0 | 39.791 | 312.5 | -17.2929 | 86.148 | -75 | 15.9303 | 180.1306 | -0.92389 | 165.0761 | 52.3262 | 52.3262 | 0 | 0 | 0 | 11/8/13:00
11 | 8 | 1900-01-13 | 10.6 | 276 | 1 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 276 | 0 | 0 | 39.791 | 312.5417 | -17.3043 | 86.148 | -75 | 15.9253 | 195.1293 | -0.89854 | 275.1015 | 87.2024 | 87.2024 | 0 | 0 | 0 | 11/8/14:00
11 | 8 | 1900-01-14 | 10.6 | 205 | 1 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 205 | 0 | 0 | 39.791 | 312.5833 | -17.3157 | 86.148 | -75 | 15.9203 | 210.1281 | -0.82494 | 204.1751 | 64.7199 | 64.7199 | 0 | 0 | 0 | 11/8/15:00
11 | 8 | 1900-01-15 | 10 | 152 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 152 | 0 | 0 | 39.791 | 312.625 | -17.327 | 86.148 | -75 | 15.9153 | 225.1268 | 0 | 152 | 48.1813 | 48.1813 | 0 | 0 | 0 | 11/8/16:00
11 | 8 | 1900-01-16 | 10 | 70 | 1 | 50 | 1 | 0 | 50 | 0 | 0 | 70 | 0 | 0 | 39.791 | 312.6667 | -17.3384 | 86.148 | -75 | 15.9102 | 240.1256 | -0.55607 | 69.4439 | 22.0125 | 22.0125 | 0 | 0 | 0 | 11/8/17:00
11 | 8 | 1900-01-17 | 9.4 | 18 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 18 | 0 | 0 | 39.791 | 312.7083 | -17.3497 | 86.148 | -75 | 15.9052 | 255.1243 | 0 | 18 | 5.7057 | 5.7057 | 0 | 0 | 0 | 11/8/18:00
11 | 8 | 1900-01-18 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.75 | -17.3611 | 86.148 | -75 | 15.9001 | 270.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/19:00
11 | 8 | 1900-01-19 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.7917 | -17.3724 | 86.148 | -75 | 15.895 | 285.1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/20:00
11 | 8 | 1900-01-20 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.8333 | -17.3837 | 86.148 | -75 | 15.8898 | 300.1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/21:00
11 | 8 | 1900-01-21 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.875 | -17.395 | 86.148 | -75 | 15.8847 | 315.1192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/22:00
11 | 8 | 1900-01-22 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.9167 | -17.4064 | 86.148 | -75 | 15.8795 | 330.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/23:00
11 | 8 | 1900-01-23 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 312.9583 | -17.4176 | 86.148 | -75 | 15.8743 | 345.1166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/8/24:00
11 | 9 | 1899-12-31 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313 | -17.4289 | 86.148 | -75 | 15.8691 | 0.11526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/1:00
11 | 9 | 1900-01-01 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.0417 | -17.4402 | 86.148 | -75 | 15.8638 | 15.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/2:00
11 | 9 | 1900-01-02 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.0833 | -17.4515 | 86.148 | -75 | 15.8585 | 30.1126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/3:00
11 | 9 | 1900-01-03 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.125 | -17.4628 | 86.148 | -75 | 15.8532 | 45.1113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/4:00
11 | 9 | 1900-01-04 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.1667 | -17.474 | 86.148 | -75 | 15.8479 | 60.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/5:00
11 | 9 | 1900-01-05 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.2083 | -17.4853 | 86.148 | -75 | 15.8426 | 75.1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/6:00
11 | 9 | 1900-01-06 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.25 | -17.4965 | 86.148 | -75 | 15.8372 | 90.1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/7:00
11 | 9 | 1900-01-07 | 1.7 | 15 | 107 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 15 | 0 | 0 | 39.791 | 313.2917 | -17.5077 | 86.148 | -75 | 15.8318 | 105.106 | -41.0344 | -26.0344 | -8.2525 | -8.2525 | 0 | 0 | 0 | 11/9/8:00
11 | 9 | 1900-01-08 | 2.8 | 37 | 543 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 37 | 0 | 0 | 39.791 | 313.3333 | -17.519 | 86.148 | -75 | 15.8264 | 120.1046 | -304.1779 | -267.1779 | -84.6907 | -84.6907 | 0 | 0 | 0 | 11/9/9:00
11 | 9 | 1900-01-09 | 4.4 | 53 | 741 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 53 | 0 | 0 | 39.791 | 313.375 | -17.5302 | 86.148 | -75 | 15.821 | 135.1032 | -527.443 | -474.443 | -150.3902 | -150.3902 | 0 | 0 | 0 | 11/9/10:00
11 | 9 | 1900-01-10 | 6.1 | 66 | 832 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 66 | 0 | 0 | 39.791 | 313.4167 | -17.5414 | 86.148 | -75 | 15.8155 | 150.1019 | -688.9262 | -622.9262 | -197.4567 | -197.4567 | 0 | 0 | 0 | 11/9/11:00
11 | 9 | 1900-01-11 | 8.3 | 104 | 732 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 104 | 0 | 0 | 39.791 | 313.4583 | -17.5526 | 86.148 | -75 | 15.81 | 165.1005 | -659.5213 | -555.5213 | -176.0905 | -176.0905 | 0 | 0 | 0 | 11/9/12:00
11 | 9 | 1900-01-12 | 8.9 | 158 | 646 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 158 | 0 | 0 | 39.791 | 313.5 | -17.5637 | 86.148 | -75 | 15.8045 | 180.0991 | -597.9955 | -439.9955 | -139.4709 | -139.4709 | 0 | 0 | 0 | 11/9/13:00
11 | 9 | 1900-01-13 | 9.4 | 282 | 326 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 282 | 0 | 0 | 39.791 | 313.5417 | -17.5749 | 86.148 | -75 | 15.799 | 195.0977 | -293.5565 | -11.5565 | -3.6632 | -3.6632 | 0 | 0 | 0 | 11/9/14:00
11 | 9 | 1900-01-14 | 7.8 | 218 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 218 | 0 | 0 | 39.791 | 313.5833 | -17.5861 | 86.148 | -75 | 15.7934 | 210.0964 | 0 | 218 | 69.1022 | 69.1022 | 0 | 0 | 0 | 11/9/15:00
11 | 9 | 1900-01-15 | 8.9 | 170 | 301 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 170 | 0 | 0 | 39.791 | 313.625 | -17.5973 | 86.148 | -75 | 15.7878 | 225.095 | -213.8694 | -43.8694 | -13.9058 | -13.9058 | 0 | 0 | 0 | 11/9/16:00
11 | 9 | 1900-01-16 | 7.8 | 65 | 288 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 65 | 0 | 0 | 39.791 | 313.6667 | -17.6084 | 86.148 | -75 | 15.7822 | 240.0936 | -160.9223 | -95.9223 | -30.4057 | -30.4057 | 0 | 0 | 0 | 11/9/17:00
11 | 9 | 1900-01-17 | 7.2 | 21 | 15 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 21 | 0 | 0 | 39.791 | 313.7083 | -17.6196 | 86.148 | -75 | 15.7766 | 255.0922 | -5.7319 | 15.2681 | 4.8397 | 4.8397 | 0 | 0 | 0 | 11/9/18:00
11 | 9 | 1900-01-18 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.75 | -17.6307 | 86.148 | -75 | 15.771 | 270.0907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/19:00
11 | 9 | 1900-01-19 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.7917 | -17.6418 | 86.148 | -75 | 15.7653 | 285.0893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/20:00
11 | 9 | 1900-01-20 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.8333 | -17.6529 | 86.148 | -75 | 15.7596 | 300.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/21:00
11 | 9 | 1900-01-21 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.875 | -17.664 | 86.148 | -75 | 15.7539 | 315.0865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/22:00
11 | 9 | 1900-01-22 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.9167 | -17.6751 | 86.148 | -75 | 15.7482 | 330.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/23:00
11 | 9 | 1900-01-23 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 313.9583 | -17.6862 | 86.148 | -75 | 15.7424 | 345.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/9/24:00
11 | 10 | 1899-12-31 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314 | -17.6973 | 86.148 | -75 | 15.7366 | 0.082153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/1:00
11 | 10 | 1900-01-01 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.0417 | -17.7084 | 86.148 | -75 | 15.7308 | 15.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/2:00
11 | 10 | 1900-01-02 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.0833 | -17.7195 | 86.148 | -75 | 15.725 | 30.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/3:00
11 | 10 | 1900-01-03 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.125 | -17.7305 | 86.148 | -75 | 15.7191 | 45.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/4:00
11 | 10 | 1900-01-04 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.1667 | -17.7416 | 86.148 | -75 | 15.7132 | 60.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/5:00
11 | 10 | 1900-01-05 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.2083 | -17.7526 | 86.148 | -75 | 15.7073 | 75.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/6:00
11 | 10 | 1900-01-06 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.25 | -17.7636 | 86.148 | -75 | 15.7014 | 90.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/7:00
11 | 10 | 1900-01-07 | 2.8 | 16 | 16 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 16 | 0 | 0 | 39.791 | 314.2917 | -17.7746 | 86.148 | -75 | 15.6955 | 105.0719 | -6.1702 | 9.8298 | 3.1159 | 3.1159 | 0 | 0 | 0 | 11/10/8:00
11 | 10 | 1900-01-08 | 3.3 | 44 | 2 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 44 | 0 | 0 | 39.791 | 314.3333 | -17.7857 | 86.148 | -75 | 15.6895 | 120.0704 | -1.1242 | 42.8758 | 13.5909 | 13.5909 | 0 | 0 | 0 | 11/10/9:00
11 | 10 | 1900-01-09 | 4.4 | 131 | 101 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 131 | 0 | 0 | 39.791 | 314.375 | -17.7967 | 86.148 | -75 | 15.6835 | 135.0689 | -72.0693 | 58.9307 | 18.68 | 18.68 | 0 | 0 | 0 | 11/10/10:00
11 | 10 | 1900-01-10 | 4.4 | 161 | 72 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 161 | 0 | 0 | 39.791 | 314.4167 | -17.8077 | 86.148 | -75 | 15.6775 | 150.0674 | -59.7392 | 101.2608 | 32.0979 | 32.0979 | 0 | 0 | 0 | 11/10/11:00
11 | 10 | 1900-01-11 | 5.6 | 287 | 216 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 287 | 0 | 0 | 39.791 | 314.4583 | -17.8186 | 86.148 | -75 | 15.6715 | 165.0659 | -194.9736 | 92.0264 | 29.1708 | 29.1708 | 0 | 0 | 0 | 11/10/12:00
11 | 10 | 1900-01-12 | 5.6 | 168 | 4 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 168 | 0 | 0 | 39.791 | 314.5 | -17.8296 | 86.148 | -75 | 15.6654 | 180.0643 | -3.7097 | 164.2903 | 52.0771 | 52.0771 | 0 | 0 | 0 | 11/10/13:00
11 | 10 | 1900-01-13 | 5 | 228 | 2 | 41 | 1 | 0 | 41 | 0 | 0 | 228 | 0 | 0 | 39.791 | 314.5417 | -17.8406 | 86.148 | -75 | 15.6593 | 195.0628 | -1.8048 | 226.1952 | 71.6999 | 71.6999 | 0 | 0 | 0 | 11/10/14:00
11 | 10 | 1900-01-14 | 5 | 160 | 12 | 41 | 1 | 0 | 41 | 0 | 0 | 160 | 0 | 0 | 39.791 | 314.5833 | -17.8516 | 86.148 | -75 | 15.6532 | 210.0613 | -9.9504 | 150.0496 | 47.5631 | 47.5631 | 0 | 0 | 0 | 11/10/15:00
11 | 10 | 1900-01-15 | 5.6 | 130 | 150 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 130 | 0 | 0 | 39.791 | 314.625 | -17.8625 | 86.148 | -75 | 15.6471 | 225.0598 | -106.9358 | 23.0642 | 7.311 | 7.311 | 0 | 0 | 0 | 11/10/16:00
11 | 10 | 1900-01-16 | 5.6 | 66 | 165 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 66 | 0 | 0 | 39.791 | 314.6667 | -17.8734 | 86.148 | -75 | 15.6409 | 240.0582 | -92.6357 | -26.6357 | -8.4431 | -8.4431 | 0 | 0 | 0 | 11/10/17:00
11 | 10 | 1900-01-17 | 3.3 | 16 | 34 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 16 | 0 | 0 | 39.791 | 314.7083 | -17.8844 | 86.148 | -75 | 15.6347 | 255.0567 | -13.0935 | 2.9065 | 0.92131 | 0.92131 | 0 | 0 | 0 | 11/10/18:00
11 | 10 | 1900-01-18 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.75 | -17.8953 | 86.148 | -75 | 15.6285 | 270.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/19:00
11 | 10 | 1900-01-19 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.7917 | -17.9062 | 86.148 | -75 | 15.6223 | 285.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/20:00
11 | 10 | 1900-01-20 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.8333 | -17.9171 | 86.148 | -75 | 15.6161 | 300.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/21:00
11 | 10 | 1900-01-21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.875 | -17.928 | 86.148 | -75 | 15.6098 | 315.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/22:00
11 | 10 | 1900-01-22 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.9167 | -17.9389 | 86.148 | -75 | 15.6035 | 330.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/23:00
11 | 10 | 1900-01-23 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 314.9583 | -17.9498 | 86.148 | -75 | 15.5972 | 345.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/10/24:00
11 | 11 | 1899-12-31 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315 | -17.9607 | 86.148 | -75 | 15.5909 | 0.045713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/1:00
11 | 11 | 1900-01-01 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.0417 | -17.9715 | 86.148 | -75 | 15.5845 | 15.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/2:00
11 | 11 | 1900-01-02 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.0833 | -17.9824 | 86.148 | -75 | 15.5781 | 30.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/3:00
11 | 11 | 1900-01-03 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.125 | -17.9932 | 86.148 | -75 | 15.5717 | 45.0409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/4:00
11 | 11 | 1900-01-04 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.1667 | -18.0041 | 86.148 | -75 | 15.5653 | 60.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/5:00
11 | 11 | 1900-01-05 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.2083 | -18.0149 | 86.148 | -75 | 15.5588 | 75.0377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/6:00
11 | 11 | 1900-01-06 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.25 | -18.0257 | 86.148 | -75 | 15.5523 | 90.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/7:00
11 | 11 | 1900-01-07 | 3.3 | 13 | 5 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 13 | 0 | 0 | 39.791 | 315.2917 | -18.0365 | 86.148 | -75 | 15.5458 | 105.0345 | -1.9384 | 11.0616 | 3.5063 | 3.5063 | 0 | 0 | 0 | 11/11/8:00
11 | 11 | 1900-01-08 | 6.1 | 69 | 159 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 69 | 0 | 0 | 39.791 | 315.3333 | -18.0473 | 86.148 | -75 | 15.5393 | 120.0328 | -89.6637 | -20.6637 | -6.55 | -6.55 | 0 | 0 | 0 | 11/11/9:00
11 | 11 | 1900-01-09 | 9.4 | 133 | 378 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 133 | 0 | 0 | 39.791 | 315.375 | -18.0581 | 86.148 | -75 | 15.5328 | 135.0312 | -270.3579 | -137.3579 | -43.54 | -43.54 | 0 | 0 | 0 | 11/11/10:00
11 | 11 | 1900-01-10 | 12.8 | 201 | 416 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 201 | 0 | 0 | 39.791 | 315.4167 | -18.0689 | 86.148 | -75 | 15.5262 | 150.0296 | -345.8254 | -144.8254 | -45.9071 | 0 | -45.9071 | 55.04 | -45.9071 | 11/11/11:00
11 | 11 | 1900-01-11 | 15.6 | 228 | 424 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 228 | 0 | 0 | 39.791 | 315.4583 | -18.0797 | 86.148 | -75 | 15.5196 | 165.0279 | -383.4071 | -155.4071 | -49.2613 | 0 | -49.2613 | 60.08 | -49.2613 | 11/11/12:00
11 | 11 | 1900-01-12 | 18.3 | 194 | 527 | 64.94 | 0 | 1 | 0 | 64.94 | 0 | 194 | 0 | 0 | 39.791 | 315.5 | -18.0904 | 86.148 | -75 | 15.513 | 180.0263 | -489.6509 | -295.6509 | -93.7162 | 0 | -93.7162 | 64.94 | -93.7162 | 11/11/13:00
11 | 11 | 1900-01-13 | 20.6 | 197 | 519 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 197 | 0 | 0 | 39.791 | 315.5417 | -18.1012 | 86.148 | -75 | 15.5064 | 195.0246 | -469.2958 | -272.2958 | -86.313 | 0 | -86.313 | 69.08 | -86.313 | 11/11/14:00
11 | 11 | 1900-01-14 | 18.9 | 188 | 355 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 188 | 0 | 0 | 39.791 | 315.5833 | -18.1119 | 86.148 | -75 | 15.4997 | 210.0229 | -295.1038 | -107.1038 | -33.95 | 0 | -33.95 | 66.02 | -33.95 | 11/11/15:00
11 | 11 | 1900-01-15 | 19.4 | 115 | 361 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 115 | 0 | 0 | 39.791 | 315.625 | -18.1227 | 86.148 | -75 | 15.493 | 225.0213 | -258.2071 | -143.2071 | -45.3941 | 0 | -45.3941 | 66.92 | -45.3941 | 11/11/16:00
11 | 11 | 1900-01-16 | 17.8 | 60 | 201 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 60 | 0 | 0 | 39.791 | 315.6667 | -18.1334 | 86.148 | -75 | 15.4863 | 240.0196 | -113.3798 | -53.3798 | -16.9205 | 0 | -16.9205 | 64.04 | -16.9205 | 11/11/17:00
11 | 11 | 1900-01-17 | 14.4 | 11 | 7 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 11 | 0 | 0 | 39.791 | 315.7083 | -18.1441 | 86.148 | -75 | 15.4796 | 255.0179 | -2.7164 | 8.2836 | 2.6257 | 0 | 2.6257 | 57.92 | 2.6257 | 11/11/18:00
11 | 11 | 1900-01-18 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 315.75 | -18.1548 | 86.148 | -75 | 15.4729 | 270.0162 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 11/11/19:00
11 | 11 | 1900-01-19 | 11.7 | 0 | 0 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.7917 | -18.1655 | 86.148 | -75 | 15.4661 | 285.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/20:00
11 | 11 | 1900-01-20 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.8333 | -18.1762 | 86.148 | -75 | 15.4593 | 300.0128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/21:00
11 | 11 | 1900-01-21 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.875 | -18.1869 | 86.148 | -75 | 15.4525 | 315.0111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/22:00
11 | 11 | 1900-01-22 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.9167 | -18.1976 | 86.148 | -75 | 15.4456 | 330.0094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/23:00
11 | 11 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 315.9583 | -18.2082 | 86.148 | -75 | 15.4388 | 345.0077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/11/24:00
11 | 12 | 1899-12-31 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316 | -18.2189 | 86.148 | -75 | 15.4319 | 0.0059693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/1:00
11 | 12 | 1900-01-01 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.0417 | -18.2295 | 86.148 | -75 | 15.425 | 15.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/2:00
11 | 12 | 1900-01-02 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.0833 | -18.2402 | 86.148 | -75 | 15.418 | 30.0025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/3:00
11 | 12 | 1900-01-03 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.125 | -18.2508 | 86.148 | -75 | 15.4111 | 45.0008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/4:00
11 | 12 | 1900-01-04 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.1667 | -18.2614 | 86.148 | -75 | 15.4041 | 59.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/5:00
11 | 12 | 1900-01-05 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.2083 | -18.272 | 86.148 | -75 | 15.3971 | 74.9973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/6:00
11 | 12 | 1900-01-06 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.25 | -18.2826 | 86.148 | -75 | 15.3901 | 89.9955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/7:00
11 | 12 | 1900-01-07 | 4.4 | 14 | 49 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 14 | 0 | 0 | 39.791 | 316.2917 | -18.2932 | 86.148 | -75 | 15.383 | 104.9938 | -19.0916 | -5.0916 | -1.614 | -1.614 | 0 | 0 | 0 | 11/12/8:00
11 | 12 | 1900-01-08 | 6.7 | 45 | 379 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 45 | 0 | 0 | 39.791 | 316.3333 | -18.3038 | 86.148 | -75 | 15.376 | 119.992 | -214.3842 | -169.3842 | -53.6918 | -53.6918 | 0 | 0 | 0 | 11/12/9:00
11 | 12 | 1900-01-09 | 8.3 | 67 | 643 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 67 | 0 | 0 | 39.791 | 316.375 | -18.3144 | 86.148 | -75 | 15.3689 | 134.9902 | -460.9181 | -393.9181 | -124.8652 | -124.8652 | 0 | 0 | 0 | 11/12/10:00
11 | 12 | 1900-01-10 | 10 | 91 | 744 | 50 | 1 | 0 | 50 | 0 | 0 | 91 | 0 | 0 | 39.791 | 316.4167 | -18.325 | 86.148 | -75 | 15.3618 | 149.9884 | -619.6311 | -528.6311 | -167.5668 | -167.5668 | 0 | 0 | 0 | 11/12/11:00
11 | 12 | 1900-01-11 | 11.7 | 95 | 791 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 95 | 0 | 0 | 39.791 | 316.4583 | -18.3355 | 86.148 | -75 | 15.3546 | 164.9867 | -716.492 | -621.492 | -197.0021 | -197.0021 | 0 | 0 | 0 | 11/12/12:00
11 | 12 | 1900-01-12 | 12.8 | 94 | 819 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 94 | 0 | 0 | 39.791 | 316.5 | -18.3461 | 86.148 | -75 | 15.3475 | 179.9849 | -762.3001 | -668.3001 | -211.8395 | 0 | -211.8395 | 55.04 | -211.8395 | 11/12/13:00
11 | 12 | 1900-01-13 | 13.9 | 91 | 805 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 91 | 0 | 0 | 39.791 | 316.5417 | -18.3566 | 86.148 | -75 | 15.3403 | 194.9831 | -729.3643 | -638.3643 | -202.3503 | 0 | -202.3503 | 57.02 | -202.3503 | 11/12/14:00
11 | 12 | 1900-01-14 | 13.9 | 81 | 754 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 81 | 0 | 0 | 39.791 | 316.5833 | -18.3671 | 86.148 | -75 | 15.3331 | 209.9813 | -628.3257 | -547.3257 | -173.4927 | 0 | -173.4927 | 57.02 | -173.4927 | 11/12/15:00
11 | 12 | 1900-01-15 | 14.4 | 67 | 641 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 67 | 0 | 0 | 39.791 | 316.625 | -18.3777 | 86.148 | -75 | 15.3259 | 224.9795 | -459.9682 | -392.9682 | -124.5641 | 0 | -124.5641 | 57.92 | -124.5641 | 11/12/16:00
11 | 12 | 1900-01-16 | 12.8 | 47 | 404 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 47 | 0 | 0 | 39.791 | 316.6667 | -18.3882 | 86.148 | -75 | 15.3186 | 239.9777 | -228.9502 | -181.9502 | -57.675 | 0 | -57.675 | 55.04 | -57.675 | 11/12/17:00
11 | 12 | 1900-01-17 | 11.1 | 13 | 36 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 13 | 0 | 0 | 39.791 | 316.7083 | -18.3987 | 86.148 | -75 | 15.3113 | 254.9758 | -14.0761 | -1.0761 | -0.34109 | -0.34109 | 0 | 0 | 0 | 11/12/18:00
11 | 12 | 1900-01-18 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.75 | -18.4092 | 86.148 | -75 | 15.304 | 269.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/19:00
11 | 12 | 1900-01-19 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.7917 | -18.4196 | 86.148 | -75 | 15.2967 | 284.9722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/20:00
11 | 12 | 1900-01-20 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.8333 | -18.4301 | 86.148 | -75 | 15.2894 | 299.9703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/21:00
11 | 12 | 1900-01-21 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.875 | -18.4406 | 86.148 | -75 | 15.282 | 314.9685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/22:00
11 | 12 | 1900-01-22 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.9167 | -18.451 | 86.148 | -75 | 15.2746 | 329.9667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/23:00
11 | 12 | 1900-01-23 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 316.9583 | -18.4615 | 86.148 | -75 | 15.2672 | 344.9648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/12/24:00
11 | 13 | 1899-12-31 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 317 | -18.4719 | 86.148 | -75 | 15.2598 | -0.03705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/13/1:00
11 | 13 | 1900-01-01 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 317.0417 | -18.4823 | 86.148 | -75 | 15.2523 | 14.9611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/13/2:00
11 | 13 | 1900-01-02 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 317.0833 | -18.4928 | 86.148 | -75 | 15.2449 | 29.9592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/13/3:00
11 | 13 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 317.125 | -18.5032 | 86.148 | -75 | 15.2374 | 44.9573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/13/4:00
11 | 13 | 1900-01-04 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 317.1667 | -18.5136 | 86.148 | -75 | 15.2299 | 59.9555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/13/5:00
11 | 13 | 1900-01-05 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 317.2083 | -18.524 | 86.148 | -75 | 15.2223 | 74.9536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/13/6:00
11 | 13 | 1900-01-06 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 317.25 | -18.5344 | 86.148 | -75 | 15.2147 | 89.9517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/13/7:00
11 | 13 | 1900-01-07 | 9.4 | 11 | 115 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 11 | 0 | 0 | 39.791 | 317.2917 | -18.5447 | 86.148 | -75 | 15.2072 | 104.9498 | -45.0196 | -34.0196 | -10.7836 | -10.7836 | 0 | 0 | 0 | 11/13/8:00
11 | 13 | 1900-01-08 | 12.2 | 30 | 568 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 30 | 0 | 0 | 39.791 | 317.3333 | -18.5551 | 86.148 | -75 | 15.1996 | 119.9479 | -322.2275 | -292.2275 | -92.631 | -92.631 | 0 | 0 | 0 | 11/13/9:00
11 | 13 | 1900-01-09 | 15.6 | 43 | 759 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 43 | 0 | 0 | 39.791 | 317.375 | -18.5654 | 86.148 | -75 | 15.1919 | 134.946 | -545.2153 | -502.2153 | -159.1935 | 0 | -159.1935 | 60.08 | -159.1935 | 11/13/10:00
11 | 13 | 1900-01-10 | 18.9 | 53 | 835 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 53 | 0 | 0 | 39.791 | 317.4167 | -18.5758 | 86.148 | -75 | 15.1843 | 149.9441 | -696.633 | -643.633 | -204.0204 | 0 | -204.0204 | 66.02 | -204.0204 | 11/13/11:00
11 | 13 | 1900-01-11 | 20.6 | 60 | 880 | 69.08 | 0 | 1 | 0 | 69.08 | 0 | 60 | 0 | 0 | 39.791 | 317.4583 | -18.5861 | 86.148 | -75 | 15.1766 | 164.9421 | -798.4115 | -738.4115 | -234.0635 | 0 | -234.0635 | 69.08 | -234.0635 | 11/13/12:00
11 | 13 | 1900-01-12 | 21.7 | 62 | 896 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 62 | 0 | 0 | 39.791 | 317.5 | -18.5964 | 86.148 | -75 | 15.1689 | 179.9402 | -835.3926 | -773.3926 | -245.1519 | 0 | -245.1519 | 71.06 | -245.1519 | 11/13/13:00
11 | 13 | 1900-01-13 | 22.2 | 60 | 886 | 71.96 | 0 | 1 | 0 | 71.96 | 0 | 60 | 0 | 0 | 39.791 | 317.5417 | -18.6068 | 86.148 | -75 | 15.1612 | 194.9383 | -804.3217 | -744.3217 | -235.937 | 0 | -235.937 | 71.96 | -235.937 | 11/13/14:00
11 | 13 | 1900-01-14 | 21.7 | 53 | 845 | 71.06 | 0 | 1 | 0 | 71.06 | 0 | 53 | 0 | 0 | 39.791 | 317.5833 | -18.6171 | 86.148 | -75 | 15.1534 | 209.9364 | -705.8581 | -652.8581 | -206.9446 | 0 | -206.9446 | 71.06 | -206.9446 | 11/13/15:00
11 | 13 | 1900-01-15 | 21.1 | 43 | 766 | 69.98 | 0 | 1 | 0 | 69.98 | 0 | 43 | 0 | 0 | 39.791 | 317.625 | -18.6274 | 86.148 | -75 | 15.1457 | 224.9344 | -551.4258 | -508.4258 | -161.1621 | 0 | -161.1621 | 69.98 | -161.1621 | 11/13/16:00
11 | 13 | 1900-01-16 | 20 | 30 | 570 | 68 | 0 | 1 | 0 | 68 | 0 | 30 | 0 | 0 | 39.791 | 317.6667 | -18.6377 | 86.148 | -75 | 15.1379 | 239.9325 | -324.5104 | -294.5104 | -93.3547 | 0 | -93.3547 | 68 | -93.3547 | 11/13/17:00
11 | 13 | 1900-01-17 | 17.2 | 11 | 117 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 11 | 0 | 0 | 39.791 | 317.7083 | -18.6479 | 86.148 | -75 | 15.1301 | 254.9305 | -46.0889 | -35.0889 | -11.1226 | 0 | -11.1226 | 62.96 | -11.1226 | 11/13/18:00
11 | 13 | 1900-01-18 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 317.75 | -18.6582 | 86.148 | -75 | 15.1222 | 269.9286 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 11/13/19:00
11 | 13 | 1900-01-19 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 317.7917 | -18.6685 | 86.148 | -75 | 15.1144 | 284.9266 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 11/13/20:00
11 | 13 | 1900-01-20 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 317.8333 | -18.6787 | 86.148 | -75 | 15.1065 | 299.9246 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 11/13/21:00
11 | 13 | 1900-01-21 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 317.875 | -18.689 | 86.148 | -75 | 15.0986 | 314.9226 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 11/13/22:00
11 | 13 | 1900-01-22 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 317.9167 | -18.6992 | 86.148 | -75 | 15.0907 | 329.9207 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 11/13/23:00
11 | 13 | 1900-01-23 | 13.3 | 0 | 0 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 0 | 0 | 0 | 39.791 | 317.9583 | -18.7094 | 86.148 | -75 | 15.0827 | 344.9187 | 0 | 0 | 0 | 0 | 0 | 55.94 | 0 | 11/13/24:00
11 | 14 | 1899-12-31 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 318 | -18.7196 | 86.148 | -75 | 15.0748 | -0.083312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/14/1:00
11 | 14 | 1900-01-01 | 13.9 | 0 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 0 | 0 | 0 | 39.791 | 318.0417 | -18.7298 | 86.148 | -75 | 15.0668 | 14.9147 | 0 | 0 | 0 | 0 | 0 | 57.02 | 0 | 11/14/2:00
11 | 14 | 1900-01-02 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 318.0833 | -18.74 | 86.148 | -75 | 15.0587 | 29.9127 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 11/14/3:00
11 | 14 | 1900-01-03 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 318.125 | -18.7502 | 86.148 | -75 | 15.0507 | 44.9107 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 11/14/4:00
11 | 14 | 1900-01-04 | 17.2 | 0 | 0 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 0 | 0 | 0 | 39.791 | 318.1667 | -18.7604 | 86.148 | -75 | 15.0427 | 59.9087 | 0 | 0 | 0 | 0 | 0 | 62.96 | 0 | 11/14/5:00
11 | 14 | 1900-01-05 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 318.2083 | -18.7706 | 86.148 | -75 | 15.0346 | 74.9066 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 11/14/6:00
11 | 14 | 1900-01-06 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 318.25 | -18.7807 | 86.148 | -75 | 15.0265 | 89.9046 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 11/14/7:00
11 | 14 | 1900-01-07 | 16.1 | 4 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 4 | 0 | 0 | 39.791 | 318.2917 | -18.7909 | 86.148 | -75 | 15.0184 | 104.9026 | 0 | 4 | 1.2679 | 0 | 1.2679 | 60.98 | 1.2679 | 11/14/8:00
11 | 14 | 1900-01-08 | 16.7 | 37 | 8 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 37 | 0 | 0 | 39.791 | 318.3333 | -18.801 | 86.148 | -75 | 15.0102 | 119.9006 | -4.5508 | 32.4492 | 10.2858 | 0 | 10.2858 | 62.06 | 10.2858 | 11/14/9:00
11 | 14 | 1900-01-09 | 16.7 | 80 | 5 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 80 | 0 | 0 | 39.791 | 318.375 | -18.8111 | 86.148 | -75 | 15.002 | 134.8985 | -3.5988 | 76.4012 | 24.2178 | 0 | 24.2178 | 62.06 | 24.2178 | 11/14/10:00
11 | 14 | 1900-01-10 | 16.7 | 93 | 3 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 93 | 0 | 0 | 39.791 | 318.4167 | -18.8213 | 86.148 | -75 | 14.9938 | 149.8965 | -2.507 | 90.493 | 28.6847 | 0 | 28.6847 | 62.06 | 28.6847 | 11/14/11:00
11 | 14 | 1900-01-11 | 15 | 134 | 3 | 59 | 0 | 1 | 0 | 59 | 0 | 134 | 0 | 0 | 39.791 | 318.4583 | -18.8314 | 86.148 | -75 | 14.9856 | 164.8944 | -2.7261 | 131.2739 | 41.6115 | 0 | 41.6115 | 59 | 41.6115 | 11/14/12:00
11 | 14 | 1900-01-12 | 15 | 204 | 7 | 59 | 0 | 1 | 0 | 59 | 0 | 204 | 0 | 0 | 39.791 | 318.5 | -18.8415 | 86.148 | -75 | 14.9774 | 179.8924 | -6.5373 | 197.4627 | 62.5922 | 0 | 62.5922 | 59 | 62.5922 | 11/14/13:00
11 | 14 | 1900-01-13 | 15 | 129 | 4 | 59 | 0 | 1 | 0 | 59 | 0 | 129 | 0 | 0 | 39.791 | 318.5417 | -18.8516 | 86.148 | -75 | 14.9691 | 194.8903 | -3.6382 | 125.3618 | 39.7375 | 0 | 39.7375 | 59 | 39.7375 | 11/14/14:00
11 | 14 | 1900-01-14 | 15 | 103 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 103 | 0 | 0 | 39.791 | 318.5833 | -18.8616 | 86.148 | -75 | 14.9609 | 209.8882 | 0 | 103 | 32.6492 | 0 | 32.6492 | 59 | 32.6492 | 11/14/15:00
11 | 14 | 1900-01-15 | 15.6 | 68 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 68 | 0 | 0 | 39.791 | 318.625 | -18.8717 | 86.148 | -75 | 14.9526 | 224.8861 | 0 | 68 | 21.5548 | 0 | 21.5548 | 60.08 | 21.5548 | 11/14/16:00
11 | 14 | 1900-01-16 | 15.6 | 37 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 37 | 0 | 0 | 39.791 | 318.6667 | -18.8818 | 86.148 | -75 | 14.9442 | 239.8841 | 0 | 37 | 11.7284 | 0 | 11.7284 | 60.08 | 11.7284 | 11/14/17:00
11 | 14 | 1900-01-17 | 15.6 | 14 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 14 | 0 | 0 | 39.791 | 318.7083 | -18.8918 | 86.148 | -75 | 14.9359 | 254.882 | 0 | 14 | 4.4378 | 0 | 4.4378 | 60.08 | 4.4378 | 11/14/18:00
11 | 14 | 1900-01-18 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 318.75 | -18.9019 | 86.148 | -75 | 14.9275 | 269.8799 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 11/14/19:00
11 | 14 | 1900-01-19 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 318.7917 | -18.9119 | 86.148 | -75 | 14.9191 | 284.8778 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 11/14/20:00
11 | 14 | 1900-01-20 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 318.8333 | -18.9219 | 86.148 | -75 | 14.9107 | 299.8757 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 11/14/21:00
11 | 14 | 1900-01-21 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 318.875 | -18.932 | 86.148 | -75 | 14.9023 | 314.8736 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 11/14/22:00
11 | 14 | 1900-01-22 | 14.4 | 0 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 0 | 0 | 0 | 39.791 | 318.9167 | -18.942 | 86.148 | -75 | 14.8938 | 329.8715 | 0 | 0 | 0 | 0 | 0 | 57.92 | 0 | 11/14/23:00
11 | 14 | 1900-01-23 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 318.9583 | -18.952 | 86.148 | -75 | 14.8854 | 344.8693 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 11/14/24:00
11 | 15 | 1899-12-31 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 319 | -18.962 | 86.148 | -75 | 14.8769 | -0.13278 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 11/15/1:00
11 | 15 | 1900-01-01 | 15.6 | 0 | 0 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 0 | 0 | 0 | 39.791 | 319.0417 | -18.9719 | 86.148 | -75 | 14.8683 | 14.8651 | 0 | 0 | 0 | 0 | 0 | 60.08 | 0 | 11/15/2:00
11 | 15 | 1900-01-02 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 319.0833 | -18.9819 | 86.148 | -75 | 14.8598 | 29.863 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 11/15/3:00
11 | 15 | 1900-01-03 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 319.125 | -18.9919 | 86.148 | -75 | 14.8512 | 44.8608 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 11/15/4:00
11 | 15 | 1900-01-04 | 16.7 | 0 | 0 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 0 | 0 | 0 | 39.791 | 319.1667 | -19.0018 | 86.148 | -75 | 14.8426 | 59.8587 | 0 | 0 | 0 | 0 | 0 | 62.06 | 0 | 11/15/5:00
11 | 15 | 1900-01-05 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 319.2083 | -19.0117 | 86.148 | -75 | 14.834 | 74.8565 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 11/15/6:00
11 | 15 | 1900-01-06 | 16.1 | 0 | 0 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 0 | 0 | 0 | 39.791 | 319.25 | -19.0217 | 86.148 | -75 | 14.8254 | 89.8544 | 0 | 0 | 0 | 0 | 0 | 60.98 | 0 | 11/15/7:00
11 | 15 | 1900-01-07 | 16.1 | 16 | 3 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 16 | 0 | 0 | 39.791 | 319.2917 | -19.0316 | 86.148 | -75 | 14.8168 | 104.8522 | -1.1847 | 14.8153 | 4.6962 | 0 | 4.6962 | 60.98 | 4.6962 | 11/15/8:00
11 | 15 | 1900-01-08 | 16.7 | 56 | 1 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 56 | 0 | 0 | 39.791 | 319.3333 | -19.0415 | 86.148 | -75 | 14.8081 | 119.85 | -0.57032 | 55.4297 | 17.5702 | 0 | 17.5702 | 62.06 | 17.5702 | 11/15/9:00
11 | 15 | 1900-01-09 | 17.8 | 125 | 45 | 64.04 | 0 | 1 | 0 | 64.04 | 0 | 125 | 0 | 0 | 39.791 | 319.375 | -19.0514 | 86.148 | -75 | 14.7994 | 134.8478 | -32.4498 | 92.5502 | 29.3368 | 0 | 29.3368 | 64.04 | 29.3368 | 11/15/10:00
11 | 15 | 1900-01-10 | 12.8 | 102 | 5 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 102 | 0 | 0 | 39.791 | 319.4167 | -19.0613 | 86.148 | -75 | 14.7907 | 149.8457 | -4.1849 | 97.8151 | 31.0057 | 0 | 31.0057 | 55.04 | 31.0057 | 11/15/11:00
11 | 15 | 1900-01-11 | 12.8 | 114 | 12 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 114 | 0 | 0 | 39.791 | 319.4583 | -19.0712 | 86.148 | -75 | 14.7819 | 164.8435 | -10.9207 | 103.0793 | 32.6743 | 0 | 32.6743 | 55.04 | 32.6743 | 11/15/12:00
11 | 15 | 1900-01-12 | 12.8 | 134 | 2 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 134 | 0 | 0 | 39.791 | 319.5 | -19.0811 | 86.148 | -75 | 14.7732 | 179.8413 | -1.8708 | 132.1292 | 41.8827 | 0 | 41.8827 | 55.04 | 41.8827 | 11/15/13:00
11 | 15 | 1900-01-13 | 12.8 | 109 | 3 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 109 | 0 | 0 | 39.791 | 319.5417 | -19.0909 | 86.148 | -75 | 14.7644 | 194.8391 | -2.7337 | 106.2663 | 33.6846 | 0 | 33.6846 | 55.04 | 33.6846 | 11/15/14:00
11 | 15 | 1900-01-14 | 12.8 | 108 | 8 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 108 | 0 | 0 | 39.791 | 319.5833 | -19.1008 | 86.148 | -75 | 14.7556 | 209.8369 | -6.7141 | 101.2859 | 32.1059 | 0 | 32.1059 | 55.04 | 32.1059 | 11/15/15:00
11 | 15 | 1900-01-15 | 9.4 | 67 | 2 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 67 | 0 | 0 | 39.791 | 319.625 | -19.1106 | 86.148 | -75 | 14.7467 | 224.8347 | -1.4488 | 65.5512 | 20.7786 | 20.7786 | 0 | 0 | 0 | 11/15/16:00
11 | 15 | 1900-01-16 | 8.3 | 31 | 4 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 31 | 0 | 0 | 39.791 | 319.6667 | -19.1205 | 86.148 | -75 | 14.7379 | 239.8325 | -2.2979 | 28.7021 | 9.0981 | 9.0981 | 0 | 0 | 0 | 11/15/17:00
11 | 15 | 1900-01-17 | 7.2 | 8 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 8 | 0 | 0 | 39.791 | 319.7083 | -19.1303 | 86.148 | -75 | 14.729 | 254.8303 | 0 | 8 | 2.5359 | 2.5359 | 0 | 0 | 0 | 11/15/18:00
11 | 15 | 1900-01-18 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 319.75 | -19.1401 | 86.148 | -75 | 14.7201 | 269.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/15/19:00
11 | 15 | 1900-01-19 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 319.7917 | -19.1499 | 86.148 | -75 | 14.7112 | 284.8258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/15/20:00
11 | 15 | 1900-01-20 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 319.8333 | -19.1597 | 86.148 | -75 | 14.7023 | 299.8236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/15/21:00
11 | 15 | 1900-01-21 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 319.875 | -19.1695 | 86.148 | -75 | 14.6933 | 314.8213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/15/22:00
11 | 15 | 1900-01-22 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 319.9167 | -19.1793 | 86.148 | -75 | 14.6843 | 329.8191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/15/23:00
11 | 15 | 1900-01-23 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 319.9583 | -19.189 | 86.148 | -75 | 14.6753 | 344.8168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/15/24:00
11 | 16 | 1899-12-31 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320 | -19.1988 | 86.148 | -75 | 14.6663 | -0.18542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/1:00
11 | 16 | 1900-01-01 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.0417 | -19.2085 | 86.148 | -75 | 14.6573 | 14.8123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/2:00
11 | 16 | 1900-01-02 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.0833 | -19.2183 | 86.148 | -75 | 14.6482 | 29.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/3:00
11 | 16 | 1900-01-03 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.125 | -19.228 | 86.148 | -75 | 14.6391 | 44.8078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/4:00
11 | 16 | 1900-01-04 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.1667 | -19.2377 | 86.148 | -75 | 14.63 | 59.8055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/5:00
11 | 16 | 1900-01-05 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.2083 | -19.2474 | 86.148 | -75 | 14.6209 | 74.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/6:00
11 | 16 | 1900-01-06 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.25 | -19.2571 | 86.148 | -75 | 14.6117 | 89.8009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/7:00
11 | 16 | 1900-01-07 | 0 | 12 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 12 | 0 | 0 | 39.791 | 320.2917 | -19.2668 | 86.148 | -75 | 14.6025 | 104.7986 | 0 | 12 | 3.8038 | 3.8038 | 0 | 0 | 0 | 11/16/8:00
11 | 16 | 1900-01-08 | 0 | 84 | 125 | 32 | 1 | 0 | 32 | 0 | 0 | 84 | 0 | 0 | 39.791 | 320.3333 | -19.2765 | 86.148 | -75 | 14.5933 | 119.7963 | -71.4619 | 12.5381 | 3.9743 | 3.9743 | 0 | 0 | 0 | 11/16/9:00
11 | 16 | 1900-01-09 | 0 | 132 | 10 | 32 | 1 | 0 | 32 | 0 | 0 | 132 | 0 | 0 | 39.791 | 320.375 | -19.2862 | 86.148 | -75 | 14.5841 | 134.794 | -7.2237 | 124.7763 | 39.5519 | 39.5519 | 0 | 0 | 0 | 11/16/10:00
11 | 16 | 1900-01-10 | 0 | 163 | 7 | 32 | 1 | 0 | 32 | 0 | 0 | 163 | 0 | 0 | 39.791 | 320.4167 | -19.2958 | 86.148 | -75 | 14.5749 | 149.7917 | -5.8675 | 157.1325 | 49.8082 | 49.8082 | 0 | 0 | 0 | 11/16/11:00
11 | 16 | 1900-01-11 | 0 | 263 | 6 | 32 | 1 | 0 | 32 | 0 | 0 | 263 | 0 | 0 | 39.791 | 320.4583 | -19.3055 | 86.148 | -75 | 14.5656 | 164.7894 | -5.4681 | 257.5319 | 81.6331 | 81.6331 | 0 | 0 | 0 | 11/16/12:00
11 | 16 | 1900-01-12 | -1.1 | 244 | 3 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 244 | 0 | 0 | 39.791 | 320.5 | -19.3151 | 86.148 | -75 | 14.5563 | 179.7871 | -2.8104 | 241.1896 | 76.4529 | 76.4529 | 0 | 0 | 0 | 11/16/13:00
11 | 16 | 1900-01-13 | -0.6 | 187 | 8 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 187 | 0 | 0 | 39.791 | 320.5417 | -19.3247 | 86.148 | -75 | 14.547 | 194.7848 | -7.303 | 179.697 | 56.9608 | 56.9608 | 0 | 0 | 0 | 11/16/14:00
11 | 16 | 1900-01-14 | -2.2 | 200 | 8 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 200 | 0 | 0 | 39.791 | 320.5833 | -19.3344 | 86.148 | -75 | 14.5377 | 209.7824 | -6.7294 | 193.2706 | 61.2634 | 61.2634 | 0 | 0 | 0 | 11/16/15:00
11 | 16 | 1900-01-15 | -2.2 | 122 | 2 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 122 | 0 | 0 | 39.791 | 320.625 | -19.344 | 86.148 | -75 | 14.5283 | 224.7801 | -1.4532 | 120.5468 | 38.2112 | 38.2112 | 0 | 0 | 0 | 11/16/16:00
11 | 16 | 1900-01-16 | -2.8 | 70 | 2 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 70 | 0 | 0 | 39.791 | 320.6667 | -19.3536 | 86.148 | -75 | 14.519 | 239.7777 | -1.154 | 68.846 | 21.823 | 21.823 | 0 | 0 | 0 | 11/16/17:00
11 | 16 | 1900-01-17 | -3.3 | 20 | 30 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 20 | 0 | 0 | 39.791 | 320.7083 | -19.3632 | 86.148 | -75 | 14.5096 | 254.7754 | -12.0767 | 7.9233 | 2.5115 | 2.5115 | 0 | 0 | 0 | 11/16/18:00
11 | 16 | 1900-01-18 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.75 | -19.3727 | 86.148 | -75 | 14.5002 | 269.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/19:00
11 | 16 | 1900-01-19 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.7917 | -19.3823 | 86.148 | -75 | 14.4907 | 284.7707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/20:00
11 | 16 | 1900-01-20 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.8333 | -19.3919 | 86.148 | -75 | 14.4813 | 299.7683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/21:00
11 | 16 | 1900-01-21 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.875 | -19.4014 | 86.148 | -75 | 14.4718 | 314.7659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/22:00
11 | 16 | 1900-01-22 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.9167 | -19.411 | 86.148 | -75 | 14.4623 | 329.7636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/23:00
11 | 16 | 1900-01-23 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 320.9583 | -19.4205 | 86.148 | -75 | 14.4528 | 344.7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/16/24:00
11 | 17 | 1899-12-31 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321 | -19.43 | 86.148 | -75 | 14.4432 | -0.24119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/1:00
11 | 17 | 1900-01-01 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.0417 | -19.4395 | 86.148 | -75 | 14.4337 | 14.7564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/2:00
11 | 17 | 1900-01-02 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.0833 | -19.449 | 86.148 | -75 | 14.4241 | 29.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/3:00
11 | 17 | 1900-01-03 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.125 | -19.4585 | 86.148 | -75 | 14.4145 | 44.7516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/4:00
11 | 17 | 1900-01-04 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.1667 | -19.468 | 86.148 | -75 | 14.4048 | 59.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/5:00
11 | 17 | 1900-01-05 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.2083 | -19.4775 | 86.148 | -75 | 14.3952 | 74.7468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/6:00
11 | 17 | 1900-01-06 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.25 | -19.487 | 86.148 | -75 | 14.3855 | 89.7444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/7:00
11 | 17 | 1900-01-07 | -7.8 | 10 | 49 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 10 | 0 | 0 | 39.791 | 321.2917 | -19.4964 | 86.148 | -75 | 14.3758 | 104.742 | -19.4977 | -9.4977 | -3.0106 | -3.0106 | 0 | 0 | 0 | 11/17/8:00
11 | 17 | 1900-01-08 | -5.6 | 40 | 424 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 40 | 0 | 0 | 39.791 | 321.3333 | -19.5059 | 86.148 | -75 | 14.3661 | 119.7395 | -242.9441 | -202.9441 | -64.3297 | -64.3297 | 0 | 0 | 0 | 11/17/9:00
11 | 17 | 1900-01-09 | -3.9 | 56 | 694 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 56 | 0 | 0 | 39.791 | 321.375 | -19.5153 | 86.148 | -75 | 14.3564 | 134.7371 | -502.1472 | -446.1472 | -141.4209 | -141.4209 | 0 | 0 | 0 | 11/17/10:00
11 | 17 | 1900-01-10 | -2.8 | 128 | 516 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 128 | 0 | 0 | 39.791 | 321.4167 | -19.5247 | 86.148 | -75 | 14.3466 | 149.7347 | -433.1226 | -305.1226 | -96.7185 | -96.7185 | 0 | 0 | 0 | 11/17/11:00
11 | 17 | 1900-01-11 | -2.2 | 212 | 16 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 212 | 0 | 0 | 39.791 | 321.4583 | -19.5341 | 86.148 | -75 | 14.3369 | 164.7322 | -14.6015 | 197.3985 | 62.5719 | 62.5719 | 0 | 0 | 0 | 11/17/12:00
11 | 17 | 1900-01-12 | -1.7 | 267 | 3 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 267 | 0 | 0 | 39.791 | 321.5 | -19.5435 | 86.148 | -75 | 14.3271 | 179.7298 | -2.8146 | 264.1854 | 83.7422 | 83.7422 | 0 | 0 | 0 | 11/17/13:00
11 | 17 | 1900-01-13 | -1.1 | 275 | 5 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 275 | 0 | 0 | 39.791 | 321.5417 | -19.5529 | 86.148 | -75 | 14.3172 | 194.7273 | -4.5724 | 270.4276 | 85.7208 | 85.7208 | 0 | 0 | 0 | 11/17/14:00
11 | 17 | 1900-01-14 | 0 | 174 | 4 | 32 | 1 | 0 | 32 | 0 | 0 | 174 | 0 | 0 | 39.791 | 321.5833 | -19.5623 | 86.148 | -75 | 14.3074 | 209.7248 | -3.3722 | 170.6278 | 54.086 | 54.086 | 0 | 0 | 0 | 11/17/15:00
11 | 17 | 1900-01-15 | 0.6 | 138 | 4 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 138 | 0 | 0 | 39.791 | 321.625 | -19.5717 | 86.148 | -75 | 14.2975 | 224.7224 | -2.9152 | 135.0848 | 42.8195 | 42.8195 | 0 | 0 | 0 | 11/17/16:00
11 | 17 | 1900-01-16 | 1.1 | 55 | 3 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 55 | 0 | 0 | 39.791 | 321.6667 | -19.581 | 86.148 | -75 | 14.2876 | 239.7199 | -1.7386 | 53.2614 | 16.8829 | 16.8829 | 0 | 0 | 0 | 11/17/17:00
11 | 17 | 1900-01-17 | 0.6 | 12 | 17 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 12 | 0 | 0 | 39.791 | 321.7083 | -19.5904 | 86.148 | -75 | 14.2777 | 254.7174 | -6.8916 | 5.1084 | 1.6193 | 1.6193 | 0 | 0 | 0 | 11/17/18:00
11 | 17 | 1900-01-18 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.75 | -19.5997 | 86.148 | -75 | 14.2678 | 269.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/19:00
11 | 17 | 1900-01-19 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.7917 | -19.6091 | 86.148 | -75 | 14.2579 | 284.7125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/20:00
11 | 17 | 1900-01-20 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.8333 | -19.6184 | 86.148 | -75 | 14.2479 | 299.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/21:00
11 | 17 | 1900-01-21 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.875 | -19.6277 | 86.148 | -75 | 14.2379 | 314.7075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/22:00
11 | 17 | 1900-01-22 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.9167 | -19.637 | 86.148 | -75 | 14.2279 | 329.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/23:00
11 | 17 | 1900-01-23 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 321.9583 | -19.6463 | 86.148 | -75 | 14.2179 | 344.7025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/17/24:00
11 | 18 | 1899-12-31 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322 | -19.6556 | 86.148 | -75 | 14.2078 | -0.30004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/1:00
11 | 18 | 1900-01-01 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.0417 | -19.6649 | 86.148 | -75 | 14.1977 | 14.6974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/2:00
11 | 18 | 1900-01-02 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.0833 | -19.6741 | 86.148 | -75 | 14.1877 | 29.6949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/3:00
11 | 18 | 1900-01-03 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.125 | -19.6834 | 86.148 | -75 | 14.1775 | 44.6924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/4:00
11 | 18 | 1900-01-04 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.1667 | -19.6926 | 86.148 | -75 | 14.1674 | 59.6899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/5:00
11 | 18 | 1900-01-05 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.2083 | -19.7019 | 86.148 | -75 | 14.1572 | 74.6873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/6:00
11 | 18 | 1900-01-06 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.25 | -19.7111 | 86.148 | -75 | 14.1471 | 89.6848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/7:00
11 | 18 | 1900-01-07 | -6.7 | 9 | 71 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 9 | 0 | 0 | 39.791 | 322.2917 | -19.7203 | 86.148 | -75 | 14.1369 | 104.6822 | -28.349 | -19.349 | -6.1333 | -6.1333 | 0 | 0 | 0 | 11/18/8:00
11 | 18 | 1900-01-08 | -6.1 | 53 | 193 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 53 | 0 | 0 | 39.791 | 322.3333 | -19.7295 | 86.148 | -75 | 14.1266 | 119.6797 | -110.8165 | -57.8165 | -18.3268 | -18.3268 | 0 | 0 | 0 | 11/18/9:00
11 | 18 | 1900-01-09 | -5.6 | 108 | 286 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 108 | 0 | 0 | 39.791 | 322.375 | -19.7387 | 86.148 | -75 | 14.1164 | 134.6771 | -207.2525 | -99.2525 | -31.4613 | -31.4613 | 0 | 0 | 0 | 11/18/10:00
11 | 18 | 1900-01-10 | -4.4 | 178 | 227 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 178 | 0 | 0 | 39.791 | 322.4167 | -19.7479 | 86.148 | -75 | 14.1061 | 149.6745 | -190.7893 | -12.7893 | -4.054 | -4.054 | 0 | 0 | 0 | 11/18/11:00
11 | 18 | 1900-01-11 | -3.9 | 176 | 474 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 176 | 0 | 0 | 39.791 | 322.4583 | -19.7571 | 86.148 | -75 | 14.0959 | 164.672 | -433.1251 | -257.1251 | -81.5042 | -81.5042 | 0 | 0 | 0 | 11/18/12:00
11 | 18 | 1900-01-12 | -3.3 | 153 | 574 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 153 | 0 | 0 | 39.791 | 322.5 | -19.7662 | 86.148 | -75 | 14.0856 | 179.6694 | -539.2918 | -386.2918 | -122.4477 | -122.4477 | 0 | 0 | 0 | 11/18/13:00
11 | 18 | 1900-01-13 | -2.2 | 137 | 704 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 137 | 0 | 0 | 39.791 | 322.5417 | -19.7754 | 86.148 | -75 | 14.0752 | 194.6668 | -644.8907 | -507.8907 | -160.9925 | -160.9925 | 0 | 0 | 0 | 11/18/14:00
11 | 18 | 1900-01-14 | -1.1 | 75 | 792 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 75 | 0 | 0 | 39.791 | 322.5833 | -19.7845 | 86.148 | -75 | 14.0649 | 209.6642 | -669.1565 | -594.1565 | -188.3372 | -188.3372 | 0 | 0 | 0 | 11/18/15:00
11 | 18 | 1900-01-15 | -1.7 | 74 | 571 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 74 | 0 | 0 | 39.791 | 322.625 | -19.7937 | 86.148 | -75 | 14.0545 | 224.6616 | -417.3787 | -343.3787 | -108.8451 | -108.8451 | 0 | 0 | 0 | 11/18/16:00
11 | 18 | 1900-01-16 | -1.7 | 59 | 199 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 59 | 0 | 0 | 39.791 | 322.6667 | -19.8028 | 86.148 | -75 | 14.0441 | 239.659 | -115.82 | -56.82 | -18.0109 | -18.0109 | 0 | 0 | 0 | 11/18/17:00
11 | 18 | 1900-01-17 | -3.9 | 15 | 20 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 15 | 0 | 0 | 39.791 | 322.7083 | -19.8119 | 86.148 | -75 | 14.0337 | 254.6564 | -8.164 | 6.836 | 2.1669 | 2.1669 | 0 | 0 | 0 | 11/18/18:00
11 | 18 | 1900-01-18 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.75 | -19.821 | 86.148 | -75 | 14.0233 | 269.6538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/19:00
11 | 18 | 1900-01-19 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.7917 | -19.8301 | 86.148 | -75 | 14.0128 | 284.6512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/20:00
11 | 18 | 1900-01-20 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.8333 | -19.8392 | 86.148 | -75 | 14.0024 | 299.6486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/21:00
11 | 18 | 1900-01-21 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.875 | -19.8483 | 86.148 | -75 | 13.9919 | 314.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/22:00
11 | 18 | 1900-01-22 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.9167 | -19.8573 | 86.148 | -75 | 13.9814 | 329.6433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/23:00
11 | 18 | 1900-01-23 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 322.9583 | -19.8664 | 86.148 | -75 | 13.9708 | 344.6407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/18/24:00
11 | 19 | 1899-12-31 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323 | -19.8754 | 86.148 | -75 | 13.9603 | -0.36193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/1:00
11 | 19 | 1900-01-01 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.0417 | -19.8845 | 86.148 | -75 | 13.9497 | 14.6354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/2:00
11 | 19 | 1900-01-02 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.0833 | -19.8935 | 86.148 | -75 | 13.9391 | 29.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/3:00
11 | 19 | 1900-01-03 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.125 | -19.9025 | 86.148 | -75 | 13.9285 | 44.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/4:00
11 | 19 | 1900-01-04 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.1667 | -19.9115 | 86.148 | -75 | 13.9179 | 59.6275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/5:00
11 | 19 | 1900-01-05 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.2083 | -19.9205 | 86.148 | -75 | 13.9072 | 74.6248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/6:00
11 | 19 | 1900-01-06 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.25 | -19.9295 | 86.148 | -75 | 13.8965 | 89.6221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/7:00
11 | 19 | 1900-01-07 | -1.7 | 4 | 1 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 4 | 0 | 0 | 39.791 | 323.2917 | -19.9385 | 86.148 | -75 | 13.8858 | 104.6195 | -0.40056 | 3.5994 | 1.141 | 1.141 | 0 | 0 | 0 | 11/19/8:00
11 | 19 | 1900-01-08 | -1.1 | 44 | 24 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 44 | 0 | 0 | 39.791 | 323.3333 | -19.9474 | 86.148 | -75 | 13.8751 | 119.6168 | -13.8069 | 30.1931 | 9.5707 | 9.5707 | 0 | 0 | 0 | 11/19/9:00
11 | 19 | 1900-01-09 | 1.1 | 116 | 12 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 116 | 0 | 0 | 39.791 | 323.375 | -19.9564 | 86.148 | -75 | 13.8644 | 134.6141 | -8.7082 | 107.2918 | 34.0096 | 34.0096 | 0 | 0 | 0 | 11/19/10:00
11 | 19 | 1900-01-10 | 3.3 | 206 | 6 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 206 | 0 | 0 | 39.791 | 323.4167 | -19.9653 | 86.148 | -75 | 13.8536 | 149.6114 | -5.049 | 200.951 | 63.6979 | 63.6979 | 0 | 0 | 0 | 11/19/11:00
11 | 19 | 1900-01-11 | 6.7 | 128 | 674 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 128 | 0 | 0 | 39.791 | 323.4583 | -19.9742 | 86.148 | -75 | 13.8428 | 164.6087 | -616.6303 | -488.6303 | -154.8873 | -154.8873 | 0 | 0 | 0 | 11/19/12:00
11 | 19 | 1900-01-12 | 7.8 | 220 | 119 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 220 | 0 | 0 | 39.791 | 323.5 | -19.9832 | 86.148 | -75 | 13.832 | 179.606 | -111.9573 | 108.0427 | 34.2477 | 34.2477 | 0 | 0 | 0 | 11/19/13:00
11 | 19 | 1900-01-13 | 9.4 | 123 | 673 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 123 | 0 | 0 | 39.791 | 323.5417 | -19.9921 | 86.148 | -75 | 13.8212 | 194.6033 | -617.5179 | -494.5179 | -156.7535 | -156.7535 | 0 | 0 | 0 | 11/19/14:00
11 | 19 | 1900-01-14 | 10.6 | 67 | 732 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 67 | 0 | 0 | 39.791 | 323.5833 | -20.001 | 86.148 | -75 | 13.8104 | 209.6006 | -619.7889 | -552.7889 | -175.2244 | -175.2244 | 0 | 0 | 0 | 11/19/15:00
11 | 19 | 1900-01-15 | 11.1 | 68 | 609 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 68 | 0 | 0 | 39.791 | 323.625 | -20.0099 | 86.148 | -75 | 13.7995 | 224.5979 | -446.4542 | -378.4542 | -119.9634 | -119.9634 | 0 | 0 | 0 | 11/19/16:00
11 | 19 | 1900-01-16 | 10.6 | 58 | 298 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 58 | 0 | 0 | 39.791 | 323.6667 | -20.0187 | 86.148 | -75 | 13.7886 | 239.5952 | -174.1733 | -116.1733 | -36.8249 | -36.8249 | 0 | 0 | 0 | 11/19/17:00
11 | 19 | 1900-01-17 | 6.7 | 14 | 33 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 14 | 0 | 0 | 39.791 | 323.7083 | -20.0276 | 86.148 | -75 | 13.7777 | 254.5924 | -13.5624 | 0.43764 | 0.13872 | 0.13872 | 0 | 0 | 0 | 11/19/18:00
11 | 19 | 1900-01-18 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.75 | -20.0365 | 86.148 | -75 | 13.7668 | 269.5897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/19:00
11 | 19 | 1900-01-19 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.7917 | -20.0453 | 86.148 | -75 | 13.7558 | 284.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/20:00
11 | 19 | 1900-01-20 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.8333 | -20.0542 | 86.148 | -75 | 13.7449 | 299.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/21:00
11 | 19 | 1900-01-21 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.875 | -20.063 | 86.148 | -75 | 13.7339 | 314.5815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/22:00
11 | 19 | 1900-01-22 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.9167 | -20.0718 | 86.148 | -75 | 13.7229 | 329.5787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/23:00
11 | 19 | 1900-01-23 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 323.9583 | -20.0806 | 86.148 | -75 | 13.7119 | 344.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/19/24:00
11 | 20 | 1899-12-31 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324 | -20.0894 | 86.148 | -75 | 13.7008 | -0.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/1:00
11 | 20 | 1900-01-01 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.0417 | -20.0982 | 86.148 | -75 | 13.6897 | 14.5704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/2:00
11 | 20 | 1900-01-02 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.0833 | -20.107 | 86.148 | -75 | 13.6787 | 29.5677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/3:00
11 | 20 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.125 | -20.1158 | 86.148 | -75 | 13.6675 | 44.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/4:00
11 | 20 | 1900-01-04 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.1667 | -20.1245 | 86.148 | -75 | 13.6564 | 59.5621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/5:00
11 | 20 | 1900-01-05 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.2083 | -20.1333 | 86.148 | -75 | 13.6453 | 74.5593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/6:00
11 | 20 | 1900-01-06 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.25 | -20.142 | 86.148 | -75 | 13.6341 | 89.5565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/7:00
11 | 20 | 1900-01-07 | 8.3 | 8 | 33 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 8 | 0 | 0 | 39.791 | 324.2917 | -20.1507 | 86.148 | -75 | 13.6229 | 104.5537 | -13.2573 | -5.2573 | -1.6665 | -1.6665 | 0 | 0 | 0 | 11/20/8:00
11 | 20 | 1900-01-08 | 10 | 37 | 371 | 50 | 1 | 0 | 50 | 0 | 0 | 37 | 0 | 0 | 39.791 | 324.3333 | -20.1594 | 86.148 | -75 | 13.6117 | 119.5509 | -213.811 | -176.811 | -56.046 | -56.046 | 0 | 0 | 0 | 11/20/9:00
11 | 20 | 1900-01-09 | 11.7 | 52 | 666 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 52 | 0 | 0 | 39.791 | 324.375 | -20.1681 | 86.148 | -75 | 13.6005 | 134.5481 | -483.9356 | -431.9356 | -136.9161 | -136.9161 | 0 | 0 | 0 | 11/20/10:00
11 | 20 | 1900-01-10 | 13.3 | 63 | 783 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 63 | 0 | 0 | 39.791 | 324.4167 | -20.1768 | 86.148 | -75 | 13.5892 | 149.5453 | -659.6513 | -596.6513 | -189.128 | 0 | -189.128 | 55.94 | -189.128 | 11/20/11:00
11 | 20 | 1900-01-11 | 15 | 158 | 503 | 59 | 0 | 1 | 0 | 59 | 0 | 158 | 0 | 0 | 39.791 | 324.4583 | -20.1855 | 86.148 | -75 | 13.578 | 164.5425 | -460.7172 | -302.7172 | -95.9561 | 0 | -95.9561 | 59 | -95.9561 | 11/20/12:00
11 | 20 | 1900-01-12 | 16.1 | 169 | 542 | 60.98 | 0 | 1 | 0 | 60.98 | 0 | 169 | 0 | 0 | 39.791 | 324.5 | -20.1942 | 86.148 | -75 | 13.5667 | 179.5397 | -510.5927 | -341.5927 | -108.2789 | 0 | -108.2789 | 60.98 | -108.2789 | 11/20/13:00
11 | 20 | 1900-01-13 | 16.7 | 220 | 168 | 62.06 | 0 | 1 | 0 | 62.06 | 0 | 220 | 0 | 0 | 39.791 | 324.5417 | -20.2029 | 86.148 | -75 | 13.5554 | 194.5368 | -154.399 | 65.601 | 20.7944 | 0 | 20.7944 | 62.06 | 20.7944 | 11/20/14:00
11 | 20 | 1900-01-14 | 15.6 | 194 | 313 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 194 | 0 | 0 | 39.791 | 324.5833 | -20.2115 | 86.148 | -75 | 13.544 | 209.534 | -265.5755 | -71.5755 | -22.6882 | 0 | -22.6882 | 60.08 | -22.6882 | 11/20/15:00
11 | 20 | 1900-01-15 | 14.4 | 77 | 540 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 77 | 0 | 0 | 39.791 | 324.625 | -20.2202 | 86.148 | -75 | 13.5327 | 224.5312 | -397.0069 | -320.0069 | -101.4366 | 0 | -101.4366 | 57.92 | -101.4366 | 11/20/16:00
11 | 20 | 1900-01-16 | 12.2 | 55 | 221 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 55 | 0 | 0 | 39.791 | 324.6667 | -20.2288 | 86.148 | -75 | 13.5213 | 239.5283 | -129.7074 | -74.7074 | -23.681 | -23.681 | 0 | 0 | 0 | 11/20/17:00
11 | 20 | 1900-01-17 | 11.7 | 10 | 28 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 10 | 0 | 0 | 39.791 | 324.7083 | -20.2374 | 86.148 | -75 | 13.5099 | 254.5255 | -11.5846 | -1.5846 | -0.50229 | -0.50229 | 0 | 0 | 0 | 11/20/18:00
11 | 20 | 1900-01-18 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.75 | -20.246 | 86.148 | -75 | 13.4985 | 269.5226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/19:00
11 | 20 | 1900-01-19 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.7917 | -20.2546 | 86.148 | -75 | 13.4871 | 284.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/20:00
11 | 20 | 1900-01-20 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.8333 | -20.2632 | 86.148 | -75 | 13.4756 | 299.5169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/21:00
11 | 20 | 1900-01-21 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.875 | -20.2718 | 86.148 | -75 | 13.4642 | 314.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/22:00
11 | 20 | 1900-01-22 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.9167 | -20.2804 | 86.148 | -75 | 13.4527 | 329.5112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/23:00
11 | 20 | 1900-01-23 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 324.9583 | -20.2889 | 86.148 | -75 | 13.4412 | 344.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/20/24:00
11 | 21 | 1899-12-31 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325 | -20.2975 | 86.148 | -75 | 13.4296 | -0.49459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/1:00
11 | 21 | 1900-01-01 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.0417 | -20.306 | 86.148 | -75 | 13.4181 | 14.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/2:00
11 | 21 | 1900-01-02 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.0833 | -20.3145 | 86.148 | -75 | 13.4065 | 29.4996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/3:00
11 | 21 | 1900-01-03 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.125 | -20.3231 | 86.148 | -75 | 13.3949 | 44.4967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/4:00
11 | 21 | 1900-01-04 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.1667 | -20.3316 | 86.148 | -75 | 13.3833 | 59.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/5:00
11 | 21 | 1900-01-05 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.2083 | -20.3401 | 86.148 | -75 | 13.3717 | 74.4909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/6:00
11 | 21 | 1900-01-06 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.25 | -20.3486 | 86.148 | -75 | 13.36 | 89.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/7:00
11 | 21 | 1900-01-07 | -2.2 | 9 | 51 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 9 | 0 | 0 | 39.791 | 325.2917 | -20.357 | 86.148 | -75 | 13.3484 | 104.4851 | -20.544 | -11.544 | -3.6592 | -3.6592 | 0 | 0 | 0 | 11/21/8:00
11 | 21 | 1900-01-08 | 0.6 | 68 | 178 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 68 | 0 | 0 | 39.791 | 325.3333 | -20.3655 | 86.148 | -75 | 13.3367 | 119.4822 | -102.7496 | -34.7496 | -11.015 | -11.015 | 0 | 0 | 0 | 11/21/9:00
11 | 21 | 1900-01-09 | 1.7 | 146 | 159 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 146 | 0 | 0 | 39.791 | 325.375 | -20.374 | 86.148 | -75 | 13.325 | 134.4792 | -115.6722 | 30.3278 | 9.6134 | 9.6134 | 0 | 0 | 0 | 11/21/10:00
11 | 21 | 1900-01-10 | 1.7 | 160 | 77 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 160 | 0 | 0 | 39.791 | 325.4167 | -20.3824 | 86.148 | -75 | 13.3132 | 149.4763 | -64.9385 | 95.0615 | 30.1328 | 30.1328 | 0 | 0 | 0 | 11/21/11:00
11 | 21 | 1900-01-11 | 2.2 | 170 | 524 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 170 | 0 | 0 | 39.791 | 325.4583 | -20.3908 | 86.148 | -75 | 13.3015 | 164.4734 | -480.4753 | -310.4753 | -98.4152 | -98.4152 | 0 | 0 | 0 | 11/21/12:00
11 | 21 | 1900-01-12 | 2.8 | 172 | 84 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 172 | 0 | 0 | 39.791 | 325.5 | -20.3993 | 86.148 | -75 | 13.2897 | 179.4704 | -79.2321 | 92.7679 | 29.4058 | 29.4058 | 0 | 0 | 0 | 11/21/13:00
11 | 21 | 1900-01-13 | 2.2 | 227 | 145 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 227 | 0 | 0 | 39.791 | 325.5417 | -20.4077 | 86.148 | -75 | 13.2779 | 194.4675 | -133.47 | 93.53 | 29.6474 | 29.6474 | 0 | 0 | 0 | 11/21/14:00
11 | 21 | 1900-01-14 | 2.8 | 156 | 409 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 156 | 0 | 0 | 39.791 | 325.5833 | -20.4161 | 86.148 | -75 | 13.2661 | 209.4645 | -347.7433 | -191.7433 | -60.7793 | -60.7793 | 0 | 0 | 0 | 11/21/15:00
11 | 21 | 1900-01-15 | 2.8 | 132 | 202 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 132 | 0 | 0 | 39.791 | 325.625 | -20.4245 | 86.148 | -75 | 13.2543 | 224.4616 | -148.9291 | -16.9291 | -5.3662 | -5.3662 | 0 | 0 | 0 | 11/21/16:00
11 | 21 | 1900-01-16 | 1.7 | 30 | 496 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 30 | 0 | 0 | 39.791 | 325.6667 | -20.4328 | 86.148 | -75 | 13.2425 | 239.4586 | -292.3035 | -262.3035 | -83.1456 | -83.1456 | 0 | 0 | 0 | 11/21/17:00
11 | 21 | 1900-01-17 | 1.1 | 11 | 59 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 11 | 0 | 0 | 39.791 | 325.7083 | -20.4412 | 86.148 | -75 | 13.2306 | 254.4556 | -24.5713 | -13.5713 | -4.3019 | -4.3019 | 0 | 0 | 0 | 11/21/18:00
11 | 21 | 1900-01-18 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.75 | -20.4496 | 86.148 | -75 | 13.2187 | 269.4527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/19:00
11 | 21 | 1900-01-19 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.7917 | -20.4579 | 86.148 | -75 | 13.2068 | 284.4497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/20:00
11 | 21 | 1900-01-20 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.8333 | -20.4663 | 86.148 | -75 | 13.1949 | 299.4467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/21:00
11 | 21 | 1900-01-21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.875 | -20.4746 | 86.148 | -75 | 13.1829 | 314.4437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/22:00
11 | 21 | 1900-01-22 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.9167 | -20.4829 | 86.148 | -75 | 13.171 | 329.4407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/23:00
11 | 21 | 1900-01-23 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 325.9583 | -20.4912 | 86.148 | -75 | 13.159 | 344.4377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/21/24:00
11 | 22 | 1899-12-31 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326 | -20.4995 | 86.148 | -75 | 13.147 | -0.56525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/1:00
11 | 22 | 1900-01-01 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.0417 | -20.5078 | 86.148 | -75 | 13.135 | 14.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/2:00
11 | 22 | 1900-01-02 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.0833 | -20.5161 | 86.148 | -75 | 13.1229 | 29.4287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/3:00
11 | 22 | 1900-01-03 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.125 | -20.5244 | 86.148 | -75 | 13.1109 | 44.4257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/4:00
11 | 22 | 1900-01-04 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.1667 | -20.5326 | 86.148 | -75 | 13.0988 | 59.4227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/5:00
11 | 22 | 1900-01-05 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.2083 | -20.5409 | 86.148 | -75 | 13.0867 | 74.4197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/6:00
11 | 22 | 1900-01-06 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.25 | -20.5491 | 86.148 | -75 | 13.0746 | 89.4166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/7:00
11 | 22 | 1900-01-07 | -1.1 | 3 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 3 | 0 | 0 | 39.791 | 326.2917 | -20.5573 | 86.148 | -75 | 13.0624 | 104.4136 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 11/22/8:00
11 | 22 | 1900-01-08 | -0.6 | 48 | 9 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 48 | 0 | 0 | 39.791 | 326.3333 | -20.5655 | 86.148 | -75 | 13.0503 | 119.4106 | -5.2028 | 42.7972 | 13.566 | 13.566 | 0 | 0 | 0 | 11/22/9:00
11 | 22 | 1900-01-09 | 0 | 119 | 39 | 32 | 1 | 0 | 32 | 0 | 0 | 119 | 0 | 0 | 39.791 | 326.375 | -20.5737 | 86.148 | -75 | 13.0381 | 134.4075 | -28.4033 | 90.5967 | 28.7176 | 28.7176 | 0 | 0 | 0 | 11/22/10:00
11 | 22 | 1900-01-10 | 0.6 | 69 | 2 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 69 | 0 | 0 | 39.791 | 326.4167 | -20.5819 | 86.148 | -75 | 13.0259 | 149.4045 | -1.6884 | 67.3116 | 21.3366 | 21.3366 | 0 | 0 | 0 | 11/22/11:00
11 | 22 | 1900-01-11 | 1.1 | 231 | 6 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 231 | 0 | 0 | 39.791 | 326.4583 | -20.5901 | 86.148 | -75 | 13.0137 | 164.4014 | -5.5073 | 225.4927 | 71.4773 | 71.4773 | 0 | 0 | 0 | 11/22/12:00
11 | 22 | 1900-01-12 | 1.7 | 210 | 4 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 210 | 0 | 0 | 39.791 | 326.5 | -20.5983 | 86.148 | -75 | 13.0014 | 179.3984 | -3.7775 | 206.2225 | 65.3689 | 65.3689 | 0 | 0 | 0 | 11/22/13:00
11 | 22 | 1900-01-13 | 1.7 | 204 | 3 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 204 | 0 | 0 | 39.791 | 326.5417 | -20.6064 | 86.148 | -75 | 12.9892 | 194.3953 | -2.7657 | 201.2343 | 63.7878 | 63.7878 | 0 | 0 | 0 | 11/22/14:00
11 | 22 | 1900-01-14 | 1.1 | 158 | 4 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 158 | 0 | 0 | 39.791 | 326.5833 | -20.6146 | 86.148 | -75 | 12.9769 | 209.3922 | -3.4078 | 154.5922 | 49.003 | 49.003 | 0 | 0 | 0 | 11/22/15:00
11 | 22 | 1900-01-15 | 0.6 | 138 | 3 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 138 | 0 | 0 | 39.791 | 326.625 | -20.6227 | 86.148 | -75 | 12.9646 | 224.3892 | -2.218 | 135.782 | 43.0405 | 43.0405 | 0 | 0 | 0 | 11/22/16:00
11 | 22 | 1900-01-16 | 0 | 54 | 2 | 32 | 1 | 0 | 32 | 0 | 0 | 54 | 0 | 0 | 39.791 | 326.6667 | -20.6309 | 86.148 | -75 | 12.9523 | 239.3861 | -1.1834 | 52.8166 | 16.7419 | 16.7419 | 0 | 0 | 0 | 11/22/17:00
11 | 22 | 1900-01-17 | -0.6 | 10 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 10 | 0 | 0 | 39.791 | 326.7083 | -20.639 | 86.148 | -75 | 12.94 | 254.383 | 0 | 10 | 3.1698 | 3.1698 | 0 | 0 | 0 | 11/22/18:00
11 | 22 | 1900-01-18 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.75 | -20.6471 | 86.148 | -75 | 12.9276 | 269.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/19:00
11 | 22 | 1900-01-19 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.7917 | -20.6552 | 86.148 | -75 | 12.9152 | 284.3768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/20:00
11 | 22 | 1900-01-20 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.8333 | -20.6633 | 86.148 | -75 | 12.9029 | 299.3737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/21:00
11 | 22 | 1900-01-21 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.875 | -20.6713 | 86.148 | -75 | 12.8904 | 314.3706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/22:00
11 | 22 | 1900-01-22 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.9167 | -20.6794 | 86.148 | -75 | 12.878 | 329.3675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/23:00
11 | 22 | 1900-01-23 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 326.9583 | -20.6874 | 86.148 | -75 | 12.8656 | 344.3644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/22/24:00
11 | 23 | 1899-12-31 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327 | -20.6955 | 86.148 | -75 | 12.8531 | -0.63872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/1:00
11 | 23 | 1900-01-01 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.0417 | -20.7035 | 86.148 | -75 | 12.8406 | 14.3582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/2:00
11 | 23 | 1900-01-02 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.0833 | -20.7115 | 86.148 | -75 | 12.8281 | 29.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/3:00
11 | 23 | 1900-01-03 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.125 | -20.7196 | 86.148 | -75 | 12.8156 | 44.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/4:00
11 | 23 | 1900-01-04 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.1667 | -20.7276 | 86.148 | -75 | 12.8031 | 59.3488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/5:00
11 | 23 | 1900-01-05 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.2083 | -20.7355 | 86.148 | -75 | 12.7905 | 74.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/6:00
11 | 23 | 1900-01-06 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.25 | -20.7435 | 86.148 | -75 | 12.7779 | 89.3425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/7:00
11 | 23 | 1900-01-07 | -3.9 | 9 | 13 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 9 | 0 | 0 | 39.791 | 327.2917 | -20.7515 | 86.148 | -75 | 12.7653 | 104.3393 | -5.2613 | 3.7387 | 1.1851 | 1.1851 | 0 | 0 | 0 | 11/23/8:00
11 | 23 | 1900-01-08 | -2.8 | 61 | 29 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 61 | 0 | 0 | 39.791 | 327.3333 | -20.7594 | 86.148 | -75 | 12.7527 | 119.3362 | -16.7868 | 44.2132 | 14.0148 | 14.0148 | 0 | 0 | 0 | 11/23/9:00
11 | 23 | 1900-01-09 | -2.2 | 107 | 58 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 107 | 0 | 0 | 39.791 | 327.375 | -20.7674 | 86.148 | -75 | 12.7401 | 134.333 | -42.2822 | 64.7178 | 20.5144 | 20.5144 | 0 | 0 | 0 | 11/23/10:00
11 | 23 | 1900-01-10 | -1.7 | 180 | 315 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 180 | 0 | 0 | 39.791 | 327.4167 | -20.7753 | 86.148 | -75 | 12.7274 | 149.3299 | -266.1546 | -86.1546 | -27.3095 | -27.3095 | 0 | 0 | 0 | 11/23/11:00
11 | 23 | 1900-01-11 | -1.7 | 207 | 15 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 207 | 0 | 0 | 39.791 | 327.4583 | -20.7832 | 86.148 | -75 | 12.7147 | 164.3267 | -13.7814 | 193.2186 | 61.2469 | 61.2469 | 0 | 0 | 0 | 11/23/12:00
11 | 23 | 1900-01-12 | -1.7 | 173 | 1 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 173 | 0 | 0 | 39.791 | 327.5 | -20.7912 | 86.148 | -75 | 12.702 | 179.3235 | -0.94547 | 172.0545 | 54.5383 | 54.5383 | 0 | 0 | 0 | 11/23/13:00
11 | 23 | 1900-01-13 | -1.7 | 194 | 19 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 194 | 0 | 0 | 39.791 | 327.5417 | -20.7991 | 86.148 | -75 | 12.6893 | 194.3203 | -17.5417 | 176.4583 | 55.9342 | 55.9342 | 0 | 0 | 0 | 11/23/14:00
11 | 23 | 1900-01-14 | -1.7 | 177 | 10 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 177 | 0 | 0 | 39.791 | 327.5833 | -20.807 | 86.148 | -75 | 12.6766 | 209.3171 | -8.5361 | 168.4639 | 53.4001 | 53.4001 | 0 | 0 | 0 | 11/23/15:00
11 | 23 | 1900-01-15 | -1.7 | 127 | 1 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 127 | 0 | 0 | 39.791 | 327.625 | -20.8148 | 86.148 | -75 | 12.6638 | 224.314 | -0.74133 | 126.2587 | 40.0218 | 40.0218 | 0 | 0 | 0 | 11/23/16:00
11 | 23 | 1900-01-16 | -2.2 | 41 | 357 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 41 | 0 | 0 | 39.791 | 327.6667 | -20.8227 | 86.148 | -75 | 12.6511 | 239.3108 | -212.078 | -171.078 | -54.2287 | -54.2287 | 0 | 0 | 0 | 11/23/17:00
11 | 23 | 1900-01-17 | -4.4 | 9 | 72 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 9 | 0 | 0 | 39.791 | 327.7083 | -20.8306 | 86.148 | -75 | 12.6383 | 254.3076 | -30.3715 | -21.3715 | -6.7744 | -6.7744 | 0 | 0 | 0 | 11/23/18:00
11 | 23 | 1900-01-18 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.75 | -20.8384 | 86.148 | -75 | 12.6255 | 269.3044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/19:00
11 | 23 | 1900-01-19 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.7917 | -20.8463 | 86.148 | -75 | 12.6127 | 284.3012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/20:00
11 | 23 | 1900-01-20 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.8333 | -20.8541 | 86.148 | -75 | 12.5998 | 299.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/21:00
11 | 23 | 1900-01-21 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.875 | -20.8619 | 86.148 | -75 | 12.5869 | 314.2947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/22:00
11 | 23 | 1900-01-22 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.9167 | -20.8697 | 86.148 | -75 | 12.5741 | 329.2915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/23:00
11 | 23 | 1900-01-23 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 327.9583 | -20.8775 | 86.148 | -75 | 12.5612 | 344.2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/23/24:00
11 | 24 | 1899-12-31 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328 | -20.8853 | 86.148 | -75 | 12.5483 | -0.71494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/1:00
11 | 24 | 1900-01-01 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.0417 | -20.8931 | 86.148 | -75 | 12.5353 | 14.2818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/2:00
11 | 24 | 1900-01-02 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.0833 | -20.9008 | 86.148 | -75 | 12.5224 | 29.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/3:00
11 | 24 | 1900-01-03 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.125 | -20.9086 | 86.148 | -75 | 12.5094 | 44.2753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/4:00
11 | 24 | 1900-01-04 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.1667 | -20.9163 | 86.148 | -75 | 12.4964 | 59.2721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/5:00
11 | 24 | 1900-01-05 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.2083 | -20.924 | 86.148 | -75 | 12.4834 | 74.2688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/6:00
11 | 24 | 1900-01-06 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.25 | -20.9318 | 86.148 | -75 | 12.4704 | 89.2656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/7:00
11 | 24 | 1900-01-07 | -5.6 | 6 | 48 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 6 | 0 | 0 | 39.791 | 328.2917 | -20.9395 | 86.148 | -75 | 12.4573 | 104.2623 | -19.4649 | -13.4649 | -4.2681 | -4.2681 | 0 | 0 | 0 | 11/24/8:00
11 | 24 | 1900-01-08 | -3.3 | 28 | 473 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 28 | 0 | 0 | 39.791 | 328.3333 | -20.9472 | 86.148 | -75 | 12.4442 | 119.2591 | -274.1201 | -246.1201 | -78.0158 | -78.0158 | 0 | 0 | 0 | 11/24/9:00
11 | 24 | 1900-01-09 | -1.1 | 43 | 717 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 43 | 0 | 0 | 39.791 | 328.375 | -20.9548 | 86.148 | -75 | 12.4312 | 134.2558 | -523.1538 | -480.1538 | -152.2004 | -152.2004 | 0 | 0 | 0 | 11/24/10:00
11 | 24 | 1900-01-10 | 1.1 | 54 | 822 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 54 | 0 | 0 | 39.791 | 328.4167 | -20.9625 | 86.148 | -75 | 12.4181 | 149.2525 | -695.1039 | -641.1039 | -203.2187 | -203.2187 | 0 | 0 | 0 | 11/24/11:00
11 | 24 | 1900-01-11 | 3.9 | 62 | 873 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 62 | 0 | 0 | 39.791 | 328.4583 | -20.9702 | 86.148 | -75 | 12.4049 | 164.2492 | -802.8034 | -740.8034 | -234.8217 | -234.8217 | 0 | 0 | 0 | 11/24/12:00
11 | 24 | 1900-01-12 | 5 | 64 | 892 | 41 | 1 | 0 | 41 | 0 | 0 | 64 | 0 | 0 | 39.791 | 328.5 | -20.9778 | 86.148 | -75 | 12.3918 | 179.2459 | -844.2897 | -780.2897 | -247.3382 | -247.3382 | 0 | 0 | 0 | 11/24/13:00
11 | 24 | 1900-01-13 | 6.1 | 62 | 877 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 62 | 0 | 0 | 39.791 | 328.5417 | -20.9855 | 86.148 | -75 | 12.3786 | 194.2427 | -810.8449 | -748.8449 | -237.3707 | -237.3707 | 0 | 0 | 0 | 11/24/14:00
11 | 24 | 1900-01-14 | 6.7 | 55 | 834 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 55 | 0 | 0 | 39.791 | 328.5833 | -20.9931 | 86.148 | -75 | 12.3655 | 209.2394 | -713.2845 | -658.2845 | -208.6647 | -208.6647 | 0 | 0 | 0 | 11/24/15:00
11 | 24 | 1900-01-15 | 6.7 | 44 | 736 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 44 | 0 | 0 | 39.791 | 328.625 | -21.0007 | 86.148 | -75 | 12.3523 | 224.2361 | -547.0809 | -503.0809 | -159.4678 | -159.4678 | 0 | 0 | 0 | 11/24/16:00
11 | 24 | 1900-01-16 | 5.6 | 33 | 478 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 33 | 0 | 0 | 39.791 | 328.6667 | -21.0083 | 86.148 | -75 | 12.3391 | 239.2328 | -285.069 | -252.069 | -79.9015 | -79.9015 | 0 | 0 | 0 | 11/24/17:00
11 | 24 | 1900-01-17 | 3.3 | 9 | 57 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 9 | 0 | 0 | 39.791 | 328.7083 | -21.0159 | 86.148 | -75 | 12.3258 | 254.2295 | -24.1943 | -15.1943 | -4.8163 | -4.8163 | 0 | 0 | 0 | 11/24/18:00
11 | 24 | 1900-01-18 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.75 | -21.0235 | 86.148 | -75 | 12.3126 | 269.2261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/19:00
11 | 24 | 1900-01-19 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.7917 | -21.0311 | 86.148 | -75 | 12.2993 | 284.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/20:00
11 | 24 | 1900-01-20 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.8333 | -21.0387 | 86.148 | -75 | 12.286 | 299.2195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/21:00
11 | 24 | 1900-01-21 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.875 | -21.0462 | 86.148 | -75 | 12.2727 | 314.2162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/22:00
11 | 24 | 1900-01-22 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.9167 | -21.0538 | 86.148 | -75 | 12.2594 | 329.2128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/23:00
11 | 24 | 1900-01-23 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 328.9583 | -21.0613 | 86.148 | -75 | 12.2461 | 344.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/24/24:00
11 | 25 | 1899-12-31 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329 | -21.0688 | 86.148 | -75 | 12.2327 | -0.79383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/1:00
11 | 25 | 1900-01-01 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.0417 | -21.0763 | 86.148 | -75 | 12.2193 | 14.2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/2:00
11 | 25 | 1900-01-02 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.0833 | -21.0838 | 86.148 | -75 | 12.2059 | 29.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/3:00
11 | 25 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.125 | -21.0913 | 86.148 | -75 | 12.1925 | 44.1961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/4:00
11 | 25 | 1900-01-04 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.1667 | -21.0988 | 86.148 | -75 | 12.1791 | 59.1928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/5:00
11 | 25 | 1900-01-05 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.2083 | -21.1063 | 86.148 | -75 | 12.1656 | 74.1894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/6:00
11 | 25 | 1900-01-06 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.25 | -21.1137 | 86.148 | -75 | 12.1522 | 89.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/7:00
11 | 25 | 1900-01-07 | 6.7 | 6 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 6 | 0 | 0 | 39.791 | 329.2917 | -21.1212 | 86.148 | -75 | 12.1387 | 104.1827 | 0 | 6 | 1.9019 | 1.9019 | 0 | 0 | 0 | 11/25/8:00
11 | 25 | 1900-01-08 | 7.8 | 58 | 15 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 58 | 0 | 0 | 39.791 | 329.3333 | -21.1286 | 86.148 | -75 | 12.1252 | 119.1793 | -8.7019 | 49.2981 | 15.6266 | 15.6266 | 0 | 0 | 0 | 11/25/9:00
11 | 25 | 1900-01-09 | 7.8 | 103 | 6 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 103 | 0 | 0 | 39.791 | 329.375 | -21.136 | 86.148 | -75 | 12.1117 | 134.1759 | -4.3812 | 98.6188 | 31.2604 | 31.2604 | 0 | 0 | 0 | 11/25/10:00
11 | 25 | 1900-01-10 | 8.3 | 142 | 7 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 142 | 0 | 0 | 39.791 | 329.4167 | -21.1434 | 86.148 | -75 | 12.0981 | 149.1725 | -5.9238 | 136.0762 | 43.1338 | 43.1338 | 0 | 0 | 0 | 11/25/11:00
11 | 25 | 1900-01-11 | 9.4 | 194 | 2 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 194 | 0 | 0 | 39.791 | 329.4583 | -21.1508 | 86.148 | -75 | 12.0846 | 164.1691 | -1.8407 | 192.1593 | 60.9111 | 60.9111 | 0 | 0 | 0 | 11/25/12:00
11 | 25 | 1900-01-12 | 9.4 | 255 | 7 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 255 | 0 | 0 | 39.791 | 329.5 | -21.1582 | 86.148 | -75 | 12.071 | 179.1657 | -6.6326 | 248.3674 | 78.7281 | 78.7281 | 0 | 0 | 0 | 11/25/13:00
11 | 25 | 1900-01-13 | 9.4 | 201 | 3 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 201 | 0 | 0 | 39.791 | 329.5417 | -21.1656 | 86.148 | -75 | 12.0574 | 194.1623 | -2.7775 | 198.2225 | 62.8331 | 62.8331 | 0 | 0 | 0 | 11/25/14:00
11 | 25 | 1900-01-14 | 8.9 | 184 | 5 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 184 | 0 | 0 | 39.791 | 329.5833 | -21.173 | 86.148 | -75 | 12.0438 | 209.1589 | -4.2843 | 179.7157 | 56.9667 | 56.9667 | 0 | 0 | 0 | 11/25/15:00
11 | 25 | 1900-01-15 | 8.9 | 129 | 2 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 129 | 0 | 0 | 39.791 | 329.625 | -21.1803 | 86.148 | -75 | 12.0302 | 224.1555 | -1.4905 | 127.5095 | 40.4183 | 40.4183 | 0 | 0 | 0 | 11/25/16:00
11 | 25 | 1900-01-16 | 8.9 | 65 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 65 | 0 | 0 | 39.791 | 329.6667 | -21.1877 | 86.148 | -75 | 12.0165 | 239.1521 | 0 | 65 | 20.6039 | 20.6039 | 0 | 0 | 0 | 11/25/17:00
11 | 25 | 1900-01-17 | 7.8 | 5 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 5 | 0 | 0 | 39.791 | 329.7083 | -21.195 | 86.148 | -75 | 12.0029 | 254.1487 | 0 | 5 | 1.5849 | 1.5849 | 0 | 0 | 0 | 11/25/18:00
11 | 25 | 1900-01-18 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.75 | -21.2023 | 86.148 | -75 | 11.9892 | 269.1453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/19:00
11 | 25 | 1900-01-19 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.7917 | -21.2097 | 86.148 | -75 | 11.9755 | 284.1419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/20:00
11 | 25 | 1900-01-20 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.8333 | -21.217 | 86.148 | -75 | 11.9618 | 299.1384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/21:00
11 | 25 | 1900-01-21 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.875 | -21.2243 | 86.148 | -75 | 11.948 | 314.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/22:00
11 | 25 | 1900-01-22 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.9167 | -21.2315 | 86.148 | -75 | 11.9343 | 329.1316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/23:00
11 | 25 | 1900-01-23 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 329.9583 | -21.2388 | 86.148 | -75 | 11.9205 | 344.1281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/25/24:00
11 | 26 | 1899-12-31 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330 | -21.2461 | 86.148 | -75 | 11.9067 | -0.87532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/1:00
11 | 26 | 1900-01-01 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.0417 | -21.2533 | 86.148 | -75 | 11.8929 | 14.1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/2:00
11 | 26 | 1900-01-02 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.0833 | -21.2605 | 86.148 | -75 | 11.8791 | 29.1178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/3:00
11 | 26 | 1900-01-03 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.125 | -21.2678 | 86.148 | -75 | 11.8653 | 44.1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/4:00
11 | 26 | 1900-01-04 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.1667 | -21.275 | 86.148 | -75 | 11.8514 | 59.1108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/5:00
11 | 26 | 1900-01-05 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.2083 | -21.2822 | 86.148 | -75 | 11.8375 | 74.1074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/6:00
11 | 26 | 1900-01-06 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.25 | -21.2894 | 86.148 | -75 | 11.8236 | 89.1039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/7:00
11 | 26 | 1900-01-07 | 2.2 | 4 | 34 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 4 | 0 | 0 | 39.791 | 330.2917 | -21.2965 | 86.148 | -75 | 11.8097 | 104.1004 | -13.833 | -9.833 | -3.1169 | -3.1169 | 0 | 0 | 0 | 11/26/8:00
11 | 26 | 1900-01-08 | 2.8 | 44 | 262 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 44 | 0 | 0 | 39.791 | 330.3333 | -21.3037 | 86.148 | -75 | 11.7958 | 119.0969 | -152.1275 | -108.1275 | -34.2745 | -34.2745 | 0 | 0 | 0 | 11/26/9:00
11 | 26 | 1900-01-09 | 4.4 | 92 | 405 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 92 | 0 | 0 | 39.791 | 330.375 | -21.3109 | 86.148 | -75 | 11.7818 | 134.0935 | -295.9319 | -203.9319 | -64.6429 | -64.6429 | 0 | 0 | 0 | 11/26/10:00
11 | 26 | 1900-01-10 | 8.3 | 119 | 538 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 119 | 0 | 0 | 39.791 | 330.4167 | -21.318 | 86.148 | -75 | 11.7679 | 149.09 | -455.584 | -336.584 | -106.6912 | -106.6912 | 0 | 0 | 0 | 11/26/11:00
11 | 26 | 1900-01-11 | 10.6 | 185 | 405 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 185 | 0 | 0 | 39.791 | 330.4583 | -21.3252 | 86.148 | -75 | 11.7539 | 164.0865 | -373.0381 | -188.0381 | -59.6048 | -59.6048 | 0 | 0 | 0 | 11/26/12:00
11 | 26 | 1900-01-12 | 10.6 | 165 | 502 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 165 | 0 | 0 | 39.791 | 330.5 | -21.3323 | 86.148 | -75 | 11.7399 | 179.083 | -476.1271 | -311.1271 | -98.6218 | -98.6218 | 0 | 0 | 0 | 11/26/13:00
11 | 26 | 1900-01-13 | 11.7 | 114 | 662 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 114 | 0 | 0 | 39.791 | 330.5417 | -21.3394 | 86.148 | -75 | 11.7259 | 194.0795 | -613.7342 | -499.7342 | -158.407 | -158.407 | 0 | 0 | 0 | 11/26/14:00
11 | 26 | 1900-01-14 | 11.7 | 132 | 581 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 132 | 0 | 0 | 39.791 | 330.5833 | -21.3465 | 86.148 | -75 | 11.7119 | 209.076 | -498.7531 | -366.7531 | -116.2543 | -116.2543 | 0 | 0 | 0 | 11/26/15:00
11 | 26 | 1900-01-15 | 10.6 | 95 | 468 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 95 | 0 | 0 | 39.791 | 330.625 | -21.3536 | 86.148 | -75 | 11.6978 | 224.0725 | -349.685 | -254.685 | -80.7307 | -80.7307 | 0 | 0 | 0 | 11/26/16:00
11 | 26 | 1900-01-16 | 8.9 | 54 | 17 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 54 | 0 | 0 | 39.791 | 330.6667 | -21.3607 | 86.148 | -75 | 11.6838 | 239.0689 | -10.2158 | 43.7842 | 13.8788 | 13.8788 | 0 | 0 | 0 | 11/26/17:00
11 | 26 | 1900-01-17 | 7.2 | 10 | 8 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 10 | 0 | 0 | 39.791 | 330.7083 | -21.3677 | 86.148 | -75 | 11.6697 | 254.0654 | -3.4371 | 6.5629 | 2.0803 | 2.0803 | 0 | 0 | 0 | 11/26/18:00
11 | 26 | 1900-01-18 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.75 | -21.3748 | 86.148 | -75 | 11.6556 | 269.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/19:00
11 | 26 | 1900-01-19 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.7917 | -21.3818 | 86.148 | -75 | 11.6414 | 284.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/20:00
11 | 26 | 1900-01-20 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.8333 | -21.3889 | 86.148 | -75 | 11.6273 | 299.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/21:00
11 | 26 | 1900-01-21 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.875 | -21.3959 | 86.148 | -75 | 11.6132 | 314.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/22:00
11 | 26 | 1900-01-22 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.9167 | -21.4029 | 86.148 | -75 | 11.599 | 329.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/23:00
11 | 26 | 1900-01-23 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 330.9583 | -21.4099 | 86.148 | -75 | 11.5848 | 344.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/26/24:00
11 | 27 | 1899-12-31 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 331 | -21.4169 | 86.148 | -75 | 11.5706 | -0.95935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/27/1:00
11 | 27 | 1900-01-01 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 331.0417 | -21.4239 | 86.148 | -75 | 11.5564 | 14.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/27/2:00
11 | 27 | 1900-01-02 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 331.0833 | -21.4308 | 86.148 | -75 | 11.5421 | 29.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/27/3:00
11 | 27 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 331.125 | -21.4378 | 86.148 | -75 | 11.5279 | 44.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/27/4:00
11 | 27 | 1900-01-04 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 331.1667 | -21.4447 | 86.148 | -75 | 11.5136 | 59.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/27/5:00
11 | 27 | 1900-01-05 | 7.2 | 0 | 0 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 331.2083 | -21.4517 | 86.148 | -75 | 11.4993 | 74.0228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/27/6:00
11 | 27 | 1900-01-06 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 331.25 | -21.4586 | 86.148 | -75 | 11.485 | 89.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/27/7:00
11 | 27 | 1900-01-07 | 8.9 | 3 | 9 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 3 | 0 | 0 | 39.791 | 331.2917 | -21.4655 | 86.148 | -75 | 11.4707 | 104.0157 | -3.6664 | -0.66645 | -0.21125 | -0.21125 | 0 | 0 | 0 | 11/27/8:00
11 | 27 | 1900-01-08 | 9.4 | 40 | 3 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 40 | 0 | 0 | 39.791 | 331.3333 | -21.4724 | 86.148 | -75 | 11.4564 | 119.0121 | -1.7432 | 38.2568 | 12.1267 | 12.1267 | 0 | 0 | 0 | 11/27/9:00
11 | 27 | 1900-01-09 | 10 | 51 | 8 | 50 | 1 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 39.791 | 331.375 | -21.4793 | 86.148 | -75 | 11.442 | 134.0085 | -5.8489 | 45.1511 | 14.3121 | 14.3121 | 0 | 0 | 0 | 11/27/10:00
11 | 27 | 1900-01-10 | 11.7 | 113 | 1 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 113 | 0 | 0 | 39.791 | 331.4167 | -21.4862 | 86.148 | -75 | 11.4276 | 149.0049 | -0.84731 | 112.1527 | 35.5504 | 35.5504 | 0 | 0 | 0 | 11/27/11:00
11 | 27 | 1900-01-11 | 13.3 | 111 | 5 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 111 | 0 | 0 | 39.791 | 331.4583 | -21.493 | 86.148 | -75 | 11.4133 | 164.0013 | -4.6087 | 106.3913 | 33.7242 | 0 | 33.7242 | 55.94 | 33.7242 | 11/27/12:00
11 | 27 | 1900-01-12 | 14.4 | 215 | 0 | 57.92 | 0 | 1 | 0 | 57.92 | 0 | 215 | 0 | 0 | 39.791 | 331.5 | -21.4999 | 86.148 | -75 | 11.3988 | 178.9977 | 0 | 215 | 68.1512 | 0 | 68.1512 | 57.92 | 68.1512 | 11/27/13:00
11 | 27 | 1900-01-13 | 15.6 | 195 | 4 | 60.08 | 0 | 1 | 0 | 60.08 | 0 | 195 | 0 | 0 | 39.791 | 331.5417 | -21.5067 | 86.148 | -75 | 11.3844 | 193.9941 | -3.7132 | 191.2868 | 60.6346 | 0 | 60.6346 | 60.08 | 60.6346 | 11/27/14:00
11 | 27 | 1900-01-14 | 17.2 | 195 | 2 | 62.96 | 0 | 1 | 0 | 62.96 | 0 | 195 | 0 | 0 | 39.791 | 331.5833 | -21.5136 | 86.148 | -75 | 11.37 | 208.9905 | -1.72 | 193.28 | 61.2664 | 0 | 61.2664 | 62.96 | 61.2664 | 11/27/15:00
11 | 27 | 1900-01-15 | 18.9 | 134 | 2 | 66.02 | 0 | 1 | 0 | 66.02 | 0 | 134 | 0 | 0 | 39.791 | 331.625 | -21.5204 | 86.148 | -75 | 11.3555 | 223.9869 | -1.4982 | 132.5018 | 42.0008 | 0 | 42.0008 | 66.02 | 42.0008 | 11/27/16:00
11 | 27 | 1900-01-16 | 19.4 | 58 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 58 | 0 | 0 | 39.791 | 331.6667 | -21.5272 | 86.148 | -75 | 11.3411 | 238.9833 | 0 | 58 | 18.385 | 0 | 18.385 | 66.92 | 18.385 | 11/27/17:00
11 | 27 | 1900-01-17 | 20 | 13 | 3 | 68 | 0 | 1 | 0 | 68 | 0 | 13 | 0 | 0 | 39.791 | 331.7083 | -21.534 | 86.148 | -75 | 11.3266 | 253.9796 | -1.2965 | 11.7035 | 3.7098 | 0 | 3.7098 | 68 | 3.7098 | 11/27/18:00
11 | 27 | 1900-01-18 | 20 | 0 | 0 | 68 | 0 | 1 | 0 | 68 | 0 | 0 | 0 | 0 | 39.791 | 331.75 | -21.5408 | 86.148 | -75 | 11.3121 | 268.976 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 11/27/19:00
11 | 27 | 1900-01-19 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 331.7917 | -21.5475 | 86.148 | -75 | 11.2975 | 283.9724 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 11/27/20:00
11 | 27 | 1900-01-20 | 19.4 | 0 | 0 | 66.92 | 0 | 1 | 0 | 66.92 | 0 | 0 | 0 | 0 | 39.791 | 331.8333 | -21.5543 | 86.148 | -75 | 11.283 | 298.9687 | 0 | 0 | 0 | 0 | 0 | 66.92 | 0 | 11/27/21:00
11 | 27 | 1900-01-21 | 15 | 0 | 0 | 59 | 0 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 39.791 | 331.875 | -21.5611 | 86.148 | -75 | 11.2684 | 313.9651 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 11/27/22:00
11 | 27 | 1900-01-22 | 12.2 | 0 | 0 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 331.9167 | -21.5678 | 86.148 | -75 | 11.2539 | 328.9615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/27/23:00
11 | 27 | 1900-01-23 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 331.9583 | -21.5745 | 86.148 | -75 | 11.2393 | 343.9578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/27/24:00
11 | 28 | 1899-12-31 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332 | -21.5812 | 86.148 | -75 | 11.2247 | -1.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/1:00
11 | 28 | 1900-01-01 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.0417 | -21.588 | 86.148 | -75 | 11.21 | 13.9505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/2:00
11 | 28 | 1900-01-02 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.0833 | -21.5947 | 86.148 | -75 | 11.1954 | 28.9469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/3:00
11 | 28 | 1900-01-03 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.125 | -21.6013 | 86.148 | -75 | 11.1807 | 43.9432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/4:00
11 | 28 | 1900-01-04 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.1667 | -21.608 | 86.148 | -75 | 11.1661 | 58.9395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/5:00
11 | 28 | 1900-01-05 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.2083 | -21.6147 | 86.148 | -75 | 11.1514 | 73.9358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/6:00
11 | 28 | 1900-01-06 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.25 | -21.6213 | 86.148 | -75 | 11.1367 | 88.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/7:00
11 | 28 | 1900-01-07 | 3.3 | 2 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 2 | 0 | 0 | 39.791 | 332.2917 | -21.628 | 86.148 | -75 | 11.122 | 103.9285 | 0 | 2 | 0.63397 | 0.63397 | 0 | 0 | 0 | 11/28/8:00
11 | 28 | 1900-01-08 | 3.3 | 22 | 7 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 22 | 0 | 0 | 39.791 | 332.3333 | -21.6346 | 86.148 | -75 | 11.1072 | 118.9248 | -4.0699 | 17.9301 | 5.6835 | 5.6835 | 0 | 0 | 0 | 11/28/9:00
11 | 28 | 1900-01-09 | 3.3 | 64 | 4 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 64 | 0 | 0 | 39.791 | 332.375 | -21.6412 | 86.148 | -75 | 11.0925 | 133.9211 | -2.9258 | 61.0742 | 19.3594 | 19.3594 | 0 | 0 | 0 | 11/28/10:00
11 | 28 | 1900-01-10 | 3.3 | 73 | 2 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 73 | 0 | 0 | 39.791 | 332.4167 | -21.6478 | 86.148 | -75 | 11.0777 | 148.9174 | -1.6955 | 71.3045 | 22.6023 | 22.6023 | 0 | 0 | 0 | 11/28/11:00
11 | 28 | 1900-01-11 | 2.8 | 209 | 7 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 209 | 0 | 0 | 39.791 | 332.4583 | -21.6544 | 86.148 | -75 | 11.0629 | 163.9137 | -6.4565 | 202.5435 | 64.2028 | 64.2028 | 0 | 0 | 0 | 11/28/12:00
11 | 28 | 1900-01-12 | 2.8 | 123 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 123 | 0 | 0 | 39.791 | 332.5 | -21.661 | 86.148 | -75 | 11.0481 | 178.91 | 0 | 123 | 38.9889 | 38.9889 | 0 | 0 | 0 | 11/28/13:00
11 | 28 | 1900-01-13 | 2.2 | 129 | 1 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 129 | 0 | 0 | 39.791 | 332.5417 | -21.6676 | 86.148 | -75 | 11.0333 | 193.9063 | -0.92946 | 128.0705 | 40.5961 | 40.5961 | 0 | 0 | 0 | 11/28/14:00
11 | 28 | 1900-01-14 | 1.7 | 158 | 3 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 158 | 0 | 0 | 39.791 | 332.5833 | -21.6741 | 86.148 | -75 | 11.0185 | 208.9026 | -2.5844 | 155.4156 | 49.264 | 49.264 | 0 | 0 | 0 | 11/28/15:00
11 | 28 | 1900-01-15 | 1.1 | 57 | 2 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 57 | 0 | 0 | 39.791 | 332.625 | -21.6807 | 86.148 | -75 | 11.0036 | 223.8989 | -1.5019 | 55.4981 | 17.5919 | 17.5919 | 0 | 0 | 0 | 11/28/16:00
11 | 28 | 1900-01-16 | 0.6 | 47 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 47 | 0 | 0 | 39.791 | 332.6667 | -21.6872 | 86.148 | -75 | 10.9887 | 238.8952 | 0 | 47 | 14.8982 | 14.8982 | 0 | 0 | 0 | 11/28/17:00
11 | 28 | 1900-01-17 | 0 | 4 | 1 | 32 | 1 | 0 | 32 | 0 | 0 | 4 | 0 | 0 | 39.791 | 332.7083 | -21.6937 | 86.148 | -75 | 10.9738 | 253.8915 | -0.43466 | 3.5653 | 1.1301 | 1.1301 | 0 | 0 | 0 | 11/28/18:00
11 | 28 | 1900-01-18 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.75 | -21.7002 | 86.148 | -75 | 10.9589 | 268.8877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/19:00
11 | 28 | 1900-01-19 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.7917 | -21.7067 | 86.148 | -75 | 10.944 | 283.884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/20:00
11 | 28 | 1900-01-20 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.8333 | -21.7132 | 86.148 | -75 | 10.9291 | 298.8803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/21:00
11 | 28 | 1900-01-21 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.875 | -21.7197 | 86.148 | -75 | 10.9142 | 313.8765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/22:00
11 | 28 | 1900-01-22 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.9167 | -21.7262 | 86.148 | -75 | 10.8992 | 328.8728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/23:00
11 | 28 | 1900-01-23 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 332.9583 | -21.7326 | 86.148 | -75 | 10.8842 | 343.8691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/28/24:00
11 | 29 | 1899-12-31 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333 | -21.7391 | 86.148 | -75 | 10.8692 | -1.1347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/1:00
11 | 29 | 1900-01-01 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.0417 | -21.7455 | 86.148 | -75 | 10.8542 | 13.8615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/2:00
11 | 29 | 1900-01-02 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.0833 | -21.7519 | 86.148 | -75 | 10.8392 | 28.8578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/3:00
11 | 29 | 1900-01-03 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.125 | -21.7583 | 86.148 | -75 | 10.8241 | 43.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/4:00
11 | 29 | 1900-01-04 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.1667 | -21.7647 | 86.148 | -75 | 10.8091 | 58.8503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/5:00
11 | 29 | 1900-01-05 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.2083 | -21.7711 | 86.148 | -75 | 10.794 | 73.8465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/6:00
11 | 29 | 1900-01-06 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.25 | -21.7775 | 86.148 | -75 | 10.7789 | 88.8427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/7:00
11 | 29 | 1900-01-07 | -5 | 1 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 1 | 0 | 0 | 39.791 | 333.2917 | -21.7839 | 86.148 | -75 | 10.7638 | 103.8389 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 11/29/8:00
11 | 29 | 1900-01-08 | -5 | 50 | 49 | 23 | 1 | 0 | 23 | 0 | 0 | 50 | 0 | 0 | 39.791 | 333.3333 | -21.7902 | 86.148 | -75 | 10.7487 | 118.8352 | -28.5021 | 21.4979 | 6.8144 | 6.8144 | 0 | 0 | 0 | 11/29/9:00
11 | 29 | 1900-01-09 | -3.3 | 82 | 448 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 82 | 0 | 0 | 39.791 | 333.375 | -21.7966 | 86.148 | -75 | 10.7335 | 133.8314 | -327.814 | -245.814 | -77.9188 | -77.9188 | 0 | 0 | 0 | 11/29/10:00
11 | 29 | 1900-01-10 | -3.3 | 100 | 402 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 100 | 0 | 0 | 39.791 | 333.4167 | -21.8029 | 86.148 | -75 | 10.7184 | 148.8276 | -340.9413 | -240.9413 | -76.3742 | -76.3742 | 0 | 0 | 0 | 11/29/11:00
11 | 29 | 1900-01-11 | -2.8 | 94 | 629 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 94 | 0 | 0 | 39.791 | 333.4583 | -21.8092 | 86.148 | -75 | 10.7032 | 163.8238 | -580.5112 | -486.5112 | -154.2156 | -154.2156 | 0 | 0 | 0 | 11/29/12:00
11 | 29 | 1900-01-12 | -1.7 | 87 | 808 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 87 | 0 | 0 | 39.791 | 333.5 | -21.8155 | 86.148 | -75 | 10.688 | 178.82 | -768.4382 | -681.4382 | -216.004 | -216.004 | 0 | 0 | 0 | 11/29/13:00
11 | 29 | 1900-01-13 | -1.1 | 49 | 786 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 49 | 0 | 0 | 39.791 | 333.5417 | -21.8218 | 86.148 | -75 | 10.6728 | 193.8162 | -731.4388 | -682.4388 | -216.3212 | -216.3212 | 0 | 0 | 0 | 11/29/14:00
11 | 29 | 1900-01-14 | -0.6 | 44 | 879 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 44 | 0 | 0 | 39.791 | 333.5833 | -21.8281 | 86.148 | -75 | 10.6576 | 208.8124 | -758.5351 | -714.5351 | -226.4951 | -226.4951 | 0 | 0 | 0 | 11/29/15:00
11 | 29 | 1900-01-15 | -0.6 | 35 | 783 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 35 | 0 | 0 | 39.791 | 333.625 | -21.8344 | 86.148 | -75 | 10.6424 | 223.8086 | -589.4096 | -554.4096 | -175.7382 | -175.7382 | 0 | 0 | 0 | 11/29/16:00
11 | 29 | 1900-01-16 | -1.7 | 23 | 566 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 23 | 0 | 0 | 39.791 | 333.6667 | -21.8406 | 86.148 | -75 | 10.6271 | 238.8048 | -343.8534 | -320.8534 | -101.7049 | -101.7049 | 0 | 0 | 0 | 11/29/17:00
11 | 29 | 1900-01-17 | -2.8 | 6 | 89 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 6 | 0 | 0 | 39.791 | 333.7083 | -21.8469 | 86.148 | -75 | 10.6118 | 253.801 | -38.9039 | -32.9039 | -10.43 | -10.43 | 0 | 0 | 0 | 11/29/18:00
11 | 29 | 1900-01-18 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.75 | -21.8531 | 86.148 | -75 | 10.5966 | 268.7971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/19:00
11 | 29 | 1900-01-19 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.7917 | -21.8593 | 86.148 | -75 | 10.5813 | 283.7933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/20:00
11 | 29 | 1900-01-20 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.8333 | -21.8656 | 86.148 | -75 | 10.566 | 298.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/21:00
11 | 29 | 1900-01-21 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.875 | -21.8718 | 86.148 | -75 | 10.5506 | 313.7857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/22:00
11 | 29 | 1900-01-22 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.9167 | -21.8779 | 86.148 | -75 | 10.5353 | 328.7818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/23:00
11 | 29 | 1900-01-23 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 333.9583 | -21.8841 | 86.148 | -75 | 10.5199 | 343.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/29/24:00
11 | 30 | 1899-12-31 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334 | -21.8903 | 86.148 | -75 | 10.5046 | -1.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/1:00
11 | 30 | 1900-01-01 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.0417 | -21.8965 | 86.148 | -75 | 10.4892 | 13.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/2:00
11 | 30 | 1900-01-02 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.0833 | -21.9026 | 86.148 | -75 | 10.4738 | 28.7664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/3:00
11 | 30 | 1900-01-03 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.125 | -21.9087 | 86.148 | -75 | 10.4583 | 43.7626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/4:00
11 | 30 | 1900-01-04 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.1667 | -21.9149 | 86.148 | -75 | 10.4429 | 58.7587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/5:00
11 | 30 | 1900-01-05 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.2083 | -21.921 | 86.148 | -75 | 10.4275 | 73.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/6:00
11 | 30 | 1900-01-06 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.25 | -21.9271 | 86.148 | -75 | 10.412 | 88.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/7:00
11 | 30 | 1900-01-07 | -5.6 | 3 | 41 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 3 | 0 | 0 | 39.791 | 334.2917 | -21.9332 | 86.148 | -75 | 10.3965 | 103.7471 | -16.7457 | -13.7457 | -4.3572 | -4.3572 | 0 | 0 | 0 | 11/30/8:00
11 | 30 | 1900-01-08 | -3.3 | 22 | 495 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 22 | 0 | 0 | 39.791 | 334.3333 | -21.9392 | 86.148 | -75 | 10.381 | 118.7433 | -288.0207 | -266.0207 | -84.3239 | -84.3239 | 0 | 0 | 0 | 11/30/9:00
11 | 30 | 1900-01-09 | -0.6 | 35 | 749 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 35 | 0 | 0 | 39.791 | 334.375 | -21.9453 | 86.148 | -75 | 10.3655 | 133.7394 | -548.2146 | -513.2146 | -162.6801 | -162.6801 | 0 | 0 | 0 | 11/30/10:00
11 | 30 | 1900-01-10 | 2.2 | 45 | 854 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 45 | 0 | 0 | 39.791 | 334.4167 | -21.9513 | 86.148 | -75 | 10.35 | 148.7355 | -724.5532 | -679.5532 | -215.4065 | -215.4065 | 0 | 0 | 0 | 11/30/11:00
11 | 30 | 1900-01-11 | 3.3 | 51 | 900 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 51 | 0 | 0 | 39.791 | 334.4583 | -21.9574 | 86.148 | -75 | 10.3344 | 163.7316 | -831.0739 | -780.0739 | -247.2698 | -247.2698 | 0 | 0 | 0 | 11/30/12:00
11 | 30 | 1900-01-12 | 5 | 53 | 915 | 41 | 1 | 0 | 41 | 0 | 0 | 53 | 0 | 0 | 39.791 | 334.5 | -21.9634 | 86.148 | -75 | 10.3189 | 178.7277 | -870.9029 | -817.9029 | -259.2609 | -259.2609 | 0 | 0 | 0 | 11/30/13:00
11 | 30 | 1900-01-13 | 6.1 | 52 | 904 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 52 | 0 | 0 | 39.791 | 334.5417 | -21.9694 | 86.148 | -75 | 10.3033 | 193.7238 | -842.2299 | -790.2299 | -250.4891 | -250.4891 | 0 | 0 | 0 | 11/30/14:00
11 | 30 | 1900-01-14 | 6.7 | 46 | 867 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 46 | 0 | 0 | 39.791 | 334.5833 | -21.9754 | 86.148 | -75 | 10.2877 | 208.7199 | -749.4234 | -703.4234 | -222.9729 | -222.9729 | 0 | 0 | 0 | 11/30/15:00
11 | 30 | 1900-01-15 | 6.7 | 37 | 773 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 37 | 0 | 0 | 39.791 | 334.625 | -21.9814 | 86.148 | -75 | 10.2721 | 223.716 | -583.265 | -546.265 | -173.1565 | -173.1565 | 0 | 0 | 0 | 11/30/16:00
11 | 30 | 1900-01-16 | 5 | 24 | 544 | 41 | 1 | 0 | 41 | 0 | 0 | 24 | 0 | 0 | 39.791 | 334.6667 | -21.9874 | 86.148 | -75 | 10.2565 | 238.7121 | -331.6444 | -307.6444 | -97.5179 | -97.5179 | 0 | 0 | 0 | 11/30/17:00
11 | 30 | 1900-01-17 | 1.1 | 6 | 80 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 6 | 0 | 0 | 39.791 | 334.7083 | -21.9934 | 86.148 | -75 | 10.2409 | 253.7082 | -35.1634 | -29.1634 | -9.2443 | -9.2443 | 0 | 0 | 0 | 11/30/18:00
11 | 30 | 1900-01-18 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.75 | -21.9993 | 86.148 | -75 | 10.2252 | 268.7043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/19:00
11 | 30 | 1900-01-19 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.7917 | -22.0053 | 86.148 | -75 | 10.2096 | 283.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/20:00
11 | 30 | 1900-01-20 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.8333 | -22.0112 | 86.148 | -75 | 10.1939 | 298.6965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/21:00
11 | 30 | 1900-01-21 | 0.3 | 0 | 0 | 32.54 | 1 | 0 | 32.54 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.875 | -22.0171 | 86.148 | -75 | 10.1782 | 313.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/22:00
11 | 30 | 1900-01-22 | 1.2 | 0 | 0 | 34.16 | 1 | 0 | 34.16 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.9167 | -22.0231 | 86.148 | -75 | 10.1625 | 328.6886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/23:00
11 | 30 | 1900-01-23 | 2.1 | 0 | 0 | 35.78 | 1 | 0 | 35.78 | 0 | 0 | 0 | 0 | 0 | 39.791 | 334.9583 | -22.029 | 86.148 | -75 | 10.1468 | 343.6847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11/30/24:00
12 | 1 | 1899-12-31 | 2.9 | 0 | 0 | 37.22 | 1 | 0 | 37.22 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335 | -22.0349 | 86.148 | -75 | 10.1311 | -1.3192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/1:00
12 | 1 | 1900-01-01 | 3.8 | 0 | 0 | 38.84 | 1 | 0 | 38.84 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.0417 | -22.0407 | 86.148 | -75 | 10.1153 | 13.6768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/2:00
12 | 1 | 1900-01-02 | 4.7 | 0 | 0 | 40.46 | 1 | 0 | 40.46 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.0833 | -22.0466 | 86.148 | -75 | 10.0995 | 28.6729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/3:00
12 | 1 | 1900-01-03 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.125 | -22.0524 | 86.148 | -75 | 10.0838 | 43.6689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/4:00
12 | 1 | 1900-01-04 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.1667 | -22.0583 | 86.148 | -75 | 10.068 | 58.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/5:00
12 | 1 | 1900-01-05 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.2083 | -22.0641 | 86.148 | -75 | 10.0522 | 73.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/6:00
12 | 1 | 1900-01-06 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.25 | -22.0699 | 86.148 | -75 | 10.0363 | 88.6571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/7:00
12 | 1 | 1900-01-07 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.2917 | -22.0757 | 86.148 | -75 | 10.0205 | 103.6531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/8:00
12 | 1 | 1900-01-08 | 1.7 | 39 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 39 | 0 | 0 | 39.791 | 335.3333 | -22.0815 | 86.148 | -75 | 10.0046 | 118.6492 | 0 | 39 | 12.3623 | 12.3623 | 0 | 0 | 0 | 12/1/9:00
12 | 1 | 1900-01-09 | 2.2 | 102 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 102 | 0 | 0 | 39.791 | 335.375 | -22.0873 | 86.148 | -75 | 9.9888 | 133.6452 | 0 | 102 | 32.3322 | 32.3322 | 0 | 0 | 0 | 12/1/10:00
12 | 1 | 1900-01-10 | 2.2 | 189 | 1 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 189 | 0 | 0 | 39.791 | 335.4167 | -22.0931 | 86.148 | -75 | 9.9729 | 148.6412 | -0.84867 | 188.1513 | 59.6407 | 59.6407 | 0 | 0 | 0 | 12/1/11:00
12 | 1 | 1900-01-11 | 2.8 | 223 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 223 | 0 | 0 | 39.791 | 335.4583 | -22.0989 | 86.148 | -75 | 9.957 | 163.6372 | 0 | 223 | 70.6871 | 70.6871 | 0 | 0 | 0 | 12/1/12:00
12 | 1 | 1900-01-12 | 2.8 | 220 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 220 | 0 | 0 | 39.791 | 335.5 | -22.1046 | 86.148 | -75 | 9.9411 | 178.6333 | 0 | 220 | 69.7362 | 69.7362 | 0 | 0 | 0 | 12/1/13:00
12 | 1 | 1900-01-13 | 3.3 | 208 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 208 | 0 | 0 | 39.791 | 335.5417 | -22.1103 | 86.148 | -75 | 9.9252 | 193.6293 | 0 | 208 | 65.9324 | 65.9324 | 0 | 0 | 0 | 12/1/14:00
12 | 1 | 1900-01-14 | 3.9 | 174 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 174 | 0 | 0 | 39.791 | 335.5833 | -22.1161 | 86.148 | -75 | 9.9092 | 208.6253 | 0 | 174 | 55.155 | 55.155 | 0 | 0 | 0 | 12/1/15:00
12 | 1 | 1900-01-15 | 4.4 | 103 | 134 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 103 | 0 | 0 | 39.791 | 335.625 | -22.1218 | 86.148 | -75 | 9.8933 | 223.6213 | -101.3445 | 1.6555 | 0.52477 | 0.52477 | 0 | 0 | 0 | 12/1/16:00
12 | 1 | 1900-01-16 | 5 | 41 | 294 | 41 | 1 | 0 | 41 | 0 | 0 | 41 | 0 | 0 | 39.791 | 335.6667 | -22.1275 | 86.148 | -75 | 9.8773 | 238.6173 | -179.8487 | -138.8487 | -44.0126 | -44.0126 | 0 | 0 | 0 | 12/1/17:00
12 | 1 | 1900-01-17 | 3.9 | 4 | 1 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 4 | 0 | 0 | 39.791 | 335.7083 | -22.1332 | 86.148 | -75 | 9.8613 | 253.6133 | -0.44192 | 3.5581 | 1.1278 | 1.1278 | 0 | 0 | 0 | 12/1/18:00
12 | 1 | 1900-01-18 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.75 | -22.1389 | 86.148 | -75 | 9.8453 | 268.6093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/19:00
12 | 1 | 1900-01-19 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.7917 | -22.1445 | 86.148 | -75 | 9.8293 | 283.6053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/20:00
12 | 1 | 1900-01-20 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.8333 | -22.1502 | 86.148 | -75 | 9.8133 | 298.6013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/21:00
12 | 1 | 1900-01-21 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.875 | -22.1558 | 86.148 | -75 | 9.7972 | 313.5973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/22:00
12 | 1 | 1900-01-22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.9167 | -22.1614 | 86.148 | -75 | 9.7812 | 328.5933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/23:00
12 | 1 | 1900-01-23 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 335.9583 | -22.1671 | 86.148 | -75 | 9.7651 | 343.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/1/24:00
12 | 2 | 1899-12-31 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336 | -22.1727 | 86.148 | -75 | 9.749 | -1.4147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/1:00
12 | 2 | 1900-01-01 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.0417 | -22.1783 | 86.148 | -75 | 9.7329 | 13.5812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/2:00
12 | 2 | 1900-01-02 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.0833 | -22.1839 | 86.148 | -75 | 9.7168 | 28.5772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/3:00
12 | 2 | 1900-01-03 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.125 | -22.1894 | 86.148 | -75 | 9.7007 | 43.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/4:00
12 | 2 | 1900-01-04 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.1667 | -22.195 | 86.148 | -75 | 9.6845 | 58.5691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/5:00
12 | 2 | 1900-01-05 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.2083 | -22.2005 | 86.148 | -75 | 9.6684 | 73.5651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/6:00
12 | 2 | 1900-01-06 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.25 | -22.2061 | 86.148 | -75 | 9.6522 | 88.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/7:00
12 | 2 | 1900-01-07 | -1.1 | 3 | 23 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 3 | 0 | 0 | 39.791 | 336.2917 | -22.2116 | 86.148 | -75 | 9.636 | 103.557 | -9.3998 | -6.3998 | -2.0286 | -2.0286 | 0 | 0 | 0 | 12/2/8:00
12 | 2 | 1900-01-08 | -1.1 | 41 | 39 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 41 | 0 | 0 | 39.791 | 336.3333 | -22.2171 | 86.148 | -75 | 9.6198 | 118.553 | -22.6976 | 18.3024 | 5.8015 | 5.8015 | 0 | 0 | 0 | 12/2/9:00
12 | 2 | 1900-01-09 | 0 | 74 | 488 | 32 | 1 | 0 | 32 | 0 | 0 | 74 | 0 | 0 | 39.791 | 336.375 | -22.2226 | 86.148 | -75 | 9.6036 | 133.5489 | -357.2752 | -283.2752 | -89.7933 | -89.7933 | 0 | 0 | 0 | 12/2/10:00
12 | 2 | 1900-01-10 | 3.3 | 101 | 602 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 101 | 0 | 0 | 39.791 | 336.4167 | -22.2281 | 86.148 | -75 | 9.5874 | 148.5449 | -511.0153 | -410.0153 | -129.9677 | -129.9677 | 0 | 0 | 0 | 12/2/11:00
12 | 2 | 1900-01-11 | 5 | 173 | 8 | 41 | 1 | 0 | 41 | 0 | 0 | 173 | 0 | 0 | 39.791 | 336.4583 | -22.2336 | 86.148 | -75 | 9.5712 | 163.5408 | -7.3942 | 165.6058 | 52.4942 | 52.4942 | 0 | 0 | 0 | 12/2/12:00
12 | 2 | 1900-01-12 | 4.4 | 205 | 9 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 205 | 0 | 0 | 39.791 | 336.5 | -22.239 | 86.148 | -75 | 9.5549 | 178.5367 | -8.5789 | 196.4211 | 62.2621 | 62.2621 | 0 | 0 | 0 | 12/2/13:00
12 | 2 | 1900-01-13 | 5.6 | 168 | 376 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 168 | 0 | 0 | 39.791 | 336.5417 | -22.2445 | 86.148 | -75 | 9.5387 | 193.5327 | -351.0815 | -183.0815 | -58.0336 | -58.0336 | 0 | 0 | 0 | 12/2/14:00
12 | 2 | 1900-01-14 | 7.2 | 161 | 127 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 161 | 0 | 0 | 39.791 | 336.5833 | -22.2499 | 86.148 | -75 | 9.5224 | 208.5286 | -110.1281 | 50.8719 | 16.1255 | 16.1255 | 0 | 0 | 0 | 12/2/15:00
12 | 2 | 1900-01-15 | 6.7 | 81 | 424 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 81 | 0 | 0 | 39.791 | 336.625 | -22.2554 | 86.148 | -75 | 9.5061 | 223.5245 | -321.4013 | -240.4013 | -76.203 | -76.203 | 0 | 0 | 0 | 12/2/16:00
12 | 2 | 1900-01-16 | 6.1 | 51 | 204 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 51 | 0 | 0 | 39.791 | 336.6667 | -22.2608 | 86.148 | -75 | 9.4898 | 238.5204 | -125.2117 | -74.2117 | -23.5238 | -23.5238 | 0 | 0 | 0 | 12/2/17:00
12 | 2 | 1900-01-17 | 3.9 | 13 | 20 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 13 | 0 | 0 | 39.791 | 336.7083 | -22.2662 | 86.148 | -75 | 9.4735 | 253.5164 | -8.8853 | 4.1147 | 1.3043 | 1.3043 | 0 | 0 | 0 | 12/2/18:00
12 | 2 | 1900-01-18 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.75 | -22.2716 | 86.148 | -75 | 9.4571 | 268.5123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/19:00
12 | 2 | 1900-01-19 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.7917 | -22.277 | 86.148 | -75 | 9.4408 | 283.5082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/20:00
12 | 2 | 1900-01-20 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.8333 | -22.2823 | 86.148 | -75 | 9.4244 | 298.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/21:00
12 | 2 | 1900-01-21 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.875 | -22.2877 | 86.148 | -75 | 9.408 | 313.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/22:00
12 | 2 | 1900-01-22 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.9167 | -22.2931 | 86.148 | -75 | 9.3916 | 328.4959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/23:00
12 | 2 | 1900-01-23 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 336.9583 | -22.2984 | 86.148 | -75 | 9.3752 | 343.4918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/2/24:00
12 | 3 | 1899-12-31 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337 | -22.3037 | 86.148 | -75 | 9.3588 | -1.5123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/1:00
12 | 3 | 1900-01-01 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.0417 | -22.309 | 86.148 | -75 | 9.3424 | 13.4836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/2:00
12 | 3 | 1900-01-02 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.0833 | -22.3143 | 86.148 | -75 | 9.326 | 28.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/3:00
12 | 3 | 1900-01-03 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.125 | -22.3196 | 86.148 | -75 | 9.3095 | 43.4754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/4:00
12 | 3 | 1900-01-04 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.1667 | -22.3249 | 86.148 | -75 | 9.293 | 58.4713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/5:00
12 | 3 | 1900-01-05 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.2083 | -22.3301 | 86.148 | -75 | 9.2765 | 73.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/6:00
12 | 3 | 1900-01-06 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.25 | -22.3354 | 86.148 | -75 | 9.26 | 88.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/7:00
12 | 3 | 1900-01-07 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.2917 | -22.3406 | 86.148 | -75 | 9.2435 | 103.4589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/8:00
12 | 3 | 1900-01-08 | 1.7 | 28 | 1 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 28 | 0 | 0 | 39.791 | 337.3333 | -22.3459 | 86.148 | -75 | 9.227 | 118.4548 | -0.58194 | 27.4181 | 8.691 | 8.691 | 0 | 0 | 0 | 12/3/9:00
12 | 3 | 1900-01-09 | 1.7 | 70 | 1 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 70 | 0 | 0 | 39.791 | 337.375 | -22.3511 | 86.148 | -75 | 9.2105 | 133.4506 | -0.73211 | 69.2679 | 21.9567 | 21.9567 | 0 | 0 | 0 | 12/3/10:00
12 | 3 | 1900-01-10 | 1.7 | 108 | 7 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 108 | 0 | 0 | 39.791 | 337.4167 | -22.3563 | 86.148 | -75 | 9.1939 | 148.4465 | -5.943 | 102.057 | 32.3503 | 32.3503 | 0 | 0 | 0 | 12/3/11:00
12 | 3 | 1900-01-11 | 2.2 | 157 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 157 | 0 | 0 | 39.791 | 337.4583 | -22.3615 | 86.148 | -75 | 9.1774 | 163.4423 | 0 | 157 | 49.7663 | 49.7663 | 0 | 0 | 0 | 12/3/12:00
12 | 3 | 1900-01-12 | 2.8 | 188 | 9 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 188 | 0 | 0 | 39.791 | 337.5 | -22.3667 | 86.148 | -75 | 9.1608 | 178.4382 | -8.5846 | 179.4154 | 56.8715 | 56.8715 | 0 | 0 | 0 | 12/3/13:00
12 | 3 | 1900-01-13 | 2.2 | 141 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 141 | 0 | 0 | 39.791 | 337.5417 | -22.3718 | 86.148 | -75 | 9.1442 | 193.434 | 0 | 141 | 44.6945 | 44.6945 | 0 | 0 | 0 | 12/3/14:00
12 | 3 | 1900-01-14 | 2.2 | 130 | 3 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 130 | 0 | 0 | 39.791 | 337.5833 | -22.377 | 86.148 | -75 | 9.1276 | 208.4299 | -2.6054 | 127.3946 | 40.3819 | 40.3819 | 0 | 0 | 0 | 12/3/15:00
12 | 3 | 1900-01-15 | 2.2 | 127 | 4 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 127 | 0 | 0 | 39.791 | 337.625 | -22.3821 | 86.148 | -75 | 9.111 | 223.4257 | -3.0388 | 123.9612 | 39.2935 | 39.2935 | 0 | 0 | 0 | 12/3/16:00
12 | 3 | 1900-01-16 | 2.2 | 25 | 4 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 25 | 0 | 0 | 39.791 | 337.6667 | -22.3873 | 86.148 | -75 | 9.0943 | 238.4216 | -2.4632 | 22.5368 | 7.1438 | 7.1438 | 0 | 0 | 0 | 12/3/17:00
12 | 3 | 1900-01-17 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.7083 | -22.3924 | 86.148 | -75 | 9.0777 | 253.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/18:00
12 | 3 | 1900-01-18 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.75 | -22.3975 | 86.148 | -75 | 9.061 | 268.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/19:00
12 | 3 | 1900-01-19 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.7917 | -22.4026 | 86.148 | -75 | 9.0444 | 283.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/20:00
12 | 3 | 1900-01-20 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.8333 | -22.4077 | 86.148 | -75 | 9.0277 | 298.4049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/21:00
12 | 3 | 1900-01-21 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.875 | -22.4127 | 86.148 | -75 | 9.011 | 313.4007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/22:00
12 | 3 | 1900-01-22 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.9167 | -22.4178 | 86.148 | -75 | 8.9943 | 328.3966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/23:00
12 | 3 | 1900-01-23 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 337.9583 | -22.4229 | 86.148 | -75 | 8.9776 | 343.3924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/3/24:00
12 | 4 | 1899-12-31 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338 | -22.4279 | 86.148 | -75 | 8.9608 | -1.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/1:00
12 | 4 | 1900-01-01 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.0417 | -22.4329 | 86.148 | -75 | 8.9441 | 13.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/2:00
12 | 4 | 1900-01-02 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.0833 | -22.4379 | 86.148 | -75 | 8.9273 | 28.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/3:00
12 | 4 | 1900-01-03 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.125 | -22.4429 | 86.148 | -75 | 8.9105 | 43.3756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/4:00
12 | 4 | 1900-01-04 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.1667 | -22.4479 | 86.148 | -75 | 8.8938 | 58.3714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/5:00
12 | 4 | 1900-01-05 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.2083 | -22.4529 | 86.148 | -75 | 8.877 | 73.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/6:00
12 | 4 | 1900-01-06 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.25 | -22.4579 | 86.148 | -75 | 8.8601 | 88.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/7:00
12 | 4 | 1900-01-07 | -5 | 2 | 12 | 23 | 1 | 0 | 23 | 0 | 0 | 2 | 0 | 0 | 39.791 | 338.2917 | -22.4628 | 86.148 | -75 | 8.8433 | 103.3588 | -4.9031 | -2.9031 | -0.92024 | -0.92024 | 0 | 0 | 0 | 12/4/8:00
12 | 4 | 1900-01-08 | -5 | 43 | 136 | 23 | 1 | 0 | 23 | 0 | 0 | 43 | 0 | 0 | 39.791 | 338.3333 | -22.4678 | 86.148 | -75 | 8.8265 | 118.3546 | -79.1258 | -36.1258 | -11.4512 | -11.4512 | 0 | 0 | 0 | 12/4/9:00
12 | 4 | 1900-01-09 | -3.9 | 98 | 141 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 98 | 0 | 0 | 39.791 | 338.375 | -22.4727 | 86.148 | -75 | 8.8096 | 133.3504 | -103.2177 | -5.2177 | -1.6539 | -1.6539 | 0 | 0 | 0 | 12/4/10:00
12 | 4 | 1900-01-10 | -1.7 | 121 | 510 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 121 | 0 | 0 | 39.791 | 338.4167 | -22.4776 | 86.148 | -75 | 8.7928 | 148.3462 | -433.0238 | -312.0238 | -98.9061 | -98.9061 | 0 | 0 | 0 | 12/4/11:00
12 | 4 | 1900-01-11 | 0 | 133 | 598 | 32 | 1 | 0 | 32 | 0 | 0 | 133 | 0 | 0 | 39.791 | 338.4583 | -22.4825 | 86.148 | -75 | 8.7759 | 163.342 | -553.1025 | -420.1025 | -133.1652 | -133.1652 | 0 | 0 | 0 | 12/4/12:00
12 | 4 | 1900-01-12 | 1.7 | 195 | 407 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 195 | 0 | 0 | 39.791 | 338.5 | -22.4874 | 86.148 | -75 | 8.759 | 178.3378 | -388.4584 | -193.4584 | -61.3229 | -61.3229 | 0 | 0 | 0 | 12/4/13:00
12 | 4 | 1900-01-13 | 3.3 | 258 | 79 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 258 | 0 | 0 | 39.791 | 338.5417 | -22.4923 | 86.148 | -75 | 8.7421 | 193.3335 | -73.9148 | 184.0852 | 58.3518 | 58.3518 | 0 | 0 | 0 | 12/4/14:00
12 | 4 | 1900-01-14 | 4.4 | 182 | 87 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 182 | 0 | 0 | 39.791 | 338.5833 | -22.4972 | 86.148 | -75 | 8.7252 | 208.3293 | -75.67 | 106.33 | 33.7047 | 33.7047 | 0 | 0 | 0 | 12/4/15:00
12 | 4 | 1900-01-15 | 3.9 | 92 | 91 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 92 | 0 | 0 | 39.791 | 338.625 | -22.502 | 86.148 | -75 | 8.7083 | 223.3251 | -69.2833 | 22.7167 | 7.2008 | 7.2008 | 0 | 0 | 0 | 12/4/16:00
12 | 4 | 1900-01-16 | 3.3 | 35 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 35 | 0 | 0 | 39.791 | 338.6667 | -22.5069 | 86.148 | -75 | 8.6913 | 238.3208 | 0 | 35 | 11.0944 | 11.0944 | 0 | 0 | 0 | 12/4/17:00
12 | 4 | 1900-01-17 | 2.8 | 1 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 1 | 0 | 0 | 39.791 | 338.7083 | -22.5117 | 86.148 | -75 | 8.6744 | 253.3166 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 12/4/18:00
12 | 4 | 1900-01-18 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.75 | -22.5165 | 86.148 | -75 | 8.6574 | 268.3124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/19:00
12 | 4 | 1900-01-19 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.7917 | -22.5213 | 86.148 | -75 | 8.6404 | 283.3081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/20:00
12 | 4 | 1900-01-20 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.8333 | -22.5261 | 86.148 | -75 | 8.6235 | 298.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/21:00
12 | 4 | 1900-01-21 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.875 | -22.5309 | 86.148 | -75 | 8.6065 | 313.2996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/22:00
12 | 4 | 1900-01-22 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.9167 | -22.5357 | 86.148 | -75 | 8.5894 | 328.2954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/23:00
12 | 4 | 1900-01-23 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 338.9583 | -22.5404 | 86.148 | -75 | 8.5724 | 343.2911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/4/24:00
12 | 5 | 1899-12-31 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339 | -22.5452 | 86.148 | -75 | 8.5554 | -1.7132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/1:00
12 | 5 | 1900-01-01 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.0417 | -22.5499 | 86.148 | -75 | 8.5383 | 13.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/2:00
12 | 5 | 1900-01-02 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.0833 | -22.5546 | 86.148 | -75 | 8.5213 | 28.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/3:00
12 | 5 | 1900-01-03 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.125 | -22.5593 | 86.148 | -75 | 8.5042 | 43.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/4:00
12 | 5 | 1900-01-04 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.1667 | -22.564 | 86.148 | -75 | 8.4871 | 58.2698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/5:00
12 | 5 | 1900-01-05 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.2083 | -22.5687 | 86.148 | -75 | 8.47 | 73.2655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/6:00
12 | 5 | 1900-01-06 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.25 | -22.5734 | 86.148 | -75 | 8.4529 | 88.2612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/7:00
12 | 5 | 1900-01-07 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.2917 | -22.5781 | 86.148 | -75 | 8.4358 | 103.2569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/8:00
12 | 5 | 1900-01-08 | 0 | 15 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 15 | 0 | 0 | 39.791 | 339.3333 | -22.5827 | 86.148 | -75 | 8.4186 | 118.2527 | 0 | 15 | 4.7547 | 4.7547 | 0 | 0 | 0 | 12/5/9:00
12 | 5 | 1900-01-09 | -0.6 | 74 | 6 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 74 | 0 | 0 | 39.791 | 339.375 | -22.5874 | 86.148 | -75 | 8.4015 | 133.2484 | -4.3914 | 69.6086 | 22.0647 | 22.0647 | 0 | 0 | 0 | 12/5/10:00
12 | 5 | 1900-01-10 | 0 | 111 | 6 | 32 | 1 | 0 | 32 | 0 | 0 | 111 | 0 | 0 | 39.791 | 339.4167 | -22.592 | 86.148 | -75 | 8.3843 | 148.2441 | -5.0945 | 105.9055 | 33.5702 | 33.5702 | 0 | 0 | 0 | 12/5/11:00
12 | 5 | 1900-01-11 | 0.6 | 145 | 1 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 145 | 0 | 0 | 39.791 | 339.4583 | -22.5966 | 86.148 | -75 | 8.3672 | 163.2398 | -0.92517 | 144.0748 | 45.6692 | 45.6692 | 0 | 0 | 0 | 12/5/12:00
12 | 5 | 1900-01-12 | 0.6 | 141 | 58 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 141 | 0 | 0 | 39.791 | 339.5 | -22.6012 | 86.148 | -75 | 8.35 | 178.2355 | -55.3897 | 85.6103 | 27.137 | 27.137 | 0 | 0 | 0 | 12/5/13:00
12 | 5 | 1900-01-13 | 0.6 | 146 | 14 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 146 | 0 | 0 | 39.791 | 339.5417 | -22.6058 | 86.148 | -75 | 8.3328 | 193.2312 | -13.1113 | 132.8887 | 42.1234 | 42.1234 | 0 | 0 | 0 | 12/5/14:00
12 | 5 | 1900-01-14 | 0.6 | 180 | 61 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 180 | 0 | 0 | 39.791 | 339.5833 | -22.6104 | 86.148 | -75 | 8.3156 | 208.2269 | -53.1326 | 126.8674 | 40.2147 | 40.2147 | 0 | 0 | 0 | 12/5/15:00
12 | 5 | 1900-01-15 | 0.6 | 89 | 120 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 89 | 0 | 0 | 39.791 | 339.625 | -22.615 | 86.148 | -75 | 8.2984 | 223.2226 | -91.556 | -2.556 | -0.81022 | -0.81022 | 0 | 0 | 0 | 12/5/16:00
12 | 5 | 1900-01-16 | 0.6 | 20 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 20 | 0 | 0 | 39.791 | 339.6667 | -22.6195 | 86.148 | -75 | 8.2811 | 238.2183 | 0 | 20 | 6.3397 | 6.3397 | 0 | 0 | 0 | 12/5/17:00
12 | 5 | 1900-01-17 | 0 | 4 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 4 | 0 | 0 | 39.791 | 339.7083 | -22.624 | 86.148 | -75 | 8.2639 | 253.214 | 0 | 4 | 1.2679 | 1.2679 | 0 | 0 | 0 | 12/5/18:00
12 | 5 | 1900-01-18 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.75 | -22.6286 | 86.148 | -75 | 8.2466 | 268.2097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/19:00
12 | 5 | 1900-01-19 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.7917 | -22.6331 | 86.148 | -75 | 8.2294 | 283.2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/20:00
12 | 5 | 1900-01-20 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.8333 | -22.6376 | 86.148 | -75 | 8.2121 | 298.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/21:00
12 | 5 | 1900-01-21 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.875 | -22.6421 | 86.148 | -75 | 8.1948 | 313.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/22:00
12 | 5 | 1900-01-22 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.9167 | -22.6466 | 86.148 | -75 | 8.1775 | 328.1924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/23:00
12 | 5 | 1900-01-23 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 339.9583 | -22.651 | 86.148 | -75 | 8.1602 | 343.1881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/5/24:00
12 | 6 | 1899-12-31 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340 | -22.6555 | 86.148 | -75 | 8.1429 | -1.8163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/1:00
12 | 6 | 1900-01-01 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.0417 | -22.66 | 86.148 | -75 | 8.1255 | 13.1794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/2:00
12 | 6 | 1900-01-02 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.0833 | -22.6644 | 86.148 | -75 | 8.1082 | 28.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/3:00
12 | 6 | 1900-01-03 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.125 | -22.6688 | 86.148 | -75 | 8.0908 | 43.1707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/4:00
12 | 6 | 1900-01-04 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.1667 | -22.6732 | 86.148 | -75 | 8.0735 | 58.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/5:00
12 | 6 | 1900-01-05 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.2083 | -22.6776 | 86.148 | -75 | 8.0561 | 73.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/6:00
12 | 6 | 1900-01-06 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.25 | -22.682 | 86.148 | -75 | 8.0387 | 88.1577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/7:00
12 | 6 | 1900-01-07 | -7.2 | 3 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 3 | 0 | 0 | 39.791 | 340.2917 | -22.6864 | 86.148 | -75 | 8.0213 | 103.1533 | 0 | 3 | 0.95095 | 0.95095 | 0 | 0 | 0 | 12/6/8:00
12 | 6 | 1900-01-08 | -9.4 | 25 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 25 | 0 | 0 | 39.791 | 340.3333 | -22.6907 | 86.148 | -75 | 8.0039 | 118.149 | 0 | 25 | 7.9246 | 7.9246 | 0 | 0 | 0 | 12/6/9:00
12 | 6 | 1900-01-09 | -11.1 | 145 | 4 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 145 | 0 | 0 | 39.791 | 340.375 | -22.6951 | 86.148 | -75 | 7.9864 | 133.1446 | -2.9268 | 142.0732 | 45.0347 | 45.0347 | 0 | 0 | 0 | 12/6/10:00
12 | 6 | 1900-01-10 | -13.3 | 125 | 13 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 125 | 0 | 0 | 39.791 | 340.4167 | -22.6994 | 86.148 | -75 | 7.969 | 148.1403 | -11.0375 | 113.9625 | 36.1241 | 36.1241 | 0 | 0 | 0 | 12/6/11:00
12 | 6 | 1900-01-11 | -13.9 | 241 | 24 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 241 | 0 | 0 | 39.791 | 340.4583 | -22.7037 | 86.148 | -75 | 7.9516 | 163.1359 | -22.209 | 218.791 | 69.3529 | 69.3529 | 0 | 0 | 0 | 12/6/12:00
12 | 6 | 1900-01-12 | -15 | 274 | 16 | 5 | 1 | 0 | 5 | 0 | 0 | 274 | 0 | 0 | 39.791 | 340.5 | -22.708 | 86.148 | -75 | 7.9341 | 178.1315 | -15.2881 | 258.7119 | 82.0072 | 82.0072 | 0 | 0 | 0 | 12/6/13:00
12 | 6 | 1900-01-13 | -15.6 | 184 | 559 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 184 | 0 | 0 | 39.791 | 340.5417 | -22.7123 | 86.148 | -75 | 7.9166 | 193.1272 | -523.9957 | -339.9957 | -107.7727 | -107.7727 | 0 | 0 | 0 | 12/6/14:00
12 | 6 | 1900-01-14 | -15.6 | 173 | 322 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 173 | 0 | 0 | 39.791 | 340.5833 | -22.7166 | 86.148 | -75 | 7.8991 | 208.1228 | -280.8632 | -107.8632 | -34.1907 | -34.1907 | 0 | 0 | 0 | 12/6/15:00
12 | 6 | 1900-01-15 | -16.7 | 122 | 324 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 122 | 0 | 0 | 39.791 | 340.625 | -22.7209 | 86.148 | -75 | 7.8816 | 223.1184 | -247.7115 | -125.7115 | -39.8484 | -39.8484 | 0 | 0 | 0 | 12/6/16:00
12 | 6 | 1900-01-16 | -17.2 | 56 | 145 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 56 | 0 | 0 | 39.791 | 340.6667 | -22.7252 | 86.148 | -75 | 7.8641 | 238.114 | -90.1334 | -34.1334 | -10.8197 | -10.8197 | 0 | 0 | 0 | 12/6/17:00
12 | 6 | 1900-01-17 | -17.8 | 6 | 31 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 6 | 0 | 0 | 39.791 | 340.7083 | -22.7294 | 86.148 | -75 | 7.8466 | 253.1097 | -14.0488 | -8.0488 | -2.5513 | -2.5513 | 0 | 0 | 0 | 12/6/18:00
12 | 6 | 1900-01-18 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.75 | -22.7337 | 86.148 | -75 | 7.8291 | 268.1053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/19:00
12 | 6 | 1900-01-19 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.7917 | -22.7379 | 86.148 | -75 | 7.8116 | 283.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/20:00
12 | 6 | 1900-01-20 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.8333 | -22.7421 | 86.148 | -75 | 7.794 | 298.0965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/21:00
12 | 6 | 1900-01-21 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.875 | -22.7463 | 86.148 | -75 | 7.7764 | 313.0921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/22:00
12 | 6 | 1900-01-22 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.9167 | -22.7505 | 86.148 | -75 | 7.7589 | 328.0877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/23:00
12 | 6 | 1900-01-23 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 340.9583 | -22.7547 | 86.148 | -75 | 7.7413 | 343.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/6/24:00
12 | 7 | 1899-12-31 | -17.2 | 0 | 0 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341 | -22.7588 | 86.148 | -75 | 7.7237 | -1.9211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/1:00
12 | 7 | 1900-01-01 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.0417 | -22.763 | 86.148 | -75 | 7.7061 | 13.0745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/2:00
12 | 7 | 1900-01-02 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.0833 | -22.7671 | 86.148 | -75 | 7.6885 | 28.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/3:00
12 | 7 | 1900-01-03 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.125 | -22.7713 | 86.148 | -75 | 7.6708 | 43.0657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/4:00
12 | 7 | 1900-01-04 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.1667 | -22.7754 | 86.148 | -75 | 7.6532 | 58.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/5:00
12 | 7 | 1900-01-05 | -18.9 | 0 | 0 | -2.02 | 1 | 0 | -2.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.2083 | -22.7795 | 86.148 | -75 | 7.6356 | 73.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/6:00
12 | 7 | 1900-01-06 | -18.9 | 0 | 0 | -2.02 | 1 | 0 | -2.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.25 | -22.7836 | 86.148 | -75 | 7.6179 | 88.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/7:00
12 | 7 | 1900-01-07 | -19.4 | 0 | 0 | -2.92 | 1 | 0 | -2.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.2917 | -22.7876 | 86.148 | -75 | 7.6002 | 103.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/8:00
12 | 7 | 1900-01-08 | -18.9 | 32 | 116 | -2.02 | 1 | 0 | -2.02 | 0 | 0 | 32 | 0 | 0 | 39.791 | 341.3333 | -22.7917 | 86.148 | -75 | 7.5826 | 118.0436 | -67.3919 | -35.3919 | -11.2186 | -11.2186 | 0 | 0 | 0 | 12/7/9:00
12 | 7 | 1900-01-09 | -17.2 | 73 | 531 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 73 | 0 | 0 | 39.791 | 341.375 | -22.7958 | 86.148 | -75 | 7.5649 | 133.0392 | -388.3849 | -315.3849 | -99.9715 | -99.9715 | 0 | 0 | 0 | 12/7/10:00
12 | 7 | 1900-01-10 | -16.1 | 116 | 578 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 116 | 0 | 0 | 39.791 | 341.4167 | -22.7998 | 86.148 | -75 | 7.5472 | 148.0348 | -490.689 | -374.689 | -118.7699 | -118.7699 | 0 | 0 | 0 | 12/7/11:00
12 | 7 | 1900-01-11 | -14.4 | 130 | 664 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 130 | 0 | 0 | 39.791 | 341.4583 | -22.8038 | 86.148 | -75 | 7.5294 | 163.0304 | -614.5515 | -484.5515 | -153.5944 | -153.5944 | 0 | 0 | 0 | 12/7/12:00
12 | 7 | 1900-01-12 | -13.3 | 144 | 681 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 144 | 0 | 0 | 39.791 | 341.5 | -22.8079 | 86.148 | -75 | 7.5117 | 178.0259 | -651.0158 | -507.0158 | -160.7152 | -160.7152 | 0 | 0 | 0 | 12/7/13:00
12 | 7 | 1900-01-13 | -11.7 | 132 | 670 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 132 | 0 | 0 | 39.791 | 341.5417 | -22.8119 | 86.148 | -75 | 7.494 | 193.0215 | -628.5927 | -496.5927 | -157.4112 | -157.4112 | 0 | 0 | 0 | 12/7/14:00
12 | 7 | 1900-01-14 | -10.6 | 116 | 606 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 116 | 0 | 0 | 39.791 | 341.5833 | -22.8159 | 86.148 | -75 | 7.4762 | 208.0171 | -529.2977 | -413.2977 | -131.0082 | -131.0082 | 0 | 0 | 0 | 12/7/15:00
12 | 7 | 1900-01-15 | -9.4 | 94 | 441 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 94 | 0 | 0 | 39.791 | 341.625 | -22.8198 | 86.148 | -75 | 7.4585 | 223.0126 | -337.8407 | -243.8407 | -77.2933 | -77.2933 | 0 | 0 | 0 | 12/7/16:00
12 | 7 | 1900-01-16 | -9.4 | 51 | 186 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 51 | 0 | 0 | 39.791 | 341.6667 | -22.8238 | 86.148 | -75 | 7.4407 | 238.0082 | -115.9645 | -64.9645 | -20.5926 | -20.5926 | 0 | 0 | 0 | 12/7/17:00
12 | 7 | 1900-01-17 | -10.6 | 4 | 1 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 4 | 0 | 0 | 39.791 | 341.7083 | -22.8278 | 86.148 | -75 | 7.4229 | 253.0037 | -0.45531 | 3.5447 | 1.1236 | 1.1236 | 0 | 0 | 0 | 12/7/18:00
12 | 7 | 1900-01-18 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.75 | -22.8317 | 86.148 | -75 | 7.4052 | 267.9993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/19:00
12 | 7 | 1900-01-19 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.7917 | -22.8356 | 86.148 | -75 | 7.3874 | 282.9948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/20:00
12 | 7 | 1900-01-20 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.8333 | -22.8396 | 86.148 | -75 | 7.3696 | 297.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/21:00
12 | 7 | 1900-01-21 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.875 | -22.8435 | 86.148 | -75 | 7.3517 | 312.9859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/22:00
12 | 7 | 1900-01-22 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.9167 | -22.8474 | 86.148 | -75 | 7.3339 | 327.9815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/23:00
12 | 7 | 1900-01-23 | -10 | 0 | 0 | 14 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 39.791 | 341.9583 | -22.8512 | 86.148 | -75 | 7.3161 | 342.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/7/24:00
12 | 8 | 1899-12-31 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342 | -22.8551 | 86.148 | -75 | 7.2982 | -2.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/1:00
12 | 8 | 1900-01-01 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.0417 | -22.859 | 86.148 | -75 | 7.2804 | 12.9681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/2:00
12 | 8 | 1900-01-02 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.0833 | -22.8628 | 86.148 | -75 | 7.2625 | 27.9636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/3:00
12 | 8 | 1900-01-03 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.125 | -22.8666 | 86.148 | -75 | 7.2446 | 42.9592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/4:00
12 | 8 | 1900-01-04 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.1667 | -22.8705 | 86.148 | -75 | 7.2267 | 57.9547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/5:00
12 | 8 | 1900-01-05 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.2083 | -22.8743 | 86.148 | -75 | 7.2088 | 72.9502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/6:00
12 | 8 | 1900-01-06 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.25 | -22.8781 | 86.148 | -75 | 7.1909 | 87.9457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/7:00
12 | 8 | 1900-01-07 | -5 | 1 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 1 | 0 | 0 | 39.791 | 342.2917 | -22.8819 | 86.148 | -75 | 7.173 | 102.9413 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 12/8/8:00
12 | 8 | 1900-01-08 | -4.4 | 27 | 4 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 27 | 0 | 0 | 39.791 | 342.3333 | -22.8856 | 86.148 | -75 | 7.1551 | 117.9368 | -2.3221 | 24.6779 | 7.8224 | 7.8224 | 0 | 0 | 0 | 12/8/9:00
12 | 8 | 1900-01-09 | -3.9 | 106 | 21 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 106 | 0 | 0 | 39.791 | 342.375 | -22.8894 | 86.148 | -75 | 7.1371 | 132.9323 | -15.3528 | 90.6472 | 28.7336 | 28.7336 | 0 | 0 | 0 | 12/8/10:00
12 | 8 | 1900-01-10 | -3.9 | 181 | 12 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 181 | 0 | 0 | 39.791 | 342.4167 | -22.8931 | 86.148 | -75 | 7.1192 | 147.9278 | -10.1855 | 170.8145 | 54.1452 | 54.1452 | 0 | 0 | 0 | 12/8/11:00
12 | 8 | 1900-01-11 | -3.9 | 82 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 82 | 0 | 0 | 39.791 | 342.4583 | -22.8969 | 86.148 | -75 | 7.1012 | 162.9233 | 0 | 82 | 25.9926 | 25.9926 | 0 | 0 | 0 | 12/8/12:00
12 | 8 | 1900-01-12 | -2.8 | 133 | 4 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 133 | 0 | 0 | 39.791 | 342.5 | -22.9006 | 86.148 | -75 | 7.0833 | 177.9188 | -3.8256 | 129.1744 | 40.946 | 40.946 | 0 | 0 | 0 | 12/8/13:00
12 | 8 | 1900-01-13 | -0.6 | 141 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 141 | 0 | 0 | 39.791 | 342.5417 | -22.9043 | 86.148 | -75 | 7.0653 | 192.9143 | 0 | 141 | 44.6945 | 44.6945 | 0 | 0 | 0 | 12/8/14:00
12 | 8 | 1900-01-14 | 0.6 | 121 | 7 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 121 | 0 | 0 | 39.791 | 342.5833 | -22.908 | 86.148 | -75 | 7.0473 | 207.9098 | -6.122 | 114.878 | 36.4143 | 36.4143 | 0 | 0 | 0 | 12/8/15:00
12 | 8 | 1900-01-15 | 1.1 | 91 | 4 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 91 | 0 | 0 | 39.791 | 342.625 | -22.9117 | 86.148 | -75 | 7.0293 | 222.9053 | -3.0703 | 87.9297 | 27.8722 | 27.8722 | 0 | 0 | 0 | 12/8/16:00
12 | 8 | 1900-01-16 | 1.7 | 54 | 1 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 54 | 0 | 0 | 39.791 | 342.6667 | -22.9154 | 86.148 | -75 | 7.0113 | 237.9008 | -0.62528 | 53.3747 | 16.9189 | 16.9189 | 0 | 0 | 0 | 12/8/17:00
12 | 8 | 1900-01-17 | 1.1 | 6 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 6 | 0 | 0 | 39.791 | 342.7083 | -22.919 | 86.148 | -75 | 6.9933 | 252.8963 | 0 | 6 | 1.9019 | 1.9019 | 0 | 0 | 0 | 12/8/18:00
12 | 8 | 1900-01-18 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.75 | -22.9227 | 86.148 | -75 | 6.9752 | 267.8918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/19:00
12 | 8 | 1900-01-19 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.7917 | -22.9263 | 86.148 | -75 | 6.9572 | 282.8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/20:00
12 | 8 | 1900-01-20 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.8333 | -22.9299 | 86.148 | -75 | 6.9391 | 297.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/21:00
12 | 8 | 1900-01-21 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.875 | -22.9335 | 86.148 | -75 | 6.9211 | 312.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/22:00
12 | 8 | 1900-01-22 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.9167 | -22.9371 | 86.148 | -75 | 6.903 | 327.8738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/23:00
12 | 8 | 1900-01-23 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 342.9583 | -22.9407 | 86.148 | -75 | 6.8849 | 342.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/8/24:00
12 | 9 | 1899-12-31 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343 | -22.9443 | 86.148 | -75 | 6.8669 | -2.1353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/1:00
12 | 9 | 1900-01-01 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.0417 | -22.9479 | 86.148 | -75 | 6.8488 | 12.8602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/2:00
12 | 9 | 1900-01-02 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.0833 | -22.9514 | 86.148 | -75 | 6.8307 | 27.8557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/3:00
12 | 9 | 1900-01-03 | -8.3 | 0 | 0 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.125 | -22.9549 | 86.148 | -75 | 6.8125 | 42.8511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/4:00
12 | 9 | 1900-01-04 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.1667 | -22.9585 | 86.148 | -75 | 6.7944 | 57.8466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/5:00
12 | 9 | 1900-01-05 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.2083 | -22.962 | 86.148 | -75 | 6.7763 | 72.8421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/6:00
12 | 9 | 1900-01-06 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.25 | -22.9655 | 86.148 | -75 | 6.7581 | 87.8375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/7:00
12 | 9 | 1900-01-07 | -16.1 | 1 | 3 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 1 | 0 | 0 | 39.791 | 343.2917 | -22.969 | 86.148 | -75 | 6.74 | 102.833 | -1.2206 | -0.22064 | -0.069938 | -0.069938 | 0 | 0 | 0 | 12/9/8:00
12 | 9 | 1900-01-08 | -16.7 | 31 | 328 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 31 | 0 | 0 | 39.791 | 343.3333 | -22.9724 | 86.148 | -75 | 6.7218 | 117.8285 | -190.2512 | -159.2512 | -50.4798 | -50.4798 | 0 | 0 | 0 | 12/9/9:00
12 | 9 | 1900-01-09 | -16.7 | 58 | 632 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 58 | 0 | 0 | 39.791 | 343.375 | -22.9759 | 86.148 | -75 | 6.7037 | 132.8239 | -461.7947 | -403.7947 | -127.9959 | -127.9959 | 0 | 0 | 0 | 12/9/10:00
12 | 9 | 1900-01-10 | -16.7 | 73 | 824 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 73 | 0 | 0 | 39.791 | 343.4167 | -22.9793 | 86.148 | -75 | 6.6855 | 147.8194 | -699.233 | -626.233 | -198.5049 | -198.5049 | 0 | 0 | 0 | 12/9/11:00
12 | 9 | 1900-01-11 | -16.1 | 132 | 676 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 132 | 0 | 0 | 39.791 | 343.4583 | -22.9828 | 86.148 | -75 | 6.6673 | 162.8148 | -625.7708 | -493.7708 | -156.5167 | -156.5167 | 0 | 0 | 0 | 12/9/12:00
12 | 9 | 1900-01-12 | -16.1 | 159 | 670 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 159 | 0 | 0 | 39.791 | 343.5 | -22.9862 | 86.148 | -75 | 6.6491 | 177.8103 | -641.0418 | -482.0418 | -152.7988 | -152.7988 | 0 | 0 | 0 | 12/9/13:00
12 | 9 | 1900-01-13 | -15.6 | 207 | 324 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 207 | 0 | 0 | 39.791 | 343.5417 | -22.9896 | 86.148 | -75 | 6.6309 | 192.8057 | -304.4688 | -97.4688 | -30.8959 | -30.8959 | 0 | 0 | 0 | 12/9/14:00
12 | 9 | 1900-01-14 | -15.6 | 155 | 548 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 155 | 0 | 0 | 39.791 | 343.5833 | -22.993 | 86.148 | -75 | 6.6127 | 207.8012 | -479.8741 | -324.8741 | -102.9794 | -102.9794 | 0 | 0 | 0 | 12/9/15:00
12 | 9 | 1900-01-15 | -15.6 | 90 | 491 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 90 | 0 | 0 | 39.791 | 343.625 | -22.9964 | 86.148 | -75 | 6.5944 | 222.7966 | -377.5972 | -287.5972 | -91.1633 | -91.1633 | 0 | 0 | 0 | 12/9/16:00
12 | 9 | 1900-01-16 | -15.6 | 50 | 329 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 50 | 0 | 0 | 39.791 | 343.6667 | -22.9998 | 86.148 | -75 | 6.5762 | 237.7921 | -206.2992 | -156.2992 | -49.5441 | -49.5441 | 0 | 0 | 0 | 12/9/17:00
12 | 9 | 1900-01-17 | -16.1 | 8 | 48 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 8 | 0 | 0 | 39.791 | 343.7083 | -23.0031 | 86.148 | -75 | 6.558 | 252.7875 | -22.0509 | -14.0509 | -4.4539 | -4.4539 | 0 | 0 | 0 | 12/9/18:00
12 | 9 | 1900-01-18 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.75 | -23.0065 | 86.148 | -75 | 6.5397 | 267.7829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/19:00
12 | 9 | 1900-01-19 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.7917 | -23.0098 | 86.148 | -75 | 6.5215 | 282.7784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/20:00
12 | 9 | 1900-01-20 | -16.1 | 0 | 0 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.8333 | -23.0132 | 86.148 | -75 | 6.5032 | 297.7738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/21:00
12 | 9 | 1900-01-21 | -16.1 | 0 | 0 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.875 | -23.0165 | 86.148 | -75 | 6.4849 | 312.7692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/22:00
12 | 9 | 1900-01-22 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.9167 | -23.0198 | 86.148 | -75 | 6.4666 | 327.7647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/23:00
12 | 9 | 1900-01-23 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 343.9583 | -23.0231 | 86.148 | -75 | 6.4483 | 342.7601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/9/24:00
12 | 10 | 1899-12-31 | -17.2 | 0 | 0 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344 | -23.0263 | 86.148 | -75 | 6.43 | -2.2445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/1:00
12 | 10 | 1900-01-01 | -17.2 | 0 | 0 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.0417 | -23.0296 | 86.148 | -75 | 6.4117 | 12.7509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/2:00
12 | 10 | 1900-01-02 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.0833 | -23.0329 | 86.148 | -75 | 6.3934 | 27.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/3:00
12 | 10 | 1900-01-03 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.125 | -23.0361 | 86.148 | -75 | 6.375 | 42.7418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/4:00
12 | 10 | 1900-01-04 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.1667 | -23.0393 | 86.148 | -75 | 6.3567 | 57.7372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/5:00
12 | 10 | 1900-01-05 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.2083 | -23.0425 | 86.148 | -75 | 6.3383 | 72.7326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/6:00
12 | 10 | 1900-01-06 | -16.7 | 0 | 0 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.25 | -23.0457 | 86.148 | -75 | 6.32 | 87.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/7:00
12 | 10 | 1900-01-07 | -18.9 | 0 | 0 | -2.02 | 1 | 0 | -2.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.2917 | -23.0489 | 86.148 | -75 | 6.3016 | 102.7234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/8:00
12 | 10 | 1900-01-08 | -19.4 | 42 | 102 | -2.92 | 1 | 0 | -2.92 | 0 | 0 | 42 | 0 | 0 | 39.791 | 344.3333 | -23.0521 | 86.148 | -75 | 6.2832 | 117.7188 | -59.105 | -17.105 | -5.422 | -5.422 | 0 | 0 | 0 | 12/10/9:00
12 | 10 | 1900-01-09 | -19.4 | 112 | 167 | -2.92 | 1 | 0 | -2.92 | 0 | 0 | 112 | 0 | 0 | 39.791 | 344.375 | -23.0553 | 86.148 | -75 | 6.2649 | 132.7142 | -121.9479 | -9.9479 | -3.1533 | -3.1533 | 0 | 0 | 0 | 12/10/10:00
12 | 10 | 1900-01-10 | -18.9 | 181 | 173 | -2.02 | 1 | 0 | -2.02 | 0 | 0 | 181 | 0 | 0 | 39.791 | 344.4167 | -23.0584 | 86.148 | -75 | 6.2465 | 147.7096 | -146.7599 | 34.2401 | 10.8535 | 10.8535 | 0 | 0 | 0 | 12/10/11:00
12 | 10 | 1900-01-11 | -17.8 | 133 | 691 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 133 | 0 | 0 | 39.791 | 344.4583 | -23.0616 | 86.148 | -75 | 6.2281 | 162.705 | -639.6656 | -506.6656 | -160.6041 | -160.6041 | 0 | 0 | 0 | 12/10/12:00
12 | 10 | 1900-01-12 | -17.2 | 115 | 807 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 115 | 0 | 0 | 39.791 | 344.5 | -23.0647 | 86.148 | -75 | 6.2097 | 177.7004 | -772.3967 | -657.3967 | -208.3833 | -208.3833 | 0 | 0 | 0 | 12/10/13:00
12 | 10 | 1900-01-13 | -16.7 | 133 | 727 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 133 | 0 | 0 | 39.791 | 344.5417 | -23.0678 | 86.148 | -75 | 6.1912 | 192.6958 | -683.6865 | -550.6865 | -174.558 | -174.558 | 0 | 0 | 0 | 12/10/14:00
12 | 10 | 1900-01-14 | -16.1 | 127 | 717 | 3.02 | 1 | 0 | 3.02 | 0 | 0 | 127 | 0 | 0 | 39.791 | 344.5833 | -23.0709 | 86.148 | -75 | 6.1728 | 207.6912 | -628.6322 | -501.6322 | -159.0087 | -159.0087 | 0 | 0 | 0 | 12/10/15:00
12 | 10 | 1900-01-15 | -15.6 | 104 | 576 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 104 | 0 | 0 | 39.791 | 344.625 | -23.074 | 86.148 | -75 | 6.1544 | 222.6866 | -443.7832 | -339.7832 | -107.7053 | -107.7053 | 0 | 0 | 0 | 12/10/16:00
12 | 10 | 1900-01-16 | -15 | 26 | 481 | 5 | 1 | 0 | 5 | 0 | 0 | 26 | 0 | 0 | 39.791 | 344.6667 | -23.0771 | 86.148 | -75 | 6.1359 | 237.682 | -302.4411 | -276.4411 | -87.627 | -87.627 | 0 | 0 | 0 | 12/10/17:00
12 | 10 | 1900-01-17 | -16.7 | 6 | 77 | 1.94 | 1 | 0 | 1.94 | 0 | 0 | 6 | 0 | 0 | 39.791 | 344.7083 | -23.0801 | 86.148 | -75 | 6.1175 | 252.6774 | -35.5249 | -29.5249 | -9.3589 | -9.3589 | 0 | 0 | 0 | 12/10/18:00
12 | 10 | 1900-01-18 | -17.2 | 0 | 0 | 1.04 | 1 | 0 | 1.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.75 | -23.0832 | 86.148 | -75 | 6.099 | 267.6728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/19:00
12 | 10 | 1900-01-19 | -17.8 | 0 | 0 | -0.04 | 1 | 0 | -0.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.7917 | -23.0862 | 86.148 | -75 | 6.0805 | 282.6681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/20:00
12 | 10 | 1900-01-20 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.8333 | -23.0892 | 86.148 | -75 | 6.0621 | 297.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/21:00
12 | 10 | 1900-01-21 | -18.9 | 0 | 0 | -2.02 | 1 | 0 | -2.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.875 | -23.0923 | 86.148 | -75 | 6.0436 | 312.6589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/22:00
12 | 10 | 1900-01-22 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.9167 | -23.0953 | 86.148 | -75 | 6.0251 | 327.6543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/23:00
12 | 10 | 1900-01-23 | -18.3 | 0 | 0 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 344.9583 | -23.0982 | 86.148 | -75 | 6.0066 | 342.6496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/10/24:00
12 | 11 | 1899-12-31 | -20 | 0 | 0 | -4 | 1 | 0 | -4 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345 | -23.1012 | 86.148 | -75 | 5.9881 | -2.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/1:00
12 | 11 | 1900-01-01 | -20.6 | 0 | 0 | -5.08 | 1 | 0 | -5.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.0417 | -23.1042 | 86.148 | -75 | 5.9696 | 12.6404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/2:00
12 | 11 | 1900-01-02 | -20 | 0 | 0 | -4 | 1 | 0 | -4 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.0833 | -23.1071 | 86.148 | -75 | 5.951 | 27.6358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/3:00
12 | 11 | 1900-01-03 | -21.1 | 0 | 0 | -5.98 | 1 | 0 | -5.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.125 | -23.1101 | 86.148 | -75 | 5.9325 | 42.6311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/4:00
12 | 11 | 1900-01-04 | -22.2 | 0 | 0 | -7.96 | 1 | 0 | -7.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.1667 | -23.113 | 86.148 | -75 | 5.914 | 57.6265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/5:00
12 | 11 | 1900-01-05 | -22.8 | 0 | 0 | -9.04 | 1 | 0 | -9.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.2083 | -23.1159 | 86.148 | -75 | 5.8954 | 72.6219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/6:00
12 | 11 | 1900-01-06 | -22.8 | 0 | 0 | -9.04 | 1 | 0 | -9.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.25 | -23.1188 | 86.148 | -75 | 5.8769 | 87.6172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/7:00
12 | 11 | 1900-01-07 | -22.8 | 0 | 0 | -9.04 | 1 | 0 | -9.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.2917 | -23.1217 | 86.148 | -75 | 5.8583 | 102.6126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/8:00
12 | 11 | 1900-01-08 | -20.6 | 21 | 409 | -5.08 | 1 | 0 | -5.08 | 0 | 0 | 21 | 0 | 0 | 39.791 | 345.3333 | -23.1246 | 86.148 | -75 | 5.8397 | 117.6079 | -236.7363 | -215.7363 | -68.3846 | -68.3846 | 0 | 0 | 0 | 12/11/9:00
12 | 11 | 1900-01-09 | -18.3 | 41 | 719 | -0.94 | 1 | 0 | -0.94 | 0 | 0 | 41 | 0 | 0 | 39.791 | 345.375 | -23.1274 | 86.148 | -75 | 5.8211 | 132.6033 | -524.6581 | -483.6581 | -153.3112 | -153.3112 | 0 | 0 | 0 | 12/11/10:00
12 | 11 | 1900-01-10 | -15.6 | 55 | 847 | 3.92 | 1 | 0 | 3.92 | 0 | 0 | 55 | 0 | 0 | 39.791 | 345.4167 | -23.1303 | 86.148 | -75 | 5.8025 | 147.5986 | -718.2644 | -663.2644 | -210.2432 | -210.2432 | 0 | 0 | 0 | 12/11/11:00
12 | 11 | 1900-01-11 | -13.9 | 64 | 894 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 64 | 0 | 0 | 39.791 | 345.4583 | -23.1331 | 86.148 | -75 | 5.7839 | 162.594 | -827.5557 | -763.5557 | -242.0338 | -242.0338 | 0 | 0 | 0 | 12/11/12:00
12 | 11 | 1900-01-12 | -12.8 | 111 | 767 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 111 | 0 | 0 | 39.791 | 345.5 | -23.136 | 86.148 | -75 | 5.7653 | 177.5893 | -734.343 | -623.343 | -197.5888 | -197.5888 | 0 | 0 | 0 | 12/11/13:00
12 | 11 | 1900-01-13 | -11.7 | 130 | 605 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 130 | 0 | 0 | 39.791 | 345.5417 | -23.1388 | 86.148 | -75 | 5.7467 | 192.5847 | -569.3573 | -439.3573 | -139.2686 | -139.2686 | 0 | 0 | 0 | 12/11/14:00
12 | 11 | 1900-01-14 | -11.1 | 70 | 830 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 70 | 0 | 0 | 39.791 | 345.5833 | -23.1416 | 86.148 | -75 | 5.7281 | 207.58 | -728.5625 | -658.5625 | -208.7528 | -208.7528 | 0 | 0 | 0 | 12/11/15:00
12 | 11 | 1900-01-15 | -10.6 | 73 | 598 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 73 | 0 | 0 | 39.791 | 345.625 | -23.1444 | 86.148 | -75 | 5.7095 | 222.5754 | -461.5583 | -388.5583 | -123.1662 | -123.1662 | 0 | 0 | 0 | 12/11/16:00
12 | 11 | 1900-01-16 | -10 | 28 | 528 | 14 | 1 | 0 | 14 | 0 | 0 | 28 | 0 | 0 | 39.791 | 345.6667 | -23.1471 | 86.148 | -75 | 5.6908 | 237.5707 | -332.8814 | -304.8814 | -96.6421 | -96.6421 | 0 | 0 | 0 | 12/11/17:00
12 | 11 | 1900-01-17 | -11.1 | 6 | 68 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 6 | 0 | 0 | 39.791 | 345.7083 | -23.1499 | 86.148 | -75 | 5.6722 | 252.5661 | -31.503 | -25.503 | -8.084 | -8.084 | 0 | 0 | 0 | 12/11/18:00
12 | 11 | 1900-01-18 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.75 | -23.1527 | 86.148 | -75 | 5.6536 | 267.5614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/19:00
12 | 11 | 1900-01-19 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.7917 | -23.1554 | 86.148 | -75 | 5.6349 | 282.5567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/20:00
12 | 11 | 1900-01-20 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.8333 | -23.1581 | 86.148 | -75 | 5.6162 | 297.5521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/21:00
12 | 11 | 1900-01-21 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.875 | -23.1608 | 86.148 | -75 | 5.5976 | 312.5474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/22:00
12 | 11 | 1900-01-22 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.9167 | -23.1635 | 86.148 | -75 | 5.5789 | 327.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/23:00
12 | 11 | 1900-01-23 | -8.9 | 0 | 0 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 345.9583 | -23.1662 | 86.148 | -75 | 5.5602 | 342.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/11/24:00
12 | 12 | 1899-12-31 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346 | -23.1689 | 86.148 | -75 | 5.5415 | -2.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/1:00
12 | 12 | 1900-01-01 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.0417 | -23.1716 | 86.148 | -75 | 5.5228 | 12.5287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/2:00
12 | 12 | 1900-01-02 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.0833 | -23.1742 | 86.148 | -75 | 5.5041 | 27.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/3:00
12 | 12 | 1900-01-03 | -3.3 | 0 | 0 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.125 | -23.1768 | 86.148 | -75 | 5.4854 | 42.5193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/4:00
12 | 12 | 1900-01-04 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.1667 | -23.1795 | 86.148 | -75 | 5.4666 | 57.5147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/5:00
12 | 12 | 1900-01-05 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.2083 | -23.1821 | 86.148 | -75 | 5.4479 | 72.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/6:00
12 | 12 | 1900-01-06 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.25 | -23.1847 | 86.148 | -75 | 5.4292 | 87.5053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/7:00
12 | 12 | 1900-01-07 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.2917 | -23.1873 | 86.148 | -75 | 5.4104 | 102.5006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/8:00
12 | 12 | 1900-01-08 | 1.7 | 18 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 18 | 0 | 0 | 39.791 | 346.3333 | -23.1898 | 86.148 | -75 | 5.3917 | 117.4959 | 0 | 18 | 5.7057 | 5.7057 | 0 | 0 | 0 | 12/12/9:00
12 | 12 | 1900-01-09 | 2.2 | 77 | 6 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 77 | 0 | 0 | 39.791 | 346.375 | -23.1924 | 86.148 | -75 | 5.3729 | 132.4912 | -4.3747 | 72.6253 | 23.0209 | 23.0209 | 0 | 0 | 0 | 12/12/10:00
12 | 12 | 1900-01-10 | 2.8 | 127 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 127 | 0 | 0 | 39.791 | 346.4167 | -23.195 | 86.148 | -75 | 5.3541 | 147.4865 | 0 | 127 | 40.2568 | 40.2568 | 0 | 0 | 0 | 12/12/11:00
12 | 12 | 1900-01-11 | 3.3 | 221 | 2 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 221 | 0 | 0 | 39.791 | 346.4583 | -23.1975 | 86.148 | -75 | 5.3354 | 162.4818 | -1.8512 | 219.1488 | 69.4663 | 69.4663 | 0 | 0 | 0 | 12/12/12:00
12 | 12 | 1900-01-12 | 3.3 | 209 | 11 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 209 | 0 | 0 | 39.791 | 346.5 | -23.2 | 86.148 | -75 | 5.3166 | 177.4771 | -10.5345 | 198.4655 | 62.9101 | 62.9101 | 0 | 0 | 0 | 12/12/13:00
12 | 12 | 1900-01-13 | 3.9 | 276 | 5 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 276 | 0 | 0 | 39.791 | 346.5417 | -23.2025 | 86.148 | -75 | 5.2978 | 192.4724 | -4.7086 | 271.2914 | 85.9946 | 85.9946 | 0 | 0 | 0 | 12/12/14:00
12 | 12 | 1900-01-14 | 4.4 | 207 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 207 | 0 | 0 | 39.791 | 346.5833 | -23.205 | 86.148 | -75 | 5.279 | 207.4677 | 0 | 207 | 65.6154 | 65.6154 | 0 | 0 | 0 | 12/12/15:00
12 | 12 | 1900-01-15 | 3.9 | 152 | 6 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 152 | 0 | 0 | 39.791 | 346.625 | -23.2075 | 86.148 | -75 | 5.2602 | 222.463 | -4.6391 | 147.3609 | 46.7108 | 46.7108 | 0 | 0 | 0 | 12/12/16:00
12 | 12 | 1900-01-16 | 3.9 | 68 | 1 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 68 | 0 | 0 | 39.791 | 346.6667 | -23.21 | 86.148 | -75 | 5.2414 | 237.4583 | -0.63209 | 67.3679 | 21.3544 | 21.3544 | 0 | 0 | 0 | 12/12/17:00
12 | 12 | 1900-01-17 | 3.3 | 6 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 6 | 0 | 0 | 39.791 | 346.7083 | -23.2125 | 86.148 | -75 | 5.2226 | 252.4536 | 0 | 6 | 1.9019 | 1.9019 | 0 | 0 | 0 | 12/12/18:00
12 | 12 | 1900-01-18 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.75 | -23.2149 | 86.148 | -75 | 5.2037 | 267.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/19:00
12 | 12 | 1900-01-19 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.7917 | -23.2173 | 86.148 | -75 | 5.1849 | 282.4442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/20:00
12 | 12 | 1900-01-20 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.8333 | -23.2198 | 86.148 | -75 | 5.1661 | 297.4395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/21:00
12 | 12 | 1900-01-21 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.875 | -23.2222 | 86.148 | -75 | 5.1472 | 312.4348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/22:00
12 | 12 | 1900-01-22 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.9167 | -23.2246 | 86.148 | -75 | 5.1284 | 327.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/23:00
12 | 12 | 1900-01-23 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 346.9583 | -23.227 | 86.148 | -75 | 5.1095 | 342.4254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/12/24:00
12 | 13 | 1899-12-31 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347 | -23.2293 | 86.148 | -75 | 5.0907 | -2.5793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/1:00
12 | 13 | 1900-01-01 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.0417 | -23.2317 | 86.148 | -75 | 5.0718 | 12.4159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/2:00
12 | 13 | 1900-01-02 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.0833 | -23.234 | 86.148 | -75 | 5.0529 | 27.4112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/3:00
12 | 13 | 1900-01-03 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.125 | -23.2364 | 86.148 | -75 | 5.034 | 42.4065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/4:00
12 | 13 | 1900-01-04 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.1667 | -23.2387 | 86.148 | -75 | 5.0151 | 57.4018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/5:00
12 | 13 | 1900-01-05 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.2083 | -23.241 | 86.148 | -75 | 4.9962 | 72.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/6:00
12 | 13 | 1900-01-06 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.25 | -23.2433 | 86.148 | -75 | 4.9773 | 87.3923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/7:00
12 | 13 | 1900-01-07 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.2917 | -23.2456 | 86.148 | -75 | 4.9584 | 102.3876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/8:00
12 | 13 | 1900-01-08 | 4.4 | 17 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 17 | 0 | 0 | 39.791 | 347.3333 | -23.2479 | 86.148 | -75 | 4.9395 | 117.3829 | 0 | 17 | 5.3887 | 5.3887 | 0 | 0 | 0 | 12/13/9:00
12 | 13 | 1900-01-09 | 4.4 | 60 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 60 | 0 | 0 | 39.791 | 347.375 | -23.2501 | 86.148 | -75 | 4.9206 | 132.3781 | 0 | 60 | 19.019 | 19.019 | 0 | 0 | 0 | 12/13/10:00
12 | 13 | 1900-01-10 | 5 | 105 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 105 | 0 | 0 | 39.791 | 347.4167 | -23.2524 | 86.148 | -75 | 4.9016 | 147.3734 | 0 | 105 | 33.2832 | 33.2832 | 0 | 0 | 0 | 12/13/11:00
12 | 13 | 1900-01-11 | 5 | 104 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 104 | 0 | 0 | 39.791 | 347.4583 | -23.2546 | 86.148 | -75 | 4.8827 | 162.3687 | 0 | 104 | 32.9662 | 32.9662 | 0 | 0 | 0 | 12/13/12:00
12 | 13 | 1900-01-12 | 5.6 | 71 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 71 | 0 | 0 | 39.791 | 347.5 | -23.2568 | 86.148 | -75 | 4.8638 | 177.3639 | 0 | 71 | 22.5058 | 22.5058 | 0 | 0 | 0 | 12/13/13:00
12 | 13 | 1900-01-13 | 5 | 142 | 1 | 41 | 1 | 0 | 41 | 0 | 0 | 142 | 0 | 0 | 39.791 | 347.5417 | -23.259 | 86.148 | -75 | 4.8448 | 192.3592 | -0.9423 | 141.0577 | 44.7128 | 44.7128 | 0 | 0 | 0 | 12/13/14:00
12 | 13 | 1900-01-14 | 5 | 52 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 52 | 0 | 0 | 39.791 | 347.5833 | -23.2612 | 86.148 | -75 | 4.8259 | 207.3545 | 0 | 52 | 16.4831 | 16.4831 | 0 | 0 | 0 | 12/13/15:00
12 | 13 | 1900-01-15 | 5.6 | 78 | 1 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 78 | 0 | 0 | 39.791 | 347.625 | -23.2634 | 86.148 | -75 | 4.8069 | 222.3497 | -0.77447 | 77.2255 | 24.4791 | 24.4791 | 0 | 0 | 0 | 12/13/16:00
12 | 13 | 1900-01-16 | 5.6 | 34 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 34 | 0 | 0 | 39.791 | 347.6667 | -23.2656 | 86.148 | -75 | 4.7879 | 237.345 | 0 | 34 | 10.7774 | 10.7774 | 0 | 0 | 0 | 12/13/17:00
12 | 13 | 1900-01-17 | 5 | 1 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 1 | 0 | 0 | 39.791 | 347.7083 | -23.2678 | 86.148 | -75 | 4.769 | 252.3402 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 12/13/18:00
12 | 13 | 1900-01-18 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.75 | -23.2699 | 86.148 | -75 | 4.75 | 267.3355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/19:00
12 | 13 | 1900-01-19 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.7917 | -23.272 | 86.148 | -75 | 4.731 | 282.3308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/20:00
12 | 13 | 1900-01-20 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.8333 | -23.2742 | 86.148 | -75 | 4.712 | 297.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/21:00
12 | 13 | 1900-01-21 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.875 | -23.2763 | 86.148 | -75 | 4.693 | 312.3213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/22:00
12 | 13 | 1900-01-22 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.9167 | -23.2784 | 86.148 | -75 | 4.674 | 327.3165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/23:00
12 | 13 | 1900-01-23 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 347.9583 | -23.2804 | 86.148 | -75 | 4.655 | 342.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/13/24:00
12 | 14 | 1899-12-31 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348 | -23.2825 | 86.148 | -75 | 4.636 | -2.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/1:00
12 | 14 | 1900-01-01 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.0417 | -23.2846 | 86.148 | -75 | 4.617 | 12.3022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/2:00
12 | 14 | 1900-01-02 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.0833 | -23.2866 | 86.148 | -75 | 4.5979 | 27.2975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/3:00
12 | 14 | 1900-01-03 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.125 | -23.2887 | 86.148 | -75 | 4.5789 | 42.2927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/4:00
12 | 14 | 1900-01-04 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.1667 | -23.2907 | 86.148 | -75 | 4.5599 | 57.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/5:00
12 | 14 | 1900-01-05 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.2083 | -23.2927 | 86.148 | -75 | 4.5408 | 72.2832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/6:00
12 | 14 | 1900-01-06 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.25 | -23.2947 | 86.148 | -75 | 4.5218 | 87.2784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/7:00
12 | 14 | 1900-01-07 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.2917 | -23.2967 | 86.148 | -75 | 4.5027 | 102.2737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/8:00
12 | 14 | 1900-01-08 | 3.9 | 18 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 18 | 0 | 0 | 39.791 | 348.3333 | -23.2986 | 86.148 | -75 | 4.4837 | 117.2689 | 0 | 18 | 5.7057 | 5.7057 | 0 | 0 | 0 | 12/14/9:00
12 | 14 | 1900-01-09 | 3.9 | 60 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 60 | 0 | 0 | 39.791 | 348.375 | -23.3006 | 86.148 | -75 | 4.4646 | 132.2641 | 0 | 60 | 19.019 | 19.019 | 0 | 0 | 0 | 12/14/10:00
12 | 14 | 1900-01-10 | 3.3 | 76 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 76 | 0 | 0 | 39.791 | 348.4167 | -23.3025 | 86.148 | -75 | 4.4455 | 147.2594 | 0 | 76 | 24.0907 | 24.0907 | 0 | 0 | 0 | 12/14/11:00
12 | 14 | 1900-01-11 | 3.3 | 169 | 14 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 169 | 0 | 0 | 39.791 | 348.4583 | -23.3045 | 86.148 | -75 | 4.4264 | 162.2546 | -12.9543 | 156.0457 | 49.4638 | 49.4638 | 0 | 0 | 0 | 12/14/12:00
12 | 14 | 1900-01-12 | 3.3 | 231 | 1 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 231 | 0 | 0 | 39.791 | 348.5 | -23.3064 | 86.148 | -75 | 4.4074 | 177.2498 | -0.95808 | 230.0419 | 72.9193 | 72.9193 | 0 | 0 | 0 | 12/14/13:00
12 | 14 | 1900-01-13 | 3.3 | 236 | 1 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 236 | 0 | 0 | 39.791 | 348.5417 | -23.3083 | 86.148 | -75 | 4.3883 | 192.2451 | -0.94285 | 235.0571 | 74.509 | 74.509 | 0 | 0 | 0 | 12/14/14:00
12 | 14 | 1900-01-14 | 3.3 | 175 | 1 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 175 | 0 | 0 | 39.791 | 348.5833 | -23.3102 | 86.148 | -75 | 4.3692 | 207.2403 | -0.88065 | 174.1193 | 55.1928 | 55.1928 | 0 | 0 | 0 | 12/14/15:00
12 | 14 | 1900-01-15 | 3.3 | 121 | 1 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 121 | 0 | 0 | 39.791 | 348.625 | -23.3121 | 86.148 | -75 | 4.3501 | 222.2355 | -0.77573 | 120.2243 | 38.109 | 38.109 | 0 | 0 | 0 | 12/14/16:00
12 | 14 | 1900-01-16 | 2.8 | 19 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 19 | 0 | 0 | 39.791 | 348.6667 | -23.3139 | 86.148 | -75 | 4.331 | 237.2307 | 0 | 19 | 6.0227 | 6.0227 | 0 | 0 | 0 | 12/14/17:00
12 | 14 | 1900-01-17 | 2.2 | 5 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 5 | 0 | 0 | 39.791 | 348.7083 | -23.3158 | 86.148 | -75 | 4.3119 | 252.226 | 0 | 5 | 1.5849 | 1.5849 | 0 | 0 | 0 | 12/14/18:00
12 | 14 | 1900-01-18 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.75 | -23.3176 | 86.148 | -75 | 4.2927 | 267.2212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/19:00
12 | 14 | 1900-01-19 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.7917 | -23.3194 | 86.148 | -75 | 4.2736 | 282.2164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/20:00
12 | 14 | 1900-01-20 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.8333 | -23.3213 | 86.148 | -75 | 4.2545 | 297.2116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/21:00
12 | 14 | 1900-01-21 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.875 | -23.3231 | 86.148 | -75 | 4.2354 | 312.2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/22:00
12 | 14 | 1900-01-22 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.9167 | -23.3249 | 86.148 | -75 | 4.2162 | 327.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/23:00
12 | 14 | 1900-01-23 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 348.9583 | -23.3266 | 86.148 | -75 | 4.1971 | 342.1973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/14/24:00
12 | 15 | 1899-12-31 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349 | -23.3284 | 86.148 | -75 | 4.1779 | -2.8075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/1:00
12 | 15 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.0417 | -23.3302 | 86.148 | -75 | 4.1588 | 12.1877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/2:00
12 | 15 | 1900-01-02 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.0833 | -23.3319 | 86.148 | -75 | 4.1396 | 27.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/3:00
12 | 15 | 1900-01-03 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.125 | -23.3336 | 86.148 | -75 | 4.1205 | 42.1781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/4:00
12 | 15 | 1900-01-04 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.1667 | -23.3353 | 86.148 | -75 | 4.1013 | 57.1733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/5:00
12 | 15 | 1900-01-05 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.2083 | -23.337 | 86.148 | -75 | 4.0821 | 72.1685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/6:00
12 | 15 | 1900-01-06 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.25 | -23.3387 | 86.148 | -75 | 4.0629 | 87.1637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/7:00
12 | 15 | 1900-01-07 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.2917 | -23.3404 | 86.148 | -75 | 4.0438 | 102.1589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/8:00
12 | 15 | 1900-01-08 | 0 | 34 | 1 | 32 | 1 | 0 | 32 | 0 | 0 | 34 | 0 | 0 | 39.791 | 349.3333 | -23.3421 | 86.148 | -75 | 4.0246 | 117.1541 | -0.57555 | 33.4244 | 10.595 | 10.595 | 0 | 0 | 0 | 12/15/9:00
12 | 15 | 1900-01-09 | 0 | 104 | 1 | 32 | 1 | 0 | 32 | 0 | 0 | 104 | 0 | 0 | 39.791 | 349.375 | -23.3437 | 86.148 | -75 | 4.0054 | 132.1493 | -0.72702 | 103.273 | 32.7357 | 32.7357 | 0 | 0 | 0 | 12/15/10:00
12 | 15 | 1900-01-10 | 0 | 91 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 91 | 0 | 0 | 39.791 | 349.4167 | -23.3454 | 86.148 | -75 | 3.9862 | 147.1445 | 0 | 91 | 28.8454 | 28.8454 | 0 | 0 | 0 | 12/15/11:00
12 | 15 | 1900-01-11 | 0.6 | 146 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 146 | 0 | 0 | 39.791 | 349.4583 | -23.347 | 86.148 | -75 | 3.967 | 162.1397 | 0 | 146 | 46.2795 | 46.2795 | 0 | 0 | 0 | 12/15/12:00
12 | 15 | 1900-01-12 | 1.1 | 177 | 53 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 177 | 0 | 0 | 39.791 | 349.5 | -23.3486 | 86.148 | -75 | 3.9478 | 177.1349 | -50.7858 | 126.2142 | 40.0077 | 40.0077 | 0 | 0 | 0 | 12/15/13:00
12 | 15 | 1900-01-13 | 2.8 | 167 | 125 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 167 | 0 | 0 | 39.791 | 349.5417 | -23.3502 | 86.148 | -75 | 3.9286 | 192.1301 | -117.9202 | 49.0798 | 15.5574 | 15.5574 | 0 | 0 | 0 | 12/15/14:00
12 | 15 | 1900-01-14 | 3.9 | 139 | 435 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 139 | 0 | 0 | 39.791 | 349.5833 | -23.3518 | 86.148 | -75 | 3.9093 | 207.1253 | -383.4654 | -244.4654 | -77.4913 | -77.4913 | 0 | 0 | 0 | 12/15/15:00
12 | 15 | 1900-01-15 | 5 | 69 | 510 | 41 | 1 | 0 | 41 | 0 | 0 | 69 | 0 | 0 | 39.791 | 349.625 | -23.3534 | 86.148 | -75 | 3.8901 | 222.1205 | -396.2391 | -327.2391 | -103.7291 | -103.7291 | 0 | 0 | 0 | 12/15/16:00
12 | 15 | 1900-01-16 | 5.6 | 64 | 85 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 64 | 0 | 0 | 39.791 | 349.6667 | -23.3549 | 86.148 | -75 | 3.8709 | 237.1157 | -54.1209 | 9.8791 | 3.1315 | 3.1315 | 0 | 0 | 0 | 12/15/17:00
12 | 15 | 1900-01-17 | 3.9 | 9 | 34 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 9 | 0 | 0 | 39.791 | 349.7083 | -23.3565 | 86.148 | -75 | 3.8517 | 252.1109 | -15.994 | -6.994 | -2.217 | -2.217 | 0 | 0 | 0 | 12/15/18:00
12 | 15 | 1900-01-18 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.75 | -23.358 | 86.148 | -75 | 3.8324 | 267.1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/19:00
12 | 15 | 1900-01-19 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.7917 | -23.3596 | 86.148 | -75 | 3.8132 | 282.1013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/20:00
12 | 15 | 1900-01-20 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.8333 | -23.3611 | 86.148 | -75 | 3.7939 | 297.0965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/21:00
12 | 15 | 1900-01-21 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.875 | -23.3626 | 86.148 | -75 | 3.7747 | 312.0917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/22:00
12 | 15 | 1900-01-22 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.9167 | -23.3641 | 86.148 | -75 | 3.7554 | 327.0869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/23:00
12 | 15 | 1900-01-23 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 349.9583 | -23.3655 | 86.148 | -75 | 3.7362 | 342.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/15/24:00
12 | 16 | 1899-12-31 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350 | -23.367 | 86.148 | -75 | 3.7169 | -2.9228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/1:00
12 | 16 | 1900-01-01 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.0417 | -23.3684 | 86.148 | -75 | 3.6976 | 12.0724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/2:00
12 | 16 | 1900-01-02 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.0833 | -23.3699 | 86.148 | -75 | 3.6784 | 27.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/3:00
12 | 16 | 1900-01-03 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.125 | -23.3713 | 86.148 | -75 | 3.6591 | 42.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/4:00
12 | 16 | 1900-01-04 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.1667 | -23.3727 | 86.148 | -75 | 3.6398 | 57.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/5:00
12 | 16 | 1900-01-05 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.2083 | -23.3741 | 86.148 | -75 | 3.6205 | 72.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/6:00
12 | 16 | 1900-01-06 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.25 | -23.3755 | 86.148 | -75 | 3.6013 | 87.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/7:00
12 | 16 | 1900-01-07 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.2917 | -23.3769 | 86.148 | -75 | 3.582 | 102.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/8:00
12 | 16 | 1900-01-08 | 1.1 | 25 | 164 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 25 | 0 | 0 | 39.791 | 350.3333 | -23.3782 | 86.148 | -75 | 3.5627 | 117.0387 | -94.2299 | -69.2299 | -21.9447 | -21.9447 | 0 | 0 | 0 | 12/16/9:00
12 | 16 | 1900-01-09 | 2.8 | 53 | 507 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 53 | 0 | 0 | 39.791 | 350.375 | -23.3796 | 86.148 | -75 | 3.5434 | 132.0338 | -368.1864 | -315.1864 | -99.9086 | -99.9086 | 0 | 0 | 0 | 12/16/10:00
12 | 16 | 1900-01-10 | 6.1 | 70 | 662 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 70 | 0 | 0 | 39.791 | 350.4167 | -23.3809 | 86.148 | -75 | 3.5241 | 147.029 | -559.8366 | -489.8366 | -155.2697 | -155.2697 | 0 | 0 | 0 | 12/16/11:00
12 | 16 | 1900-01-11 | 8.3 | 82 | 732 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 82 | 0 | 0 | 39.791 | 350.4583 | -23.3822 | 86.148 | -75 | 3.5047 | 162.0242 | -676.9856 | -594.9856 | -188.6 | -188.6 | 0 | 0 | 0 | 12/16/12:00
12 | 16 | 1900-01-12 | 11.7 | 86 | 755 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 86 | 0 | 0 | 39.791 | 350.5 | -23.3835 | 86.148 | -75 | 3.4854 | 177.0194 | -723.5339 | -637.5339 | -202.0871 | -202.0871 | 0 | 0 | 0 | 12/16/13:00
12 | 16 | 1900-01-13 | 13.3 | 84 | 742 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 84 | 0 | 0 | 39.791 | 350.5417 | -23.3848 | 86.148 | -75 | 3.4661 | 192.0145 | -700.3252 | -616.3252 | -195.3643 | 0 | -195.3643 | 55.94 | -195.3643 | 12/16/14:00
12 | 16 | 1900-01-14 | 13.9 | 75 | 688 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 75 | 0 | 0 | 39.791 | 350.5833 | -23.3861 | 86.148 | -75 | 3.4468 | 207.0097 | -607.0683 | -532.0683 | -168.6564 | 0 | -168.6564 | 57.02 | -168.6564 | 12/16/15:00
12 | 16 | 1900-01-15 | 13.9 | 60 | 570 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 60 | 0 | 0 | 39.791 | 350.625 | -23.3874 | 86.148 | -75 | 3.4275 | 222.0049 | -443.5213 | -383.5213 | -121.5696 | 0 | -121.5696 | 57.02 | -121.5696 | 12/16/16:00
12 | 16 | 1900-01-16 | 12.2 | 38 | 306 | 53.96 | 1 | 0 | 53.96 | 0 | 0 | 38 | 0 | 0 | 39.791 | 350.6667 | -23.3886 | 86.148 | -75 | 3.4081 | 237 | -195.2768 | -157.2768 | -49.854 | -49.854 | 0 | 0 | 0 | 12/16/17:00
12 | 16 | 1900-01-17 | 11.1 | 6 | 14 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 6 | 0 | 0 | 39.791 | 350.7083 | -23.3899 | 86.148 | -75 | 3.3888 | 251.9952 | -6.6088 | -0.60876 | -0.19297 | -0.19297 | 0 | 0 | 0 | 12/16/18:00
12 | 16 | 1900-01-18 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.75 | -23.3911 | 86.148 | -75 | 3.3695 | 266.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/19:00
12 | 16 | 1900-01-19 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.7917 | -23.3923 | 86.148 | -75 | 3.3501 | 281.9855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/20:00
12 | 16 | 1900-01-20 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.8333 | -23.3935 | 86.148 | -75 | 3.3308 | 296.9807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/21:00
12 | 16 | 1900-01-21 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.875 | -23.3947 | 86.148 | -75 | 3.3114 | 311.9759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/22:00
12 | 16 | 1900-01-22 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.9167 | -23.3959 | 86.148 | -75 | 3.2921 | 326.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/23:00
12 | 16 | 1900-01-23 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 350.9583 | -23.3971 | 86.148 | -75 | 3.2727 | 341.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/16/24:00
12 | 17 | 1899-12-31 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351 | -23.3982 | 86.148 | -75 | 3.2534 | -3.0387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/1:00
12 | 17 | 1900-01-01 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.0417 | -23.3994 | 86.148 | -75 | 3.234 | 11.9565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/2:00
12 | 17 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.0833 | -23.4005 | 86.148 | -75 | 3.2146 | 26.9517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/3:00
12 | 17 | 1900-01-03 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.125 | -23.4016 | 86.148 | -75 | 3.1953 | 41.9468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/4:00
12 | 17 | 1900-01-04 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.1667 | -23.4027 | 86.148 | -75 | 3.1759 | 56.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/5:00
12 | 17 | 1900-01-05 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.2083 | -23.4038 | 86.148 | -75 | 3.1565 | 71.9371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/6:00
12 | 17 | 1900-01-06 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.25 | -23.4049 | 86.148 | -75 | 3.1371 | 86.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/7:00
12 | 17 | 1900-01-07 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.2917 | -23.406 | 86.148 | -75 | 3.1178 | 101.9274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/8:00
12 | 17 | 1900-01-08 | 10 | 17 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 17 | 0 | 0 | 39.791 | 351.3333 | -23.407 | 86.148 | -75 | 3.0984 | 116.9226 | 0 | 17 | 5.3887 | 5.3887 | 0 | 0 | 0 | 12/17/9:00
12 | 17 | 1900-01-09 | 10.6 | 57 | 6 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 57 | 0 | 0 | 39.791 | 351.375 | -23.4081 | 86.148 | -75 | 3.079 | 131.9177 | -4.352 | 52.648 | 16.6885 | 16.6885 | 0 | 0 | 0 | 12/17/10:00
12 | 17 | 1900-01-10 | 11.7 | 101 | 8 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 101 | 0 | 0 | 39.791 | 351.4167 | -23.4091 | 86.148 | -75 | 3.0596 | 146.9129 | -6.7605 | 94.2395 | 29.8723 | 29.8723 | 0 | 0 | 0 | 12/17/11:00
12 | 17 | 1900-01-11 | 12.8 | 164 | 3 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 164 | 0 | 0 | 39.791 | 351.4583 | -23.4101 | 86.148 | -75 | 3.0402 | 161.908 | -2.7736 | 161.2264 | 51.1059 | 0 | 51.1059 | 55.04 | 51.1059 | 12/17/12:00
12 | 17 | 1900-01-12 | 13.9 | 227 | 6 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 227 | 0 | 0 | 39.791 | 351.5 | -23.4111 | 86.148 | -75 | 3.0208 | 176.9032 | -5.7503 | 221.2497 | 70.1323 | 0 | 70.1323 | 57.02 | 70.1323 | 12/17/13:00
12 | 17 | 1900-01-13 | 13.9 | 147 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 147 | 0 | 0 | 39.791 | 351.5417 | -23.4121 | 86.148 | -75 | 3.0014 | 191.8983 | 0 | 147 | 46.5964 | 0 | 46.5964 | 57.02 | 46.5964 | 12/17/14:00
12 | 17 | 1900-01-14 | 13.9 | 125 | 0 | 57.02 | 0 | 1 | 0 | 57.02 | 0 | 125 | 0 | 0 | 39.791 | 351.5833 | -23.4131 | 86.148 | -75 | 2.982 | 206.8935 | 0 | 125 | 39.6228 | 0 | 39.6228 | 57.02 | 39.6228 | 12/17/15:00
12 | 17 | 1900-01-15 | 13.3 | 92 | 3 | 55.94 | 0 | 1 | 0 | 55.94 | 0 | 92 | 0 | 0 | 39.791 | 351.625 | -23.4141 | 86.148 | -75 | 2.9626 | 221.8886 | -2.3377 | 89.6623 | 28.4214 | 0 | 28.4214 | 55.94 | 28.4214 | 12/17/16:00
12 | 17 | 1900-01-16 | 12.8 | 39 | 11 | 55.04 | 0 | 1 | 0 | 55.04 | 0 | 39 | 0 | 0 | 39.791 | 351.6667 | -23.415 | 86.148 | -75 | 2.9431 | 236.8838 | -7.0351 | 31.9649 | 10.1323 | 0 | 10.1323 | 55.04 | 10.1323 | 12/17/17:00
12 | 17 | 1900-01-17 | 11.7 | 5 | 24 | 53.06 | 1 | 0 | 53.06 | 0 | 0 | 5 | 0 | 0 | 39.791 | 351.7083 | -23.4159 | 86.148 | -75 | 2.9237 | 251.8789 | -11.3673 | -6.3673 | -2.0183 | -2.0183 | 0 | 0 | 0 | 12/17/18:00
12 | 17 | 1900-01-18 | 11.1 | 0 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.75 | -23.4169 | 86.148 | -75 | 2.9043 | 266.8741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/19:00
12 | 17 | 1900-01-19 | 10.6 | 0 | 0 | 51.08 | 1 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.7917 | -23.4178 | 86.148 | -75 | 2.8849 | 281.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/20:00
12 | 17 | 1900-01-20 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.8333 | -23.4187 | 86.148 | -75 | 2.8655 | 296.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/21:00
12 | 17 | 1900-01-21 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.875 | -23.4196 | 86.148 | -75 | 2.846 | 311.8595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/22:00
12 | 17 | 1900-01-22 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.9167 | -23.4204 | 86.148 | -75 | 2.8266 | 326.8547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/23:00
12 | 17 | 1900-01-23 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 351.9583 | -23.4213 | 86.148 | -75 | 2.8072 | 341.8498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/17/24:00
12 | 18 | 1899-12-31 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352 | -23.4222 | 86.148 | -75 | 2.7877 | -3.1551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/1:00
12 | 18 | 1900-01-01 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.0417 | -23.423 | 86.148 | -75 | 2.7683 | 11.8401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/2:00
12 | 18 | 1900-01-02 | 8.3 | 0 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.0833 | -23.4238 | 86.148 | -75 | 2.7488 | 26.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/3:00
12 | 18 | 1900-01-03 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.125 | -23.4246 | 86.148 | -75 | 2.7294 | 41.8303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/4:00
12 | 18 | 1900-01-04 | 7.8 | 0 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.1667 | -23.4254 | 86.148 | -75 | 2.7099 | 56.8255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/5:00
12 | 18 | 1900-01-05 | 6.7 | 0 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.2083 | -23.4262 | 86.148 | -75 | 2.6905 | 71.8206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/6:00
12 | 18 | 1900-01-06 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.25 | -23.427 | 86.148 | -75 | 2.671 | 86.8158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/7:00
12 | 18 | 1900-01-07 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.2917 | -23.4278 | 86.148 | -75 | 2.6516 | 101.8109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/8:00
12 | 18 | 1900-01-08 | 5.6 | 24 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 24 | 0 | 0 | 39.791 | 352.3333 | -23.4285 | 86.148 | -75 | 2.6321 | 116.806 | 0 | 24 | 7.6076 | 7.6076 | 0 | 0 | 0 | 12/18/9:00
12 | 18 | 1900-01-09 | 5.6 | 75 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 75 | 0 | 0 | 39.791 | 352.375 | -23.4292 | 86.148 | -75 | 2.6127 | 131.8012 | 0 | 75 | 23.7737 | 23.7737 | 0 | 0 | 0 | 12/18/10:00
12 | 18 | 1900-01-10 | 6.7 | 122 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 122 | 0 | 0 | 39.791 | 352.4167 | -23.43 | 86.148 | -75 | 2.5932 | 146.7963 | 0 | 122 | 38.6719 | 38.6719 | 0 | 0 | 0 | 12/18/11:00
12 | 18 | 1900-01-11 | 6.7 | 155 | 1 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 155 | 0 | 0 | 39.791 | 352.4583 | -23.4307 | 86.148 | -75 | 2.5737 | 161.7914 | -0.92421 | 154.0758 | 48.8393 | 48.8393 | 0 | 0 | 0 | 12/18/12:00
12 | 18 | 1900-01-12 | 6.7 | 196 | 1 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 196 | 0 | 0 | 39.791 | 352.5 | -23.4314 | 86.148 | -75 | 2.5543 | 176.7866 | -0.9584 | 195.0416 | 61.8248 | 61.8248 | 0 | 0 | 0 | 12/18/13:00
12 | 18 | 1900-01-13 | 6.7 | 195 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 195 | 0 | 0 | 39.791 | 352.5417 | -23.432 | 86.148 | -75 | 2.5348 | 191.7817 | 0 | 195 | 61.8116 | 61.8116 | 0 | 0 | 0 | 12/18/14:00
12 | 18 | 1900-01-14 | 6.7 | 169 | 1 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 169 | 0 | 0 | 39.791 | 352.5833 | -23.4327 | 86.148 | -75 | 2.5153 | 206.7768 | -0.88392 | 168.1161 | 53.2899 | 53.2899 | 0 | 0 | 0 | 12/18/15:00
12 | 18 | 1900-01-15 | 6.7 | 115 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 115 | 0 | 0 | 39.791 | 352.625 | -23.4334 | 86.148 | -75 | 2.4958 | 221.772 | 0 | 115 | 36.453 | 36.453 | 0 | 0 | 0 | 12/18/16:00
12 | 18 | 1900-01-16 | 6.7 | 44 | 0 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 44 | 0 | 0 | 39.791 | 352.6667 | -23.434 | 86.148 | -75 | 2.4764 | 236.7671 | 0 | 44 | 13.9472 | 13.9472 | 0 | 0 | 0 | 12/18/17:00
12 | 18 | 1900-01-17 | 6.1 | 7 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 7 | 0 | 0 | 39.791 | 352.7083 | -23.4347 | 86.148 | -75 | 2.4569 | 251.7622 | 0 | 7 | 2.2189 | 2.2189 | 0 | 0 | 0 | 12/18/18:00
12 | 18 | 1900-01-18 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.75 | -23.4353 | 86.148 | -75 | 2.4374 | 266.7573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/19:00
12 | 18 | 1900-01-19 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.7917 | -23.4359 | 86.148 | -75 | 2.4179 | 281.7525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/20:00
12 | 18 | 1900-01-20 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.8333 | -23.4365 | 86.148 | -75 | 2.3984 | 296.7476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/21:00
12 | 18 | 1900-01-21 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.875 | -23.4371 | 86.148 | -75 | 2.3789 | 311.7427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/22:00
12 | 18 | 1900-01-22 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.9167 | -23.4376 | 86.148 | -75 | 2.3594 | 326.7379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/23:00
12 | 18 | 1900-01-23 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 352.9583 | -23.4382 | 86.148 | -75 | 2.3399 | 341.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/18/24:00
12 | 19 | 1899-12-31 | 5 | 0 | 0 | 41 | 1 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353 | -23.4387 | 86.148 | -75 | 2.3204 | -3.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/1:00
12 | 19 | 1900-01-01 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.0417 | -23.4393 | 86.148 | -75 | 2.3009 | 11.7232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/2:00
12 | 19 | 1900-01-02 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.0833 | -23.4398 | 86.148 | -75 | 2.2814 | 26.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/3:00
12 | 19 | 1900-01-03 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.125 | -23.4403 | 86.148 | -75 | 2.2619 | 41.7135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/4:00
12 | 19 | 1900-01-04 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.1667 | -23.4408 | 86.148 | -75 | 2.2424 | 56.7086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/5:00
12 | 19 | 1900-01-05 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.2083 | -23.4412 | 86.148 | -75 | 2.2229 | 71.7037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/6:00
12 | 19 | 1900-01-06 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.25 | -23.4417 | 86.148 | -75 | 2.2034 | 86.6988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/7:00
12 | 19 | 1900-01-07 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.2917 | -23.4422 | 86.148 | -75 | 2.1839 | 101.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/8:00
12 | 19 | 1900-01-08 | 3.9 | 18 | 15 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 18 | 0 | 0 | 39.791 | 353.3333 | -23.4426 | 86.148 | -75 | 2.1644 | 116.6891 | -8.5686 | 9.4314 | 2.9896 | 2.9896 | 0 | 0 | 0 | 12/19/9:00
12 | 19 | 1900-01-09 | 4.4 | 79 | 182 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 79 | 0 | 0 | 39.791 | 353.375 | -23.443 | 86.148 | -75 | 2.1449 | 131.6842 | -131.6636 | -52.6636 | -16.6934 | -16.6934 | 0 | 0 | 0 | 12/19/10:00
12 | 19 | 1900-01-10 | 5 | 130 | 33 | 41 | 1 | 0 | 41 | 0 | 0 | 130 | 0 | 0 | 39.791 | 353.4167 | -23.4435 | 86.148 | -75 | 2.1253 | 146.6793 | -27.8416 | 102.1584 | 32.3824 | 32.3824 | 0 | 0 | 0 | 12/19/11:00
12 | 19 | 1900-01-11 | 5.6 | 175 | 129 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 175 | 0 | 0 | 39.791 | 353.4583 | -23.4439 | 86.148 | -75 | 2.1058 | 161.6745 | -119.1731 | 55.8269 | 17.6961 | 17.6961 | 0 | 0 | 0 | 12/19/12:00
12 | 19 | 1900-01-12 | 7.2 | 159 | 492 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 159 | 0 | 0 | 39.791 | 353.5 | -23.4442 | 86.148 | -75 | 2.0863 | 176.6696 | -471.5256 | -312.5256 | -99.0652 | -99.0652 | 0 | 0 | 0 | 12/19/13:00
12 | 19 | 1900-01-13 | 8.9 | 107 | 655 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 107 | 0 | 0 | 39.791 | 353.5417 | -23.4446 | 86.148 | -75 | 2.0668 | 191.6647 | -618.9874 | -511.9874 | -162.2911 | -162.2911 | 0 | 0 | 0 | 12/19/14:00
12 | 19 | 1900-01-14 | 10 | 95 | 596 | 50 | 1 | 0 | 50 | 0 | 0 | 95 | 0 | 0 | 39.791 | 353.5833 | -23.445 | 86.148 | -75 | 2.0473 | 206.6598 | -527.2418 | -432.2418 | -137.0131 | -137.0131 | 0 | 0 | 0 | 12/19/15:00
12 | 19 | 1900-01-15 | 9.4 | 101 | 298 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 101 | 0 | 0 | 39.791 | 353.625 | -23.4453 | 86.148 | -75 | 2.0277 | 221.6549 | -232.8404 | -131.8404 | -41.7911 | -41.7911 | 0 | 0 | 0 | 12/19/16:00
12 | 19 | 1900-01-16 | 8.9 | 47 | 204 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 47 | 0 | 0 | 39.791 | 353.6667 | -23.4457 | 86.148 | -75 | 2.0082 | 236.65 | -131.0053 | -84.0053 | -26.6282 | -26.6282 | 0 | 0 | 0 | 12/19/17:00
12 | 19 | 1900-01-17 | 8.9 | 3 | 1 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 3 | 0 | 0 | 39.791 | 353.7083 | -23.446 | 86.148 | -75 | 1.9887 | 251.6452 | -0.47663 | 2.5234 | 0.79986 | 0.79986 | 0 | 0 | 0 | 12/19/18:00
12 | 19 | 1900-01-18 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.75 | -23.4463 | 86.148 | -75 | 1.9691 | 266.6403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/19:00
12 | 19 | 1900-01-19 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.7917 | -23.4466 | 86.148 | -75 | 1.9496 | 281.6354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/20:00
12 | 19 | 1900-01-20 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.8333 | -23.4469 | 86.148 | -75 | 1.9301 | 296.6305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/21:00
12 | 19 | 1900-01-21 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.875 | -23.4472 | 86.148 | -75 | 1.9105 | 311.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/22:00
12 | 19 | 1900-01-22 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.9167 | -23.4474 | 86.148 | -75 | 1.891 | 326.6207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/23:00
12 | 19 | 1900-01-23 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 353.9583 | -23.4477 | 86.148 | -75 | 1.8715 | 341.6159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/19/24:00
12 | 20 | 1899-12-31 | 10 | 0 | 0 | 50 | 1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354 | -23.4479 | 86.148 | -75 | 1.8519 | -3.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/1:00
12 | 20 | 1900-01-01 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.0417 | -23.4482 | 86.148 | -75 | 1.8324 | 11.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/2:00
12 | 20 | 1900-01-02 | 9.4 | 0 | 0 | 48.92 | 1 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.0833 | -23.4484 | 86.148 | -75 | 1.8128 | 26.6012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/3:00
12 | 20 | 1900-01-03 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.125 | -23.4486 | 86.148 | -75 | 1.7933 | 41.5963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/4:00
12 | 20 | 1900-01-04 | 6.1 | 0 | 0 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.1667 | -23.4487 | 86.148 | -75 | 1.7737 | 56.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/5:00
12 | 20 | 1900-01-05 | 3.9 | 0 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.2083 | -23.4489 | 86.148 | -75 | 1.7542 | 71.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/6:00
12 | 20 | 1900-01-06 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.25 | -23.4491 | 86.148 | -75 | 1.7347 | 86.5817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/7:00
12 | 20 | 1900-01-07 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.2917 | -23.4492 | 86.148 | -75 | 1.7151 | 101.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/8:00
12 | 20 | 1900-01-08 | 0.6 | 26 | 2 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 26 | 0 | 0 | 39.791 | 354.3333 | -23.4494 | 86.148 | -75 | 1.6956 | 116.5719 | -1.14 | 24.86 | 7.8802 | 7.8802 | 0 | 0 | 0 | 12/20/9:00
12 | 20 | 1900-01-09 | 0 | 69 | 2 | 32 | 1 | 0 | 32 | 0 | 0 | 69 | 0 | 0 | 39.791 | 354.375 | -23.4495 | 86.148 | -75 | 1.676 | 131.567 | -1.4448 | 67.5552 | 21.4138 | 21.4138 | 0 | 0 | 0 | 12/20/10:00
12 | 20 | 1900-01-10 | -1.1 | 111 | 4 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 111 | 0 | 0 | 39.791 | 354.4167 | -23.4496 | 86.148 | -75 | 1.6564 | 146.5621 | -3.3717 | 107.6283 | 34.1163 | 34.1163 | 0 | 0 | 0 | 12/20/11:00
12 | 20 | 1900-01-11 | -1.1 | 208 | 12 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 208 | 0 | 0 | 39.791 | 354.4583 | -23.4497 | 86.148 | -75 | 1.6369 | 161.5572 | -11.0808 | 196.9192 | 62.42 | 62.42 | 0 | 0 | 0 | 12/20/12:00
12 | 20 | 1900-01-12 | -1.7 | 187 | 3 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 187 | 0 | 0 | 39.791 | 354.5 | -23.4498 | 86.148 | -75 | 1.6173 | 176.5523 | -2.875 | 184.125 | 58.3644 | 58.3644 | 0 | 0 | 0 | 12/20/13:00
12 | 20 | 1900-01-13 | -1.7 | 171 | 7 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 171 | 0 | 0 | 39.791 | 354.5417 | -23.4498 | 86.148 | -75 | 1.5978 | 191.5474 | -6.6173 | 164.3827 | 52.1064 | 52.1064 | 0 | 0 | 0 | 12/20/14:00
12 | 20 | 1900-01-14 | -1.7 | 118 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 118 | 0 | 0 | 39.791 | 354.5833 | -23.4499 | 86.148 | -75 | 1.5782 | 206.5426 | 0 | 118 | 37.4039 | 37.4039 | 0 | 0 | 0 | 12/20/15:00
12 | 20 | 1900-01-15 | -2.2 | 70 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 70 | 0 | 0 | 39.791 | 354.625 | -23.4499 | 86.148 | -75 | 1.5587 | 221.5377 | 0 | 70 | 22.1888 | 22.1888 | 0 | 0 | 0 | 12/20/16:00
12 | 20 | 1900-01-16 | -2.2 | 42 | 55 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 42 | 0 | 0 | 39.791 | 354.6667 | -23.45 | 86.148 | -75 | 1.5391 | 236.5328 | -35.388 | 6.612 | 2.0959 | 2.0959 | 0 | 0 | 0 | 12/20/17:00
12 | 20 | 1900-01-17 | -2.2 | 1 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 1 | 0 | 0 | 39.791 | 354.7083 | -23.45 | 86.148 | -75 | 1.5196 | 251.5279 | 0 | 1 | 0.31698 | 0.31698 | 0 | 0 | 0 | 12/20/18:00
12 | 20 | 1900-01-18 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.75 | -23.45 | 86.148 | -75 | 1.5 | 266.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/19:00
12 | 20 | 1900-01-19 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.7917 | -23.45 | 86.148 | -75 | 1.4804 | 281.5181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/20:00
12 | 20 | 1900-01-20 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.8333 | -23.45 | 86.148 | -75 | 1.4609 | 296.5132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/21:00
12 | 20 | 1900-01-21 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.875 | -23.4499 | 86.148 | -75 | 1.4413 | 311.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/22:00
12 | 20 | 1900-01-22 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.9167 | -23.4499 | 86.148 | -75 | 1.4218 | 326.5034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/23:00
12 | 20 | 1900-01-23 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 354.9583 | -23.4498 | 86.148 | -75 | 1.4022 | 341.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/20/24:00
12 | 21 | 1899-12-31 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355 | -23.4498 | 86.148 | -75 | 1.3826 | -3.5063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/1:00
12 | 21 | 1900-01-01 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.0417 | -23.4497 | 86.148 | -75 | 1.3631 | 11.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/2:00
12 | 21 | 1900-01-02 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.0833 | -23.4496 | 86.148 | -75 | 1.3435 | 26.4839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/3:00
12 | 21 | 1900-01-03 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.125 | -23.4495 | 86.148 | -75 | 1.3239 | 41.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/4:00
12 | 21 | 1900-01-04 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.1667 | -23.4494 | 86.148 | -75 | 1.3044 | 56.4741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/5:00
12 | 21 | 1900-01-05 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.2083 | -23.4492 | 86.148 | -75 | 1.2848 | 71.4692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/6:00
12 | 21 | 1900-01-06 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.25 | -23.4491 | 86.148 | -75 | 1.2652 | 86.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/7:00
12 | 21 | 1900-01-07 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.2917 | -23.4489 | 86.148 | -75 | 1.2457 | 101.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/8:00
12 | 21 | 1900-01-08 | -6.1 | 29 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 29 | 0 | 0 | 39.791 | 355.3333 | -23.4487 | 86.148 | -75 | 1.2261 | 116.4545 | 0 | 29 | 9.1925 | 9.1925 | 0 | 0 | 0 | 12/21/9:00
12 | 21 | 1900-01-09 | -6.1 | 72 | 6 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 72 | 0 | 0 | 39.791 | 355.375 | -23.4486 | 86.148 | -75 | 1.2065 | 131.4496 | -4.3278 | 67.6722 | 21.4509 | 21.4509 | 0 | 0 | 0 | 12/21/10:00
12 | 21 | 1900-01-10 | -6.1 | 157 | 2 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 157 | 0 | 0 | 39.791 | 355.4167 | -23.4484 | 86.148 | -75 | 1.187 | 146.4447 | -1.6842 | 155.3158 | 49.2324 | 49.2324 | 0 | 0 | 0 | 12/21/11:00
12 | 21 | 1900-01-11 | -6.1 | 160 | 76 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 160 | 0 | 0 | 39.791 | 355.4583 | -23.4482 | 86.148 | -75 | 1.1674 | 161.4399 | -70.1428 | 89.8572 | 28.4832 | 28.4832 | 0 | 0 | 0 | 12/21/12:00
12 | 21 | 1900-01-12 | -5.6 | 194 | 40 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 194 | 0 | 0 | 39.791 | 355.5 | -23.4479 | 86.148 | -75 | 1.1478 | 176.435 | -38.3292 | 155.6708 | 49.3449 | 49.3449 | 0 | 0 | 0 | 12/21/13:00
12 | 21 | 1900-01-13 | -5.6 | 149 | 107 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 149 | 0 | 0 | 39.791 | 355.5417 | -23.4477 | 86.148 | -75 | 1.1283 | 191.4301 | -101.1805 | 47.8195 | 15.1579 | 15.1579 | 0 | 0 | 0 | 12/21/14:00
12 | 21 | 1900-01-14 | -5.6 | 166 | 28 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 166 | 0 | 0 | 39.791 | 355.5833 | -23.4474 | 86.148 | -75 | 1.1087 | 206.4252 | -24.8062 | 141.1938 | 44.756 | 44.756 | 0 | 0 | 0 | 12/21/15:00
12 | 21 | 1900-01-15 | -5.6 | 105 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 105 | 0 | 0 | 39.791 | 355.625 | -23.4472 | 86.148 | -75 | 1.0891 | 221.4203 | 0 | 105 | 33.2832 | 33.2832 | 0 | 0 | 0 | 12/21/16:00
12 | 21 | 1900-01-16 | -5.6 | 52 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 52 | 0 | 0 | 39.791 | 355.6667 | -23.4469 | 86.148 | -75 | 1.0696 | 236.4154 | 0 | 52 | 16.4831 | 16.4831 | 0 | 0 | 0 | 12/21/17:00
12 | 21 | 1900-01-17 | -5.6 | 8 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 8 | 0 | 0 | 39.791 | 355.7083 | -23.4466 | 86.148 | -75 | 1.05 | 251.4105 | 0 | 8 | 2.5359 | 2.5359 | 0 | 0 | 0 | 12/21/18:00
12 | 21 | 1900-01-18 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.75 | -23.4463 | 86.148 | -75 | 1.0304 | 266.4056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/19:00
12 | 21 | 1900-01-19 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.7917 | -23.446 | 86.148 | -75 | 1.0109 | 281.4007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/20:00
12 | 21 | 1900-01-20 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.8333 | -23.4457 | 86.148 | -75 | 0.99128 | 296.3958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/21:00
12 | 21 | 1900-01-21 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.875 | -23.4453 | 86.148 | -75 | 0.97171 | 311.3909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/22:00
12 | 21 | 1900-01-22 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.9167 | -23.445 | 86.148 | -75 | 0.95214 | 326.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/23:00
12 | 21 | 1900-01-23 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 355.9583 | -23.4446 | 86.148 | -75 | 0.93258 | 341.3811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/21/24:00
12 | 22 | 1899-12-31 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356 | -23.4442 | 86.148 | -75 | 0.91301 | -3.6237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/1:00
12 | 22 | 1900-01-01 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.0417 | -23.4439 | 86.148 | -75 | 0.89344 | 11.3714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/2:00
12 | 22 | 1900-01-02 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.0833 | -23.4435 | 86.148 | -75 | 0.87387 | 26.3665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/3:00
12 | 22 | 1900-01-03 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.125 | -23.443 | 86.148 | -75 | 0.8543 | 41.3616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/4:00
12 | 22 | 1900-01-04 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.1667 | -23.4426 | 86.148 | -75 | 0.83474 | 56.3567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/5:00
12 | 22 | 1900-01-05 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.2083 | -23.4422 | 86.148 | -75 | 0.81517 | 71.3518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/6:00
12 | 22 | 1900-01-06 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.25 | -23.4417 | 86.148 | -75 | 0.7956 | 86.3469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/7:00
12 | 22 | 1900-01-07 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.2917 | -23.4412 | 86.148 | -75 | 0.77603 | 101.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/8:00
12 | 22 | 1900-01-08 | -4.4 | 23 | 53 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 23 | 0 | 0 | 39.791 | 356.3333 | -23.4408 | 86.148 | -75 | 0.75647 | 116.3371 | -30.0695 | -7.0695 | -2.2409 | -2.2409 | 0 | 0 | 0 | 12/22/9:00
12 | 22 | 1900-01-09 | -5 | 67 | 389 | 23 | 1 | 0 | 23 | 0 | 0 | 67 | 0 | 0 | 39.791 | 356.375 | -23.4403 | 86.148 | -75 | 0.7369 | 131.3322 | -280.144 | -213.144 | -67.5629 | -67.5629 | 0 | 0 | 0 | 12/22/10:00
12 | 22 | 1900-01-10 | -5 | 93 | 569 | 23 | 1 | 0 | 23 | 0 | 0 | 93 | 0 | 0 | 39.791 | 356.4167 | -23.4398 | 86.148 | -75 | 0.71734 | 146.3273 | -478.6839 | -385.6839 | -122.2551 | -122.2551 | 0 | 0 | 0 | 12/22/11:00
12 | 22 | 1900-01-11 | -3.3 | 111 | 654 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 111 | 0 | 0 | 39.791 | 356.4583 | -23.4393 | 86.148 | -75 | 0.69777 | 161.3224 | -603.2655 | -492.2655 | -156.0396 | -156.0396 | 0 | 0 | 0 | 12/22/12:00
12 | 22 | 1900-01-12 | -2.2 | 118 | 683 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 118 | 0 | 0 | 39.791 | 356.5 | -23.4387 | 86.148 | -75 | 0.67821 | 176.3176 | -654.3777 | -536.3777 | -170.0224 | -170.0224 | 0 | 0 | 0 | 12/22/13:00
12 | 22 | 1900-01-13 | -1.1 | 165 | 510 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 165 | 0 | 0 | 39.791 | 356.5417 | -23.4382 | 86.148 | -75 | 0.65864 | 191.3127 | -482.3831 | -317.3831 | -100.6049 | -100.6049 | 0 | 0 | 0 | 12/22/14:00
12 | 22 | 1900-01-14 | 0.6 | 126 | 516 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 126 | 0 | 0 | 39.791 | 356.5833 | -23.4376 | 86.148 | -75 | 0.63908 | 206.3078 | -457.447 | -331.447 | -105.0629 | -105.0629 | 0 | 0 | 0 | 12/22/15:00
12 | 22 | 1900-01-15 | 0 | 128 | 52 | 32 | 1 | 0 | 32 | 0 | 0 | 128 | 0 | 0 | 39.791 | 356.625 | -23.4371 | 86.148 | -75 | 0.61952 | 221.3029 | -40.7764 | 87.2236 | 27.6484 | 27.6484 | 0 | 0 | 0 | 12/22/16:00
12 | 22 | 1900-01-16 | 0 | 51 | 19 | 32 | 1 | 0 | 32 | 0 | 0 | 51 | 0 | 0 | 39.791 | 356.6667 | -23.4365 | 86.148 | -75 | 0.59996 | 236.298 | -12.2688 | 38.7312 | 12.2771 | 12.2771 | 0 | 0 | 0 | 12/22/17:00
12 | 22 | 1900-01-17 | 0 | 6 | 1 | 32 | 1 | 0 | 32 | 0 | 0 | 6 | 0 | 0 | 39.791 | 356.7083 | -23.4359 | 86.148 | -75 | 0.5804 | 251.2931 | -0.48065 | 5.5194 | 1.7495 | 1.7495 | 0 | 0 | 0 | 12/22/18:00
12 | 22 | 1900-01-18 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.75 | -23.4353 | 86.148 | -75 | 0.56084 | 266.2882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/19:00
12 | 22 | 1900-01-19 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.7917 | -23.4347 | 86.148 | -75 | 0.54128 | 281.2833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/20:00
12 | 22 | 1900-01-20 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.8333 | -23.434 | 86.148 | -75 | 0.52172 | 296.2784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/21:00
12 | 22 | 1900-01-21 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.875 | -23.4334 | 86.148 | -75 | 0.50216 | 311.2735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/22:00
12 | 22 | 1900-01-22 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.9167 | -23.4327 | 86.148 | -75 | 0.4826 | 326.2687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/23:00
12 | 22 | 1900-01-23 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 356.9583 | -23.432 | 86.148 | -75 | 0.46305 | 341.2638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/22/24:00
12 | 23 | 1899-12-31 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357 | -23.4314 | 86.148 | -75 | 0.44349 | -3.7411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/1:00
12 | 23 | 1900-01-01 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.0417 | -23.4307 | 86.148 | -75 | 0.42394 | 11.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/2:00
12 | 23 | 1900-01-02 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.0833 | -23.43 | 86.148 | -75 | 0.40438 | 26.2491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/3:00
12 | 23 | 1900-01-03 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.125 | -23.4292 | 86.148 | -75 | 0.38483 | 41.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/4:00
12 | 23 | 1900-01-04 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.1667 | -23.4285 | 86.148 | -75 | 0.36528 | 56.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/5:00
12 | 23 | 1900-01-05 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.2083 | -23.4278 | 86.148 | -75 | 0.34573 | 71.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/6:00
12 | 23 | 1900-01-06 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.25 | -23.427 | 86.148 | -75 | 0.32618 | 86.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/7:00
12 | 23 | 1900-01-07 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.2917 | -23.4262 | 86.148 | -75 | 0.30663 | 101.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/8:00
12 | 23 | 1900-01-08 | 3.9 | 29 | 77 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 29 | 0 | 0 | 39.791 | 357.3333 | -23.4254 | 86.148 | -75 | 0.28709 | 116.2198 | -43.5769 | -14.5769 | -4.6206 | -4.6206 | 0 | 0 | 0 | 12/23/9:00
12 | 23 | 1900-01-09 | 4.4 | 86 | 193 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 86 | 0 | 0 | 39.791 | 357.375 | -23.4246 | 86.148 | -75 | 0.26754 | 131.2149 | -138.762 | -52.762 | -16.7246 | -16.7246 | 0 | 0 | 0 | 12/23/10:00
12 | 23 | 1900-01-10 | 5 | 155 | 202 | 41 | 1 | 0 | 41 | 0 | 0 | 155 | 0 | 0 | 39.791 | 357.4167 | -23.4238 | 86.148 | -75 | 0.248 | 146.21 | -169.7563 | -14.7563 | -4.6775 | -4.6775 | 0 | 0 | 0 | 12/23/11:00
12 | 23 | 1900-01-11 | 5.6 | 128 | 518 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 128 | 0 | 0 | 39.791 | 357.4583 | -23.423 | 86.148 | -75 | 0.22845 | 161.2051 | -477.5318 | -349.5318 | -110.7955 | -110.7955 | 0 | 0 | 0 | 12/23/12:00
12 | 23 | 1900-01-12 | 7.2 | 89 | 757 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 89 | 0 | 0 | 39.791 | 357.5 | -23.4222 | 86.148 | -75 | 0.20891 | 176.2002 | -725.1435 | -636.1435 | -201.6464 | -201.6464 | 0 | 0 | 0 | 12/23/13:00
12 | 23 | 1900-01-13 | 7.2 | 88 | 747 | 44.96 | 1 | 0 | 44.96 | 0 | 0 | 88 | 0 | 0 | 39.791 | 357.5417 | -23.4213 | 86.148 | -75 | 0.18937 | 191.1953 | -706.6966 | -618.6966 | -196.116 | -196.116 | 0 | 0 | 0 | 12/23/14:00
12 | 23 | 1900-01-14 | 7.8 | 79 | 694 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 79 | 0 | 0 | 39.791 | 357.5833 | -23.4204 | 86.148 | -75 | 0.16983 | 206.1905 | -615.6265 | -536.6265 | -170.1012 | -170.1012 | 0 | 0 | 0 | 12/23/15:00
12 | 23 | 1900-01-15 | 7.8 | 63 | 574 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 63 | 0 | 0 | 39.791 | 357.625 | -23.4196 | 86.148 | -75 | 0.15029 | 221.1856 | -450.5919 | -387.5919 | -122.8599 | -122.8599 | 0 | 0 | 0 | 12/23/16:00
12 | 23 | 1900-01-16 | 6.7 | 40 | 313 | 44.06 | 1 | 0 | 44.06 | 0 | 0 | 40 | 0 | 0 | 39.791 | 357.6667 | -23.4187 | 86.148 | -75 | 0.13076 | 236.1807 | -202.4474 | -162.4474 | -51.493 | -51.493 | 0 | 0 | 0 | 12/23/17:00
12 | 23 | 1900-01-17 | 4.4 | 8 | 16 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 8 | 0 | 0 | 39.791 | 357.7083 | -23.4178 | 86.148 | -75 | 0.11122 | 251.1758 | -7.7098 | 0.29021 | 0.091992 | 0.091992 | 0 | 0 | 0 | 12/23/18:00
12 | 23 | 1900-01-18 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.75 | -23.4169 | 86.148 | -75 | 0.09169 | 266.1709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/19:00
12 | 23 | 1900-01-19 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.7917 | -23.4159 | 86.148 | -75 | 0.072159 | 281.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/20:00
12 | 23 | 1900-01-20 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.8333 | -23.415 | 86.148 | -75 | 0.052628 | 296.1612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/21:00
12 | 23 | 1900-01-21 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.875 | -23.4141 | 86.148 | -75 | 0.0331 | 311.1563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/22:00
12 | 23 | 1900-01-22 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.9167 | -23.4131 | 86.148 | -75 | 0.013573 | 326.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/23:00
12 | 23 | 1900-01-23 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 357.9583 | -23.4121 | 86.148 | -75 | -0.0059525 | 341.1465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/23/24:00
12 | 24 | 1899-12-31 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358 | -23.4111 | 86.148 | -75 | -0.025476 | -3.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/1:00
12 | 24 | 1900-01-01 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.0417 | -23.4101 | 86.148 | -75 | -0.044998 | 11.1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/2:00
12 | 24 | 1900-01-02 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.0833 | -23.4091 | 86.148 | -75 | -0.064518 | 26.1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/3:00
12 | 24 | 1900-01-03 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.125 | -23.4081 | 86.148 | -75 | -0.084037 | 41.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/4:00
12 | 24 | 1900-01-04 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.1667 | -23.407 | 86.148 | -75 | -0.10355 | 56.1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/5:00
12 | 24 | 1900-01-05 | -0.6 | 0 | 0 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.2083 | -23.406 | 86.148 | -75 | -0.12307 | 71.1172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/6:00
12 | 24 | 1900-01-06 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.25 | -23.4049 | 86.148 | -75 | -0.14258 | 86.1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/7:00
12 | 24 | 1900-01-07 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.2917 | -23.4038 | 86.148 | -75 | -0.16209 | 101.1075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/8:00
12 | 24 | 1900-01-08 | 1.7 | 12 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 12 | 0 | 0 | 39.791 | 358.3333 | -23.4027 | 86.148 | -75 | -0.1816 | 116.1026 | 0 | 12 | 3.8038 | 3.8038 | 0 | 0 | 0 | 12/24/9:00
12 | 24 | 1900-01-09 | 2.8 | 76 | 5 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 76 | 0 | 0 | 39.791 | 358.375 | -23.4016 | 86.148 | -75 | -0.20111 | 131.0977 | -3.5887 | 72.4113 | 22.9531 | 22.9531 | 0 | 0 | 0 | 12/24/10:00
12 | 24 | 1900-01-10 | 3.9 | 129 | 13 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 129 | 0 | 0 | 39.791 | 358.4167 | -23.4005 | 86.148 | -75 | -0.22061 | 146.0928 | -10.9127 | 118.0873 | 37.4316 | 37.4316 | 0 | 0 | 0 | 12/24/11:00
12 | 24 | 1900-01-11 | 5 | 181 | 3 | 41 | 1 | 0 | 41 | 0 | 0 | 181 | 0 | 0 | 39.791 | 358.4583 | -23.3994 | 86.148 | -75 | -0.24012 | 161.088 | -2.7639 | 178.2361 | 56.4977 | 56.4977 | 0 | 0 | 0 | 12/24/12:00
12 | 24 | 1900-01-12 | 6.1 | 254 | 12 | 42.98 | 1 | 0 | 42.98 | 0 | 0 | 254 | 0 | 0 | 39.791 | 358.5 | -23.3982 | 86.148 | -75 | -0.25962 | 176.0831 | -11.4924 | 242.5076 | 76.8707 | 76.8707 | 0 | 0 | 0 | 12/24/13:00
12 | 24 | 1900-01-13 | 7.8 | 194 | 3 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 194 | 0 | 0 | 39.791 | 358.5417 | -23.3971 | 86.148 | -75 | -0.27912 | 191.0782 | -2.8386 | 191.1614 | 60.5948 | 60.5948 | 0 | 0 | 0 | 12/24/14:00
12 | 24 | 1900-01-14 | 7.8 | 169 | 0 | 46.04 | 1 | 0 | 46.04 | 0 | 0 | 169 | 0 | 0 | 39.791 | 358.5833 | -23.3959 | 86.148 | -75 | -0.29861 | 206.0733 | 0 | 169 | 53.57 | 53.57 | 0 | 0 | 0 | 12/24/15:00
12 | 24 | 1900-01-15 | 8.3 | 113 | 1 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 113 | 0 | 0 | 39.791 | 358.625 | -23.3947 | 86.148 | -75 | -0.31811 | 221.0685 | -0.7858 | 112.2142 | 35.5699 | 35.5699 | 0 | 0 | 0 | 12/24/16:00
12 | 24 | 1900-01-16 | 8.3 | 32 | 0 | 46.94 | 1 | 0 | 46.94 | 0 | 0 | 32 | 0 | 0 | 39.791 | 358.6667 | -23.3935 | 86.148 | -75 | -0.3376 | 236.0636 | 0 | 32 | 10.1434 | 10.1434 | 0 | 0 | 0 | 12/24/17:00
12 | 24 | 1900-01-17 | 11.1 | 8 | 0 | 51.98 | 1 | 0 | 51.98 | 0 | 0 | 8 | 0 | 0 | 39.791 | 358.7083 | -23.3923 | 86.148 | -75 | -0.35709 | 251.0587 | 0 | 8 | 2.5359 | 2.5359 | 0 | 0 | 0 | 12/24/18:00
12 | 24 | 1900-01-18 | 8.9 | 0 | 0 | 48.02 | 1 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.75 | -23.3911 | 86.148 | -75 | -0.37658 | 266.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/19:00
12 | 24 | 1900-01-19 | 5.6 | 0 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.7917 | -23.3899 | 86.148 | -75 | -0.39606 | 281.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/20:00
12 | 24 | 1900-01-20 | 4.4 | 0 | 0 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.8333 | -23.3886 | 86.148 | -75 | -0.41555 | 296.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/21:00
12 | 24 | 1900-01-21 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.875 | -23.3874 | 86.148 | -75 | -0.43503 | 311.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/22:00
12 | 24 | 1900-01-22 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.9167 | -23.3861 | 86.148 | -75 | -0.45451 | 326.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/23:00
12 | 24 | 1900-01-23 | -2.2 | 0 | 0 | 28.04 | 1 | 0 | 28.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 358.9583 | -23.3848 | 86.148 | -75 | -0.47398 | 341.0295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/24/24:00
12 | 25 | 1899-12-31 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359 | -23.3835 | 86.148 | -75 | -0.49346 | -3.9754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/1:00
12 | 25 | 1900-01-01 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.0417 | -23.3822 | 86.148 | -75 | -0.51293 | 11.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/2:00
12 | 25 | 1900-01-02 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.0833 | -23.3809 | 86.148 | -75 | -0.5324 | 26.0149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/3:00
12 | 25 | 1900-01-03 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.125 | -23.3796 | 86.148 | -75 | -0.55186 | 41.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/4:00
12 | 25 | 1900-01-04 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.1667 | -23.3782 | 86.148 | -75 | -0.57133 | 56.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/5:00
12 | 25 | 1900-01-05 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.2083 | -23.3769 | 86.148 | -75 | -0.59079 | 71.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/6:00
12 | 25 | 1900-01-06 | -7.2 | 0 | 0 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.25 | -23.3755 | 86.148 | -75 | -0.61025 | 85.9954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/7:00
12 | 25 | 1900-01-07 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.2917 | -23.3741 | 86.148 | -75 | -0.6297 | 100.9906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/8:00
12 | 25 | 1900-01-08 | -8.9 | 26 | 111 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 26 | 0 | 0 | 39.791 | 359.3333 | -23.3727 | 86.148 | -75 | -0.64916 | 115.9857 | -62.4852 | -36.4852 | -11.5652 | -11.5652 | 0 | 0 | 0 | 12/25/9:00
12 | 25 | 1900-01-09 | -8.9 | 82 | 268 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 82 | 0 | 0 | 39.791 | 359.375 | -23.3713 | 86.148 | -75 | -0.66861 | 130.9808 | -192.0068 | -110.0068 | -34.8702 | -34.8702 | 0 | 0 | 0 | 12/25/10:00
12 | 25 | 1900-01-10 | -8.3 | 122 | 162 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 122 | 0 | 0 | 39.791 | 359.4167 | -23.3699 | 86.148 | -75 | -0.68805 | 145.976 | -135.8299 | -13.8299 | -4.3838 | -4.3838 | 0 | 0 | 0 | 12/25/11:00
12 | 25 | 1900-01-11 | -8.3 | 149 | 162 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 149 | 0 | 0 | 39.791 | 359.4583 | -23.3684 | 86.148 | -75 | -0.7075 | 160.9711 | -149.1466 | -0.14661 | -0.046473 | -0.046473 | 0 | 0 | 0 | 12/25/12:00
12 | 25 | 1900-01-12 | -7.8 | 160 | 9 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 160 | 0 | 0 | 39.791 | 359.5 | -23.367 | 86.148 | -75 | -0.72694 | 175.9663 | -8.617 | 151.383 | 47.9858 | 47.9858 | 0 | 0 | 0 | 12/25/13:00
12 | 25 | 1900-01-13 | -7.8 | 182 | 68 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 182 | 0 | 0 | 39.791 | 359.5417 | -23.3655 | 86.148 | -75 | -0.74638 | 190.9614 | -64.3497 | 117.6503 | 37.2931 | 37.2931 | 0 | 0 | 0 | 12/25/14:00
12 | 25 | 1900-01-14 | -7.2 | 139 | 81 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 139 | 0 | 0 | 39.791 | 359.5833 | -23.3641 | 86.148 | -75 | -0.76582 | 205.9565 | -71.9302 | 67.0698 | 21.26 | 21.26 | 0 | 0 | 0 | 12/25/15:00
12 | 25 | 1900-01-15 | -7.2 | 86 | 58 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 86 | 0 | 0 | 39.791 | 359.625 | -23.3626 | 86.148 | -75 | -0.78525 | 220.9517 | -45.6193 | 40.3807 | 12.8 | 12.8 | 0 | 0 | 0 | 12/25/16:00
12 | 25 | 1900-01-16 | -8.3 | 63 | 121 | 17.06 | 1 | 0 | 17.06 | 0 | 0 | 63 | 0 | 0 | 39.791 | 359.6667 | -23.3611 | 86.148 | -75 | -0.80468 | 235.9468 | -78.5006 | -15.5006 | -4.9134 | -4.9134 | 0 | 0 | 0 | 12/25/17:00
12 | 25 | 1900-01-17 | -10 | 3 | 5 | 14 | 1 | 0 | 14 | 0 | 0 | 3 | 0 | 0 | 39.791 | 359.7083 | -23.3596 | 86.148 | -75 | -0.82411 | 250.942 | -2.4204 | 0.57956 | 0.18371 | 0.18371 | 0 | 0 | 0 | 12/25/18:00
12 | 25 | 1900-01-18 | -10.6 | 0 | 0 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.75 | -23.358 | 86.148 | -75 | -0.84353 | 265.9371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/19:00
12 | 25 | 1900-01-19 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.7917 | -23.3565 | 86.148 | -75 | -0.86295 | 280.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/20:00
12 | 25 | 1900-01-20 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.8333 | -23.3549 | 86.148 | -75 | -0.88237 | 295.9274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/21:00
12 | 25 | 1900-01-21 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.875 | -23.3534 | 86.148 | -75 | -0.90179 | 310.9226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/22:00
12 | 25 | 1900-01-22 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.9167 | -23.3518 | 86.148 | -75 | -0.9212 | 325.9177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/23:00
12 | 25 | 1900-01-23 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 359.9583 | -23.3502 | 86.148 | -75 | -0.94061 | 340.9128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/25/24:00
12 | 26 | 1899-12-31 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360 | -23.3486 | 86.148 | -75 | -0.96001 | -4.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/1:00
12 | 26 | 1900-01-01 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.0417 | -23.347 | 86.148 | -75 | -0.97941 | 10.9031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/2:00
12 | 26 | 1900-01-02 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.0833 | -23.3454 | 86.148 | -75 | -0.99881 | 25.8983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/3:00
12 | 26 | 1900-01-03 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.125 | -23.3437 | 86.148 | -75 | -1.0182 | 40.8934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/4:00
12 | 26 | 1900-01-04 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.1667 | -23.3421 | 86.148 | -75 | -1.0376 | 55.8886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/5:00
12 | 26 | 1900-01-05 | -15 | 0 | 0 | 5 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.2083 | -23.3404 | 86.148 | -75 | -1.057 | 70.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/6:00
12 | 26 | 1900-01-06 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.25 | -23.3387 | 86.148 | -75 | -1.0764 | 85.8789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/7:00
12 | 26 | 1900-01-07 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.2917 | -23.337 | 86.148 | -75 | -1.0958 | 100.8741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/8:00
12 | 26 | 1900-01-08 | -14.4 | 22 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 22 | 0 | 0 | 39.791 | 360.3333 | -23.3353 | 86.148 | -75 | -1.1151 | 115.8692 | 0 | 22 | 6.9736 | 6.9736 | 0 | 0 | 0 | 12/26/9:00
12 | 26 | 1900-01-09 | -13.3 | 45 | 567 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 45 | 0 | 0 | 39.791 | 360.375 | -23.3336 | 86.148 | -75 | -1.1345 | 130.8644 | -405.4643 | -360.4643 | -114.2609 | -114.2609 | 0 | 0 | 0 | 12/26/10:00
12 | 26 | 1900-01-10 | -11.7 | 72 | 624 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 72 | 0 | 0 | 39.791 | 360.4167 | -23.3319 | 86.148 | -75 | -1.1539 | 145.8595 | -522.5567 | -450.5567 | -142.8186 | -142.8186 | 0 | 0 | 0 | 12/26/11:00
12 | 26 | 1900-01-11 | -10 | 138 | 514 | 14 | 1 | 0 | 14 | 0 | 0 | 138 | 0 | 0 | 39.791 | 360.4583 | -23.3302 | 86.148 | -75 | -1.1733 | 160.8547 | -472.8744 | -334.8744 | -106.1493 | -106.1493 | 0 | 0 | 0 | 12/26/12:00
12 | 26 | 1900-01-12 | -8.9 | 169 | 203 | 15.98 | 1 | 0 | 15.98 | 0 | 0 | 169 | 0 | 0 | 39.791 | 360.5 | -23.3284 | 86.148 | -75 | -1.1926 | 175.8498 | -194.3024 | -25.3024 | -8.0204 | -8.0204 | 0 | 0 | 0 | 12/26/13:00
12 | 26 | 1900-01-13 | -7.8 | 161 | 390 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 161 | 0 | 0 | 39.791 | 360.5417 | -23.3266 | 86.148 | -75 | -1.212 | 190.845 | -369.0938 | -208.0938 | -65.9621 | -65.9621 | 0 | 0 | 0 | 12/26/14:00
12 | 26 | 1900-01-14 | -7.2 | 162 | 147 | 19.04 | 1 | 0 | 19.04 | 0 | 0 | 162 | 0 | 0 | 39.791 | 360.5833 | -23.3249 | 86.148 | -75 | -1.2313 | 205.8402 | -130.6004 | 31.3996 | 9.9531 | 9.9531 | 0 | 0 | 0 | 12/26/15:00
12 | 26 | 1900-01-15 | -6.7 | 99 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 99 | 0 | 0 | 39.791 | 360.625 | -23.3231 | 86.148 | -75 | -1.2507 | 220.8353 | 0 | 99 | 31.3813 | 31.3813 | 0 | 0 | 0 | 12/26/16:00
12 | 26 | 1900-01-16 | -6.1 | 36 | 6 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 36 | 0 | 0 | 39.791 | 360.6667 | -23.3213 | 86.148 | -75 | -1.27 | 235.8305 | -3.898 | 32.102 | 10.1758 | 10.1758 | 0 | 0 | 0 | 12/26/17:00
12 | 26 | 1900-01-17 | -6.1 | 6 | 1 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 6 | 0 | 0 | 39.791 | 360.7083 | -23.3194 | 86.148 | -75 | -1.2894 | 250.8257 | -0.4851 | 5.5149 | 1.7481 | 1.7481 | 0 | 0 | 0 | 12/26/18:00
12 | 26 | 1900-01-18 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.75 | -23.3176 | 86.148 | -75 | -1.3087 | 265.8208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/19:00
12 | 26 | 1900-01-19 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.7917 | -23.3158 | 86.148 | -75 | -1.3281 | 280.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/20:00
12 | 26 | 1900-01-20 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.8333 | -23.3139 | 86.148 | -75 | -1.3474 | 295.8111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/21:00
12 | 26 | 1900-01-21 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.875 | -23.3121 | 86.148 | -75 | -1.3667 | 310.8063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/22:00
12 | 26 | 1900-01-22 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.9167 | -23.3102 | 86.148 | -75 | -1.3861 | 325.8015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/23:00
12 | 26 | 1900-01-23 | -7.8 | 0 | 0 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 360.9583 | -23.3083 | 86.148 | -75 | -1.4054 | 340.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/26/24:00
12 | 27 | 1899-12-31 | -9.4 | 0 | 0 | 15.08 | 1 | 0 | 15.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361 | -23.3064 | 86.148 | -75 | -1.4247 | -4.2082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/1:00
12 | 27 | 1900-01-01 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.0417 | -23.3045 | 86.148 | -75 | -1.444 | 10.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/2:00
12 | 27 | 1900-01-02 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.0833 | -23.3025 | 86.148 | -75 | -1.4633 | 25.7822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/3:00
12 | 27 | 1900-01-03 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.125 | -23.3006 | 86.148 | -75 | -1.4826 | 40.7773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/4:00
12 | 27 | 1900-01-04 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.1667 | -23.2986 | 86.148 | -75 | -1.5019 | 55.7725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/5:00
12 | 27 | 1900-01-05 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.2083 | -23.2967 | 86.148 | -75 | -1.5212 | 70.7677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/6:00
12 | 27 | 1900-01-06 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.25 | -23.2947 | 86.148 | -75 | -1.5405 | 85.7629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/7:00
12 | 27 | 1900-01-07 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.2917 | -23.2927 | 86.148 | -75 | -1.5598 | 100.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/8:00
12 | 27 | 1900-01-08 | -13.3 | 31 | 84 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 31 | 0 | 0 | 39.791 | 361.3333 | -23.2907 | 86.148 | -75 | -1.5791 | 115.7532 | -47.015 | -16.015 | -5.0765 | -5.0765 | 0 | 0 | 0 | 12/27/9:00
12 | 27 | 1900-01-09 | -13.3 | 44 | 469 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 44 | 0 | 0 | 39.791 | 361.375 | -23.2887 | 86.148 | -75 | -1.5984 | 130.7484 | -334.7338 | -290.7338 | -92.1575 | -92.1575 | 0 | 0 | 0 | 12/27/10:00
12 | 27 | 1900-01-10 | -13.3 | 113 | 330 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 113 | 0 | 0 | 39.791 | 361.4167 | -23.2866 | 86.148 | -75 | -1.6177 | 145.7436 | -275.9995 | -162.9995 | -51.668 | -51.668 | 0 | 0 | 0 | 12/27/11:00
12 | 27 | 1900-01-11 | -12.2 | 55 | 847 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 55 | 0 | 0 | 39.791 | 361.4583 | -23.2846 | 86.148 | -75 | -1.6369 | 160.7388 | -778.6303 | -723.6303 | -229.3782 | -229.3782 | 0 | 0 | 0 | 12/27/12:00
12 | 27 | 1900-01-12 | -11.1 | 90 | 765 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 90 | 0 | 0 | 39.791 | 361.5 | -23.2825 | 86.148 | -75 | -1.6562 | 175.7339 | -731.9689 | -641.9689 | -203.4929 | -203.4929 | 0 | 0 | 0 | 12/27/13:00
12 | 27 | 1900-01-13 | -11.1 | 118 | 656 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 118 | 0 | 0 | 39.791 | 361.5417 | -23.2804 | 86.148 | -75 | -1.6755 | 190.7291 | -620.857 | -502.857 | -159.3969 | -159.3969 | 0 | 0 | 0 | 12/27/14:00
12 | 27 | 1900-01-14 | -10.6 | 45 | 904 | 12.92 | 1 | 0 | 12.92 | 0 | 0 | 45 | 0 | 0 | 39.791 | 361.5833 | -23.2784 | 86.148 | -75 | -1.6947 | 205.7243 | -803.4787 | -758.4787 | -240.4245 | -240.4245 | 0 | 0 | 0 | 12/27/15:00
12 | 27 | 1900-01-15 | -10 | 34 | 808 | 14 | 1 | 0 | 14 | 0 | 0 | 34 | 0 | 0 | 39.791 | 361.625 | -23.2763 | 86.148 | -75 | -1.714 | 220.7195 | -636.5991 | -602.5991 | -191.0134 | -191.0134 | 0 | 0 | 0 | 12/27/16:00
12 | 27 | 1900-01-16 | -10 | 22 | 618 | 14 | 1 | 0 | 14 | 0 | 0 | 22 | 0 | 0 | 39.791 | 361.6667 | -23.2742 | 86.148 | -75 | -1.7333 | 235.7147 | -402.0082 | -380.0082 | -120.456 | -120.456 | 0 | 0 | 0 | 12/27/17:00
12 | 27 | 1900-01-17 | -11.1 | 7 | 128 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 7 | 0 | 0 | 39.791 | 361.7083 | -23.272 | 86.148 | -75 | -1.7525 | 250.7099 | -62.2134 | -55.2134 | -17.5017 | -17.5017 | 0 | 0 | 0 | 12/27/18:00
12 | 27 | 1900-01-18 | -11.7 | 0 | 0 | 10.94 | 1 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.75 | -23.2699 | 86.148 | -75 | -1.7717 | 265.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/19:00
12 | 27 | 1900-01-19 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.7917 | -23.2678 | 86.148 | -75 | -1.791 | 280.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/20:00
12 | 27 | 1900-01-20 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.8333 | -23.2656 | 86.148 | -75 | -1.8102 | 295.6954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/21:00
12 | 27 | 1900-01-21 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.875 | -23.2634 | 86.148 | -75 | -1.8294 | 310.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/22:00
12 | 27 | 1900-01-22 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.9167 | -23.2612 | 86.148 | -75 | -1.8487 | 325.6858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/23:00
12 | 27 | 1900-01-23 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 361.9583 | -23.259 | 86.148 | -75 | -1.8679 | 340.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/27/24:00
12 | 28 | 1899-12-31 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362 | -23.2568 | 86.148 | -75 | -1.8871 | -4.3238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/1:00
12 | 28 | 1900-01-01 | -14.4 | 0 | 0 | 6.08 | 1 | 0 | 6.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.0417 | -23.2546 | 86.148 | -75 | -1.9063 | 10.6714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/2:00
12 | 28 | 1900-01-02 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.0833 | -23.2524 | 86.148 | -75 | -1.9255 | 25.6666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/3:00
12 | 28 | 1900-01-03 | -13.9 | 0 | 0 | 6.98 | 1 | 0 | 6.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.125 | -23.2501 | 86.148 | -75 | -1.9447 | 40.6618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/4:00
12 | 28 | 1900-01-04 | -13.3 | 0 | 0 | 8.06 | 1 | 0 | 8.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.1667 | -23.2479 | 86.148 | -75 | -1.9639 | 55.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/5:00
12 | 28 | 1900-01-05 | -12.8 | 0 | 0 | 8.96 | 1 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.2083 | -23.2456 | 86.148 | -75 | -1.9831 | 70.6522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/6:00
12 | 28 | 1900-01-06 | -12.2 | 0 | 0 | 10.04 | 1 | 0 | 10.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.25 | -23.2433 | 86.148 | -75 | -2.0023 | 85.6474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/7:00
12 | 28 | 1900-01-07 | -11.1 | 0 | 0 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.2917 | -23.241 | 86.148 | -75 | -2.0215 | 100.6426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/8:00
12 | 28 | 1900-01-08 | -11.1 | 27 | 52 | 12.02 | 1 | 0 | 12.02 | 0 | 0 | 27 | 0 | 0 | 39.791 | 362.3333 | -23.2387 | 86.148 | -75 | -2.0407 | 115.6378 | -29.0164 | -2.0164 | -0.63917 | -0.63917 | 0 | 0 | 0 | 12/28/9:00
12 | 28 | 1900-01-09 | -10 | 71 | 314 | 14 | 1 | 0 | 14 | 0 | 0 | 71 | 0 | 0 | 39.791 | 362.375 | -23.2364 | 86.148 | -75 | -2.0598 | 130.633 | -223.6573 | -152.6573 | -48.3897 | -48.3897 | 0 | 0 | 0 | 12/28/10:00
12 | 28 | 1900-01-10 | -7.8 | 172 | 106 | 17.96 | 1 | 0 | 17.96 | 0 | 0 | 172 | 0 | 0 | 39.791 | 362.4167 | -23.234 | 86.148 | -75 | -2.079 | 145.6283 | -88.5367 | 83.4633 | 26.4564 | 26.4564 | 0 | 0 | 0 | 12/28/11:00
12 | 28 | 1900-01-11 | -6.1 | 179 | 150 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 179 | 0 | 0 | 39.791 | 362.4583 | -23.2317 | 86.148 | -75 | -2.0982 | 160.6235 | -137.7798 | 41.2202 | 13.0661 | 13.0661 | 0 | 0 | 0 | 12/28/12:00
12 | 28 | 1900-01-12 | -5 | 174 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 174 | 0 | 0 | 39.791 | 362.5 | -23.2293 | 86.148 | -75 | -2.1173 | 175.6187 | 0 | 174 | 55.155 | 55.155 | 0 | 0 | 0 | 12/28/13:00
12 | 28 | 1900-01-13 | -3.3 | 76 | 755 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 76 | 0 | 0 | 39.791 | 362.5417 | -23.227 | 86.148 | -75 | -2.1365 | 190.6139 | -714.5477 | -638.5477 | -202.4085 | -202.4085 | 0 | 0 | 0 | 12/28/14:00
12 | 28 | 1900-01-14 | -1.7 | 67 | 775 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 67 | 0 | 0 | 39.791 | 362.5833 | -23.2246 | 86.148 | -75 | -2.1556 | 205.6091 | -689.0707 | -622.0707 | -197.1855 | -197.1855 | 0 | 0 | 0 | 12/28/15:00
12 | 28 | 1900-01-15 | -1.1 | 70 | 571 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 70 | 0 | 0 | 39.791 | 362.625 | -23.2222 | 86.148 | -75 | -2.1747 | 220.6043 | -450.209 | -380.209 | -120.5196 | -120.5196 | 0 | 0 | 0 | 12/28/16:00
12 | 28 | 1900-01-16 | -0.6 | 62 | 64 | 30.92 | 1 | 0 | 30.92 | 0 | 0 | 62 | 0 | 0 | 39.791 | 362.6667 | -23.2198 | 86.148 | -75 | -2.1939 | 235.5995 | -41.6816 | 20.3184 | 6.4406 | 6.4406 | 0 | 0 | 0 | 12/28/17:00
12 | 28 | 1900-01-17 | -3.3 | 7 | 22 | 26.06 | 1 | 0 | 26.06 | 0 | 0 | 7 | 0 | 0 | 39.791 | 362.7083 | -23.2173 | 86.148 | -75 | -2.213 | 250.5947 | -10.7121 | -3.7121 | -1.1767 | -1.1767 | 0 | 0 | 0 | 12/28/18:00
12 | 28 | 1900-01-18 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.75 | -23.2149 | 86.148 | -75 | -2.2321 | 265.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/19:00
12 | 28 | 1900-01-19 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.7917 | -23.2125 | 86.148 | -75 | -2.2513 | 280.5852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/20:00
12 | 28 | 1900-01-20 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.8333 | -23.21 | 86.148 | -75 | -2.2704 | 295.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/21:00
12 | 28 | 1900-01-21 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.875 | -23.2075 | 86.148 | -75 | -2.2895 | 310.5756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/22:00
12 | 28 | 1900-01-22 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.9167 | -23.205 | 86.148 | -75 | -2.3086 | 325.5709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/23:00
12 | 28 | 1900-01-23 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 362.9583 | -23.2025 | 86.148 | -75 | -2.3277 | 340.5661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/28/24:00
12 | 29 | 1899-12-31 | -6.7 | 0 | 0 | 19.94 | 1 | 0 | 19.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363 | -23.2 | 86.148 | -75 | -2.3468 | -4.4387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/1:00
12 | 29 | 1900-01-01 | -6.1 | 0 | 0 | 21.02 | 1 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.0417 | -23.1975 | 86.148 | -75 | -2.3659 | 10.5565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/2:00
12 | 29 | 1900-01-02 | -5.6 | 0 | 0 | 21.92 | 1 | 0 | 21.92 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.0833 | -23.195 | 86.148 | -75 | -2.3849 | 25.5518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/3:00
12 | 29 | 1900-01-03 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.125 | -23.1924 | 86.148 | -75 | -2.404 | 40.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/4:00
12 | 29 | 1900-01-04 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.1667 | -23.1898 | 86.148 | -75 | -2.4231 | 55.5422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/5:00
12 | 29 | 1900-01-05 | -5 | 0 | 0 | 23 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.2083 | -23.1873 | 86.148 | -75 | -2.4422 | 70.5375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/6:00
12 | 29 | 1900-01-06 | -4.4 | 0 | 0 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.25 | -23.1847 | 86.148 | -75 | -2.4612 | 85.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/7:00
12 | 29 | 1900-01-07 | -3.9 | 0 | 0 | 24.98 | 1 | 0 | 24.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.2917 | -23.1821 | 86.148 | -75 | -2.4803 | 100.5279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/8:00
12 | 29 | 1900-01-08 | -4.4 | 22 | 99 | 24.08 | 1 | 0 | 24.08 | 0 | 0 | 22 | 0 | 0 | 39.791 | 363.3333 | -23.1795 | 86.148 | -75 | -2.4993 | 115.5232 | -55.0698 | -33.0698 | -10.4825 | -10.4825 | 0 | 0 | 0 | 12/29/9:00
12 | 29 | 1900-01-09 | -2.8 | 64 | 461 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 64 | 0 | 0 | 39.791 | 363.375 | -23.1768 | 86.148 | -75 | -2.5184 | 130.5184 | -327.681 | -263.681 | -83.5823 | -83.5823 | 0 | 0 | 0 | 12/29/10:00
12 | 29 | 1900-01-10 | -1.1 | 61 | 713 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 61 | 0 | 0 | 39.791 | 363.4167 | -23.1742 | 86.148 | -75 | -2.5374 | 145.5137 | -594.7129 | -533.7129 | -169.1777 | -169.1777 | 0 | 0 | 0 | 12/29/11:00
12 | 29 | 1900-01-11 | 0.6 | 70 | 761 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 70 | 0 | 0 | 39.791 | 363.4583 | -23.1716 | 86.148 | -75 | -2.5564 | 160.5089 | -698.4033 | -628.4033 | -199.1929 | -199.1929 | 0 | 0 | 0 | 12/29/12:00
12 | 29 | 1900-01-12 | 1.7 | 244 | 257 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 244 | 0 | 0 | 39.791 | 363.5 | -23.1689 | 86.148 | -75 | -2.5755 | 175.5041 | -245.7019 | -1.7019 | -0.53948 | -0.53948 | 0 | 0 | 0 | 12/29/13:00
12 | 29 | 1900-01-13 | 2.8 | 166 | 435 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 166 | 0 | 0 | 39.791 | 363.5417 | -23.1662 | 86.148 | -75 | -2.5945 | 190.4994 | -411.6714 | -245.6714 | -77.8736 | -77.8736 | 0 | 0 | 0 | 12/29/14:00
12 | 29 | 1900-01-14 | 3.3 | 188 | 70 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 188 | 0 | 0 | 39.791 | 363.5833 | -23.1635 | 86.148 | -75 | -2.6135 | 205.4946 | -62.2577 | 125.7423 | 39.8581 | 39.8581 | 0 | 0 | 0 | 12/29/15:00
12 | 29 | 1900-01-15 | 4.4 | 101 | 264 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 101 | 0 | 0 | 39.791 | 363.625 | -23.1608 | 86.148 | -75 | -2.6325 | 220.4899 | -208.2935 | -107.2935 | -34.0102 | -34.0102 | 0 | 0 | 0 | 12/29/16:00
12 | 29 | 1900-01-16 | 3.3 | 58 | 36 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 58 | 0 | 0 | 39.791 | 363.6667 | -23.1581 | 86.148 | -75 | -2.6515 | 235.4851 | -23.4716 | 34.5284 | 10.9449 | 10.9449 | 0 | 0 | 0 | 12/29/17:00
12 | 29 | 1900-01-17 | 3.3 | 10 | 7 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 10 | 0 | 0 | 39.791 | 363.7083 | -23.1554 | 86.148 | -75 | -2.6705 | 250.4804 | -3.414 | 6.586 | 2.0876 | 2.0876 | 0 | 0 | 0 | 12/29/18:00
12 | 29 | 1900-01-18 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.75 | -23.1527 | 86.148 | -75 | -2.6895 | 265.4756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/19:00
12 | 29 | 1900-01-19 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.7917 | -23.1499 | 86.148 | -75 | -2.7085 | 280.4709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/20:00
12 | 29 | 1900-01-20 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.8333 | -23.1471 | 86.148 | -75 | -2.7274 | 295.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/21:00
12 | 29 | 1900-01-21 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.875 | -23.1444 | 86.148 | -75 | -2.7464 | 310.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/22:00
12 | 29 | 1900-01-22 | -1.1 | 0 | 0 | 30.02 | 1 | 0 | 30.02 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.9167 | -23.1416 | 86.148 | -75 | -2.7654 | 325.4567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/23:00
12 | 29 | 1900-01-23 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 363.9583 | -23.1388 | 86.148 | -75 | -2.7843 | 340.4519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/29/24:00
12 | 30 | 1899-12-31 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364 | -23.136 | 86.148 | -75 | -2.8033 | -4.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/1:00
12 | 30 | 1900-01-01 | -2.8 | 0 | 0 | 26.96 | 1 | 0 | 26.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.0417 | -23.1331 | 86.148 | -75 | -2.8222 | 10.4424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/2:00
12 | 30 | 1900-01-02 | -1.7 | 0 | 0 | 28.94 | 1 | 0 | 28.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.0833 | -23.1303 | 86.148 | -75 | -2.8412 | 25.4377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/3:00
12 | 30 | 1900-01-03 | 0 | 0 | 0 | 32 | 1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.125 | -23.1274 | 86.148 | -75 | -2.8601 | 40.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/4:00
12 | 30 | 1900-01-04 | 0.6 | 0 | 0 | 33.08 | 1 | 0 | 33.08 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.1667 | -23.1246 | 86.148 | -75 | -2.879 | 55.4282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/5:00
12 | 30 | 1900-01-05 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.2083 | -23.1217 | 86.148 | -75 | -2.898 | 70.4235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/6:00
12 | 30 | 1900-01-06 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.25 | -23.1188 | 86.148 | -75 | -2.9169 | 85.4188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/7:00
12 | 30 | 1900-01-07 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.2917 | -23.1159 | 86.148 | -75 | -2.9358 | 100.4141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/8:00
12 | 30 | 1900-01-08 | 1.7 | 22 | 2 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 22 | 0 | 0 | 39.791 | 364.3333 | -23.113 | 86.148 | -75 | -2.9547 | 115.4093 | -1.1089 | 20.8911 | 6.6221 | 6.6221 | 0 | 0 | 0 | 12/30/9:00
12 | 30 | 1900-01-09 | 2.2 | 60 | 9 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 60 | 0 | 0 | 39.791 | 364.375 | -23.1101 | 86.148 | -75 | -2.9736 | 130.4046 | -6.3835 | 53.6165 | 16.9955 | 16.9955 | 0 | 0 | 0 | 12/30/10:00
12 | 30 | 1900-01-10 | 2.8 | 131 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 131 | 0 | 0 | 39.791 | 364.4167 | -23.1071 | 86.148 | -75 | -2.9925 | 145.3999 | 0 | 131 | 41.5247 | 41.5247 | 0 | 0 | 0 | 12/30/11:00
12 | 30 | 1900-01-11 | 4.4 | 162 | 391 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 162 | 0 | 0 | 39.791 | 364.4583 | -23.1042 | 86.148 | -75 | -3.0114 | 160.3952 | -358.5147 | -196.5147 | -62.2917 | -62.2917 | 0 | 0 | 0 | 12/30/12:00
12 | 30 | 1900-01-12 | 5 | 189 | 65 | 41 | 1 | 0 | 41 | 0 | 0 | 189 | 0 | 0 | 39.791 | 364.5 | -23.1012 | 86.148 | -75 | -3.0302 | 175.3904 | -62.1132 | 126.8868 | 40.2209 | 40.2209 | 0 | 0 | 0 | 12/30/13:00
12 | 30 | 1900-01-13 | 5.6 | 136 | 29 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 136 | 0 | 0 | 39.791 | 364.5417 | -23.0982 | 86.148 | -75 | -3.0491 | 190.3857 | -27.4421 | 108.5579 | 34.411 | 34.411 | 0 | 0 | 0 | 12/30/14:00
12 | 30 | 1900-01-14 | 5.6 | 105 | 0 | 42.08 | 1 | 0 | 42.08 | 0 | 0 | 105 | 0 | 0 | 39.791 | 364.5833 | -23.0953 | 86.148 | -75 | -3.068 | 205.381 | 0 | 105 | 33.2832 | 33.2832 | 0 | 0 | 0 | 12/30/15:00
12 | 30 | 1900-01-15 | 5 | 117 | 2 | 41 | 1 | 0 | 41 | 0 | 0 | 117 | 0 | 0 | 39.791 | 364.625 | -23.0923 | 86.148 | -75 | -3.0868 | 220.3763 | -1.5789 | 115.4211 | 36.5865 | 36.5865 | 0 | 0 | 0 | 12/30/16:00
12 | 30 | 1900-01-16 | 4.4 | 62 | 59 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 62 | 0 | 0 | 39.791 | 364.6667 | -23.0892 | 86.148 | -75 | -3.1057 | 235.3716 | -38.5058 | 23.4942 | 7.4473 | 7.4473 | 0 | 0 | 0 | 12/30/17:00
12 | 30 | 1900-01-17 | 3.3 | 10 | 14 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 10 | 0 | 0 | 39.791 | 364.7083 | -23.0862 | 86.148 | -75 | -3.1245 | 250.3669 | -6.8383 | 3.1617 | 1.0022 | 1.0022 | 0 | 0 | 0 | 12/30/18:00
12 | 30 | 1900-01-18 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.75 | -23.0832 | 86.148 | -75 | -3.1434 | 265.3622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/19:00
12 | 30 | 1900-01-19 | 2.2 | 0 | 0 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.7917 | -23.0801 | 86.148 | -75 | -3.1622 | 280.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/20:00
12 | 30 | 1900-01-20 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.8333 | -23.0771 | 86.148 | -75 | -3.181 | 295.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/21:00
12 | 30 | 1900-01-21 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.875 | -23.074 | 86.148 | -75 | -3.1998 | 310.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/22:00
12 | 30 | 1900-01-22 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.9167 | -23.0709 | 86.148 | -75 | -3.2186 | 325.3433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/23:00
12 | 30 | 1900-01-23 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 364.9583 | -23.0678 | 86.148 | -75 | -3.2374 | 340.3386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/30/24:00
12 | 31 | 1899-12-31 | 1.1 | 0 | 0 | 33.98 | 1 | 0 | 33.98 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365 | -23.0647 | 86.148 | -75 | -3.2562 | -4.6661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/1:00
12 | 31 | 1900-01-01 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.0417 | -23.0616 | 86.148 | -75 | -3.275 | 10.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/2:00
12 | 31 | 1900-01-02 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.0833 | -23.0584 | 86.148 | -75 | -3.2938 | 25.3245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/3:00
12 | 31 | 1900-01-03 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.125 | -23.0553 | 86.148 | -75 | -3.3126 | 40.3199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/4:00
12 | 31 | 1900-01-04 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.1667 | -23.0521 | 86.148 | -75 | -3.3313 | 55.3152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/5:00
12 | 31 | 1900-01-05 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.2083 | -23.0489 | 86.148 | -75 | -3.3501 | 70.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/6:00
12 | 31 | 1900-01-06 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.25 | -23.0457 | 86.148 | -75 | -3.3689 | 85.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/7:00
12 | 31 | 1900-01-07 | 1.7 | 0 | 0 | 35.06 | 1 | 0 | 35.06 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.2917 | -23.0425 | 86.148 | -75 | -3.3876 | 100.3011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/8:00
12 | 31 | 1900-01-08 | 2.2 | 17 | 3 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 17 | 0 | 0 | 39.791 | 365.3333 | -23.0393 | 86.148 | -75 | -3.4063 | 115.2964 | -1.6578 | 15.3422 | 4.8632 | 4.8632 | 0 | 0 | 0 | 12/31/9:00
12 | 31 | 1900-01-09 | 2.2 | 102 | 6 | 35.96 | 1 | 0 | 35.96 | 0 | 0 | 102 | 0 | 0 | 39.791 | 365.375 | -23.0361 | 86.148 | -75 | -3.4251 | 130.2917 | -4.2463 | 97.7537 | 30.9862 | 30.9862 | 0 | 0 | 0 | 12/31/10:00
12 | 31 | 1900-01-10 | 2.8 | 136 | 7 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 136 | 0 | 0 | 39.791 | 365.4167 | -23.0329 | 86.148 | -75 | -3.4438 | 145.287 | -5.8217 | 130.1783 | 41.2642 | 41.2642 | 0 | 0 | 0 | 12/31/11:00
12 | 31 | 1900-01-11 | 2.8 | 173 | 9 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 173 | 0 | 0 | 39.791 | 365.4583 | -23.0296 | 86.148 | -75 | -3.4625 | 160.2824 | -8.2445 | 164.7555 | 52.2246 | 52.2246 | 0 | 0 | 0 | 12/31/12:00
12 | 31 | 1900-01-12 | 3.3 | 195 | 8 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 195 | 0 | 0 | 39.791 | 365.5 | -23.0263 | 86.148 | -75 | -3.4812 | 175.2777 | -7.6408 | 187.3592 | 59.3896 | 59.3896 | 0 | 0 | 0 | 12/31/13:00
12 | 31 | 1900-01-13 | 3.9 | 207 | 6 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 207 | 0 | 0 | 39.791 | 365.5417 | -23.0231 | 86.148 | -75 | -3.4999 | 190.273 | -5.6769 | 201.3231 | 63.8159 | 63.8159 | 0 | 0 | 0 | 12/31/14:00
12 | 31 | 1900-01-14 | 4.4 | 174 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 174 | 0 | 0 | 39.791 | 365.5833 | -23.0198 | 86.148 | -75 | -3.5186 | 205.2683 | -0.8898 | 173.1102 | 54.8729 | 54.8729 | 0 | 0 | 0 | 12/31/15:00
12 | 31 | 1900-01-15 | 4.4 | 126 | 1 | 39.92 | 1 | 0 | 39.92 | 0 | 0 | 126 | 0 | 0 | 39.791 | 365.625 | -23.0165 | 86.148 | -75 | -3.5373 | 220.2637 | -0.78989 | 125.2101 | 39.6894 | 39.6894 | 0 | 0 | 0 | 12/31/16:00
12 | 31 | 1900-01-16 | 3.9 | 70 | 1 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 70 | 0 | 0 | 39.791 | 365.6667 | -23.0132 | 86.148 | -75 | -3.556 | 235.259 | -0.65323 | 69.3468 | 21.9817 | 21.9817 | 0 | 0 | 0 | 12/31/17:00
12 | 31 | 1900-01-17 | 3.9 | 11 | 0 | 39.02 | 1 | 0 | 39.02 | 0 | 0 | 11 | 0 | 0 | 39.791 | 365.7083 | -23.0098 | 86.148 | -75 | -3.5747 | 250.2543 | 0 | 11 | 3.4868 | 3.4868 | 0 | 0 | 0 | 12/31/18:00
12 | 31 | 1900-01-18 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.75 | -23.0065 | 86.148 | -75 | -3.5933 | 265.2497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/19:00
12 | 31 | 1900-01-19 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.7917 | -23.0031 | 86.148 | -75 | -3.612 | 280.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/20:00
12 | 31 | 1900-01-20 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.8333 | -22.9998 | 86.148 | -75 | -3.6306 | 295.2403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/21:00
12 | 31 | 1900-01-21 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.875 | -22.9964 | 86.148 | -75 | -3.6493 | 310.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/22:00
12 | 31 | 1900-01-22 | 3.3 | 0 | 0 | 37.94 | 1 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.9167 | -22.993 | 86.148 | -75 | -3.6679 | 325.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/23:00
12 | 31 | 1900-01-23 | 2.8 | 0 | 0 | 37.04 | 1 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0 | 39.791 | 365.9583 | -22.9896 | 86.148 | -75 | -3.6866 | 340.2264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12/31/24:00

## Energy Savings Calculations (hidden)
Energy Savings Calculations
Constants
ho= | 3 | [Btuh/ ft2 °F]
hin = | 1.68 | [Btuh/ ft2 °F]
ΔR= | 20 | [Btuh/ ft2 ]
Roofing Properties
Existing Roof Properties
U= | 0.13166 | [Btuh/ ft2 °F]
ε= | 0.87
ρ= | 0.221
Post Roof Properties
U= | 0.032685 | [Btuh/ ft2 °F]
ε= | 0.85
ρ= | 0.69
Month | Avg. OAT (F) | Outside Temp Sums [F] |  | Respond Hrs Sum [hrs] |  | Incoming Radiation Sum [Btu/ft^2] |  | Peak Radiation and Current Temp |  |  | Operating Hours | Hours In Month | HVAC Operating Hrs Multiplier | tin (F) | Monthly Loads |  |  |  | Existing and New Load Differtial |  | Existing Roof | New Roof
|  | Heating | Cooling | Heating | Cooling | Heating | Cooling | Peak Cooling Incoming Radiation [Btuh/ft^2] | Temp During Peak Cooling Radiation [F] | Time of Peak Cooling Incoming Radiation |  |  |  |  | Existing Heat Load [Btu/ft2] | Existing Cooling Load [Btu/ft2] | New Heat Load [Btu/ft2] | New Cooling Load [Btu/ft2] | Heating Load Differential - Penalty [Btu/ft2] | Cooling Load Differential - Savings [Btu/ft2] | Peak Cooling Load from Peak Radiation [Btuh/ft2] | Peak Cooling Load from Peak Radiation [Btuh/ft2]
1 | 23.9953 | 17852.52 | 0 | 744 | 0 | -6842.863 | 0 | 0 | 0 | 1/1/1:00 | 151.814 | 744 | 0.20405 | 70 | -1083.2108 | 0 | -261.1097 | 0 | 822.101 | 0 | 0 | 0
2 | 26.6177 | 16000.7 | 1886.38 | 640 | 32 | -4766.9728 | 1886.38 | 99.3971 | 55.94 | 2/24/12:00 | 151.814 | 672 | 0.22591 | 70 | -1003.8378 | -1.4691 | -243.0689 | -2.5107 | 760.7689 | 1.0417 | 0.7834 | -0.30906
3 | 43.497 | 21448.38 | 10913.4 | 573 | 171 | 2728.5886 | 10913.4 | 103.8317 | 59 | 3/13/15:00 | 151.814 | 744 | 0.20405 | 70 | -571.6069 | 21.1015 | -144.2363 | -5.9883 | 427.3706 | 27.0898 | 1.3379 | -0.19406
4 | 52.6437 | 19021.86 | 18881.64 | 423 | 297 | 5935.8464 | 18881.64 | 135.471 | 64.94 | 4/22/15:00 | 151.814 | 720 | 0.21085 | 70 | -319.259 | 35.3114 | -85.2623 | -11.3041 | 233.9967 | 46.6156 | 3.2017 | 0.10694
5 | 64.4856 | 5736.02 | 42241.3 | 118 | 626 | 1459.5496 | 42241.3 | 151.1275 | 80.06 | 5/30/14:00 | 151.814 | 744 | 0.20405 | 70 | -76.0132 | 154.7235 | -20.2871 | -5.0761 | 55.7262 | 159.7996 | 5.7276 | 0.65402
6 | 72.6995 | 927.18 | 51416.46 | 18 | 702 | 165.9977 | 51416.46 | 154.6562 | 84.02 | 6/29/14:00 | 75.907 | 720 | 0.10543 | 70 | -5.4706 | 160.4041 | -1.4392 | 12.4446 | 4.0313 | 147.9594 | 6.3697 | 0.79537
7 | 76.281 | 160.98 | 56592.06 | 3 | 741 | 5.3286 | 56592.06 | 181.8067 | 84.02 | 7/20/13:00 | 75.907 | 744 | 0.10203 | 70 | -0.87362 | 203.0953 | -0.21832 | 21.245 | 0.6553 | 181.8504 | 7.2979 | 0.88707
8 | 73.6313 | 578.26 | 54203.42 | 11 | 733 | 12.13 | 54203.42 | 156.5162 | 84.02 | 8/8/14:00 | 113.8605 | 744 | 0.15304 | 70 | -5.0855 | 256.2347 | -1.2646 | 21.7127 | 3.8209 | 234.522 | 6.4332 | 0.80165
9 | 64.793 | 5914.36 | 40736.6 | 119 | 601 | 714.9429 | 40736.6 | 97.1052 | 73.04 | 9/18/14:00 | 151.814 | 720 | 0.21085 | 70 | -81.068 | 159.8693 | -20.786 | -3.65 | 60.282 | 163.5193 | 2.9565 | 0.24211
10 | 52.8169 | 18662.04 | 20633.7 | 414 | 330 | -4095.1883 | 20633.7 | 113.4531 | 60.98 | 10/10/13:00 | 151.814 | 744 | 0.20405 | 70 | -370.277 | 26.2634 | -87.2829 | -14.7003 | 282.9941 | 40.9637 | 1.9275 | -0.096851
11 | 41.1628 | 23611.68 | 6025.5 | 621 | 99 | -6349.8655 | 6025.5 | 68.1512 | 57.92 | 11/27/13:00 | 151.814 | 720 | 0.21085 | 70 | -697.0544 | 2.3853 | -165.6311 | -5.8088 | 531.4233 | 8.194 | -0.024146 | -0.34987
12 | 28.43 | 20644.86 | 507.06 | 735 | 9 | -6002.0272 | 507.06 | 70.1323 | 57.02 | 12/17/13:00 | 151.814 | 744 | 0.20405 | 70 | -983.9992 | -1.1679 | -237.3653 | -0.81062 | 746.634 | -0.35732 | -0.074913 | -0.3726
Yearly Heating Penalty [Btu/ft2] | Yearly Cooling Savings [Btu/ft2] | Existing Peak Load [Btuh/ft2] | New Peak Load [Btuh/ft2]
3929.8042 | 1011.1982 | 7.2979 | 0.88707
0.96 | kW/ton
SEER conversion from PA TRM - reference to US DOE Building American
Heating Savings
Electric Resistance | 57585.6243 | kWh
Gas | 1964.9021 | Therms
Heat Pump | 16453.0355 | kWh | <----Heat Pump Eff is assumed to be equal to the Cooling Eff

## Operating Hours LookUp (hidden)
Operating Hours Look Up
Month | College | Elementary/Secondary Schools | Grocery/Supermarket | Health | Hospital | Lodging - Common Area | Lodging - Guest Rooms | Manufacturing | Office | Restaurant | Retail | Warehouse | Operating Hours Known |  | School multipliers below considered for Education - School based on summer break. |  | College/University multipliers below considered for Education - College/University based on summer break.
1 | 213.4545 | 151.814 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 1 | 0.093023 | 1 | 0.090909
2 | 213.4545 | 151.814 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 1 | 0.093023 | 1 | 0.090909
3 | 213.4545 | 151.814 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 1 | 0.093023 | 1 | 0.090909
4 | 213.4545 | 151.814 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 1 | 0.093023 | 1 | 0.090909
5 | 170.7636 | 151.814 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 1 | 0.093023 | 0.8 | 0.072727
6 | 149.4182 | 75.907 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 0.5 | 0.046512 | 0.7 | 0.063636
7 | 149.4182 | 75.907 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 0.5 | 0.046512 | 0.7 | 0.063636
8 | 170.7636 | 113.8605 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 0.75 | 0.069767 | 0.8 | 0.072727
9 | 213.4545 | 151.814 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 1 | 0.093023 | 1 | 0.090909
10 | 213.4545 | 151.814 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 1 | 0.093023 | 1 | 0.090909
11 | 213.4545 | 151.814 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 1 | 0.093023 | 1 | 0.090909
12 | 213.4545 | 151.814 | 395.7808 | 272.8849 | 440.1151 | 669.6 | 77.6274 | 253.0959 | 218.0192 | 306.8575 | 240.2712 | 196.7014 | 0 | 1 | 0.093023 | 1 | 0.090909
Annual Operating Hours | 2348 | 1632 | 4660 | 3213 | 5182 | 7884 | 914 | 2980 | 2567 | 3613 | 2829 | 2316 | 0 |  | Source: Recommended Values for Annual Hours of Use for Linear Lighting. Itron, Inc. “Development of Interior Lighting Hours of Use and Coincidence Factor Values for Evaluation of EmPOWER Maryland Commercial Lighting Programs.” International Energy Program

## Roofing Properties LookUp (hidden)
Roofing Properties Look Up
Typical Roofing Types | New Values |  | Aged Values
| Reflectance | Emittance | Reflectance
Black EPDM | 0.06 | 0.86 | 0.102 | 0.87 Emittance, 0.54 Reflectivity
Dark Gravel on BUR | 0.12 | 0.9 | 0.144 | 0.87 Emittance, 0.22 Reflectivity
Gray EPDM | 0.23 | 0.87 | 0.221 | 0.86 Emittance, 0.10 Reflectivity
Light Gravel on BUR | 0.34 | 0.9 | 0.298 | 0.92 Emittance, 0.24 Reflectivity
Smooth Bitumen | 0.06 | 0.96 | 0.102 | 0.96 Emittance, 0.10 Reflectivity
White EPDM | 0.69 | 0.87 | 0.543 | 0.90 Emittance, 0.52 Reflectivity
White Granular Bitumen | 0.26 | 0.92 | 0.242 | 0.90 Emittance, 0.30 Reflectivity
White-Coated Gravel on BUR | 0.65 | 0.9 | 0.515 | 0.90 Emittance, 0.14 Reflectivity
Roofing Properties Known |  | 0 | 0
Source: | Lawrence Berkley National Laboratory http://energy.lbl.gov/coolroof/membrane.htm#membrane |  | Determined based on LBNL methodology: Aged=0.06+0.7New

## LSTM LookUp (hidden)
Local Standard Time Meridian Look Up
Time Zone | GTM Offset [hours] | LSTM [°]
Eastern (ET) | -5 | -75
Central (CT) | -6 | -90
Mountain (MT) | -7 | -105
Pacific (PT) | -8 | -120
General Location Inputs
Latitude [°]* |  | 39.791 | <---Latitude for Indianapolis
Longitude [°]* |  | 86.148 | <---Longitude for Indianapolis
Time Zone |  | Eastern (ET)

## Version Log (hidden)
Version Log
Instructions: Document all changes.
Version | Date | Changes | Contact, Department | QC Engineer
1 | 2014-06-04 | Original calculator developed based on Tom Davidson's Nevada roofing calculator. | Mary Clayton, Core Engineering
2 | 2014-04-21 | Adaptation to IPL Electric Program | Jeremy Selwyn, Engineering
3 | 2017-01-13 | Updated Incentive Caps for IPL 2017 Program Year | Ben Reinhart, Engineering | Will Nichols
4 | 2018-01-08 | Updated incentive to $0.08 per kWh saved for 2018 Program Year (from $0.07) | Ben Reinhart, Engineering | Will Nichols
5 | 2019-01-14 | Updated so that the project cost calculates correctly; formula was accidently deleted and then locked. Also, made it easy for engineering to adjust zone temperature and switchover temperature as needed. This is still hidden from the client though. | Ben Reinhart, Engineering | Will Nichols
6 | 2022-08-15 | Updated for 2022 Project Cost cap of $,1000,000 per project and per building per year. | Ben Reinhart, Engineering | Will Nichols
7 | 2026-06-17 | Added example calc. | Josh Porter, Engineering
8 | 2026-07-29 | Updated first page calculator description text. Was copied over form another calculator and never updated. | Josh Porter, Engineering
9
10
11
12
13
14
15
16

## Dropdowns (hidden)
EER | kW/Ton | Boiler/Furnace EFF | COP | Electric Res
Default | Default | Default | Default | 100%
7 | 0.45 | 65% | 1.5
7.5 | 0.5 | 66% | 1.6
8 | 0.55 | 67% | 1.7
8.5 | 0.6 | 68% | 1.8
9 | 0.65 | 69% | 1.9
9.5 | 0.7 | 70% | 2
10 | 0.75 | 71% | 2.1
10.5 | 0.8 | 72% | 2.2
11 | 0.85 | 73% | 2.3
11.5 | 0.9 | 74% | 2.4
12 | 0.95 | 75% | 2.5
12.5 | 1 | 76% | 2.6
13 | 1.05 | 77% | 2.7
13.5 | 1.1 | 78% | 2.8
14 | 1.15 | 79% | 2.9
14.5 | 1.2 | 80% | 3
15 | 1.25 | 81% | 3.1
15.5 | 1.3 | 82% | 3.2
16 | 1.35 | 83% | 3.3
16.5 | 1.4 | 84% | 3.4
17 |  | 85% | 3.5
|  | 86% | 3.6
|  | 87% | 3.7
|  | 88% | 3.8
|  | 89% | 3.9
|  | 90% | 4
|  | 91% | 4.1
|  | 92% | 4.2
4.3
4.4
4.5
4.6
4.7
4.8
4.9
5
5.1
5.2
5.3
5.4
5.5
5.6
5.7
5.8
5.9
6